## Sheet1
cable imbalance calculation: summary
8/12/14 dmd
inputs:
cable imbalance: | 5% | from Wayne
cable R/meter: | 0.0938 | from Yair: resistance of single strand = resistance of 1 pair round trip
cordage R/meter | 0.14 | from Wayne: same as above
90/10 cable/cord split | 0.09842 | calculated
connector min R: | 0.03 | from Yair: resistance of single conductor = resistance of one pair round trip
connector max R: | 0.05 | from Yair: same as above
number of connectors: | 4 | from Wayne
index | cable length | cable R min | cable R max | conn min | conn max | total R min | total R max | CP2PRUNB
-1 | 0.1 | 0.0093499 | 0.010334 | 0.12 | 0.2 | 0.12935 | 0.21033 | 23.84%
-0.8 | 0.15849 | 0.014819 | 0.016378 | 0.12 | 0.2 | 0.13482 | 0.21638 | 23.22%
-0.6 | 0.25119 | 0.023486 | 0.025958 | 0.12 | 0.2 | 0.14349 | 0.22596 | 22.32%
-0.4 | 0.39811 | 0.037223 | 0.041141 | 0.12 | 0.2 | 0.15722 | 0.24114 | 21.07%
-0.2 | 0.63096 | 0.058994 | 0.065204 | 0.12 | 0.2 | 0.17899 | 0.2652 | 19.41%
0 | 1 | 0.093499 | 0.10334 | 0.12 | 0.2 | 0.2135 | 0.30334 | 17.38%
0.2 | 1.5849 | 0.14819 | 0.16378 | 0.12 | 0.2 | 0.26819 | 0.36378 | 15.13%
0.4 | 2.5119 | 0.23486 | 0.25958 | 0.12 | 0.2 | 0.35486 | 0.45958 | 12.86%
0.6 | 3.9811 | 0.37223 | 0.41141 | 0.12 | 0.2 | 0.49223 | 0.61141 | 10.8%
0.8 | 6.3096 | 0.58994 | 0.65204 | 0.12 | 0.2 | 0.70994 | 0.85204 | 9.097%
1 | 10 | 0.93499 | 1.0334 | 0.12 | 0.2 | 1.055 | 1.2334 | 7.797%
1.2 | 15.8489 | 1.4819 | 1.6378 | 0.12 | 0.2 | 1.6019 | 1.8378 | 6.861%
1.4 | 25.1189 | 2.3486 | 2.5958 | 0.12 | 0.2 | 2.4686 | 2.7958 | 6.216%
1.6 | 39.8107 | 3.7223 | 4.1141 | 0.12 | 0.2 | 3.8423 | 4.3141 | 5.785%
1.8 | 63.0957 | 5.8994 | 6.5204 | 0.12 | 0.2 | 6.0194 | 6.7204 | 5.502%
2 | 100 | 9.3499 | 10.3341 | 0.12 | 0.2 | 9.4699 | 10.5341 | 5.32%
PSE voltage: | 50
PD power: | 80
current with constant power load:
index | cable length | parallel R (4P) | PD current | PD voltage | cable drop | PSE power | I (min R leg) | I (max R leg)
-1 | 0.1 | 0.080094 | 1.6041 | 49.8715 | 0.12848 | 80.2061 | 0.99328 | 0.61084 | 80W:
-0.8 | 0.15849 | 0.083064 | 1.6043 | 49.8667 | 0.13326 | 80.2138 | 0.98842 | 0.61585 | 1.076 at 7.5%
-0.6 | 0.25119 | 0.087758 | 1.6045 | 49.8592 | 0.14081 | 80.2259 | 0.98135 | 0.62317 | 1.052 at 5%
-0.4 | 0.39811 | 0.095171 | 1.6049 | 49.8473 | 0.15274 | 80.2451 | 0.97149 | 0.63341 | 2.2% increase = 24mA
-0.2 | 0.63096 | 0.10687 | 1.6055 | 49.8284 | 0.17158 | 80.2755 | 0.95855 | 0.64696
0 | 1 | 0.12531 | 1.6065 | 49.7987 | 0.2013 | 80.3234 | 0.94286 | 0.66361 | 50W:
0.2 | 1.5849 | 0.15438 | 1.608 | 49.7518 | 0.24824 | 80.3992 | 0.92561 | 0.68237 | 0.607 at 7.5%
0.4 | 2.5119 | 0.20024 | 1.6104 | 49.6775 | 0.32247 | 80.5193 | 0.90873 | 0.70166 | 0.593 at 5%
0.6 | 3.9811 | 0.27269 | 1.6142 | 49.5598 | 0.44018 | 80.7105 | 0.89426 | 0.71995 | 2.3% increase = 14mA
0.8 | 6.3096 | 0.38726 | 1.6203 | 49.3725 | 0.62749 | 81.0168 | 0.88387 | 0.73646
1 | 10 | 0.56862 | 1.6302 | 49.073 | 0.92698 | 81.5112 | 0.87866 | 0.75156
1.2 | 15.8489 | 0.85588 | 1.6464 | 48.5909 | 1.4091 | 82.32 | 0.87968 | 0.76672
1.4 | 25.1189 | 1.311 | 1.6734 | 47.8061 | 2.1939 | 83.6713 | 0.88872 | 0.78471
1.6 | 39.8107 | 2.0323 | 1.7203 | 46.5039 | 3.4961 | 86.0142 | 0.9099 | 0.81039
1.8 | 63.0957 | 3.1753 | 1.8075 | 44.2607 | 5.7393 | 90.3735 | 0.95346 | 0.85401
2 | 100 | 4.9868 | 1.9982 | 40.035 | 9.965 | 99.9125 | 1.0523 | 0.94597