## Read Me
| SolutionAnalyzer_2012_01_17 |  | Paul Kolesar
Overall Description
This workbook permits comparison of PMD solution sets and associated cabling targeted to support data center environments.
"PMD Sol'n Set" Tab
The worksheet "PMD Sol'n Set" allows comparison of up to four sets, each with up to four PMDs, on a variety of metrics.
The cells in columns B, C and D in bold font are inputs to the analysis.
In column B input the description of the PMDs within the sets, in order of ascending reach (i.e. ascending supportable distance) capability.
In column C input relative values of the metric to be compared such as cost, power consumption, size, etc.
In column D input the reach capability in meters. The column E reach values in US customary units of feet are calculated, not input.
Note: The default input values are placeholders.
The calculation produces Figures of Merit for each of the five data center channel length cumulative density functions (CDFs) provided in columns M thru S and plotted to the right in both metric (meters) and US customary (feet) units.
The originating source of the CDFs is referenced within the comments imbedded in the title cells above the CDF columns.
Two categories of channel CDFs are provided.
Columns O and P are the CDFs for access channels between servers and switches in two different time periods that illustrate migration of switch placement closer to servers.
Columns Q, R and S are the CDFs for aggregation channels between switches for three different topology mixes detailed in the referenced source material.
The calculation proceeds as follows:
The channel coverage of each PMD is determined by comparison to the CDFs using linear interpolation starting with the first PMD listed in the set.
The channel coverage of the next PMD in the set is determined from where the previous PMD stopped, and so on, thus necessitating ascending reach order.
A coverage check is determined by summing the coverage of all the PMDs in the set for each CDF, wherein a value less than 100% indicates that a portion of that CDF is not covered.
The Figures of Merit are determined by summing coverage-weighted comparison metrics. These are plotted below the PMD tables in the order of channels with increasing CDF.
Note: Setting reach to 0 effectively eliminates a PMD from the calculation provided that PMD is listed before others in compliance with the ascending reach ordering requirement.
For this reason, it is recommended to fill in the PMDs starting at the bottom row of each set.
"Cabling Sol'n Cost" Tab
| The worksheet "Cabling Sol'n Cost" allows comparison of cabling costs for up to four PMD sets, each with up to four PMDs. |  |  | Cabling / Fiber Designation Cross Reference
|  | Five cabling connectivity types can be examined that include 2-lane OS2, 8-lane OM3, 8-lane OM4, 8-lane OS2, and no structured cabling. |  | ISO | IEC | ITU | Description
|  | The 2-lane and 8-lane types represent structured cabling associated with PMDs that use one fiber and four fibers in each direction, respectively. |  | OS2 | B1.3 | G.652D | Low-water-peak single-mode
|  | The last type, "no structured cabling", is associated with of the use of Active Optical Cables (AOCs) or Direct Attach Copper (DAC) cables. |  | OM3 | A1a.2 | G.651.1 | 2000 MHz*km laser-optimized 50 µm
| The cells in columns B thru G in bold font are inputs to the analysis. |  |  | OM4 | A1a.3 | n.a. | 4700 MHz*km laser-optimized 50 µm
In column B input the description of the PMDs within the sets, in order of increasing cost.
In columns C thru G input the PMD's reach capability in meters for each cabling type over which it is intended to operate.
Note: The default input values are placeholders.
The calculation produces relative cabling cost values for each of the five data center channel length cumulative density functions (CDFs) provided in columns AQ thru AU.
These are the same CDFs used in the "PMD Sol'n Set" worksheet and described previously.
The cost calculations are based on cabling cost CDFs in columns BA thru BT which are normalized to the cost of a 100GBASE-SR10 CXP module.
The originating source of the cabling cost CDFs is referenced within the comment imbedded in the title cell above first set of cabling CDF columns.
The calculation proceeds as follows:
The cabling cost for each PMD is determined by comparison to the cabling cost CDFs in colmns BA thru BT using linear interpolation starting with the first PMD listed in the set and moving to the right thru the five cabling types.
Because the cabling types are placed in ascending cost order from left to right, the cost calculation can find the lowest cost scenario by applying priority to the lowest cost PMD / cabling-type combination defined in the set.
The calculation then applies increasingly higher cost combinations in succession to channel lengths that may exceed the reach of the prior combinations until all PMD / cabling-type combinations are analyzed.
The values in the grey cells below each PMD set, determined from the maximum reach of lower-cost combinations, provide the shortest channel length to which the corresponding PMD / cable-type combination is applied.
Cost values for individual PMD / cabling-type combinations are collected in columns N thru AL in arrays aligned with the PMD sets.
A zero cost value is assigned to any input cell left blank and any entry in the "no structured cabling" column.
A cost contribution is calculated for any PMD / cable-type combination that is required to complete coverage of the five data center channel length CDFs.
The cost for each of the five channel CDFs is the sum of all cost values for each PMD / cable-type combination within the set that is required to reach complete coverage.
However, complete cost values can only be determined for channels where the reach of the PMD set provides complete channel coverage, as determined by the "coverage check" on the "PMD Sol'n Set" worksheet.
The summed cost values are tabulateed in columns H thru L and plotted below the PMD sets to allow a graphical comparison of all PMD sets for each channel CDF.
"Total Sol'n Cost" Tab
The worksheet "Total Sol'n Cost" produces the total cost (i.e. 2 PMDs + cabling) for each PMD set defined by cost comparison metrics on worksheet "PMD Sol'n Set".
The calculation requires no user input on this worksheet, as the cost values come from the other worksheets and the PMD descriptions in column B are imported from the "PMD Sol'n Set" worksheet.
The calculation of total cost is determined by multiplying the PMD cost figure-of-merit by two (because two PMDs are required in each channel) and adding the cost of the associated cabling for each of the five channel topologies.
Important: Because the cabling cost values are relative to the cost of a 100GBASE-SR10 CXP module, the PMDs in each solution set must also use this same basis in order to produce meaningful combined cost values.
The total cost values are graphically displayed for each PMD solution set for the five channel topologies.

## PMD Sol'n Set
PMD set number | PMD description | comparison metric | PMD reach capability |  | PMD coverage for server-to-switch channels |  | PMD coverage for switch-to-switch channels |  |  | for interpolation | channel length |  | server-to-switch channel cumulative density functions |  | data center switch-to-switch channel cumulative density functions in 2010
| (ordered by increasing reach) | (relative values) | (m) | (ft) | server-to-switch post-2012 | server-to-switch pre-2008 | switch-to-switch single-link | switch-to-switch 2:1 mix | switch-to-switch double-link |  | (m) | (ft) | post-2012 | pre-2008 | single link: concat ratio = 0 | 2:1 mix: concat ratio = 0.33 | double link: concat ratio = 1
1 |  |  |  | 0 | 0% | 0% | 0% | 0% | 0% |  | 0 | 0 | 0% | 0% | 0% | 0% | 0%
|  |  |  | 0 | 0% | 0% | 0% | 0% | 0% | 0 | 9.1436 | 30 | 63.9% | 30.5% | 0% | 0% | 0%
| SR4 | 1.2 | 75 | 246.075 | 98.5% | 96.66% | 80.12% | 67.17% | 41.27% | 30 | 18.2871 | 60 | 84.9% | 65.9% | 6.028% | 4.021% | 0.006942%
| LR4 | 50 | 10000 | 32810 | 1.499% | 3.337% | 19.88% | 32.83% | 58.73% | 60 | 27.4307 | 90 | 91.6% | 80.5% | 22.93% | 15.37% | 0.2586%
|  |  |  | coverage check: | 100% | 100% | 100% | 100% | 100% | 90 | 36.5742 | 120 | 93.9% | 87.2% | 41.13% | 28.06% | 1.92%
|  |  |  | Figures of Merit: | 1.9314 | 2.8283 | 10.9028 | 17.2212 | 29.858 | 120 | 45.7178 | 150 | 95.8% | 90.5% | 55.37% | 39.13% | 6.656%
[10 empty] | 150 | 54.8613 | 180 | 96.8% | 92.6% | 66.44% | 50.95% | 19.98%
2 |  |  |  | 0 | 0% | 0% | 0% | 0% | 0% | 180 | 64.0049 | 210 | 97.6% | 94.6% | 74.22% | 59.42% | 29.81%
|  |  |  | 0 | 0% | 0% | 0% | 0% | 0% | 210 | 73.1484 | 240 | 98.4% | 96.4% | 79.37% | 66.08% | 39.5%
| SR4 | 1.3 | 115 | 377.315 | 100% | 100% | 91.25% | 84.17% | 70.02% | 240 | 82.292 | 270 | 98.9% | 97.7% | 83.05% | 71.46% | 48.28%
| LR4 | 50 | 10000 | 32810 | 0% | 0% | 8.749% | 15.83% | 29.98% | 270 | 91.4355 | 300 | 99.5% | 98.7% | 85.99% | 75.93% | 55.81%
|  |  |  | coverage check: | 100% | 100% | 100% | 100% | 100% | 300 | 100.5791 | 330 | 100% | 100% | 88.3% | 79.58% | 62.13%
|  |  |  | Figures of Merit: | 1.3 | 1.3 | 5.561 | 9.008 | 15.902 | 330 | 109.7226 | 360 | 100% | 100% | 90.18% | 82.6% | 67.43%
[10 empty] | 360 | 118.8662 | 390 | 100% | 100% | 92.04% | 85.33% | 71.91%
3 |  |  |  | 0 | 0% | 0% | 0% | 0% | 0% | 390 | 128.0098 | 420 | 100% | 100% | 93.56% | 87.63% | 75.78%
|  |  |  | 0 | 0% | 0% | 0% | 0% | 0% | 420 | 137.1533 | 450 | 100% | 100% | 94.94% | 89.7% | 79.21%
| SR4 | 1.5 | 150 | 492.15 | 100% | 100% | 96.32% | 92% | 83.37% | 450 | 146.2969 | 480 | 100% | 100% | 96% | 91.42% | 82.27%
| LR4 | 50 | 10000 | 32810 | 0% | 0% | 3.68% | 7.998% | 16.63% | 480 | 155.4404 | 510 | 100% | 100% | 96.79% | 92.86% | 84.98%
|  |  |  | coverage check: | 100% | 100% | 100% | 100% | 100% | 510 | 164.584 | 540 | 100% | 100% | 97.41% | 94.06% | 87.35%
|  |  |  | Figures of Merit: | 1.5 | 1.5 | 3.285 | 5.3791 | 9.5673 | 540 | 173.7275 | 570 | 100% | 100% | 98.03% | 94.95% | 88.79%
[10 empty] | 570 | 182.8711 | 600 | 100% | 100% | 98.28% | 95.62% | 90.3%
4 |  |  |  | 0 | 0% | 0% | 0% | 0% | 0% | 600 | 192.0146 | 630 | 100% | 100% | 98.58% | 96.45% | 92.21%
|  |  |  | 0 | 0% | 0% | 0% | 0% | 0% | 630 | 201.1582 | 660 | 100% | 100% | 98.91% | 97.02% | 93.24%
| SR4 |  |  | 0 | 0% | 0% | 0% | 0% | 0% | 660 | 210.3017 | 690 | 100% | 100% | 99.09% | 97.49% | 94.31%
| LR4 |  |  | 0 | 0% | 0% | 0% | 0% | 0% | 690 | 219.4453 | 720 | 100% | 100% | 99.13% | 97.84% | 95.26%
|  |  |  | coverage check: | 0% | 0% | 0% | 0% | 0% | 720 | 228.5888 | 750 | 100% | 100% | 99.13% | 98.1% | 96.05%
|  |  |  | Figures of Merit: | 0 | 0 | 0 | 0 | 0 | 750 | 237.7324 | 780 | 100% | 100% | 99.13% | 98.28% | 96.58%
[10 empty] | 780 | 246.876 | 810 | 100% | 100% | 99.67% | 98.79% | 97.01%
[10 empty] | 810 | 256.0195 | 840 | 100% | 100% | 99.94% | 99.09% | 97.41%
[10 empty] | 840 | 265.1631 | 870 | 100% | 100% | 99.99% | 99.29% | 97.89%
[10 empty] | 870 | 274.3066 | 900 | 100% | 100% | 100% | 99.45% | 98.37%
[10 empty] | 900 | 283.4502 | 930 | 100% | 100% | 100% | 99.59% | 98.76%
[10 empty] | 930 | 292.5937 | 960 | 100% | 100% | 100% | 99.64% | 98.91%
[10 empty] | 960 | 301.7373 | 990 | 100% | 100% | 100% | 99.65% | 98.95%
[10 empty] | 990 | 310.8808 | 1020 | 100% | 100% | 100% | 99.65% | 98.96%
[10 empty] | 1020 | 320.0244 | 1050 | 100% | 100% | 100% | 99.65% | 98.96%
[10 empty] | 1050 | 329.1679 | 1080 | 100% | 100% | 100% | 99.65% | 98.96%
[10 empty] | 1080 | 341.3593 | 1120 | 100% | 100% | 100% | 99.78% | 99.33%
[10 empty] | 1120 | 350.5029 | 1150 | 100% | 100% | 100% | 99.93% | 99.78%
[10 empty] | 1150 | 356.5986 | 1170 | 100% | 100% | 100% | 99.98% | 99.95%
[10 empty] | 1170 | 365.7422 | 1200 | 100% | 100% | 100% | 100% | 99.99%
[10 empty] | 1200 | 374.8857 | 1230 | 100% | 100% | 100% | 100% | 100%
[10 empty] | 1230 | 384.0293 | 1260 | 100% | 100% | 100% | 100% | 100%
[10 empty] | 1260 | 393.1728 | 1290 | 100% | 100% | 100% | 100% | 100%
[10 empty] | 1290 | 402.3164 | 1320 | 100% | 100% | 100% | 100% | 100%
1320
Note on E7: pkolesar: Will sum to 100% for solution sets that provide complete coverage.
Note on E14: pkolesar: Will sum to 100% for solution sets that provide complete coverage.
Note on E21: pkolesar: Will sum to 100% for solution sets that provide complete coverage.
Note on E28: pkolesar: Will sum to 100% for solution sets that provide complete coverage.
Note on O2: pkolesar: post-2012 projection per flatman_01_0311
Note on P2: pkolesar: pre 2008 per flatman_01_0108
Note on Q1: pkolesar: from kolesar_02_0911.pdf

## Cabling Sol'n Cost
PMD set number | PMD description | PMD reach capability for structured cabling type (m) |  |  |  |  | Structured cabling cost for server-to-switch channels |  | Structured cabling cost for switch-to-switch channels |  |  | Cabling cost for server-to-switch channels for PMD and structured cabling type | [9 empty] | Cabling cost for switch-to-switch channels for PMD and structured cabling type | [14 empty] | for interpolation | channel length |  | server-to-switch channel cumulative density functions |  | data center switch-to-switch channel cumulative density functions in 2010 |  |  | cumulative cabling costs post-2012 server-to-switch channles |  |  |  | cumulative cabling costs pre-2008 server-to-switch channels |  |  |  | cumulative cabling costs single-link switch-to-switch channels |  |  |  | cumulative cabling costs 2:1-mix switch-to-switch channels |  |  |  | cumulative cabling costs double-link switch-to-switch channels
| (ordered by increasing cost) | no structured cabling (n.s.c.) | 2-lane OS2 | 8-lane OM3 | 8-lane OM4 | 8-lane OS2 | server-to-switch post-2012 | server-to-switch pre-2008 | switch-to-switch single-link | switch-to-switch 2:1 mix | switch-to-switch double-link | post-2012 |  |  |  |  | pre-2008 |  |  |  |  | single-link |  |  |  |  | 2:1 mix |  |  |  |  | double-link |  |  |  |  | 3.281 | (m) | (ft) | post-2012 | pre-2008 | single link: concat ratio = 0 | 2:1 mix: concat ratio = 0.33 | double link: concat ratio = 1 | 2-lane OS2 | 8-lane OM3 | 8-lane OM4 | 8-lane OS2 | 2-lane OS2 | 8-lane OM3 | 8-lane OM4 | 8-lane OS2 | 2-lane OS2 | 8-lane OM3 | 8-lane OM4 | 8-lane OS2 | 2-lane OS2 | 8-lane OM3 | 8-lane OM4 | 8-lane OS2 | 2-lane OS2 | 8-lane OM3 | 8-lane OM4 | 8-lane OS2
[12 empty] | n.s.c. | 2-OS2 | 8-OM3 | 8-OM4 | 8-OS2 | n.s.c. | 2-OS2 | 8-OM3 | 8-OM4 | 8-OS2 | n.s.c. | 2-OS2 | 8-OM3 | 8-OM4 | 8-OS2 | n.s.c. | 2-OS2 | 8-OM3 | 8-OM4 | 8-OS2 | n.s.c. | 2-OS2 | 8-OM3 | 8-OM4 | 8-OS2 |  | 0 | 0 | 0% | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | [36 empty] | 0 | 9.1436 | 30 | 63.9% | 30.5% | 0% | 0% | 0% | 0.13368 | 0.49478 | 0.50321 | 0.65651 | 0.063806 | 0.23616 | 0.24019 | 0.31336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[37 empty] | 30 | 18.2871 | 60 | 84.9% | 65.9% | 6.028% | 4.021% | 0.006942% | 0.17893 | 0.66796 | 0.68169 | 0.87881 | 0.14009 | 0.52811 | 0.54105 | 0.6881 | 0.012991 | 0.049716 | 0.051235 | 0.063817 | 0.010954 | 0.040454 | 0.041475 | 0.052695 | 2.6816e-05 | 9.5019e-05 | 9.6797e-05 | 0.00012592
| SR4 |  |  | 50 | 75 | [31 empty] | 60 | 27.4307 | 90 | 91.6% | 80.5% | 22.93% | 15.37% | 0.2586% | 0.19379 | 0.7266 | 0.74282 | 0.95183 | 0.17248 | 0.65587 | 0.67425 | 0.84721 | 0.050475 | 0.19761 | 0.20541 | 0.24799 | 0.042588 | 0.16036 | 0.16563 | 0.20497 | 0.0010147 | 0.0036661 | 0.0037625 | 0.0047687
| LR4 |  | 10000 | [33 empty] | 90 | 36.5742 | 120 | 93.9% | 87.2% | 41.13% | 28.06% | 1.92% | 0.19904 | 0.74788 | 0.76523 | 0.97761 | 0.18776 | 0.71788 | 0.73955 | 0.92232 | 0.092 | 0.36609 | 0.38285 | 0.45207 | 0.078755 | 0.30082 | 0.31235 | 0.37919 | 0.007644 | 0.028089 | 0.02901 | 0.035951
Cabling cost analysis for all PMDs in set | [36 empty] | 120 | 45.7178 | 150 | 95.8% | 90.5% | 55.37% | 39.13% | 6.656% | 0.20349 | 0.76643 | 0.78494 | 0.99951 | 0.19549 | 0.75008 | 0.77378 | 0.96034 | 0.12537 | 0.50502 | 0.53049 | 0.61609 | 0.111 | 0.42891 | 0.44724 | 0.5346 | 0.026834 | 0.10008 | 0.10391 | 0.12629
Calculations presume the above PMDs are deployed when channel length exceeds: | [6 empty] | 0.80146 | 0.83 | 0.84341 | 0.91488 | 0.96128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 54.8613 | 180 | 96.8% | 92.6% | 66.44% | 50.95% | 19.98% | 0.2059 | 0.77669 | 0.79593 | 1.0113 | 0.20055 | 0.77164 | 0.79687 | 0.98519 | 0.15202 | 0.61866 | 0.65224 | 0.74712 | 0.14619 | 0.57169 | 0.5987 | 0.70428 | 0.081664 | 0.30932 | 0.32297 | 0.38461
|  | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 64.0049 | 210 | 97.6% | 94.6% | 74.22% | 59.42% | 29.81% | 0.20788 | 0.7853 | 0.80523 | 1.0211 | 0.20549 | 0.79317 | 0.8201 | 1.0095 | 0.17123 | 0.70241 | 0.74261 | 0.8416 | 0.17191 | 0.67815 | 0.71239 | 0.82839 | 0.12275 | 0.46869 | 0.49076 | 0.57831
|  | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0.77123 | 0.026238 | 0 | 0 | 0 | 0.76018 | 0.060939 | 0 | 0 | 0 | 0.55824 | 0.22777 | 0 | 0 | 0 | 0.49578 | 0.30388 | 0 | 0 | 0 | 0.19807 | 0.48808 | 0 | 210 | 73.1484 | 240 | 98.4% | 96.4% | 79.37% | 66.08% | 39.5% | 0.2099 | 0.79432 | 0.81502 | 1.031 | 0.21005 | 0.81346 | 0.84214 | 1.0319 | 0.18428 | 0.76047 | 0.80569 | 0.90578 | 0.19257 | 0.76532 | 0.80604 | 0.92816 | 0.16381 | 0.63049 | 0.662 | 0.77204
|  | 0 | 0 | 0 | 50 | 75 | [5 empty] | 0 | 0.0039916 | 0 | 0 | 0 | 0 | 0.008889 | 0 | 0 | 0 | 0 | 0.057403 | 0 | 0 | 0 | 0 | 0.11522 | 0 | 0 | 0 | 0 | 0.27513 | 0 | 0 | 0 | 240 | 82.292 | 270 | 98.9% | 97.7% | 83.05% | 71.46% | 48.28% | 0.2112 | 0.80021 | 0.82146 | 1.0374 | 0.21342 | 0.82876 | 0.85887 | 1.0485 | 0.19384 | 0.80383 | 0.85306 | 0.9528 | 0.20961 | 0.83847 | 0.88509 | 1.0105 | 0.20163 | 0.78177 | 0.82291 | 0.95063 | zz
|  | 0 | 75 | 10000 | 10000 | 10000 | [30 empty] | 270 | 91.4355 | 300 | 99.5% | 98.7% | 85.99% | 75.93% | 55.81% | 0.2128 | 0.80757 | 0.82955 | 1.0453 | 0.21608 | 0.84104 | 0.87236 | 1.0616 | 0.20165 | 0.8399 | 0.89269 | 0.99123 | 0.22403 | 0.90142 | 0.95346 | 1.0802 | 0.23449 | 0.91515 | 0.96544 | 1.1059
[37 empty] | 300 | 100.5791 | 330 | 100% | 100% | 88.3% | 79.58% | 62.13% | 0.21416 | 0.81396 | 0.83661 | 1.052 | 0.21962 | 0.85766 | 0.89071 | 1.079 | 0.20793 | 0.86938 | 0.92524 | 1.0221 | 0.23603 | 0.95463 | 1.0115 | 1.1382 | 0.26251 | 1.0304 | 1.0891 | 1.2384
2 | [36 empty] | 330 | 109.7226 | 360 | 100% | 100% | 90.18% | 82.6% | 67.43% | 0.21416 | 0.81396 | 0.83661 | 1.052 | 0.21962 | 0.85766 | 0.89071 | 1.079 | 0.21317 | 0.89436 | 0.95296 | 1.0479 | 0.24616 | 1.0002 | 1.0615 | 1.1872 | 0.28633 | 1.1297 | 1.1961 | 1.3511
[37 empty] | 360 | 118.8662 | 390 | 100% | 100% | 92.04% | 85.33% | 71.91% | 0.21416 | 0.81396 | 0.83661 | 1.052 | 0.21962 | 0.85766 | 0.89071 | 1.079 | 0.21846 | 0.92 | 0.98152 | 1.074 | 0.25549 | 1.0429 | 1.1084 | 1.2323 | 0.30671 | 1.2157 | 1.2892 | 1.4476
| SR4 |  |  | 75 | 115 | [31 empty] | 390 | 128.0098 | 420 | 100% | 100% | 93.56% | 87.63% | 75.78% | 0.21416 | 0.81396 | 0.83661 | 1.052 | 0.21962 | 0.85766 | 0.89071 | 1.079 | 0.2229 | 0.94178 | 1.0059 | 1.0958 | 0.26351 | 1.08 | 1.1495 | 1.2712 | 0.32459 | 1.2921 | 1.3722 | 1.5323
| LR4 |  | 10000 | [33 empty] | 420 | 137.1533 | 450 | 100% | 100% | 94.94% | 89.7% | 79.21% | 0.21416 | 0.81396 | 0.83661 | 1.052 | 0.21962 | 0.85766 | 0.89071 | 1.079 | 0.22701 | 0.96225 | 1.0289 | 1.116 | 0.27083 | 1.1143 | 1.1875 | 1.3066 | 0.34063 | 1.3615 | 1.4478 | 1.6084
Cabling cost analysis for all PMDs in set | [36 empty] | 450 | 146.2969 | 480 | 100% | 100% | 96% | 91.42% | 82.27% | 0.21416 | 0.81396 | 0.83661 | 1.052 | 0.21962 | 0.85766 | 0.89071 | 1.079 | 0.23021 | 0.97838 | 1.047 | 1.1318 | 0.27704 | 1.1438 | 1.2203 | 1.3367 | 0.35515 | 1.4249 | 1.5172 | 1.6772
Calculations presume the above PMDs are deployed when channel length exceeds: | [6 empty] | 0.81579 | 0.86174 | 0.95081 | 1.1064 | 1.3649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 480 | 155.4404 | 510 | 100% | 100% | 96.79% | 92.86% | 84.98% | 0.21416 | 0.81396 | 0.83661 | 1.052 | 0.21962 | 0.85766 | 0.89071 | 1.079 | 0.23268 | 0.99095 | 1.0612 | 1.1439 | 0.28231 | 1.1691 | 1.2486 | 1.3622 | 0.36822 | 1.4827 | 1.5805 | 1.7393
|  | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 510 | 164.584 | 540 | 100% | 100% | 97.41% | 94.06% | 87.35% | 0.21416 | 0.81396 | 0.83661 | 1.052 | 0.21962 | 0.85766 | 0.89071 | 1.079 | 0.23464 | 1.0011 | 1.0727 | 1.1536 | 0.2868 | 1.1909 | 1.273 | 1.384 | 0.37976 | 1.5342 | 1.6372 | 1.7941
|  | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0.79551 | 0.020283 | 0 | 0 | 0 | 0.81656 | 0.04518 | 0 | 0 | 0 | 0.76925 | 0.15416 | 0 | 0 | 0 | 0.78013 | 0.26656 | 0 | 0 | 0 | 0.66113 | 0.55528 | 0 | 540 | 173.7275 | 570 | 100% | 100% | 98.03% | 94.95% | 88.79% | 0.21416 | 0.81396 | 0.83661 | 1.052 | 0.21962 | 0.85766 | 0.89071 | 1.079 | 0.23662 | 1.0114 | 1.0844 | 1.1634 | 0.29018 | 1.2075 | 1.2917 | 1.4004 | 0.38687 | 1.5663 | 1.6726 | 1.8278
|  | 0 | 0 | 0 | 75 | 115 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0274 | 0 | 0 | 0 | 0 | 0.059701 | 0 | 0 | 0 | 0 | 0.1485 | 0 | 0 | 0 | 570 | 182.8711 | 600 | 100% | 100% | 98.28% | 95.62% | 90.3% | 0.21416 | 0.81396 | 0.83661 | 1.052 | 0.21962 | 0.85766 | 0.89071 | 1.079 | 0.23744 | 1.0157 | 1.0893 | 1.1674 | 0.29275 | 1.2202 | 1.306 | 1.4129 | 0.39441 | 1.6006 | 1.7105 | 1.8637
|  | 0 | 115 | 10000 | 10000 | 10000 | [30 empty] | 600 | 192.0146 | 630 | 100% | 100% | 98.58% | 96.45% | 92.21% | 0.21416 | 0.81396 | 0.83661 | 1.052 | 0.21962 | 0.85766 | 0.89071 | 1.079 | 0.23844 | 1.021 | 1.0954 | 1.1723 | 0.29603 | 1.2366 | 1.3246 | 1.4288 | 0.40405 | 1.645 | 1.7597 | 1.9095
[37 empty] | 630 | 201.1582 | 660 | 100% | 100% | 98.91% | 97.02% | 93.24% | 0.21416 | 0.81396 | 0.83661 | 1.052 | 0.21962 | 0.85766 | 0.89071 | 1.079 | 0.2396 | 1.0272 | 1.1025 | 1.178 | 0.2983 | 1.2481 | 1.3376 | 1.4398 | 0.40936 | 1.6696 | 1.7871 | 1.9348
3 | [36 empty] | 660 | 210.3017 | 690 | 100% | 100% | 99.09% | 97.49% | 94.31% | 0.21416 | 0.81396 | 0.83661 | 1.052 | 0.21962 | 0.85766 | 0.89071 | 1.079 | 0.2402 | 1.0305 | 1.1063 | 1.181 | 0.30021 | 1.2579 | 1.3486 | 1.4491 | 0.41487 | 1.6954 | 1.8158 | 1.961
[37 empty] | 690 | 219.4453 | 720 | 100% | 100% | 99.13% | 97.84% | 95.26% | 0.21416 | 0.81396 | 0.83661 | 1.052 | 0.21962 | 0.85766 | 0.89071 | 1.079 | 0.24034 | 1.0313 | 1.1072 | 1.1817 | 0.30163 | 1.2652 | 1.3569 | 1.456 | 0.4199 | 1.7191 | 1.8423 | 1.985
| SR4 |  |  | 100 | 150 | [31 empty] | 720 | 228.5888 | 750 | 100% | 100% | 99.13% | 98.1% | 96.05% | 0.21416 | 0.81396 | 0.83661 | 1.052 | 0.21962 | 0.85766 | 0.89071 | 1.079 | 0.24036 | 1.0314 | 1.1073 | 1.1818 | 0.30273 | 1.2709 | 1.3634 | 1.4613 | 0.42406 | 1.7389 | 1.8645 | 2.0048
| LR4 |  | 10000 | [33 empty] | 750 | 237.7324 | 780 | 100% | 100% | 99.13% | 98.28% | 96.58% | 0.21416 | 0.81396 | 0.83661 | 1.052 | 0.21962 | 0.85766 | 0.89071 | 1.079 | 0.24036 | 1.0314 | 1.1073 | 1.1818 | 0.30348 | 1.2748 | 1.3679 | 1.465 | 0.42692 | 1.7527 | 1.8799 | 2.0185
Cabling cost analysis for all PMDs in set | [36 empty] | 780 | 246.876 | 810 | 100% | 100% | 99.67% | 98.79% | 97.01% | 0.21416 | 0.81396 | 0.83661 | 1.052 | 0.21962 | 0.85766 | 0.89071 | 1.079 | 0.24237 | 1.0426 | 1.1203 | 1.1917 | 0.30565 | 1.2863 | 1.381 | 1.4755 | 0.42928 | 1.7641 | 1.8927 | 2.0297
Calculations presume the above PMDs are deployed when channel length exceeds: | [6 empty] | 0.81401 | 0.85777 | 1.0095 | 1.2073 | 1.5708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 810 | 256.0195 | 840 | 100% | 100% | 99.94% | 99.09% | 97.41% | 0.21416 | 0.81396 | 0.83661 | 1.052 | 0.21962 | 0.85766 | 0.89071 | 1.079 | 0.24338 | 1.0483 | 1.1269 | 1.1967 | 0.30699 | 1.2934 | 1.3892 | 1.4821 | 0.43143 | 1.7745 | 1.9045 | 2.04
|  | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 840 | 265.1631 | 870 | 100% | 100% | 99.99% | 99.29% | 97.89% | 0.21416 | 0.81396 | 0.83661 | 1.052 | 0.21962 | 0.85766 | 0.89071 | 1.079 | 0.24358 | 1.0495 | 1.1282 | 1.1977 | 0.30786 | 1.298 | 1.3945 | 1.4863 | 0.43412 | 1.7877 | 1.9194 | 2.0528
|  | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0.81356 | 0.00044698 | 0 | 0 | 0 | 0.85661 | 0.0011621 | 0 | 0 | 0 | 0.86751 | 0.12959 | 0 | 0 | 0 | 0.95126 | 0.22394 | 0 | 0 | 0 | 1.0231 | 0.46151 | 0 | 870 | 274.3066 | 900 | 100% | 100% | 100% | 99.45% | 98.37% | 0.21416 | 0.81396 | 0.83661 | 1.052 | 0.21962 | 0.85766 | 0.89071 | 1.079 | 0.24361 | 1.0496 | 1.1283 | 1.1978 | 0.3086 | 1.302 | 1.399 | 1.4899 | 0.43683 | 1.8011 | 1.9346 | 2.0658
|  | 0 | 0 | 0 | 100 | 150 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012413 | 0 | 0 | 0 | 0 | 0.032071 | 0 | 0 | 0 | 0 | 0.086145 | 0 | 0 | 0 | 900 | 283.4502 | 930 | 100% | 100% | 100% | 99.59% | 98.76% | 0.21416 | 0.81396 | 0.83661 | 1.052 | 0.21962 | 0.85766 | 0.89071 | 1.079 | 0.24362 | 1.0497 | 1.1284 | 1.1979 | 0.30921 | 1.3053 | 1.4028 | 1.4928 | 0.43907 | 1.8122 | 1.9471 | 2.0765
|  | 0 | 150 | 10000 | 10000 | 10000 | [30 empty] | 930 | 292.5937 | 960 | 100% | 100% | 100% | 99.64% | 98.91% | 0.21416 | 0.81396 | 0.83661 | 1.052 | 0.21962 | 0.85766 | 0.89071 | 1.079 | 0.24362 | 1.0497 | 1.1284 | 1.1979 | 0.30944 | 1.3066 | 1.4043 | 1.494 | 0.43993 | 1.8166 | 1.952 | 2.0806
[37 empty] | 960 | 301.7373 | 990 | 100% | 100% | 100% | 99.65% | 98.95% | 0.21416 | 0.81396 | 0.83661 | 1.052 | 0.21962 | 0.85766 | 0.89071 | 1.079 | 0.24362 | 1.0497 | 1.1284 | 1.1979 | 0.3095 | 1.3069 | 1.4047 | 1.4943 | 0.44016 | 1.8177 | 1.9534 | 2.0817
4 | [36 empty] | 990 | 310.8808 | 1020 | 100% | 100% | 100% | 99.65% | 98.96% | 0.21416 | 0.81396 | 0.83661 | 1.052 | 0.21962 | 0.85766 | 0.89071 | 1.079 | 0.24362 | 1.0497 | 1.1284 | 1.1979 | 0.30951 | 1.3069 | 1.4047 | 1.4943 | 0.4402 | 1.8179 | 1.9536 | 2.0819
[37 empty] | 1020 | 320.0244 | 1050 | 100% | 100% | 100% | 99.65% | 98.96% | 0.21416 | 0.81396 | 0.83661 | 1.052 | 0.21962 | 0.85766 | 0.89071 | 1.079 | 0.24362 | 1.0497 | 1.1284 | 1.1979 | 0.30951 | 1.307 | 1.4048 | 1.4943 | 0.4402 | 1.8179 | 1.9536 | 2.0819
[37 empty] | 1050 | 329.1679 | 1080 | 100% | 100% | 100% | 99.65% | 98.96% | 0.21416 | 0.81396 | 0.83661 | 1.052 | 0.21962 | 0.85766 | 0.89071 | 1.079 | 0.24362 | 1.0497 | 1.1284 | 1.1979 | 0.30951 | 1.307 | 1.4048 | 1.4943 | 0.44021 | 1.8179 | 1.9536 | 2.0819
[37 empty] | 1080 | 341.3593 | 1120 | 100% | 100% | 100% | 99.78% | 99.33% | 0.21416 | 0.81396 | 0.83661 | 1.052 | 0.21962 | 0.85766 | 0.89071 | 1.079 | 0.24362 | 1.0497 | 1.1284 | 1.1979 | 0.31013 | 1.3104 | 1.4088 | 1.4973 | 0.44248 | 1.8297 | 1.967 | 2.0928
Cabling cost analysis for all PMDs in set | [36 empty] | 1120 | 350.5029 | 1150 | 100% | 100% | 100% | 99.93% | 99.78% | 0.21416 | 0.81396 | 0.83661 | 1.052 | 0.21962 | 0.85766 | 0.89071 | 1.079 | 0.24362 | 1.0497 | 1.1284 | 1.1979 | 0.31088 | 1.3147 | 1.4137 | 1.501 | 0.44524 | 1.8441 | 1.9835 | 2.106
Calculations presume the above PMDs are deployed when channel length exceeds: | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1150 | 356.5986 | 1170 | 100% | 100% | 100% | 99.98% | 99.95% | 0.21416 | 0.81396 | 0.83661 | 1.052 | 0.21962 | 0.85766 | 0.89071 | 1.079 | 0.24362 | 1.0497 | 1.1284 | 1.1979 | 0.31117 | 1.3163 | 1.4156 | 1.5024 | 0.44631 | 1.8496 | 1.9898 | 2.1111
|  | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1170 | 365.7422 | 1200 | 100% | 100% | 100% | 100% | 99.99% | 0.21416 | 0.81396 | 0.83661 | 1.052 | 0.21962 | 0.85766 | 0.89071 | 1.079 | 0.24362 | 1.0497 | 1.1284 | 1.1979 | 0.31123 | 1.3167 | 1.4161 | 1.5027 | 0.44655 | 1.8509 | 1.9913 | 2.1123
|  | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 374.8857 | 1230 | 100% | 100% | 100% | 100% | 100% | 0.21416 | 0.81396 | 0.83661 | 1.052 | 0.21962 | 0.85766 | 0.89071 | 1.079 | 0.24362 | 1.0497 | 1.1284 | 1.1979 | 0.31124 | 1.3168 | 1.4161 | 1.5028 | 0.44659 | 1.8511 | 1.9915 | 2.1125
|  | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1230 | 384.0293 | 1260 | 100% | 100% | 100% | 100% | 100% | 0.21416 | 0.81396 | 0.83661 | 1.052 | 0.21962 | 0.85766 | 0.89071 | 1.079 | 0.24362 | 1.0497 | 1.1284 | 1.1979 | 0.31124 | 1.3168 | 1.4161 | 1.5028 | 0.44659 | 1.8511 | 1.9916 | 2.1125
|  | 0 | 0 | 0 | 0 | 0 | [30 empty] | 1260 | 393.1728 | 1290 | 100% | 100% | 100% | 100% | 100% | 0.21416 | 0.81396 | 0.83661 | 1.052 | 0.21962 | 0.85766 | 0.89071 | 1.079 | 0.24362 | 1.0497 | 1.1284 | 1.1979 | 0.31124 | 1.3168 | 1.4161 | 1.5028 | 0.44659 | 1.8511 | 1.9916 | 2.1125
[37 empty] | 1290 | 402.3164 | 1320 | 100% | 100% | 100% | 100% | 100% | 0.21416 | 0.81396 | 0.83661 | 1.052 | 0.21962 | 0.85766 | 0.89071 | 1.079 | 0.24362 | 1.0497 | 1.1284 | 1.1979 | 0.31124 | 1.3168 | 1.4161 | 1.5028 | 0.44659 | 1.8511 | 1.9916 | 2.1125
[37 empty] | 1320 | [7 empty] | cost ratios (vs 2-lane OS2)
[45 empty] | 1 | 3.8008 | 3.9065 | 4.912 | 1 | 3.9052 | 4.0557 | 4.913 | 1 | 4.3086 | 4.6319 | 4.9169 | 1 | 4.2306 | 4.5499 | 4.8283 | 1 | 4.145 | 4.4595 | 4.7302
Note on A8: pkolesar: The analysis examines 2-lane OS2 and 8-lane composite (i.e. OM3, OM4 and OS2 8-lane) connectivity as a combined solution set including the effect of AOCs and DACs. The analysis assumes that 2-lane OS2 PMDs will be deployed only for reaches not satisfied by others.
Note on A19: pkolesar: The analysis examines 2-lane OS2 and 8-lane composite (i.e. OM3, OM4 and OS2 8-lane) connectivity as a combined solution set including the effect of AOCs and DACs. Here 2-lane OS2 PMDs are deployed only for reaches not satisfied by others.
Note on A30: pkolesar: The analysis examines 2-lane OS2 and 8-lane composite (i.e. OM3, OM4 and OS2 8-lane) connectivity as a combined solution set including the effect of AOCs and DACs. Here 2-lane OS2 PMDs are deployed only for reaches not satisfied by others.
Note on A41: pkolesar: The analysis examines 2-lane OS2 and 8-lane composite (i.e. OM3, OM4 and OS2 8-lane) connectivity as a combined solution set including the effect of AOCs and DACs. Here 2-lane OS2 PMDs are deployed only for reaches not satisfied by others.
Note on C2: pkolesar: Place reach of AOCs and DACs in this column.
Note on AQ2: pkolesar: post-2012 projection per flatman_01_0311
Note on AR2: pkolesar: pre 2008 per flatman_01_0108
Note on AS1: pkolesar: from kolesar_02_0911.pdf
Note on BA1: pkolesar: Source of cabling cost: kolesar_01_0112.pdf

## Total Sol'n Cost
PMD set number | PMD description | Total cost for server-to-switch channels |  | Total cost for switch-to-switch channels
| (copied from PMD Sol'n Set worksheet) | server-to-switch post-2012 | server-to-switch pre-2008 | switch-to-switch single-link | switch-to-switch 2:1 mix | switch-to-switch double-link
1
SR4
LR4
|  | 4.6642 | 6.4867 | 22.649 | 35.3573 | 60.6772
2
SR4
LR4
|  | 3.4158 | 3.4617 | 12.0728 | 19.1224 | 33.1689
3
SR4
LR4
|  | 3.814 | 3.8578 | 7.5796 | 11.9655 | 20.7054
4
SR4
LR4
|  | 0 | 0 | 0 | 0 | 0