## Slide 1: PD power, Vpse and Rcable
Chad Jones
Cisco Systems

## Slide 2: Cable current
The equation for Icable is a quadratic:
  R * I2 – VPSE * I + PPD = 0 => I = ((VPSE ± SQRT(VPSE2 – 4 * R * PPD)) / 2 * R)
    The ’plus’ solution is an unstable mode, use on the ‘minus’ solution
  PPSE = VPSE * I
PPSE = VPSE ( (VPSE – SQRT(VPSE2– 4 * R * PPD)) / 2 * R )

## Slide 3: Max Current, Max PD power
The max of that quadratic can be found by taking the derivate wrt I, solving for I. But I don’t really care about IMAX as much as I want to know PPD_MAX
PPD_MAX occurs when PPD = PCABLE
(PPD) VPSE * I – R * I2 = R * I2 => VPSE * I = 2 * I2 * R => I = VPSE / 2 * R
And PPD = VPD* I = (VPSE / 2)* VPSE / 2 * R = VPSE2 / 4 * R
PPD_MAX = VPSE2 / 4 * R

## Slide 4: Which is more important, RCABLEor VPSE
Chart: PD power delivered
| 6.25 | 7.0 | 8.0 | 9.0 | 10.0 | 11.0 | 12.0 | 13.0 | 14.0 | 15.0 | 16.0 | 17.0 | 18.0 | 19.0 | 20.0 | 21.0 | 22.0 | 23.0 | 24.0 | 25.0 | 26.0 | 27.0 | 28.0 | 29.0 | 30.0 | 31.0 | 32.0 | 33.0 | 34.0 | 35.0 | 36.0 | 37.0 | 38.0 | 39.0 | 40.0
50V | 100 | 89.2857 | 78.125 | 69.4444 | 62.5 | 56.8182 | 52.0833 | 48.0769 | 44.6429 | 41.6667 | 39.0625 | 36.7647 | 34.7222 | 32.8947 | 31.25 | 29.7619 | 28.4091 | 27.1739 | 26.0417 | 25 | 24.0385 | 23.1481 | 22.3214 | 21.5517 | 20.8333 | 20.1613 | 19.5312 | 18.9394 | 18.3824 | 17.8571 | 17.3611 | 16.8919 | 16.4474 | 16.0256 | 15.625
40V | 64 | 57.1429 | 50 | 44.4444 | 40 | 36.3636 | 33.3333 | 30.7692 | 28.5714 | 26.6667 | 25 | 23.5294 | 22.2222 | 21.0526 | 20 | 19.0476 | 18.1818 | 17.3913 | 16.6667 | 16 | 15.3846 | 14.8148 | 14.2857 | 13.7931 | 13.3333 | 12.9032 | 12.5 | 12.1212 | 11.7647 | 11.4286 | 11.1111 | 10.8108 | 10.5263 | 10.2564 | 10
30V | 36 | 32.1429 | 28.125 | 25 | 22.5 | 20.4545 | 18.75 | 17.3077 | 16.0714 | 15 | 14.0625 | 13.2353 | 12.5 | 11.8421 | 11.25 | 10.7143 | 10.2273 | 9.7826 | 9.375 | 9 | 8.6538 | 8.3333 | 8.0357 | 7.7586 | 7.5 | 7.2581 | 7.0312 | 6.8182 | 6.6176 | 6.4286 | 6.25 | 6.0811 | 5.9211 | 5.7692 | 5.625
24V | 23.04 | 20.5714 | 18 | 16 | 14.4 | 13.0909 | 12 | 11.0769 | 10.2857 | 9.6 | 9 | 8.4706 | 8 | 7.5789 | 7.2 | 6.8571 | 6.5455 | 6.2609 | 6 | 5.76 | 5.5385 | 5.3333 | 5.1429 | 4.9655 | 4.8 | 4.6452 | 4.5 | 4.3636 | 4.2353 | 4.1143 | 4 | 3.8919 | 3.7895 | 3.6923 | 3.6
12V | 5.76 | 5.1429 | 4.5 | 4 | 3.6 | 3.2727 | 3 | 2.7692 | 2.5714 | 2.4 | 2.25 | 2.1176 | 2 | 1.8947 | 1.8 | 1.7143 | 1.6364 | 1.5652 | 1.5 | 1.44 | 1.3846 | 1.3333 | 1.2857 | 1.2414 | 1.2 | 1.1613 | 1.125 | 1.0909 | 1.0588 | 1.0286 | 1 | 0.97297 | 0.94737 | 0.92308 | 0.9

## Slide 5: Efficiency
The problem with the previous analysis is it ignores efficiency
  It’s not ignored, it’s just 50%.
STANDARD/TYPE | VPSE | RCABLE | PPSE | PPD | EFFICIENCY
AF | 44V | 20 Ohms | 15.4W | 13W | 84%
AT | 50V | 12.5 Ohms | 30W | 25.5W | 85%
BT Type 3 | 50V | 6.25 Ohms | 60W | 51W | 85%
BT Type 4 | 52V | 6.25 Ohms | 91W | 71.3W | 78%
BT Type 4* | 52V | 6.25 Ohms | 100W | 75W | 75%
*802.3bt does not have a 100W PPSE mode, this is the theoretical max for demonstration purposes

## Slide 6: How does efficiency affect power delivered?
Chart: 65% Efficiency
| 6.25 | 12.5 | 20.0 | 40.0
12V | 5.2416 | 2.6208 | 1.638 | 0.819
24V | 20.9664 | 10.4832 | 6.552 | 3.276
30V | 32.76 | 16.38 | 10.2375 | 5.1187
40V | 58.24 | 29.12 | 18.2 | 9.1
50V | 91 | 45.5 | 28.4375 | 14.2188
52V | 98.4256 | 49.2128 | 30.758 | 15.379
Chart: 60% Efficiency
| 6.25 | 12.5 | 20.0 | 40.0
12V | 5.5296 | 2.7648 | 1.728 | 0.864
24V | 22.1184 | 11.0592 | 6.912 | 3.456
30V | 34.56 | 17.28 | 10.8 | 5.4
40V | 61.44 | 30.72 | 19.2 | 9.6
50V | 96 | 48 | 30 | 15
52V | 103.8336 | 51.9168 | 32.448 | 16.224
Chart: 70% Efficiency
| 6.25 | 12.5 | 20.0 | 40.0
12V | 4.8384 | 2.4192 | 1.512 | 0.756
24V | 19.3536 | 9.6768 | 6.048 | 3.024
30V | 30.24 | 15.12 | 9.45 | 4.725
40V | 53.76 | 26.88 | 16.8 | 8.4
50V | 84 | 42 | 26.25 | 13.125
52V | 90.8544 | 45.4272 | 28.392 | 14.196
Chart: 75% Efficiency
| 6.25 | 12.5 | 20.0 | 40.0
12V | 4.32 | 2.16 | 1.35 | 0.675
24V | 17.28 | 8.64 | 5.4 | 2.7
30V | 27 | 13.5 | 8.4375 | 4.2188
40V | 48 | 24 | 15 | 7.5
50V | 75 | 37.5 | 23.4375 | 11.7188
52V | 81.12 | 40.56 | 25.35 | 12.675

## Slide 7: How does efficiency affect power delivered?
Chart: 85% Efficiency
| 6.25 | 12.5 | 20.0 | 40.0
12V | 2.9376 | 1.4688 | 0.918 | 0.459
24V | 11.7504 | 5.8752 | 3.672 | 1.836
30V | 18.36 | 9.18 | 5.7375 | 2.8688
40V | 32.64 | 16.32 | 10.2 | 5.1
50V | 51 | 25.5 | 15.9375 | 7.9688
52V | 55.1616 | 27.5808 | 17.238 | 8.619
Chart: 95% Efficiency
| 6.25 | 12.5 | 20.0 | 40.0
12V | 1.0944 | 0.5472 | 0.342 | 0.171
24V | 4.3776 | 2.1888 | 1.368 | 0.684
30V | 6.84 | 3.42 | 2.1375 | 1.0688
40V | 12.16 | 6.08 | 3.8 | 1.9
50V | 19 | 9.5 | 5.9375 | 2.9687
52V | 20.5504 | 10.2752 | 6.422 | 3.211
Chart: 80% Efficiency
| 6.25 | 12.5 | 20.0 | 40.0
12V | 3.6864 | 1.8432 | 1.152 | 0.576
24V | 14.7456 | 7.3728 | 4.608 | 2.304
30V | 23.04 | 11.52 | 7.2 | 3.6
40V | 40.96 | 20.48 | 12.8 | 6.4
50V | 64 | 32 | 20 | 10
52V | 69.2224 | 34.6112 | 21.632 | 10.816
Chart: 90% Efficiency
| 6.25 | 12.5 | 20.0 | 40.0
12V | 2.0736 | 1.0368 | 0.648 | 0.324
24V | 8.2944 | 4.1472 | 2.592 | 1.296
30V | 12.96 | 6.48 | 4.05 | 2.025
40V | 23.04 | 11.52 | 7.2 | 3.6
50V | 36 | 18 | 11.25 | 5.625
52V | 38.9376 | 19.4688 | 12.168 | 6.084
Notes: Chart look very similar. The real difference is the magnitude on the Y axis.

## Slide 8: Efficiency
More realistic: PPD = VPSE2 / 6 * R
This yields an efficiency of about 80% and is good simple guide to estimate power delivered to a PD

## Slide 9: More Realistic Efficiency
Chart: PD power delivered
| 6.25 | 7.0 | 8.0 | 9.0 | 10.0 | 11.0 | 12.0 | 13.0 | 14.0 | 15.0 | 16.0 | 17.0 | 18.0 | 19.0 | 20.0 | 21.0 | 22.0 | 23.0 | 24.0 | 25.0 | 26.0 | 27.0 | 28.0 | 29.0 | 30.0 | 31.0 | 32.0 | 33.0 | 34.0 | 35.0 | 36.0 | 37.0 | 38.0 | 39.0 | 40.0
50V | 66.6667 | 59.5238 | 52.0833 | 46.2963 | 41.6667 | 37.8788 | 34.7222 | 32.0513 | 29.7619 | 27.7778 | 26.0417 | 24.5098 | 23.1481 | 21.9298 | 20.8333 | 19.8413 | 18.9394 | 18.1159 | 17.3611 | 16.6667 | 16.0256 | 15.4321 | 14.881 | 14.3678 | 13.8889 | 13.4409 | 13.0208 | 12.6263 | 12.2549 | 11.9048 | 11.5741 | 11.2613 | 10.9649 | 10.6838 | 10.4167
40V | 42.6667 | 38.0952 | 33.3333 | 29.6296 | 26.6667 | 24.2424 | 22.2222 | 20.5128 | 19.0476 | 17.7778 | 16.6667 | 15.6863 | 14.8148 | 14.0351 | 13.3333 | 12.6984 | 12.1212 | 11.5942 | 11.1111 | 10.6667 | 10.2564 | 9.8765 | 9.5238 | 9.1954 | 8.8889 | 8.6022 | 8.3333 | 8.0808 | 7.8431 | 7.619 | 7.4074 | 7.2072 | 7.0175 | 6.8376 | 6.6667
30V | 24 | 21.4286 | 18.75 | 16.6667 | 15 | 13.6364 | 12.5 | 11.5385 | 10.7143 | 10 | 9.375 | 8.8235 | 8.3333 | 7.8947 | 7.5 | 7.1429 | 6.8182 | 6.5217 | 6.25 | 6 | 5.7692 | 5.5556 | 5.3571 | 5.1724 | 5 | 4.8387 | 4.6875 | 4.5455 | 4.4118 | 4.2857 | 4.1667 | 4.0541 | 3.9474 | 3.8462 | 3.75
24V | 15.36 | 13.7143 | 12 | 10.6667 | 9.6 | 8.7273 | 8 | 7.3846 | 6.8571 | 6.4 | 6 | 5.6471 | 5.3333 | 5.0526 | 4.8 | 4.5714 | 4.3636 | 4.1739 | 4 | 3.84 | 3.6923 | 3.5556 | 3.4286 | 3.3103 | 3.2 | 3.0968 | 3 | 2.9091 | 2.8235 | 2.7429 | 2.6667 | 2.5946 | 2.5263 | 2.4615 | 2.4
12V | 3.84 | 3.4286 | 3 | 2.6667 | 2.4 | 2.1818 | 2 | 1.8462 | 1.7143 | 1.6 | 1.5 | 1.4118 | 1.3333 | 1.2632 | 1.2 | 1.1429 | 1.0909 | 1.0435 | 1 | 0.96 | 0.92308 | 0.88889 | 0.85714 | 0.82759 | 0.8 | 0.77419 | 0.75 | 0.72727 | 0.70588 | 0.68571 | 0.66667 | 0.64865 | 0.63158 | 0.61538 | 0.6
Notes: This is the chart for Vpse^2/6R. Result in an efficiency of about 79%.

## Slide 10: Conclusions
Need to keep VPSE higher, RCABLE lower.
Target worst case efficiency of about 80%.
12V VPSE is a tough target. Looking at less than 4W PPD.
24V can deliver about 10W over 10 ohms.
Can get significant power from 50V with a reasonable RCABLE (10 ohms is about 42W).