## Sheet1
This is primary parameter channel data for Cat6 channel with connectors having improved Return loss (equivalent to 4 dB improvement over Cat6 spec) . The channel topology is 4 connectors, solid, stranded, solid, stranded, solid, 9m = 1,1,5,1,1. 14m = 1,1,10,1,1. 19 m = 1,1,15,1,1 lengths according to the above description. The data is for short channels where NEXT and Return Loss are typically worst case. The data is not scaled. TIA TR 42.7 working group has agreed on the 14m (1,1,10,1,1) topology as representing the worst case short channel for modeling purposes. This data is conformant to predictions from modeling.
Near End
a
b
c
d
e
Far End
solid
flexible
flexible
solid
solid
C2
C1
CP
TO

## 9m_channel_Conn2
[62 empty] | Parameter | [8 empty] | Parameter
[62 empty] | Frequency | [8 empty] | Frequency
Parameter | Insertion loss Magnitude in dB | [7 empty] | NEXT loss near Magnitude in dB | [11 empty] | NEXT loss far Magnitude in dB | [11 empty] | Return loss nearMagnitude in dB | [7 empty] | Return loss farMagnitude in dB | [8 empty] | FEXT loss
Frequency | '45 | '45 | '12 | '12 | '36 | '36 | '78 | '78 | '12-45 | '12-45 | '36-45 | '36-45 | '45-78 | '45-78 | '12-36 | '12-36 | '12-78 | '12-78 | '36-78 | '36-78 | '12-45 | '12-45 | '36-45 | '36-45 | '45-78 | '45-78 | '12-36 | '12-36 | '12-78 | '12-78 | '36-78 | '36-78 | '45 | '45 | '12 | '12 | '36 | '36 | '78 | '78 | '45 | '45 | '12 | '12 | '36 | '36 | '78 | '78 |  | '12-45 | '36-45 | '45-78 | '12-36 | '12-78 | '36-78 | '45-12 | '45-36 | '78-45 | '36-12 | '78-12 | '78-36 |  | Pr1 PSNEXT | Pr2 PSNEXT | Pr3 PSNEXT | Pr4 PSNEXT | Pr1 PSNEXT | Pr2 PSNEXT | Pr3 PSNEXT | Pr4 PSNEXT |  | 12-1ELFEXT | 13-1ELFEXT | 14-1ELFEXT | 23-2ELFEXT | 24-2ELFEXT | 34-3ELFEXT | 12-2ELFEXT | 13-3ELFEXT | 14-4ELFEXT | 23-3ELFEXT | 24-4ELFEXT | 34-4ELFEXT | 21-1ELFEXT | 31-1ELFEXT | 41-1ELFEXT | 32-2ELFEXT | 42-2ELFEXT | 43-3ELFEXT | 21-2ELFEXT | 31-3ELFEXT | 41-4ELFEXT | 32-3ELFEXT | 42-4ELFEXT | 43-4ELFEXT
1 | -0.1827 | 0 | -0.1592 | 0 | -0.1788 | 0 | -0.1944 | 0 | -104.3972 | 102.1129 | -84.5383 | -119.5954 | -88.8275 | -113.1266 | -107.1053 | -68.2585 | -200 | -180 | -90.9939 | -133.5461 | -200 | -180 | -84.3871 | -116.5847 | -86.6 | -102.6481 | -99.5563 | -149.182 | -117.141 | 106.696 | -95.1065 | -123.7836 | -37.3018 | -27.088 | -35.0475 | -42.3351 | -37.9658 | -46.9483 | -34.0953 | -54.1703 | -35.6243 | -43.9637 | -34.319 | -49.329 | -34.8134 | 35.5007 | -35.9439 | -28.8188 | -85.932 | -92.893 | -78.1586 | -80.6195 | -100.2797 | -79.6312 | -85.4678 | -92.6006 | -78.2256 | -80.2217 | -105.7061 | -79.5733 | -81.2881 | 1 | -83.1307 | -102.5332 | -83.6332 | -86.7667 | -82.3438 | -99.4812 | -83.9138 | -86.0236 | 1 | -92.4179 | -78.0429 | -80.4368 | -100.1205 | -79.472 | -85.289 | -92.4414 | -78.0468 | -80.4251 | -100.1009 | -79.4368 | -85.2734 | -92.7103 | -77.9759 | -80.039 | -105.5469 | -79.4141 | -81.1093 | -92.7338 | -77.9798 | -80.0273 | -105.5273 | -79.3789 | -81.0937
2 | -0.2251 | 0 | -0.2016 | 0 | -0.2368 | 0 | -0.2602 | 0 | -106.8293 | -72.0007 | -79.9891 | -137.58 | -81.0863 | -125.8458 | -106.0236 | 109.8384 | -108.3896 | 142.8764 | -88.8844 | -168.5937 | -100.9996 | -47.8123 | -80.4751 | -133.2106 | -80.5907 | -107.4344 | -95.1987 | 149.3371 | -200 | 0 | -90.5286 | -131.1711 | -29.0977 | 13.9842 | -29.9794 | 8.3898 | -29.4996 | 14.3365 | -30.5845 | 5.2246 | -29.8707 | 10.3162 | -30.1535 | 7.3916 | -26.7673 | 23.649 | -29.1567 | 9.0058 | -80.2161 | -84.7435 | -72.4779 | -75.1458 | -97.3099 | -74.263 | -80.1743 | -84.5337 | -72.3071 | -75.1743 | -96.6587 | -74.2915 | -74.4474 | 2 | -77.4878 | -102.2023 | -79.4527 | -80.4123 | -77.5028 | -94.1848 | -79.9348 | -80.1711 | 2 | -84.3086 | -72.082 | -74.9207 | -97.1083 | -74.0614 | -79.9375 | -84.3321 | -72.0703 | -74.8856 | -97.0731 | -74.0028 | -79.9141 | -84.5184 | -72.2528 | -74.9492 | -96.4571 | -74.0899 | -74.2106 | -84.5419 | -72.2411 | -74.9141 | -96.4219 | -74.0313 | -74.1872
3 | -0.2755 | 0 | -0.2521 | 0 | -0.2755 | 0 | -0.2755 | 0 | -100.3811 | -167.1229 | -78.0956 | -154.7244 | -77.7065 | -152.8422 | -102.1619 | 42.4796 | -107.0102 | 119.7918 | -85.9987 | 169.7103 | -94.609 | -67.7929 | -78.5202 | -147.0298 | -77.8548 | -122.7284 | -92.1411 | 106.9654 | -101.2415 | -53.2713 | -89.6409 | -110.7389 | -26.9807 | -5.9383 | -27.8109 | -8.1722 | -27.0169 | -5.7784 | -28.0895 | -10.8093 | -27.515 | -6.2227 | -27.7532 | -8.9234 | -25.2459 | -2.0865 | -27.3693 | -9.9814 | -76.9813 | -80.0047 | -68.9969 | -71.9383 | -95.0438 | -71.161 | -76.8576 | -80.1857 | -68.8966 | -71.9669 | -94.4865 | -71.0724 | -70.8023 | 3 | -74.8742 | -97.6374 | -77.4287 | -77.102 | -75.1154 | -89.8634 | -78.0253 | -77.5574 | 3 | -79.9102 | -68.6211 | -71.6628 | -94.7917 | -70.9089 | -76.5821 | -79.9336 | -68.6211 | -71.6628 | -94.7683 | -70.8855 | -76.5821 | -79.7292 | -68.7214 | -71.6914 | -94.2344 | -70.8203 | -70.5268 | -79.7526 | -68.7214 | -71.6914 | -94.211 | -70.7969 | -70.5268
4 | -0.295 | 0 | -0.2833 | 0 | -0.3106 | 0 | -0.3301 | 0 | -93.8193 | 154.8555 | -77.3822 | -174.1948 | -76.2805 | -176.4269 | -101.6225 | 5.8175 | -98.4578 | 101.0045 | -84.494 | 144.6332 | -92.9844 | -98.4485 | -77.7616 | -159.7295 | -76.5132 | -135.6862 | -89.6781 | 82.1137 | -97.6052 | -53.7345 | -85.9839 | -102.6027 | -26.7772 | -24.7596 | -27.7267 | -25.5222 | -26.7767 | -25.2522 | -27.776 | -29.5068 | -27.2057 | -22.9973 | -27.6042 | -27.0992 | -25.4679 | -23.867 | -27.5471 | -28.7981 | -74.3602 | -77.0399 | -66.4813 | -69.6805 | -92.6805 | -68.7977 | -74.459 | -76.7989 | -66.4747 | -69.6153 | -93.4981 | -68.92 | -68.1573 | 4 | -73.7433 | -92.0309 | -76.5968 | -75.6474 | -74.0268 | -87.5609 | -76.9162 | -76.0182 | 4 | -76.5039 | -66.1797 | -69.3855 | -92.3972 | -68.5144 | -74.1484 | -76.5156 | -66.1641 | -69.3504 | -92.3699 | -68.4676 | -74.1289 | -76.7449 | -66.1863 | -69.3203 | -93.2148 | -68.6367 | -67.8467 | -76.7566 | -66.1707 | -69.2852 | -93.1875 | -68.5899 | -67.8272
5 | -0.3418 | 0 | -0.3301 | 0 | -0.3535 | 0 | -0.3418 | 0 | -90.3898 | 137.5145 | -77.581 | 168.9786 | -75.3975 | 155.5933 | -95.5175 | -63.5141 | -96.9526 | 81.4243 | -83.1474 | 119.1567 | -90.7822 | -117.1778 | -78.1421 | -168.3884 | -76.1471 | -144.524 | -88.4276 | 74.9561 | -94.3154 | -83.099 | -83.2575 | -105.3144 | -27.504 | -41.389 | -28.6408 | -42.085 | -27.5839 | -42.8075 | -28.5141 | -48.2013 | -27.9675 | -38.5175 | -28.5908 | -44.4116 | -26.7686 | -43.2595 | -28.8793 | -46.6337 | -72.7119 | -74.8642 | -64.622 | -67.8681 | -90.9501 | -67.0088 | -72.6621 | -74.7754 | -64.6035 | -67.8496 | -92.0137 | -67.123 | -66.3092 | 5 | -73.2583 | -88.5494 | -76.4629 | -74.6976 | -73.9301 | -85.7812 | -76.6759 | -75.3201 | 5 | -74.4336 | -64.2617 | -67.5263 | -90.62 | -66.6787 | -72.3086 | -74.4453 | -64.25 | -67.5263 | -90.5966 | -66.667 | -72.3203 | -74.5224 | -64.2802 | -67.5078 | -91.6836 | -66.7929 | -65.9557 | -74.5341 | -64.2685 | -67.5078 | -91.6602 | -66.7812 | -65.9674
6 | -0.3886 | 0 | -0.3652 | 0 | -0.4003 | 0 | -0.3769 | 0 | -87.9802 | 115.5754 | -79.2413 | 149.3943 | -75.5894 | 129.6041 | -90.9235 | -98.8555 | -92.4915 | 76.8265 | -81.5854 | 103.239 | -89.4491 | -137.6877 | -79.5241 | -175.9581 | -76.9391 | -151.9409 | -87.2166 | 69.2592 | -91.9817 | -98.7129 | -79.7003 | -113.8286 | -28.9083 | -55.7578 | -30.5496 | -57.5274 | -29.1121 | -58.1135 | -30.1705 | -66.8945 | -29.4128 | -50.8072 | -30.6515 | -60.5311 | -28.9727 | -59.6586 | -31.4451 | -63.0278 | -71.3487 | -73.0909 | -63.1651 | -66.4698 | -89.4346 | -65.5518 | -71.1425 | -73.0956 | -63.1113 | -66.4042 | -90.2871 | -65.6621 | -64.7932 | 6 | -73.8605 | -85.2812 | -77.0644 | -74.5451 | -74.8775 | -84.3568 | -76.2396 | -75.0055 | 6 | -72.707 | -62.7227 | -66.0812 | -89.0694 | -65.1866 | -70.7422 | -72.7304 | -62.711 | -66.0929 | -89.0343 | -65.1749 | -70.7656 | -72.7023 | -62.7765 | -66.0156 | -89.9219 | -65.2969 | -64.3929 | -72.7257 | -62.7648 | -66.0273 | -89.8868 | -65.2852 | -64.4163
7 | -0.4121 | 0 | -0.4238 | 0 | -0.4355 | 0 | -0.4238 | 0 | -85.964 | 101.7247 | -82.509 | 121.2719 | -76.1087 | 95.3451 | -87.345 | -125.726 | -91.796 | 65.0142 | -80.8847 | 76.5624 | -88.9642 | -150.6619 | -82.5057 | -175.7166 | -78.062 | -146.1805 | -86.164 | 58.9727 | -89.7669 | -116.8296 | -78.7901 | -123.9176 | -30.9163 | -66.2553 | -33.6896 | -70.994 | -31.5517 | -70.467 | -32.8972 | -86.3232 | -31.4695 | -59.104 | -34.1293 | -74.7607 | -32.3444 | -70.4004 | -36.0073 | -77.8632 | -69.9153 | -71.6653 | -61.884 | -65.2356 | -87.9543 | -64.3059 | -69.9668 | -71.6738 | -61.7949 | -65.2285 | -88.9355 | -64.3574 | -63.5547 | 7 | -74.8622 | -82.9783 | -78.0655 | -74.7734 | -76.4763 | -83.2392 | -76.7269 | -75.2444 | 7 | -71.2617 | -61.3828 | -64.8235 | -87.5305 | -63.8821 | -69.5313 | -71.25 | -61.3594 | -64.8118 | -87.5188 | -63.8821 | -69.543 | -71.2532 | -61.4719 | -64.8164 | -88.5117 | -63.9336 | -63.1192 | -71.2415 | -61.4485 | -64.8047 | -88.5 | -63.9336 | -63.1309
8 | -0.459 | 0 | -0.4707 | 0 | -0.4707 | 0 | -0.459 | 0 | -85.3983 | 80.1421 | -89.6459 | 59.3344 | -76.0614 | 55.1305 | -83.9661 | -150.1951 | -88.7032 | 51.4703 | -81.1052 | 55.3982 | -88.3811 | -161.6889 | -84.6251 | -141.2706 | -78.6127 | -127.8428 | -85.4501 | 65.2471 | -87.6423 | -137.525 | -77.3834 | -133.2787 | -33.388 | -69.9701 | -39.2864 | -79.1145 | -34.7362 | -75.3446 | -37.2734 | -109.5293 | -33.6288 | -58.8482 | -40.5134 | -82.3064 | -37.0629 | -67.1816 | -47.1187 | -77.0299 | -68.9857 | -70.3958 | -60.8138 | -64.1888 | -87.0247 | -63.2474 | -68.9199 | -70.498 | -60.7363 | -64.1816 | -87.0527 | -63.2636 | -62.4257 | 8 | -75.4157 | -80.8379 | -78.9108 | -74.7022 | -77.2903 | -82.2014 | -76.0968 | -74.7171 | 8 | -70.039 | -60.2773 | -63.7298 | -86.554 | -62.7767 | -68.4492 | -70.0273 | -60.2656 | -63.7298 | -86.554 | -62.7884 | -68.4609 | -69.9368 | -60.3548 | -63.7226 | -86.582 | -62.7929 | -61.955 | -69.9251 | -60.3431 | -63.7226 | -86.582 | -62.8046 | -61.9667
9 | -0.498 | 0 | -0.4863 | 0 | -0.5097 | 0 | -0.498 | 0 | -85.064 | 63.5958 | -83.2052 | -35.6795 | -75.8189 | 13.136 | -81.5595 | -175.464 | -87.9203 | 37.9687 | -80.7761 | 22.7757 | -89.1655 | -179.4399 | -80.0905 | -111.1209 | -75.6622 | -112.6334 | -84.1541 | 59.0477 | -86.4101 | -153.2592 | -76.8921 | -142.0735 | -35.1952 | -63.29 | -50.0605 | -28.1666 | -37.9471 | -64.0725 | -45.2147 | -154.4363 | -34.7121 | -51.5808 | -50.0373 | 0.4738 | -39.5792 | -34.1465 | -42.3593 | 50.9706 | -68.0794 | -69.2318 | -59.8373 | -63.2943 | -85.4818 | -62.2943 | -67.9316 | -69.2988 | -59.7948 | -63.2636 | -86.0058 | -62.3222 | -61.4059 | 9 | -74.6744 | -79.3132 | -76.9622 | -74.417 | -74.1843 | -81.3432 | -74.6737 | -73.0198 | 9 | -68.8008 | -59.2968 | -62.7963 | -84.9955 | -61.808 | -67.4219 | -68.8125 | -59.2851 | -62.7963 | -84.9721 | -61.7963 | -67.4336 | -68.7338 | -59.3393 | -62.7656 | -85.5195 | -61.8359 | -60.8962 | -68.7455 | -59.3276 | -62.7656 | -85.4961 | -61.8242 | -60.9079
10 | -0.5565 | 0 | -0.533 | 0 | -0.533 | 0 | -0.5096 | 0 | -86.2536 | 45.9372 | -76.2187 | -68.1345 | -73.6496 | -27.4615 | -79.5013 | 162.8941 | -85.1401 | 23.8801 | -81.5775 | -3.1049 | -90.2306 | 171.3287 | -75.1546 | -110.9562 | -72.5752 | -108.8123 | -81.927 | 52.9597 | -85.9341 | -169.8636 | -77.0979 | -152.416 | -34.866 | -53.9029 | -40.4311 | 34.4054 | -37.71 | -44.2153 | -44.277 | 91.7991 | -33.7864 | -45.6278 | -39.0265 | 33.3325 | -36.0712 | -17.44 | -34.8291 | 41.4073 | -67.1653 | -68.1614 | -58.9895 | -62.4817 | -84.6263 | -61.5208 | -67.1697 | -68.3572 | -58.9588 | -62.5018 | -84.7596 | -61.5018 | -60.4876 | 10 | -71.5857 | -77.7863 | -73.7617 | -72.7432 | -70.6181 | -80.037 | -72.484 | -71.1167 | 10 | -67.8007 | -58.4023 | -61.9252 | -84.0933 | -60.9878 | -66.6367 | -67.8242 | -58.4258 | -61.9721 | -84.0933 | -61.0112 | -66.6601 | -67.6049 | -58.433 | -61.9453 | -84.2266 | -60.9688 | -59.9546 | -67.6284 | -58.4565 | -61.9922 | -84.2266 | -60.9922 | -59.978
11 | -0.5681 | 0 | -0.5564 | 0 | -0.5564 | 0 | -0.5564 | 0 | -87.7258 | 22.4679 | -72.3129 | -91.2648 | -71.3412 | -61.2732 | -78.1583 | 143.2045 | -84.0676 | 10.773 | -82.1778 | -35.6608 | -90.8881 | 173.4695 | -71.5847 | -119.6216 | -69.6857 | -114.7777 | -80.2248 | 44.2776 | -85.399 | 175.8811 | -77.5118 | -157.7549 | -33.0985 | -55.0252 | -35.264 | 28.1733 | -35.1735 | -41.6684 | -37.958 | 55.7665 | -32.1797 | -51.1976 | -34.5384 | 23.9034 | -33.1464 | -25.635 | -31.4888 | 27.4648 | -66.3645 | -67.177 | -58.1575 | -61.7434 | -84.0481 | -60.7903 | -66.4158 | -67.4627 | -58.1619 | -61.7478 | -83.408 | -60.7478 | -59.5577 | 11 | -68.7345 | -76.8007 | -70.9665 | -70.788 | -67.502 | -78.7958 | -70.1477 | -68.9237 | 11 | -66.8946 | -57.5938 | -61.1753 | -83.4917 | -60.2339 | -65.8594 | -66.9063 | -57.6055 | -61.187 | -83.4917 | -60.2339 | -65.8594 | -66.6089 | -57.5894 | -61.1797 | -82.8516 | -60.1914 | -59.0013 | -66.6206 | -57.6011 | -61.1914 | -82.8516 | -60.1914 | -59.0013
12 | -0.5916 | 0 | -0.5564 | 0 | -0.5916 | 0 | -0.5682 | 0 | -91.9117 | -4.9367 | -69.4659 | -111.0093 | -69.3001 | -91.3994 | -77.0765 | 124.3688 | -83.3673 | -9.1094 | -81.3315 | -72.397 | -92.19 | -172.2668 | -68.9354 | -133.3446 | -67.5628 | -125.0101 | -79.0814 | 30.5768 | -84.9626 | 157.7065 | -78.0892 | -154.2158 | -31.2761 | -66.1535 | -32.6507 | 15.739 | -33.1831 | -54.5041 | -34.9754 | 35.0007 | -30.7114 | -64.4145 | -32.2858 | 10.8765 | -31.6286 | -43.5719 | -29.6309 | 12.6541 | -65.6576 | -66.2826 | -57.4388 | -61.0716 | -83.3568 | -60.1771 | -65.6736 | -66.5682 | -57.4549 | -61.0643 | -82.3728 | -60.0877 | -58.7569 | 12 | -66.3598 | -76.0461 | -68.5372 | -68.8789 | -65.1762 | -77.9185 | -68.0782 | -67.1222 | 12 | -65.9766 | -56.8633 | -60.48 | -82.8004 | -59.6207 | -65.082 | -66.0118 | -56.8633 | -60.5034 | -82.7652 | -59.6089 | -65.1054 | -65.691 | -56.8472 | -60.4727 | -81.8164 | -59.5313 | -58.1653 | -65.7262 | -56.8472 | -60.4961 | -81.7812 | -59.5195 | -58.1887
13 | -0.6385 | 0 | -0.6034 | 0 | -0.6268 | 0 | -0.5799 | 0 | -99.6266 | -85.7389 | -67.3793 | -130.0058 | -67.7193 | -116.4633 | -76.8401 | 105.5047 | -82.5712 | -21.5509 | -79.3952 | -111.8847 | -89.7909 | -166.7363 | -67.0582 | -146.9005 | -66.0376 | -136.6366 | -78.4531 | 13.8505 | -85.4157 | 145.57 | -77.733 | -148.0809 | -29.8585 | -83.5565 | -31.2815 | 2.4061 | -31.8209 | -73.233 | -33.4914 | 17.843 | -29.5795 | -83.14 | -31.2103 | -3.003 | -30.8646 | -66.4179 | -28.6712 | -2.5322 | -64.9897 | -65.4818 | -56.7553 | -60.4623 | -82.9311 | -59.6147 | -65.076 | -65.7792 | -56.8221 | -60.537 | -81.1971 | -59.5487 | -57.9836 | 13 | -64.5343 | -75.7935 | -66.6749 | -67.3026 | -63.4975 | -77.3989 | -66.4206 | -65.7065 | 13 | -65.1407 | -56.1836 | -59.8238 | -82.3277 | -59.0113 | -64.4492 | -65.1758 | -56.1953 | -59.8824 | -82.3043 | -59.0348 | -64.4961 | -64.8433 | -56.1168 | -59.8985 | -80.5937 | -58.9453 | -57.3568 | -64.8784 | -56.1285 | -59.9571 | -80.5703 | -58.9688 | -57.4037
14 | -0.6347 | 0 | -0.623 | 0 | -0.6581 | 0 | -0.623 | 0 | -89.3004 | -163.6485 | -65.9621 | -148.5744 | -66.4593 | -140.6849 | -77.2396 | 90.7162 | -82.1332 | -37.8539 | -76.9905 | -144.9584 | -86.5867 | -165.5862 | -65.6515 | -161.9897 | -64.808 | -149.3543 | -78.3951 | -0.7304 | -86.3107 | 136.2796 | -76.7864 | -143.6627 | -28.6995 | -104.037 | -30.7835 | -11.0777 | -30.8048 | -95.9897 | -32.9826 | 2.2302 | -28.741 | -104.5254 | -31 | -16.2792 | -30.5076 | -93.6171 | -28.4097 | -17.9363 | -64.3648 | -64.7554 | -56.1108 | -59.896 | -82.521 | -59.1226 | -64.4628 | -65.0605 | -56.205 | -59.9589 | -80.5605 | -59.0058 | -57.308 | 14 | -63.1827 | -75.8211 | -65.3422 | -65.9844 | -62.1832 | -77.2116 | -65.1201 | -64.5122 | 14 | -64.4258 | -55.5703 | -59.2613 | -81.898 | -58.4996 | -63.8047 | -64.4375 | -55.5469 | -59.273 | -81.8629 | -58.4996 | -63.8398 | -64.1207 | -55.4761 | -59.3242 | -79.9375 | -58.3828 | -56.6499 | -64.1324 | -55.4527 | -59.3359 | -79.9024 | -58.3828 | -56.685
15 | -0.7051 | 0 | -0.6465 | 0 | -0.6816 | 0 | -0.6465 | 0 | -83.6513 | 172.4785 | -64.9394 | -166.647 | -65.5912 | -164.4994 | -77.8659 | 73.427 | -81.7651 | -56.0275 | -74.9701 | -170.0311 | -84.0012 | -172.4925 | -64.7606 | -177.3912 | -64.0982 | -161.2437 | -78.8868 | -19.1878 | -86.7848 | 128.8651 | -75.0304 | -141.92 | -27.739 | -126.7372 | -30.9607 | -24.7388 | -29.9479 | -121.8272 | -33.3258 | -11.8228 | -27.9962 | -129.0311 | -31.436 | -29.688 | -30.1518 | -123.8727 | -28.6878 | -32.8217 | -63.8375 | -64.1422 | -55.5601 | -59.3336 | -82.6969 | -58.65 | -63.8496 | -64.3809 | -55.7246 | -59.3809 | -80.0879 | -58.4981 | -56.6988 | 15 | -62.2115 | -75.6352 | -64.3314 | -65.024 | -61.3827 | -77.2129 | -64.2197 | -63.7396 | 15 | -63.6758 | -55.0195 | -58.6285 | -82.0504 | -58.0035 | -63.168 | -63.7344 | -55.043 | -58.6871 | -82.0153 | -58.0035 | -63.2031 | -63.4371 | -54.855 | -58.6758 | -79.4414 | -57.8516 | -56.0172 | -63.4957 | -54.8785 | -58.7344 | -79.4063 | -57.8516 | -56.0523
16 | -0.7285 | 0 | -0.67 | 0 | -0.7285 | 0 | -0.6582 | 0 | -80.2474 | 153.0691 | -64.3361 | 175.5152 | -65.1059 | 174.7451 | -79.5324 | 63.0735 | -81.7995 | -73.4406 | -73.1447 | 164.2977 | -81.3226 | 173.4059 | -64.1935 | 167.1794 | -63.807 | -174.1192 | -80.6231 | -37.8081 | -88.8455 | 125.074 | -73.0505 | -148.8411 | -26.8994 | -150.0269 | -31.8144 | -37.4489 | -29.003 | -148.5133 | -34.3071 | -24.7968 | -27.2549 | -153.9965 | -32.5684 | -42.2629 | -29.4678 | -155.1005 | -29.5862 | -47.7 | -63.3297 | -63.568 | -55.029 | -58.8297 | -83.2048 | -58.2047 | -63.334 | -63.8379 | -55.2207 | -58.8653 | -79.7246 | -58.041 | -56.2027 | 16 | -61.6335 | -75.6558 | -63.6848 | -64.3926 | -60.9456 | -77.6089 | -63.5757 | -63.3064 | 16 | -63.1094 | -54.4922 | -58.1012 | -82.5348 | -57.5347 | -62.6055 | -63.1679 | -54.4922 | -58.1715 | -82.4763 | -57.5465 | -62.6758 | -62.8395 | -54.3005 | -58.1368 | -79.0546 | -57.371 | -55.4742 | -62.898 | -54.3005 | -58.2071 | -78.9961 | -57.3828 | -55.5445
17 | -0.752 | 0 | -0.6817 | 0 | -0.752 | 0 | -0.6934 | 0 | -77.6978 | 135.6451 | -64.0666 | 157.8296 | -64.8059 | 152.3651 | -82.2678 | 59.1394 | -82.3451 | -89.0215 | -71.762 | 143.6158 | -79.5628 | 159.1111 | -63.9587 | 152.0554 | -63.78 | 172.9515 | -83.5107 | -59.927 | -88.7916 | 131.9422 | -71.4366 | -157.9387 | -26.1474 | -173.6873 | -33.4163 | -49.3477 | -28.1673 | -175.0649 | -36.3402 | -35.2807 | -26.4975 | -178.8821 | -34.4636 | -53.0793 | -28.4937 | 174.4948 | -31.1764 | -62.0746 | -62.8493 | -63.072 | -54.5368 | -58.3103 | -83.0759 | -57.7595 | -62.7559 | -63.2168 | -54.7481 | -58.3575 | -79.7129 | -57.5723 | -55.6988 | 17 | -61.3093 | -75.4135 | -63.3289 | -63.9452 | -60.8 | -77.7377 | -63.2039 | -63.0808 | 17 | -62.4648 | -53.9961 | -57.5583 | -82.3942 | -57.0778 | -62.0039 | -62.5351 | -53.9961 | -57.6169 | -82.3239 | -57.0661 | -62.0625 | -62.32 | -53.7848 | -57.6055 | -79.0312 | -56.8906 | -54.9468 | -62.3903 | -53.7848 | -57.6641 | -78.9609 | -56.8789 | -55.0054
18 | -0.7754 | 0 | -0.7208 | 0 | -0.7754 | 0 | -0.7169 | 0 | -76.0095 | 121.1959 | -64.1149 | 140.494 | -64.8452 | 130.6442 | -85.5422 | 71.3702 | -83.422 | -106.9827 | -70.7209 | 122.9696 | -78.2838 | 142.1919 | -64.1938 | 136.9429 | -64.1265 | 161.9506 | -91.5771 | -85.405 | -88.7258 | 141.3141 | -70.5679 | -171.2885 | -25.569 | 163.7208 | -35.8733 | -58.547 | -27.3458 | 160.3284 | -39.2603 | -41.6734 | -25.9232 | 156.6874 | -37.2786 | -58.0939 | -27.5099 | 146.6471 | -33.8277 | -74.9661 | -62.4392 | -62.615 | -54.1072 | -57.8416 | -83.4509 | -57.3338 | -62.3614 | -62.7442 | -54.3379 | -57.8575 | -79.5528 | -57.1348 | -55.3238 | 18 | -61.3049 | -74.8942 | -63.2312 | -63.7991 | -61.0665 | -77.7255 | -63.2867 | -63.2261 | 18 | -61.9688 | -53.5625 | -57.0662 | -82.7301 | -56.613 | -61.586 | -62.0234 | -53.5625 | -57.1247 | -82.6755 | -56.6169 | -61.6445 | -61.8396 | -53.3318 | -57.0821 | -78.832 | -56.414 | -54.5484 | -61.8942 | -53.3318 | -57.1406 | -78.7774 | -56.4179 | -54.6069
19 | -0.7872 | 0 | -0.7442 | 0 | -0.7872 | 0 | -0.7169 | 0 | -74.7701 | 107.3973 | -64.6136 | 122.3062 | -65.2925 | 107.7929 | -85.6589 | 104.7934 | -84.8782 | -131.6448 | -69.7072 | 102.9945 | -77.0502 | 126.0853 | -64.8214 | 121.0805 | -64.8684 | 152.2255 | -91.7975 | 121.1919 | -86.4052 | 139.397 | -69.6649 | 172.9922 | -25.2338 | 141.3623 | -39.6817 | -60.3665 | -26.7667 | 136.9262 | -43.2573 | -32.8388 | -25.3905 | 134.0317 | -41.5395 | -54.4565 | -26.6153 | 122.0022 | -38.065 | -86.4351 | -62.0252 | -62.1893 | -53.6502 | -57.3807 | -83.7088 | -56.8846 | -61.9591 | -62.2169 | -53.9239 | -57.3848 | -79.3184 | -56.6661 | -54.9566 | 19 | -61.7094 | -74.0548 | -63.4166 | -63.9163 | -61.7058 | -76.445 | -63.5834 | -63.6025 | 19 | -61.4297 | -53.1367 | -56.5935 | -82.9646 | -56.1404 | -61.1719 | -61.4727 | -53.1367 | -56.6638 | -82.9216 | -56.1677 | -61.2422 | -61.4021 | -52.863 | -56.5976 | -78.5742 | -55.9219 | -54.1694 | -61.4451 | -52.863 | -56.6679 | -78.5312 | -55.9492 | -54.2397
20 | -0.8224 | 0 | -0.7794 | 0 | -0.8341 | 0 | -0.7638 | 0 | -73.9221 | 94.2047 | -65.5728 | 104.0159 | -65.4628 | 87.0357 | -81.2403 | 124.2802 | -87.9312 | -159.9739 | -69.8956 | 79.6802 | -76.3254 | 108.0141 | -65.9285 | 106.9594 | -65.8657 | 142.1199 | -82.0898 | 87.7921 | -83.942 | 133.5122 | -69.7686 | 158.5095 | -25.1877 | 120.0562 | -44.406 | -38.0297 | -26.4671 | 114.8042 | -45.3628 | 1.986 | -25.2616 | 112.0277 | -44.4813 | -24.2545 | -26.1334 | 98.93 | -46.1347 | -82.5739 | -61.6855 | -61.7753 | -53.287 | -56.9355 | -83.0878 | -56.4862 | -61.6075 | -61.7677 | -53.5607 | -56.9161 | -79.045 | -56.2403 | -54.687 | 20 | -62.2044 | -73.0402 | -64.1217 | -64.1083 | -62.6943 | -74.7469 | -64.3532 | -64.3346 | 20 | -60.9453 | -52.7383 | -56.1131 | -82.3084 | -55.7068 | -60.7734 | -60.9883 | -52.7266 | -56.1717 | -82.2537 | -55.7224 | -60.8437 | -60.9529 | -52.4646 | -56.0937 | -78.2656 | -55.4609 | -53.8529 | -60.9959 | -52.4529 | -56.1523 | -78.2109 | -55.4765 | -53.9232
21 | -0.8381 | 0 | -0.7795 | 0 | -0.8225 | 0 | -0.7795 | 0 | -73.5884 | 82.4624 | -67.0336 | 84.8364 | -67.005 | 60.2284 | -77.5649 | 119.0496 | -92.6047 | 159.7622 | -69.3434 | 61.9229 | -75.6926 | 90.3278 | -67.6479 | 92.3203 | -67.0877 | 135.4004 | -77.8179 | 67.0298 | -83.1707 | 127.0802 | -70.511 | 143.8281 | -25.549 | 99.1476 | -43.2261 | 7.5768 | -26.5896 | 93.8196 | -41.9757 | 26.2064 | -25.532 | 90.9484 | -42.1725 | 5.3793 | -26.1359 | 77.6734 | -47.5448 | 15.2889 | -61.3456 | -61.33 | -52.9237 | -56.5253 | -82.0878 | -56.037 | -61.2365 | -61.2053 | -53.1779 | -56.4514 | -78.6506 | -55.76 | -54.3593 | 21 | -63.5551 | -72.0876 | -64.7909 | -65.0008 | -64.0409 | -73.1598 | -65.5705 | -65.3872 | 21 | -60.3672 | -52.3398 | -55.6872 | -81.3083 | -55.2575 | -60.414 | -60.4258 | -52.3554 | -55.7458 | -81.2653 | -55.2575 | -60.457 | -60.4919 | -52.0856 | -55.6133 | -77.8711 | -54.9805 | -53.5368 | -60.5505 | -52.1012 | -55.6719 | -77.8281 | -54.9805 | -53.5798
22 | -0.846 | 0 | -0.803 | 0 | -0.846 | 0 | -0.7874 | 0 | -73.4863 | 72.6813 | -69.4231 | 63.2431 | -68.0384 | 34.33 | -74.7971 | 111.3671 | -92.6838 | 84.5248 | -70.1885 | 39.3173 | -75.2642 | 75.5782 | -70.5181 | 81.0342 | -68.6098 | 130.3155 | -74.7263 | 48.1282 | -81.5931 | 116.9137 | -72.1021 | 130.547 | -26.5202 | 78.2463 | -38.9587 | 15.7834 | -27.3524 | 73.4667 | -39.0999 | 25.2143 | -26.353 | 69.6377 | -38.9842 | 10.0069 | -26.7253 | 57.1586 | -39.2867 | 23.2702 | -61.0058 | -60.916 | -52.5683 | -56.1113 | -80.6074 | -55.58 | -60.9045 | -60.7561 | -52.803 | -56.01 | -78.3225 | -55.3538 | -54.0939 | 22 | -65.0016 | -71.0522 | -66.1423 | -65.9622 | -65.9136 | -71.5264 | -67.3503 | -66.8553 | 22 | -59.9101 | -51.957 | -55.2653 | -79.8044 | -54.777 | -60.0585 | -59.9531 | -51.957 | -55.3239 | -79.7614 | -54.7926 | -60.1171 | -60.07 | -51.7223 | -55.164 | -77.5195 | -54.5508 | -53.2479 | -60.113 | -51.7223 | -55.2226 | -77.4765 | -54.5664 | -53.3065
23 | -0.846 | 0 | -0.8226 | 0 | -0.8694 | 0 | -0.8265 | 0 | -73.5537 | 63.6731 | -73.2432 | 37.069 | -69.503 | 3.5346 | -72.6869 | 100.583 | -88.5439 | 44.2342 | -71.2675 | 15.8332 | -75.0744 | 59.0456 | -75.219 | 79.8406 | -70.212 | 132.7074 | -72.6724 | 31.9635 | -81.2531 | 107.7932 | -74.7386 | 116.7554 | -28.3712 | 56.858 | -36.3147 | 10.5066 | -28.9461 | 53.5714 | -37.3652 | 17.9056 | -28.0929 | 48.5679 | -37.3412 | 4.8708 | -28.2531 | 36.9472 | -35.8677 | 12.5254 | -60.6582 | -60.4355 | -52.2402 | -55.7793 | -79.166 | -55.1777 | -60.5687 | -60.2874 | -52.3968 | -55.678 | -77.5726 | -54.971 | -53.7932 | 23 | -66.9115 | -70.0269 | -67.5463 | -67.2536 | -68.0579 | -70.3327 | -69.2923 | -68.6546 | 23 | -59.4414 | -51.5508 | -54.9333 | -78.3434 | -54.3551 | -59.6993 | -59.4648 | -51.5274 | -54.9528 | -78.2966 | -54.3512 | -59.7422 | -59.5895 | -51.3942 | -54.832 | -76.75 | -54.1484 | -52.9238 | -59.6129 | -51.3708 | -54.8515 | -76.7032 | -54.1445 | -52.9667
24 | -0.8851 | 0 | -0.8499 | 0 | -0.8695 | 0 | -0.8382 | 0 | -73.6888 | 55.0345 | -79.372 | -16.2443 | -71.2206 | -33.2098 | -71.1406 | 87.704 | -83.644 | 8.5159 | -72.7387 | -11.0756 | -75.2328 | 43.27 | -80.3367 | 125.5871 | -70.8901 | 140.6603 | -71.1288 | 13.9446 | -80.7515 | 95.4481 | -78.9795 | 111.8892 | -31.7763 | 32.3464 | -34.8198 | 0.0433 | -32.0948 | 32.2898 | -36.9106 | 7.8251 | -31.127 | 24.1553 | -36.6107 | -3.0041 | -31.0894 | 14.3752 | -33.8915 | -1.0957 | -60.334 | -59.8965 | -51.9278 | -55.4668 | -78.1621 | -54.7442 | -60.2562 | -59.807 | -52.0492 | -55.4007 | -76.8851 | -54.5843 | -53.4183 | 24 | -68.8665 | -69.0661 | -68.4868 | -68.76 | -69.1831 | -69.3744 | -70.043 | -69.8916 | 24 | -58.9219 | -51.1641 | -54.5817 | -77.3122 | -53.8943 | -59.3867 | -58.9571 | -51.1797 | -54.6286 | -77.2926 | -53.906 | -59.418 | -59.0114 | -51.0427 | -54.5156 | -76.0352 | -53.7344 | -52.5488 | -59.0466 | -51.0583 | -54.5625 | -76.0156 | -53.7461 | -52.5801
25 | -0.8968 | 0 | -0.8617 | 0 | -0.8929 | 0 | -0.85 | 0 | -73.9323 | 47.8334 | -77.0795 | -110.0788 | -71.0084 | -69.5019 | -70.1376 | 74.0835 | -80.8544 | -15.2278 | -77.2113 | -45.7104 | -75.3665 | 28.5351 | -74.4881 | 163.485 | -70.7578 | 149.1488 | -70.0463 | -3.5974 | -80.1813 | 86.1075 | -85.6758 | 131.2934 | -38.6984 | -10.7308 | -34.248 | -11.2284 | -39.2319 | 2.7593 | -36.9199 | -1.9335 | -37.3665 | -16.0354 | -36.6626 | -11.8677 | -36.7718 | -18.1143 | -33.0047 | -16.078 | -59.9825 | -59.4122 | -51.6075 | -55.1739 | -77.3028 | -54.4044 | -59.9515 | -59.4281 | -51.6625 | -55.1429 | -76.4242 | -54.3148 | -53.0785 | 25 | -68.5603 | -68.3704 | -68.6813 | -69.7266 | -68.2789 | -68.614 | -68.6257 | -70.1644 | 25 | -58.5313 | -50.7657 | -54.2771 | -76.4411 | -53.5427 | -59.0586 | -58.5664 | -50.7696 | -54.3239 | -76.4099 | -53.5544 | -59.1015 | -58.5154 | -50.7107 | -54.2461 | -75.5625 | -53.4531 | -52.1856 | -58.5505 | -50.7146 | -54.2929 | -75.5313 | -53.4648 | -52.2285
26 | -0.9086 | 0 | -0.8852 | 0 | -0.932 | 0 | -0.8617 | 0 | -74.0303 | 44.0951 | -71.4904 | -150.6437 | -71.236 | -115.4835 | -69.6085 | 60.8621 | -78.7455 | -34.1217 | -77.1673 | -93.9784 | -75.8084 | 14.428 | -69.6587 | 159.2571 | -70.1143 | 152.7055 | -69.3664 | -22.0262 | -79.7461 | 75.7967 | -82.977 | -160.2439 | -37.6274 | -128.8515 | -34.3272 | -23.2216 | -42.3625 | -145.1503 | -37.8901 | -11.0436 | -38.3817 | -127.904 | -37.3711 | -19.0268 | -41.0451 | -130.531 | -32.9138 | -30.82 | -59.6388 | -58.9591 | -51.3145 | -54.9239 | -76.2794 | -54.1153 | -59.6234 | -59.0805 | -51.307 | -54.9516 | -75.8383 | -54.0961 | -52.6919 | 26 | -67.3115 | -67.8964 | -66.9988 | -69.6747 | -66.3483 | -68.1656 | -66.4031 | -69.4676 | 26 | -58.1719 | -50.3984 | -54.0153 | -75.3942 | -53.2301 | -58.6914 | -58.1953 | -50.375 | -54.0622 | -75.3474 | -53.2536 | -58.7617 | -58.0505 | -50.4059 | -54.043 | -74.9531 | -53.2109 | -51.7599 | -58.0739 | -50.3825 | -54.0899 | -74.9063 | -53.2344 | -51.8302
27 | -0.9321 | 0 | -0.8852 | 0 | -0.9438 | 0 | -0.8969 | 0 | -74.1028 | 40.3688 | -67.8469 | -176.0369 | -69.905 | -149.6042 | -69.5789 | 48.3831 | -77.2939 | -52.7917 | -76.4201 | -150.4635 | -76.4766 | 3.1995 | -66.6201 | 147.5878 | -68.9076 | 147.2234 | -69.1355 | -40.4096 | -79.4454 | 64.5288 | -78.0187 | -155.5191 | -29.7139 | -169.0784 | -35.1309 | -35.2821 | -31.6303 | 176.8817 | -39.8955 | -18.8303 | -30.1757 | -174.5163 | -38.8683 | -24.503 | -31.6759 | 174.4696 | -33.5059 | -45.9835 | -59.3107 | -58.5099 | -51.0333 | -54.6896 | -75.8107 | -53.8419 | -59.2797 | -58.811 | -50.9789 | -54.7407 | -75.6742 | -53.8969 | -52.2936 | 27 | -65.1532 | -67.7545 | -65.2701 | -68.4266 | -64.3312 | -68.0717 | -64.4907 | -68.0759 | 27 | -57.8789 | -50.0468 | -53.7575 | -74.9255 | -52.9567 | -58.3359 | -57.9258 | -50.0351 | -53.7927 | -74.8669 | -52.945 | -58.3828 | -57.5778 | -50.1012 | -53.8086 | -74.789 | -53.0117 | -51.3498 | -57.6247 | -50.0895 | -53.8438 | -74.7304 | -53 | -51.3967
28 | -0.979 | 0 | -0.9204 | 0 | -0.9673 | 0 | -0.9087 | 0 | -73.997 | 37.0941 | -65.6354 | 162.874 | -67.7069 | -177.1771 | -70.0311 | 37.1495 | -76.2599 | -71.6696 | -73.8362 | 170.7728 | -77.5364 | -6.3022 | -64.6616 | 132.5695 | -67.8847 | 143.5848 | -69.4337 | -61.2697 | -79.6725 | 55.5425 | -73.2077 | -160.8517 | -25.293 | 168.1684 | -36.7652 | -47.2612 | -26.6808 | 156.5299 | -43.1351 | -19.0849 | -25.576 | 161.461 | -41.0346 | -24.8102 | -26.6829 | 150.597 | -34.8763 | -62.5039 | -59.0217 | -58.174 | -50.7873 | -54.5021 | -75.424 | -53.6232 | -58.9751 | -58.518 | -50.6743 | -54.5766 | -75.6743 | -53.7407 | -51.9187 | 28 | -63.1643 | -67.8839 | -63.8319 | -66.2975 | -62.8213 | -68.4666 | -62.9795 | -66.5499 | 28 | -57.539 | -49.6953 | -53.5231 | -74.5036 | -52.7028 | -58.0078 | -57.5976 | -49.707 | -53.5934 | -74.4567 | -52.7145 | -58.0664 | -57.195 | -49.8083 | -53.5976 | -74.7539 | -52.8203 | -50.9514 | -57.2536 | -49.82 | -53.6679 | -74.707 | -52.832 | -51.01
29 | -1.0064 | 0 | -0.9283 | 0 | -1.0064 | 0 | -0.9322 | 0 | -73.5929 | 30.8229 | -64.2015 | 143.337 | -67.652 | 153.7305 | -71.0985 | 29.0076 | -75.3974 | -89.2205 | -70.6882 | 145.6662 | -77.9461 | -9.9385 | -63.3549 | 117.0385 | -67.6948 | 135.1887 | -70.2703 | -82.409 | -80.0531 | 40.1819 | -70.3402 | -175.0747 | -22.411 | 149.0939 | -39.5525 | -57.8227 | -23.6007 | 138.5946 | -47.4123 | 1.5171 | -22.5636 | 141.7995 | -43.5996 | -13.6536 | -23.5444 | 131.4273 | -37.2141 | -79.4566 | -58.7327 | -57.8772 | -50.5295 | -54.2991 | -75.4983 | -53.4202 | -58.6782 | -58.2798 | -50.3579 | -54.397 | -75.5884 | -53.6118 | -51.5907 | 29 | -62.2512 | -68.2324 | -62.6516 | -65.4376 | -61.8847 | -69.2121 | -61.8823 | -65.6484 | 29 | -57.2734 | -49.3515 | -53.2927 | -74.57 | -52.4919 | -57.6718 | -57.3515 | -49.3515 | -53.3669 | -74.4919 | -52.488 | -57.746 | -56.8708 | -49.5231 | -53.3906 | -74.6601 | -52.6835 | -50.5843 | -56.9489 | -49.5231 | -53.4648 | -74.582 | -52.6796 | -50.6585
30 | -1.0416 | 0 | -0.9439 | 0 | -1.0299 | 0 | -0.9439 | 0 | -73.0986 | 24.5929 | -63.3553 | 124.5459 | -66.6626 | 129.4984 | -72.3402 | 25.7984 | -74.758 | -109.1956 | -68.8459 | 123.4723 | -78.3298 | -11.2039 | -62.5808 | 100.6454 | -66.6541 | 128.6922 | -71.7774 | -106.4614 | -80.6227 | 31.4529 | -69.1394 | 171.0926 | -20.3883 | 131.3999 | -44.4205 | -63.5728 | -21.4776 | 121.2177 | -46.2729 | 43.5155 | -20.4729 | 123.6827 | -44.5488 | 9.0381 | -21.3896 | 114.1169 | -41.0245 | -101.149 | -58.4866 | -57.6546 | -50.2562 | -54.0765 | -75.5921 | -53.2327 | -58.4088 | -58.1158 | -50.1314 | -54.1978 | -75.7642 | -53.4947 | -51.2822 | 30 | -61.3879 | -68.5149 | -61.8669 | -64.2077 | -61.0639 | -70.4688 | -61.3059 | -64.6011 | 30 | -57.0742 | -49.0898 | -53.0349 | -74.6482 | -52.2888 | -57.3789 | -57.1719 | -49.1015 | -53.1326 | -74.5622 | -52.2888 | -57.4649 | -56.613 | -49.2146 | -53.1562 | -74.8203 | -52.5508 | -50.2523 | -56.7107 | -49.2263 | -53.2539 | -74.7343 | -52.5508 | -50.3383
31 | -1.0651 | 0 | -0.9557 | 0 | -1.0651 | 0 | -0.9713 | 0 | -72.9465 | 15.232 | -62.9879 | 106.0828 | -66.1221 | 107.5886 | -73.4462 | 29.8201 | -74.2941 | -126.236 | -67.2998 | 102.1809 | -77.7902 | -12.8956 | -62.2217 | 83.7896 | -67.728 | 120.1429 | -73.7547 | -135.1097 | -82.0917 | 25.0512 | -67.6042 | 153.3563 | -18.9711 | 114.4847 | -54.4145 | -37.1736 | -20.0109 | 104.826 | -42.2462 | 56.2824 | -18.9896 | 106.5779 | -43.0788 | 27.2597 | -19.8947 | 97.7677 | -47.734 | -137.2233 | -58.2953 | -57.5023 | -49.9867 | -53.8656 | -75.7367 | -53.057 | -58.1588 | -58.0338 | -49.8854 | -53.9518 | -75.987 | -53.319 | -51.0363 | 31 | -60.9824 | -68.756 | -61.3429 | -63.3008 | -61.0517 | -71.8752 | -60.8869 | -64.5777 | 31 | -56.9687 | -48.8203 | -52.8005 | -74.781 | -52.1013 | -57.0937 | -57.0781 | -48.8203 | -52.8943 | -74.6716 | -52.0857 | -57.1875 | -56.4372 | -48.9216 | -52.8867 | -75.0313 | -52.3633 | -49.9712 | -56.5466 | -48.9216 | -52.9805 | -74.9219 | -52.3477 | -50.065
32 | -1.0819 | 0 | -0.9799 | 0 | -1.0669 | 0 | -0.974 | 0 | -73.1057 | 4.3021 | -63.0353 | 87.6676 | -65.7794 | 84.3246 | -73.2639 | 41.2393 | -74.9768 | -149.4884 | -66.3403 | 84.205 | -76.7916 | -16.3259 | -62.2489 | 66.7098 | -67.8506 | 112.375 | -76.3688 | -178.423 | -83.0633 | 21.9138 | -67.2565 | 135.9479 | -18.0171 | 98.225 | -47.8713 | 50.1529 | -19.0479 | 88.8807 | -39.5328 | 54.0793 | -18.0044 | 90.0493 | -41.1043 | 35.3768 | -18.9189 | 81.8664 | -49.8722 | 118.4508 | -58.0968 | -57.3752 | -49.7223 | -53.628 | -76.3468 | -52.8479 | -57.972 | -57.8833 | -49.6561 | -53.6556 | -76.4916 | -53.1333 | -50.8037 | 32 | -60.9134 | -68.9323 | -61.0983 | -62.771 | -61.0747 | -73.1028 | -60.9314 | -64.4726 | 32 | -56.8014 | -48.5742 | -52.5461 | -75.3669 | -51.868 | -56.9051 | -56.9034 | -48.5892 | -52.654 | -75.2799 | -51.8739 | -56.998 | -56.2933 | -48.6404 | -52.5737 | -75.5117 | -52.1534 | -49.7368 | -56.3953 | -48.6554 | -52.6816 | -75.4247 | -52.1593 | -49.8297
33 | -1.1099 | 0 | -0.9936 | 0 | -1.1019 | 0 | -0.9902 | 0 | -73.5314 | -8.374 | -63.5634 | 70.0191 | -65.1282 | 58.9746 | -71.9471 | 47.9844 | -75.2995 | -170.6121 | -65.9848 | 65.977 | -75.6917 | -23.5968 | -62.7443 | 49.3804 | -68.123 | 94.2589 | -76.5991 | 127.5853 | -84.5166 | 27.5995 | -67.3071 | 124.7852 | -17.4837 | 82.3721 | -41.8232 | 50.1002 | -18.5311 | 73.2321 | -37.9682 | 47.3905 | -17.4415 | 73.9612 | -39.5351 | 37.0886 | -18.3914 | 66.4835 | -43.0452 | 72.095 | -57.8996 | -57.2423 | -49.4691 | -53.4074 | -76.8918 | -52.6329 | -57.7749 | -57.7308 | -49.4381 | -53.3296 | -76.8022 | -52.9456 | -50.6513 | 33 | -61.015 | -68.6097 | -61.2139 | -62.3017 | -61.4715 | -72.808 | -61.3114 | -64.6407 | 33 | -56.6209 | -48.3282 | -52.2975 | -75.8982 | -51.6393 | -56.673 | -56.7372 | -48.3362 | -52.4172 | -75.7899 | -51.6427 | -56.7847 | -56.1324 | -48.3592 | -52.2197 | -75.8086 | -51.952 | -49.5494 | -56.2487 | -48.3672 | -52.3394 | -75.7003 | -51.9554 | -49.6611
34 | -1.1167 | 0 | -1.0154 | 0 | -1.1201 | 0 | -0.9986 | 0 | -74.8173 | -21.4629 | -64.5136 | 52.2545 | -65.9344 | 38.2752 | -69.8983 | 47.9718 | -76.0506 | 167.1653 | -65.6427 | 46.6805 | -74.9675 | -33.1115 | -63.5225 | 31.2253 | -69.6722 | 94.2962 | -73.9577 | 79.5812 | -82.4118 | 29.6176 | -68.0996 | 105.6287 | -17.3246 | 66.9539 | -38.8275 | 42.5859 | -18.4233 | 57.9303 | -37.3321 | 39.875 | -17.2464 | 58.1535 | -38.5733 | 36.5887 | -18.2667 | 51.3975 | -39.5268 | 49.6292 | -57.7339 | -57.1082 | -49.2181 | -53.1362 | -77.3237 | -52.3933 | -57.6325 | -57.5381 | -49.2105 | -52.9763 | -76.7888 | -52.6943 | -50.5406 | 34 | -61.9267 | -67.954 | -61.3739 | -62.5761 | -62.3353 | -71.0902 | -61.9418 | -65.711 | 34 | -56.4214 | -48.0938 | -52.0195 | -76.3083 | -51.3779 | -56.5124 | -56.5227 | -48.0904 | -52.1376 | -76.2036 | -51.3947 | -56.6339 | -55.9915 | -48.1014 | -51.8596 | -75.7734 | -51.6789 | -49.4205 | -56.0928 | -48.098 | -51.9777 | -75.6687 | -51.6957 | -49.542
35 | -1.1214 | 0 | -1.0335 | 0 | -1.1197 | 0 | -1.0162 | 0 | -77.2465 | -32.0758 | -65.9076 | 34.5554 | -66.7074 | 16.4815 | -68.101 | 43.0643 | -77.2463 | 143.1557 | -65.9731 | 25.9432 | -74.5532 | -42.7349 | -64.9249 | 12.5958 | -71.3751 | 84.4648 | -70.9824 | 48.1822 | -82.3204 | 23.1345 | -69.4993 | 84.9447 | -17.5624 | 52.0052 | -37.1798 | 32.363 | -18.7374 | 43.2182 | -37.3337 | 33.4835 | -17.4883 | 42.9372 | -37.9067 | 36.3955 | -18.5708 | 37.0067 | -37.598 | 32.6532 | -57.5176 | -56.932 | -48.9728 | -52.8497 | -77.1544 | -52.1234 | -57.4514 | -57.2564 | -49.0276 | -52.6077 | -76.4866 | -52.3736 | -50.4114 | 35 | -63.108 | -67.1546 | -61.7771 | -63.1423 | -63.6688 | -69.1842 | -62.8927 | -67.191 | 35 | -56.135 | -47.9062 | -51.7283 | -76.1209 | -51.0899 | -56.3317 | -56.2229 | -47.9079 | -51.8335 | -76.0347 | -51.1072 | -56.4352 | -55.8106 | -47.8514 | -51.4863 | -75.4531 | -51.3401 | -49.2917 | -55.8985 | -47.8531 | -51.5915 | -75.3669 | -51.3574 | -49.3952
36 | -1.1424 | 0 | -1.0394 | 0 | -1.1442 | 0 | -1.0404 | 0 | -80.6434 | -32.6364 | -68.0869 | 15.5608 | -67.47 | -7.071 | -66.6112 | 35.095 | -78.6131 | 118.3428 | -66.9793 | 5.8244 | -74.631 | -49.9314 | -66.8929 | -6.9478 | -75.5071 | 65.9613 | -68.5079 | 24.2397 | -81.1543 | 18.8119 | -70.5215 | 76.1662 | -18.2142 | 37.7452 | -36.4248 | 22.3659 | -19.5288 | 29.1665 | -37.975 | 30.1292 | -18.1225 | 28.0818 | -37.2728 | 37.7263 | -19.3539 | 23.1075 | -36.7982 | 17.2999 | -57.2657 | -56.6635 | -48.7594 | -52.547 | -76.5938 | -51.8549 | -57.2698 | -56.9254 | -48.8221 | -52.2815 | -75.7542 | -52.0582 | -50.2953 | 36 | -64.6466 | -66.1871 | -62.4106 | -64.0527 | -65.7337 | -67.3734 | -63.6232 | -69.0487 | 36 | -55.783 | -47.6797 | -51.4046 | -75.5544 | -50.8155 | -56.1256 | -55.886 | -47.6779 | -51.5066 | -75.4496 | -50.8145 | -56.2294 | -55.5211 | -47.617 | -51.1391 | -74.7148 | -51.0188 | -49.1511 | -55.6241 | -47.6152 | -51.2411 | -74.61 | -51.0178 | -49.2549
37 | -1.1309 | 0 | -1.0581 | 0 | -1.153 | 0 | -1.0636 | 0 | -84.5859 | -13.1754 | -71.3404 | -4.5771 | -68.8977 | -29.2641 | -65.4392 | 26.9096 | -79.5564 | 91.2826 | -68.8316 | -14.1103 | -74.4036 | -55.6009 | -69.6536 | -29.7963 | -77.7911 | 74.0041 | -66.6681 | 3.7249 | -80.8063 | 9.1426 | -74.568 | 61.4897 | -19.395 | 24.4622 | -36.2265 | 12.3671 | -20.9318 | 16.2934 | -38.8583 | 31.2459 | -19.2941 | 13.9671 | -36.6279 | 39.0776 | -20.7026 | 10.4043 | -36.6761 | 2.9304 | -57.0462 | -56.3794 | -48.5487 | -52.2844 | -75.6985 | -51.5826 | -57.0307 | -56.5359 | -48.6114 | -51.9956 | -74.7846 | -51.7507 | -50.1128 | 37 | -66.8652 | -65.2235 | -63.0969 | -65.6729 | -67.9261 | -65.851 | -64.4538 | -72.2282 | 37 | -55.405 | -47.4805 | -51.1535 | -74.6404 | -50.5245 | -55.8777 | -55.4778 | -47.4584 | -51.2208 | -74.5455 | -50.519 | -55.9671 | -55.2485 | -47.4178 | -50.8647 | -73.7265 | -50.6926 | -48.9598 | -55.3213 | -47.3957 | -50.932 | -73.6316 | -50.6871 | -49.0492
38 | -1.1585 | 0 | -1.0618 | 0 | -1.1631 | 0 | -1.0658 | 0 | -82.3253 | 24.8402 | -76.6445 | -31.4229 | -69.935 | -59.5789 | -64.5053 | 16.3715 | -80.7494 | 62.0262 | -71.6354 | -29.376 | -74.2941 | -60.6932 | -73.8631 | -60.2064 | -82.8735 | 114.5913 | -65.2914 | -15.7559 | -80.1362 | 2.596 | -78.4205 | 48.0661 | -21.2643 | 12.6175 | -36.6254 | 2.7959 | -23.1576 | 5.4737 | -39.505 | 38.5414 | -21.1391 | 1.2255 | -35.8114 | 39.9506 | -22.862 | -0.2225 | -37.2543 | -9.1106 | -56.8039 | -56.0555 | -48.3478 | -52.0128 | -74.837 | -51.3856 | -56.7786 | -56.1826 | -48.4105 | -51.7474 | -74.1848 | -51.4795 | -49.8826 | 38 | -68.8935 | -64.3339 | -63.5198 | -67.4825 | -70.7858 | -64.6521 | -64.5447 | -75.3406 | 38 | -55.0241 | -47.252 | -50.8543 | -73.7752 | -50.3238 | -55.6155 | -55.1208 | -47.2474 | -50.947 | -73.6739 | -50.3198 | -55.7128 | -54.897 | -47.1893 | -50.5889 | -73.123 | -50.4177 | -48.7195 | -54.9937 | -47.1847 | -50.6816 | -73.0217 | -50.4137 | -48.8168
39 | -1.1457 | 0 | -1.0867 | 0 | -1.1714 | 0 | -1.0726 | 0 | -77.8701 | 28.7532 | -85.2919 | -118.1646 | -72.3108 | -84.6903 | -63.7813 | 4.9964 | -81.507 | 29.9827 | -76.6861 | -54.2891 | -74.0442 | -64.2544 | -79.1925 | -121.683 | -80.3625 | 146.3568 | -64.2893 | -35.0542 | -79.8199 | -2.7279 | -92.1541 | 44.6516 | -24.1099 | 4.7387 | -37.6064 | -4.7841 | -26.5914 | 0.9726 | -38.8296 | 48.3351 | -24.1427 | -8.8707 | -34.9128 | 39.1456 | -26.2864 | -5.6126 | -38.7031 | -20.8345 | -56.5768 | -55.7083 | -48.1475 | -51.7975 | -74.102 | -51.222 | -56.5574 | -55.7729 | -48.1926 | -51.6024 | -73.6785 | -51.2651 | -49.6156 | 39 | -71.0777 | -63.5451 | -63.5352 | -70.5921 | -72.1717 | -63.744 | -64.1442 | -76.9397 | 39 | -54.6272 | -47.0469 | -50.6518 | -73.0153 | -50.1353 | -55.386 | -54.6862 | -47.0212 | -50.7249 | -72.9306 | -50.1494 | -55.4848 | -54.5626 | -47.0018 | -50.4567 | -72.5918 | -50.1784 | -48.4442 | -54.6216 | -46.9761 | -50.5298 | -72.5071 | -50.1925 | -48.543
40 | -1.169 | 0 | -1.0963 | 0 | -1.1813 | 0 | -1.0875 | 0 | -75.0086 | 20.1673 | -76.7831 | 157.1957 | -74.3494 | -121.6267 | -63.4561 | -7.1096 | -81.2506 | 1.6139 | -86.1354 | -105.8003 | -73.7199 | -65.7179 | -76.0545 | 158.1198 | -76.2461 | 149.0178 | -63.604 | -54.1994 | -79.3245 | -11.3679 | -83.4054 | -141.9621 | -28.4718 | 8.3239 | -39.3006 | -10.4555 | -31.3761 | 17.7323 | -37.4255 | 53.0274 | -29.0477 | -8.0376 | -34.1017 | 37.0314 | -31.2738 | 9.4531 | -40.8347 | -26.7908 | -56.3462 | -55.3492 | -47.9775 | -51.5962 | -73.6196 | -51.0914 | -56.3268 | -55.4352 | -48.0167 | -51.4713 | -73.3189 | -51.0837 | -49.3092 | 40 | -70.493 | -63.0956 | -63.2364 | -73.31 | -70.4094 | -63.0957 | -63.3209 | -73.9812 | 40 | -54.2662 | -46.8477 | -50.4272 | -72.5233 | -49.9951 | -55.1455 | -54.3389 | -46.8354 | -50.5087 | -72.4383 | -50.0039 | -55.2393 | -54.1802 | -46.8085 | -50.3023 | -72.2226 | -49.9874 | -48.1279 | -54.2529 | -46.7962 | -50.3838 | -72.1376 | -49.9962 | -48.2217
41 | -1.1675 | 0 | -1.1243 | 0 | -1.1924 | 0 | -1.1082 | 0 | -72.5251 | 6.6363 | -71.8098 | 130.2685 | -75.6868 | -168.4422 | -63.3667 | -19.321 | -80.2129 | -25.6587 | -83.0092 | 123.7218 | -73.1564 | -65.6678 | -71.5228 | 119.5218 | -75.2481 | 141.7849 | -63.337 | -73.6378 | -78.5802 | -20.7688 | -76.158 | -175.8762 | -31.6508 | 47.9983 | -41.8824 | -11.3418 | -30.6515 | 64.9177 | -35.8551 | 50.8858 | -33.6525 | 39.36 | -33.3975 | 34.0124 | -31.0411 | 59.6854 | -43.5596 | -24.8107 | -56.1632 | -55.0439 | -47.7612 | -51.4367 | -73.1086 | -50.9736 | -56.0969 | -55.1416 | -47.7925 | -51.3704 | -73.0071 | -50.9658 | -49.0274 | 41 | -68.2732 | -62.7898 | -62.7447 | -73.8174 | -68.2787 | -62.7903 | -62.5304 | -71.6778 | 41 | -53.9741 | -46.625 | -50.2692 | -71.9843 | -49.8493 | -54.9045 | -54.0173 | -46.6001 | -50.3285 | -71.9162 | -49.8654 | -54.9887 | -53.8764 | -46.5937 | -50.2029 | -71.8828 | -49.8415 | -47.835 | -53.9196 | -46.5688 | -50.2622 | -71.8147 | -49.8576 | -47.9192
42 | -1.1826 | 0 | -1.1442 | 0 | -1.2 | 0 | -1.1273 | 0 | -70.8567 | -9.0518 | -69.0394 | 108.9857 | -75.8553 | 148.3886 | -63.7733 | -31.3695 | -79.3121 | -51.1767 | -77.2882 | 100.1653 | -71.8349 | -67.8946 | -68.7765 | 93.1853 | -75.2661 | 132.1396 | -63.4788 | -94.3074 | -78.3201 | -30.1212 | -72.2449 | 168.1291 | -27.2501 | 78.4288 | -45.3081 | 0.4376 | -25.6736 | 76.567 | -34.6982 | 44.6526 | -27.8055 | 75.5128 | -32.964 | 30.3898 | -25.8054 | 73.6157 | -45.8684 | -8.319 | -55.9371 | -54.782 | -47.6122 | -51.2925 | -72.8667 | -50.8992 | -55.9176 | -54.868 | -47.5576 | -51.3199 | -72.6949 | -50.8328 | -48.7147 | 42 | -66.3297 | -62.8967 | -62.4959 | -72.4905 | -66.424 | -62.7644 | -61.9311 | -69.8254 | 42 | -53.6854 | -46.375 | -50.1099 | -71.7225 | -49.755 | -54.7176 | -53.7238 | -46.3576 | -50.1652 | -71.6667 | -49.7719 | -54.7903 | -53.5994 | -46.4296 | -50.1373 | -71.5507 | -49.6886 | -47.5147 | -53.6378 | -46.4122 | -50.1926 | -71.4949 | -49.7055 | -47.5874
43 | -1.213 | 0 | -1.1556 | 0 | -1.2285 | 0 | -1.1439 | 0 | -69.5826 | -26.9688 | -67.5826 | 89.3765 | -75.6312 | 95.3809 | -64.7089 | -42.4432 | -78.5305 | -73.0009 | -73.2827 | 85.7303 | -70.4964 | -71.2307 | -66.9331 | 69.8682 | -75.9913 | 121.72 | -63.933 | -115.9885 | -77.9028 | -38.6693 | -69.8961 | 155.2654 | -23.1398 | 78.6459 | -46.9715 | 37.6623 | -22.2949 | 71.0739 | -34.0964 | 35.9776 | -23.2329 | 73.2711 | -32.7483 | 27.0925 | -22.2653 | 68.4347 | -45.1426 | 12.6546 | -55.7805 | -54.5605 | -47.4551 | -51.1829 | -72.7493 | -50.8105 | -55.6829 | -54.6855 | -47.4122 | -51.2376 | -72.9095 | -50.7441 | -48.4737 | 43 | -65.0597 | -63.3511 | -62.5213 | -70.5388 | -64.9895 | -62.9268 | -61.4914 | -68.4225 | 43 | -53.4725 | -46.1992 | -49.9699 | -71.5937 | -49.6549 | -54.4544 | -53.5299 | -46.1837 | -50.039 | -71.5208 | -49.6666 | -54.539 | -53.3475 | -46.2421 | -50.0246 | -71.7539 | -49.5885 | -47.2452 | -53.4049 | -46.2266 | -50.0937 | -71.681 | -49.6002 | -47.3298
44 | -1.2387 | 0 | -1.158 | 0 | -1.2595 | 0 | -1.156 | 0 | -68.4918 | -45.4079 | -66.651 | 70.1055 | -71.972 | 45.8893 | -66.0626 | -51.0317 | -78.8301 | -96.4383 | -70.8527 | 76.7891 | -68.9297 | -77.7816 | -65.9165 | 46.7637 | -77.5438 | 112.8395 | -64.8371 | -138.7088 | -77.6939 | -48.2327 | -68.2453 | 140.1109 | -20.4257 | 70.0584 | -43.4431 | 65.7018 | -20.0548 | 60.5378 | -34.1014 | 25.1092 | -20.4147 | 63.1369 | -32.7378 | 24.3188 | -19.9528 | 57.9372 | -43.2452 | 16.6762 | -55.6189 | -54.404 | -47.3051 | -51.1033 | -72.4939 | -50.7477 | -55.5174 | -54.529 | -47.2387 | -51.2049 | -73.0642 | -50.6579 | -48.2118 | 44 | -63.7546 | -63.9555 | -62.6282 | -67.9924 | -63.9619 | -63.2489 | -61.3421 | -67.3425 | 44 | -53.2903 | -46 | -49.8646 | -71.3359 | -49.5897 | -54.2579 | -53.371 | -45.9792 | -49.9473 | -71.2344 | -49.5917 | -54.3614 | -53.1653 | -46.0664 | -49.9662 | -71.9062 | -49.4999 | -46.9523 | -53.246 | -46.0456 | -50.0489 | -71.8047 | -49.5019 | -47.0558
45 | -1.2852 | 0 | -1.1859 | 0 | -1.2918 | 0 | -1.1833 | 0 | -67.6599 | -65.1137 | -66.6818 | 51.0022 | -71.3508 | 21.2056 | -67.9788 | -55.281 | -78.9589 | -120.8554 | -69.7857 | 59.4944 | -67.4824 | -86.232 | -65.3264 | 24.1637 | -82.7192 | 99.2354 | -66.0042 | -165.6478 | -77.6154 | -58.4754 | -67.3707 | 124.8087 | -18.6012 | 59.0707 | -39.577 | 72.8056 | -18.5522 | 48.3723 | -34.8496 | 14.6481 | -18.5272 | 50.5951 | -32.7137 | 23.2916 | -18.3804 | 45.6345 | -41.5082 | 10.3392 | -55.4594 | -54.2605 | -47.1641 | -51.014 | -72.4984 | -50.6394 | -55.393 | -54.4442 | -47.1094 | -51.1508 | -72.9281 | -50.5613 | -48.0098 | 45 | -63.3784 | -64.6423 | -63.1965 | -67.1888 | -63.2127 | -63.4987 | -61.3818 | -66.8642 | 45 | -53.159 | -45.8242 | -49.7288 | -71.3125 | -49.4535 | -54.1012 | -53.2583 | -45.8176 | -49.8307 | -71.2066 | -49.4561 | -54.2097 | -52.9753 | -45.8789 | -49.8656 | -71.7422 | -49.3754 | -46.718 | -53.0746 | -45.8723 | -49.9675 | -71.6363 | -49.378 | -46.8265
46 | -1.3312 | 0 | -1.1801 | 0 | -1.3355 | 0 | -1.2063 | 0 | -67.1804 | -85.9471 | -67.2891 | 31.8569 | -70.0232 | -9.8909 | -70.1314 | -48.8058 | -79.5216 | -141.4396 | -68.9982 | 44.393 | -66.2108 | -97.147 | -65.2831 | -0.0062 | -91.45 | -78.9944 | -67.3721 | 162.8545 | -77.4003 | -60.5508 | -66.1552 | 113.4225 | -17.4248 | 46.8203 | -36.7413 | 70.1016 | -17.6528 | 35.1655 | -36.5805 | 2.3999 | -17.3532 | 37.2811 | -32.6274 | 23.5109 | -17.4325 | 32.5636 | -40.9309 | 0.3943 | -55.3012 | -54.2222 | -47.0461 | -50.9262 | -72.6215 | -50.5659 | -55.2582 | -54.3902 | -46.9914 | -51.0395 | -72.9575 | -50.4761 | -47.8426 | 46 | -63.2098 | -65.2347 | -63.876 | -66.2603 | -62.7061 | -63.5593 | -61.4159 | -65.8289 | 46 | -53.059 | -45.6602 | -49.595 | -71.4414 | -49.3858 | -53.9227 | -53.2101 | -45.6559 | -49.7199 | -71.286 | -49.3596 | -54.0519 | -52.891 | -45.7149 | -49.7083 | -71.7774 | -49.296 | -46.5071 | -53.0421 | -45.7106 | -49.8332 | -71.622 | -49.2698 | -46.6363
47 | -1.3531 | 0 | -1.1935 | 0 | -1.3902 | 0 | -1.2156 | 0 | -66.8549 | -107.3727 | -68.5863 | 11.9962 | -68.0345 | -40.8446 | -70.7899 | -31.5383 | -79.8958 | -162.1732 | -68.8257 | 33.08 | -65.2539 | -109.4056 | -65.4913 | -24.4344 | -75.8251 | -99.8411 | -68.3296 | 125.2037 | -77.1115 | -68.008 | -65.6787 | 99.6775 | -16.7207 | 34.3294 | -34.6049 | 64.2446 | -17.1822 | 21.8702 | -40.0146 | -6.2766 | -16.6646 | 23.4393 | -32.3343 | 23.7376 | -16.9299 | 19.1607 | -41.0164 | -13.1724 | -55.1271 | -54.1597 | -46.8922 | -50.8342 | -72.4357 | -50.4449 | -55.131 | -54.3394 | -46.8727 | -50.9201 | -72.7951 | -50.3785 | -47.6865 | 47 | -62.9928 | -65.23 | -64.5236 | -65.2502 | -62.1694 | -63.329 | -61.5503 | -65.0021 | 47 | -52.9863 | -45.5196 | -49.4811 | -71.2422 | -49.2514 | -53.7408 | -53.1459 | -45.4825 | -49.6186 | -71.0455 | -49.2293 | -53.9154 | -52.8066 | -45.5391 | -49.567 | -71.6016 | -49.185 | -46.2963 | -52.9662 | -45.502 | -49.7045 | -71.4049 | -49.1629 | -46.4709
48 | -1.3906 | 0 | -1.2242 | 0 | -1.413 | 0 | -1.217 | 0 | -66.7103 | -128.8197 | -70.9344 | -6.3874 | -66.6319 | -69.6055 | -69.0494 | -18.3744 | -81.1859 | 175.3659 | -69.4712 | 21.383 | -64.6199 | -122.4345 | -65.8027 | -51.0337 | -70.6212 | -117.2753 | -67.9386 | 84.9153 | -76.4839 | -74.6323 | -65.5871 | 86.6515 | -16.4029 | 21.6482 | -32.9543 | 56.487 | -17.1308 | 8.4419 | -47.9995 | -3.5657 | -16.3729 | 9.4667 | -31.7306 | 23.8852 | -16.8319 | 5.567 | -41.7696 | -30.7084 | -54.9469 | -54.1006 | -46.7539 | -50.7359 | -71.9742 | -50.3154 | -54.9976 | -54.2568 | -46.7578 | -50.7867 | -72.2828 | -50.2607 | -47.518 | 48 | -62.9149 | -64.6172 | -64.9749 | -64.7143 | -61.5821 | -62.7706 | -61.5499 | -64.1411 | 48 | -52.8662 | -45.3672 | -49.3453 | -70.75 | -49.0912 | -53.5846 | -53.0326 | -45.3448 | -49.5189 | -70.5612 | -49.0984 | -53.7806 | -52.71 | -45.3633 | -49.3961 | -71.0586 | -49.0365 | -46.105 | -52.8764 | -45.3409 | -49.5697 | -70.8698 | -49.0437 | -46.301
49 | -1.4077 | 0 | -1.2439 | 0 | -1.4256 | 0 | -1.2247 | 0 | -66.848 | -150.4232 | -74.4011 | -27.8962 | -65.5887 | -96.5128 | -66.6216 | -15.3249 | -82.6441 | 154.583 | -70.9543 | 13.1045 | -64.3347 | -135.9991 | -66.1627 | -78.9109 | -66.2922 | -132.6532 | -66.4512 | 49.2874 | -75.5927 | -82.5788 | -65.9618 | 72.8447 | -16.4489 | 9.0087 | -31.7405 | 47.6738 | -17.4826 | -4.9841 | -48.2212 | 109.3961 | -16.4751 | -4.4646 | -31.0411 | 21.8827 | -17.1552 | -8.089 | -43.6689 | -52.5014 | -54.7674 | -53.9842 | -46.6187 | -50.615 | -71.6619 | -50.1991 | -54.865 | -54.117 | -46.6343 | -50.6306 | -71.8689 | -50.1092 | -47.3198 | 49 | -62.8477 | -63.6677 | -64.7591 | -64.4147 | -60.7295 | -62.0581 | -61.4161 | -62.8748 | 49 | -52.7093 | -45.2266 | -49.2073 | -70.418 | -48.9552 | -53.4394 | -52.8731 | -45.2087 | -49.3903 | -70.2363 | -48.9744 | -53.6403 | -52.5765 | -45.211 | -49.2229 | -70.625 | -48.8653 | -45.8942 | -52.7403 | -45.1931 | -49.4059 | -70.4433 | -48.8845 | -46.0951
50 | -1.4193 | 0 | -1.2498 | 0 | -1.4308 | 0 | -1.2419 | 0 | -67.1335 | -172.7558 | -81.4218 | -57.2967 | -64.2427 | -124.2865 | -64.3837 | -20.6236 | -83.2483 | 127.2541 | -72.4308 | 16.1732 | -64.3137 | -148.8605 | -66.4236 | -107.5432 | -63.7191 | -146.879 | -64.6771 | 19.3505 | -74.6993 | -90.3857 | -66.4948 | 62.187 | -16.8406 | -3.1903 | -30.9532 | 38.1396 | -18.2588 | -17.9123 | -38.8299 | 113.3898 | -16.9682 | -18.3859 | -30.4143 | 18.1984 | -17.9031 | -21.4363 | -46.5387 | -83.2987 | -54.5155 | -53.8137 | -46.4779 | -50.4686 | -71.3045 | -50.0285 | -54.6951 | -53.9465 | -46.5169 | -50.449 | -71.2967 | -49.9855 | -47.1024 | 50 | -62.387 | -62.4975 | -63.6776 | -63.5819 | -59.9016 | -61.2791 | -61.0093 | -61.6575 | 50 | -52.5272 | -45.0976 | -49.0493 | -70.0547 | -48.7787 | -53.2643 | -52.6967 | -45.0861 | -49.2267 | -69.8737 | -48.7866 | -53.4532 | -52.3944 | -45.0586 | -49.0297 | -70.0469 | -48.7357 | -45.6716 | -52.5639 | -45.0471 | -49.2071 | -69.8659 | -48.7436 | -45.8605
51 | -1.4263 | 0 | -1.2648 | 0 | -1.438 | 0 | -1.2637 | 0 | -67.8199 | 163.5641 | -88.3704 | 177.9507 | -63.5324 | -152.2414 | -62.7247 | -29.44 | -83.3469 | 100.698 | -73.1299 | 12.6268 | -64.8279 | -162.2896 | -66.3536 | -137.4798 | -61.671 | -160.5333 | -63.0969 | -5.7435 | -74.102 | -100.358 | -66.9609 | 49.3536 | -17.6057 | -15.0517 | -30.5421 | 28.2202 | -19.5095 | -30.4413 | -34.4526 | 102.7822 | -17.8858 | -32.2351 | -29.9265 | 12.3318 | -19.1606 | -34.3171 | -47.8587 | -128.4388 | -54.3156 | -53.6099 | -46.3287 | -50.3312 | -71.0031 | -49.9537 | -54.4991 | -53.6958 | -46.3365 | -50.2999 | -70.9835 | -49.8872 | -46.8402 | 51 | -62.1466 | -61.5254 | -62.3353 | -63.0396 | -59.0617 | -60.665 | -60.348 | -60.3582 | 51 | -52.2695 | -44.9102 | -48.9049 | -69.7383 | -48.6889 | -53.0611 | -52.431 | -44.8985 | -49.0675 | -69.5651 | -48.69 | -53.2354 | -52.1836 | -44.9024 | -48.8736 | -69.7187 | -48.6224 | -45.4022 | -52.3451 | -44.8907 | -49.0362 | -69.5455 | -48.6235 | -45.5765
52 | -1.4214 | 0 | -1.2941 | 0 | -1.4212 | 0 | -1.2674 | 0 | -68.8692 | 138.7075 | -78.1224 | 122.7676 | -62.9936 | -174.4211 | -61.4585 | -40.1674 | -82.9246 | 68.5872 | -72.3984 | 29.4517 | -65.7143 | -174.3503 | -66.2172 | -165.1213 | -59.9121 | -174.9044 | -61.8482 | -27.8913 | -73.5156 | -111.2681 | -68.0884 | 34.9941 | -18.7712 | -25.9286 | -30.4564 | 17.8206 | -21.394 | -41.3347 | -31.6606 | 89.7242 | -19.2899 | -45.5008 | -29.7765 | 5.5254 | -21.0421 | -45.8613 | -46.5459 | -179.6806 | -54.1145 | -53.3743 | -46.1715 | -50.2004 | -70.6613 | -49.847 | -54.3058 | -53.4329 | -46.187 | -50.1535 | -70.6496 | -49.7766 | -46.589 | 52 | -61.8904 | -60.7079 | -61.0363 | -62.4827 | -58.1598 | -60.1494 | -59.7979 | -59.1355 | 52 | -52.0115 | -44.7656 | -48.779 | -69.3672 | -48.5529 | -52.8846 | -52.1388 | -44.7658 | -48.933 | -69.2401 | -48.5796 | -53.0384 | -51.9529 | -44.7501 | -48.7321 | -69.3555 | -48.4825 | -45.1678 | -52.0802 | -44.7503 | -48.8861 | -69.2284 | -48.5092 | -45.3216
53 | -1.4166 | 0 | -1.3066 | 0 | -1.4089 | 0 | -1.3065 | 0 | -70.4568 | 110.3097 | -73.7694 | 102.1053 | -62.1123 | 157.6684 | -60.5673 | -52.1188 | -82.9198 | 40.2049 | -71.534 | 24.6698 | -67.0831 | 175.9529 | -65.9905 | 168.3312 | -58.7355 | 167.4526 | -60.9366 | -48.6156 | -72.4181 | -121.7969 | -70.6922 | 19.3807 | -20.4215 | -35.1959 | -30.8023 | 7.923 | -24.1515 | -48.9213 | -29.9007 | 75.8802 | -21.3739 | -57.5166 | -29.9475 | -1.5252 | -23.847 | -54.5779 | -43.7047 | 147.2005 | -53.9629 | -53.1355 | -45.9831 | -50.0605 | -70.5098 | -49.7487 | -54.1035 | -53.1393 | -46.0065 | -50.0371 | -70.416 | -49.7057 | -46.3659 | 53 | -61.2677 | -60.1204 | -60.0447 | -61.6103 | -57.4825 | -59.7508 | -59.4195 | -58.2958 | 53 | -51.7227 | -44.5899 | -48.6439 | -69.2032 | -48.4421 | -52.6946 | -51.8327 | -44.5976 | -48.754 | -69.1009 | -48.4422 | -52.797 | -51.7189 | -44.5665 | -48.6205 | -69.1094 | -48.3991 | -44.957 | -51.8289 | -44.5742 | -48.7306 | -69.0071 | -48.3992 | -45.0594
54 | -1.3982 | 0 | -1.3013 | 0 | -1.3995 | 0 | -1.303 | 0 | -72.779 | 75.4369 | -71.7661 | 82.9068 | -61.7905 | 139.6794 | -60.0547 | -65.1513 | -81.7757 | 16.9806 | -69.0714 | 25.4195 | -69.3071 | 169.2831 | -65.8308 | 142.6162 | -58.3869 | 152.2496 | -60.5404 | -68.4385 | -72.6196 | -133.6863 | -74.148 | 18.5904 | -22.6849 | -40.9477 | -31.6391 | -1.1197 | -28.0742 | -47.1819 | -28.7978 | 62.4072 | -24.4389 | -67.1014 | -30.514 | -8.6975 | -27.9976 | -54.8146 | -42.0387 | 126.928 | -53.7935 | -52.8878 | -45.7733 | -49.938 | -70.4575 | -49.6652 | -53.9106 | -52.8761 | -45.7967 | -49.9145 | -70.4692 | -49.6222 | -46.1144 | 54 | -61.0709 | -59.8011 | -59.2889 | -61.0093 | -57.3796 | -59.7675 | -59.2715 | -58.1164 | 54 | -51.4779 | -44.3985 | -48.5398 | -69.1562 | -48.3639 | -52.5111 | -51.5748 | -44.3972 | -48.635 | -69.058 | -48.3622 | -52.6076 | -51.4896 | -44.3751 | -48.5163 | -69.1679 | -48.3209 | -44.7149 | -51.5865 | -44.3738 | -48.6115 | -69.0697 | -48.3192 | -44.8114
55 | -1.3905 | 0 | -1.3296 | 0 | -1.4254 | 0 | -1.3178 | 0 | -73.945 | 26.0934 | -70.1301 | 63.9223 | -61.3274 | 111.9456 | -59.9054 | -78.2582 | -81.4649 | 1.4794 | -68.0788 | 17.102 | -71.9033 | 177.3147 | -66.1494 | 119.2542 | -57.551 | 139.3165 | -60.4113 | -88.194 | -71.6238 | -148.1428 | -78.6718 | -0.7128 | -25.472 | -39.9623 | -32.9803 | -8.5036 | -31.6863 | -19.0823 | -28.2603 | 48.0876 | -29.1658 | -68.7022 | -31.5093 | -14.1717 | -32.4784 | -24.9437 | -40.9701 | 109.7276 | -53.7632 | -52.6793 | -45.5663 | -49.8725 | -70.4155 | -49.5973 | -53.7866 | -52.6676 | -45.6014 | -49.8491 | -70.4858 | -49.5895 | -45.9177 | 55 | -60.5848 | -59.7083 | -58.9459 | -60.4604 | -56.8514 | -59.8173 | -59.3333 | -57.3521 | 55 | -51.2771 | -44.2109 | -48.482 | -69.0859 | -48.2677 | -52.3612 | -51.338 | -44.176 | -48.5547 | -68.9901 | -48.2795 | -52.4688 | -51.2888 | -44.1758 | -48.4586 | -69.1562 | -48.2599 | -44.4923 | -51.3497 | -44.1409 | -48.5313 | -69.0604 | -48.2717 | -44.5999
56 | -1.4021 | 0 | -1.3419 | 0 | -1.4228 | 0 | -1.3346 | 0 | -72.7001 | -29.3906 | -69.6547 | 44.9866 | -60.9494 | 88.7215 | -60.1093 | -91.5603 | -80.7695 | -12.9713 | -67.4255 | 6.9723 | -72.5494 | -158.6205 | -67.0466 | 96.3475 | -57.5294 | 124.487 | -60.654 | -107.6532 | -71.8854 | -161.78 | -87.2812 | 59.9085 | -27.9847 | -25.5303 | -35.0609 | -11.5315 | -29.2589 | 13.5926 | -28.2764 | 34.1454 | -34.8935 | -32.8635 | -32.9327 | -15.536 | -29.5095 | 14.0165 | -40.5426 | 95.7917 | -53.6733 | -52.5081 | -45.3741 | -49.7475 | -70.3491 | -49.5355 | -53.6466 | -52.4931 | -45.4138 | -49.7521 | -70.6818 | -49.5049 | -45.7566 | 56 | -60.152 | -59.8413 | -58.9814 | -60.0309 | -56.948 | -60.0852 | -59.7491 | -57.3685 | 56 | -51.091 | -44.0117 | -48.3454 | -69.0072 | -48.1936 | -52.2238 | -51.1512 | -43.991 | -48.4129 | -68.9263 | -48.2009 | -52.312 | -51.106 | -43.972 | -48.35 | -69.3399 | -48.163 | -44.3338 | -51.1662 | -43.9513 | -48.4175 | -69.259 | -48.1703 | -44.422
57 | -1.4129 | 0 | -1.3324 | 0 | -1.4331 | 0 | -1.3459 | 0 | -69.5469 | -70.5509 | -70.1211 | 23.4364 | -61.1524 | 60.0212 | -60.8095 | -104.4671 | -78.3518 | -27.6814 | -67.2645 | -1.8563 | -69.5764 | -143.357 | -68.7842 | 74.0252 | -57.8442 | 108.9723 | -61.4257 | -127.3513 | -72.2727 | -173.6586 | -76.7427 | 126.8328 | -27.7762 | -3.2618 | -37.3806 | -6.3081 | -25.5687 | 18.1776 | -28.7857 | 19.6564 | -30.7727 | 12.7542 | -34.4902 | -12.211 | -25.4428 | 17.2923 | -41.3323 | 85.2967 | -53.6089 | -52.3776 | -45.1894 | -49.6832 | -70.316 | -49.4362 | -53.5082 | -52.3589 | -45.2527 | -49.6762 | -70.7231 | -49.4292 | -45.6221 | 57 | -60.1091 | -60.1974 | -59.5275 | -60.1355 | -57.2461 | -60.5077 | -60.5867 | -57.6366 | 57 | -50.946 | -43.8398 | -48.2703 | -68.9836 | -48.1038 | -52.0751 | -51.0265 | -43.8196 | -48.3373 | -68.8829 | -48.0903 | -52.1623 | -50.9647 | -43.7765 | -48.2633 | -69.3907 | -48.0968 | -44.189 | -51.0452 | -43.7563 | -48.3303 | -69.29 | -48.0833 | -44.2762
58 | -1.4313 | 0 | -1.3555 | 0 | -1.4584 | 0 | -1.3494 | 0 | -66.6062 | -101.3521 | -71.638 | -0.7335 | -61.3998 | 30.8594 | -61.8978 | -117.2986 | -77.4308 | -38.8381 | -67.5346 | -15.0911 | -66.4163 | -145.0403 | -72.0042 | 52.2463 | -58.9573 | 95.0583 | -62.6013 | -148.5477 | -73.1142 | 172.185 | -72.0327 | 128.1171 | -25.5125 | 7.2371 | -38.5729 | 14.6126 | -23.0318 | 11.8061 | -29.8583 | 5.8875 | -26.2598 | 15.2607 | -35.4488 | 1.1596 | -22.7973 | 9.8131 | -42.4551 | 80.2291 | -53.5422 | -52.3053 | -45.0829 | -49.6398 | -70.1906 | -49.3522 | -53.4102 | -52.2905 | -45.1384 | -49.6484 | -70.5781 | -49.3491 | -45.5308 | 58 | -59.9503 | -60.5428 | -60.5013 | -60.3671 | -58.0614 | -60.828 | -61.7067 | -58.5924 | 58 | -50.8592 | -43.7071 | -48.2085 | -68.8351 | -47.9967 | -51.9518 | -50.935 | -43.68 | -48.2904 | -68.7322 | -48.0028 | -52.0608 | -50.874 | -43.6516 | -48.2171 | -69.2226 | -47.9936 | -44.0724 | -50.9498 | -43.6245 | -48.299 | -69.1197 | -47.9997 | -44.1814
59 | -1.4567 | 0 | -1.359 | 0 | -1.4667 | 0 | -1.3694 | 0 | -64.4253 | -126.4793 | -74.5295 | -32.3094 | -61.6009 | -0.6768 | -63.622 | -128.9709 | -76.4616 | -48.6713 | -67.7596 | -31.4811 | -63.9097 | -153.7105 | -79.4238 | 29.0689 | -60.9661 | 83.381 | -64.3643 | -172.1014 | -74.8324 | 163.302 | -68.6608 | 112.2026 | -23.3866 | 6.0688 | -36.6823 | 32.3357 | -21.4529 | 1.0504 | -31.7973 | -7.2852 | -23.5786 | 6.0234 | -34.3516 | 14.313 | -21.1626 | -1.8844 | -43.5067 | 82.5831 | -53.4052 | -52.2667 | -44.9872 | -49.5458 | -69.8075 | -49.2667 | -53.2731 | -52.2401 | -45.0934 | -49.5817 | -70.2419 | -49.2284 | -45.4459 | 59 | -59.6341 | -60.8732 | -61.9582 | -60.5464 | -59.1419 | -60.9398 | -62.8936 | -60.1343 | 59 | -50.7834 | -43.6367 | -48.0891 | -68.4485 | -47.9077 | -51.8064 | -50.8811 | -43.6267 | -48.1764 | -68.3408 | -47.8973 | -51.9037 | -50.81 | -43.5305 | -48.125 | -68.8829 | -47.8694 | -43.9792 | -50.9077 | -43.5205 | -48.2123 | -68.7752 | -47.859 | -44.0765
60 | -1.4613 | 0 | -1.3805 | 0 | -1.501 | 0 | -1.3824 | 0 | -62.6326 | -148.2606 | -78.1182 | -91.8581 | -62.1827 | -34.5917 | -66.1746 | -139.0994 | -75.4298 | -60.4498 | -68.8212 | -50.2523 | -62.0511 | -166.1859 | -84.5219 | -152.8452 | -64.2301 | 76.5457 | -66.6649 | 159.0165 | -76.9025 | 159.3231 | -66.2365 | 105.173 | -21.8836 | -0.3464 | -33.903 | 36.3036 | -20.5248 | -10.6388 | -34.9212 | -19.1266 | -21.9384 | -5.5444 | -32.327 | 19.7543 | -20.2243 | -14.7191 | -44.7693 | 92.9116 | -53.2392 | -52.2426 | -44.9333 | -49.5244 | -69.3134 | -49.2191 | -53.1071 | -52.2159 | -45.0512 | -49.5328 | -69.6969 | -49.1925 | -45.3517 | 60 | -59.3337 | -60.8865 | -64.1128 | -61.1646 | -59.9798 | -60.6575 | -63.4014 | -61.9665 | 60 | -50.7546 | -43.5899 | -48.0631 | -67.9329 | -47.8386 | -51.6061 | -50.8354 | -43.5502 | -48.142 | -67.8124 | -47.8367 | -51.7247 | -50.7813 | -43.472 | -48.0715 | -68.3164 | -47.812 | -43.8507 | -50.8621 | -43.4323 | -48.1504 | -68.1959 | -47.8101 | -43.9693
61 | -1.4845 | 0 | -1.391 | 0 | -1.5166 | 0 | -1.4085 | 0 | -61.2473 | -169.4822 | -75.4835 | -168.5735 | -61.3038 | -70.0676 | -70.2449 | -142.0366 | -74.6123 | -71.992 | -72.6607 | -75.8506 | -60.6397 | 179.616 | -72.5157 | -178.8871 | -69.2463 | 95.7705 | -69.2234 | 117.2375 | -79.7387 | 165.1719 | -63.89 | 93.2027 | -20.9162 | -9.7786 | -31.657 | 30.4559 | -20.1182 | -23.5529 | -40.6733 | -24.0722 | -21.0879 | -18.6265 | -30.5278 | 17.2379 | -19.8688 | -28.7905 | -43.3803 | 109.656 | -53.0271 | -52.1997 | -44.898 | -49.4998 | -68.7927 | -49.2114 | -52.9183 | -52.1495 | -45.0509 | -49.4847 | -68.9456 | -49.1612 | -45.1685 | 61 | -58.1835 | -60.5579 | -67.5203 | -60.8122 | -59.8379 | -60.0295 | -62.3364 | -62.6931 | 61 | -50.665 | -43.5664 | -48.0153 | -67.4017 | -47.8204 | -51.4017 | -50.7585 | -43.5343 | -48.0913 | -67.2761 | -47.8029 | -51.5098 | -50.7152 | -43.4135 | -48.0002 | -67.5546 | -47.7702 | -43.6519 | -50.8087 | -43.3814 | -48.0762 | -67.429 | -47.7527 | -43.76
62 | -1.52 | 0 | -1.41 | 0 | -1.5366 | 0 | -1.4168 | 0 | -60.2088 | 170.1636 | -70.6835 | 150.5295 | -60.5013 | -105.7725 | -75.7766 | -113.4317 | -74.0895 | -83.8561 | -76.2593 | -122.2866 | -59.6759 | 163.632 | -67.6777 | 162.8936 | -67.2697 | 147.7895 | -69.3797 | 63.0808 | -78.9953 | -170.5781 | -62.3864 | 77.0914 | -20.4768 | -20.1244 | -30.0907 | 21.3865 | -20.1701 | -37.1074 | -50.3311 | 50.5287 | -20.7887 | -32.2594 | -29.077 | 10.1747 | -19.9753 | -43.2622 | -41.4355 | 117.0659 | -52.8079 | -52.0674 | -44.9024 | -49.5071 | -68.3899 | -49.2432 | -52.7342 | -52.0406 | -45.063 | -49.4685 | -68.1756 | -49.1812 | -44.8959 | 62 | -57.1456 | -59.9204 | -68.6791 | -60.2061 | -58.4294 | -59.1886 | -60.6384 | -61.0938 | 62 | -50.5206 | -43.543 | -47.9871 | -66.9799 | -47.8332 | -51.1976 | -50.6306 | -43.5264 | -48.0903 | -66.8533 | -47.8264 | -51.3174 | -50.5474 | -43.3824 | -47.9485 | -66.7656 | -47.7712 | -43.3593 | -50.6574 | -43.3658 | -48.0517 | -66.639 | -47.7644 | -43.4791
63 | -1.5444 | 0 | -1.4192 | 0 | -1.5606 | 0 | -1.4247 | 0 | -59.5371 | 149.7342 | -67.391 | 124.7283 | -58.89 | -137.0286 | -72.6491 | -63.538 | -73.4109 | -97.6801 | -75.8229 | 139.3147 | -59.1708 | 146.2882 | -64.5438 | 144.9853 | -61.9589 | 149.4982 | -66.913 | 19.3494 | -76.0498 | -151.4898 | -61.8408 | 67.3616 | -20.4535 | -31.0459 | -29.1135 | 10.2961 | -20.7094 | -50.5351 | -38.8841 | 93.3609 | -20.9481 | -46.4922 | -28.1659 | 0.8149 | -20.5914 | -57.8421 | -39.7637 | 118.5289 | -52.6181 | -51.8923 | -44.8057 | -49.5282 | -68.0829 | -49.3727 | -52.5716 | -51.795 | -45.0053 | -49.47 | -67.5989 | -49.2872 | -44.5412 | 63 | -55.8736 | -59.1635 | -65.8029 | -58.6551 | -56.5786 | -58.4201 | -59.1745 | -58.8064 | 63 | -50.2506 | -43.4609 | -47.9838 | -66.6637 | -47.9535 | -51.011 | -50.3758 | -43.4447 | -48.1035 | -66.5223 | -47.948 | -51.1469 | -50.3479 | -43.2613 | -47.9256 | -66.1797 | -47.868 | -42.9806 | -50.4731 | -43.2451 | -48.0453 | -66.0383 | -47.8625 | -43.1165
64 | -1.5535 | 0 | -1.4331 | 0 | -1.5706 | 0 | -1.4335 | 0 | -59.3733 | 128.7516 | -65.1976 | 103.4424 | -57.6772 | -167.9411 | -67.6608 | -59.3822 | -73.0933 | -112.3994 | -70.7645 | 110.7838 | -59.146 | 128.0189 | -62.3915 | 128.3808 | -58.1706 | 147.5797 | -64.3399 | -11.1183 | -72.0242 | -153.668 | -61.0458 | 57.2377 | -20.8088 | -42.2867 | -28.6302 | -2.6853 | -21.6798 | -64.2493 | -33.9449 | 84.3843 | -21.6431 | -60.346 | -27.7638 | -9.5258 | -21.6793 | -72.8263 | -37.8032 | 115.9072 | -52.5148 | -51.6523 | -44.6275 | -49.5422 | -68.3195 | -49.5391 | -52.4878 | -51.4846 | -44.9012 | -49.4682 | -67.2495 | -49.4221 | -44.1685 | 64 | -54.9968 | -58.6149 | -62.5384 | -57.3516 | -54.7916 | -57.8299 | -57.6178 | -56.2478 | 64 | -49.9311 | -43.3477 | -47.9887 | -66.8864 | -48.106 | -50.9172 | -50.0515 | -43.3306 | -48.1087 | -66.7489 | -48.1056 | -51.0543 | -50.0988 | -43.074 | -47.9147 | -65.8164 | -47.989 | -42.5979 | -50.2192 | -43.0569 | -48.0347 | -65.6789 | -47.9886 | -42.735
65 | -1.5597 | 0 | -1.4346 | 0 | -1.5875 | 0 | -1.4427 | 0 | -59.6808 | 107.4969 | -63.6726 | 84.6343 | -55.8992 | 167.8584 | -64.5023 | -68.2593 | -72.2311 | -130.4351 | -66.2736 | 78.6814 | -59.7292 | 108.8955 | -60.9373 | 111.2748 | -54.94 | 136.2778 | -62.3506 | -34.3214 | -69.0018 | -167.5922 | -60.3562 | 46.0001 | -21.6638 | -53.0825 | -28.7558 | -15.6518 | -23.3089 | -77.2295 | -30.9188 | 73.6648 | -22.8557 | -74.4191 | -27.8137 | -20.3577 | -23.4932 | -87.4818 | -36.4049 | 110.9406 | -52.5399 | -51.3296 | -44.3408 | -49.5555 | -69.0985 | -49.7085 | -52.4893 | -51.15 | -44.6418 | -49.4815 | -67.2588 | -49.5524 | -43.8183 | 65 | -53.8972 | -58.266 | -59.915 | -55.4264 | -52.9444 | -57.5149 | -56.3655 | -53.7127 | 65 | -49.5903 | -43.0821 | -47.9958 | -67.6639 | -48.2739 | -50.9018 | -49.7154 | -43.0543 | -48.1128 | -67.511 | -48.2658 | -51.0466 | -49.7699 | -42.7811 | -47.9218 | -65.8242 | -48.1178 | -42.2308 | -49.895 | -42.7533 | -48.0388 | -65.6713 | -48.1097 | -42.3756
66 | -1.5687 | 0 | -1.4698 | 0 | -1.5952 | 0 | -1.4623 | 0 | -60.6401 | 86.031 | -62.5412 | 66.4048 | -54.9604 | 141.8437 | -62.6662 | -79.6761 | -72.2629 | -155.0142 | -62.8004 | 67.7219 | -61.0617 | 90.2038 | -59.9325 | 94.5763 | -52.8445 | 121.0746 | -60.9973 | -53.7753 | -67.0285 | 175.7537 | -60.3226 | 36.1478 | -22.9338 | -63.2627 | -29.3918 | -28.9815 | -25.6188 | -89.0889 | -29.099 | 60.5874 | -24.7467 | -88.329 | -28.5063 | -30.5657 | -26.0982 | -101.9883 | -35.2842 | 106.4994 | -52.7159 | -51.021 | -44.014 | -49.6026 | -70.4308 | -49.8374 | -52.6573 | -50.8062 | -44.346 | -49.505 | -67.755 | -49.689 | -43.5213 | 66 | -53.3618 | -58.3458 | -57.8968 | -54.2304 | -51.5531 | -57.5052 | -55.6242 | -51.992 | 66 | -49.2375 | -42.7773 | -48.0339 | -68.961 | -48.3676 | -51.0621 | -49.3364 | -42.7508 | -48.1403 | -68.8356 | -48.3751 | -51.195 | -49.4523 | -42.4453 | -47.9363 | -66.2852 | -48.2192 | -41.9261 | -49.5512 | -42.4188 | -48.0427 | -66.1598 | -48.2267 | -42.059
67 | -1.5871 | 0 | -1.48 | 0 | -1.5856 | 0 | -1.4693 | 0 | -62.2917 | 65.6769 | -61.8298 | 48.4535 | -53.6066 | 116.5793 | -61.5188 | -91.2464 | -72.7447 | 174.584 | -60.9322 | 49.4352 | -63.172 | 73.4249 | -59.499 | 77.8277 | -51.3257 | 103.5294 | -60.0376 | -71.0745 | -65.9096 | 158.2701 | -59.9517 | 27.9459 | -24.8691 | -72.153 | -30.9169 | -42.0427 | -29.0683 | -98.7371 | -28.0269 | 48.962 | -27.4618 | -101.5097 | -29.6598 | -40.5267 | -29.9188 | -114.4451 | -34.6852 | 102.2047 | -52.9762 | -50.7302 | -43.7005 | -49.6012 | -72.5309 | -49.906 | -52.8667 | -50.4918 | -44.0363 | -49.5034 | -68.8941 | -49.7379 | -43.2616 | 67 | -52.5145 | -58.7031 | -56.6396 | -52.8245 | -50.4704 | -57.6206 | -55.0517 | -50.6364 | 67 | -48.9047 | -42.4492 | -48.0141 | -71.0509 | -48.426 | -51.2811 | -49.0118 | -42.4507 | -48.1319 | -70.9453 | -48.4367 | -51.3974 | -49.1431 | -42.1134 | -47.9163 | -67.4141 | -48.2579 | -41.676 | -49.2502 | -42.1149 | -48.0341 | -67.3085 | -48.2686 | -41.7923
68 | -1.5877 | 0 | -1.4896 | 0 | -1.5854 | 0 | -1.4847 | 0 | -64.6949 | 45.5805 | -61.5624 | 30.3934 | -53.1283 | 92.3312 | -60.8473 | -102.7042 | -73.9199 | 138.2052 | -58.5247 | 33.5041 | -66.1813 | 59.7617 | -59.4987 | 61.8301 | -50.7466 | 84.904 | -59.4359 | -86.8726 | -65.061 | 141.6159 | -58.7585 | 21.696 | -27.459 | -76.8166 | -33.2621 | -53.5338 | -34.5014 | -97.1775 | -27.3955 | 36.1617 | -31.8413 | -112.026 | -31.5869 | -46.8496 | -37.0615 | -118.2439 | -33.8828 | 97.3375 | -53.15 | -50.5075 | -43.4747 | -49.5406 | -74.8805 | -49.8942 | -53.017 | -50.2807 | -43.8026 | -49.4545 | -70.3021 | -49.7612 | -43.1439 | 68 | -52.2892 | -59.199 | -55.3386 | -51.999 | -50.0949 | -57.7174 | -54.4467 | -49.9726 | 68 | -48.693 | -42.2149 | -47.9529 | -73.3909 | -48.4046 | -51.4316 | -48.7911 | -42.2172 | -48.0559 | -73.2951 | -48.4095 | -51.5323 | -48.9198 | -41.887 | -47.8668 | -68.8125 | -48.2716 | -41.5585 | -49.0179 | -41.8893 | -47.9698 | -68.7167 | -48.2765 | -41.6592
69 | -1.5926 | 0 | -1.4966 | 0 | -1.6014 | 0 | -1.5035 | 0 | -68.1404 | 24.969 | -61.6805 | 11.4156 | -52.6043 | 67.7918 | -60.4392 | -113.6867 | -74.6887 | 95.1286 | -57.6322 | 17.2668 | -70.6879 | 50.1535 | -60.0501 | 46.4594 | -50.4369 | 68.7311 | -59.1508 | -101.7216 | -64.9694 | 126.0666 | -58.5238 | 9.5591 | -30.819 | -72.9538 | -37.4459 | -60.6949 | -39.3438 | -50.4332 | -27.2566 | 24.0258 | -40.3246 | -108.1274 | -34.2314 | -46.584 | -44.1011 | -32.4115 | -33.2676 | 91.7772 | -53.2157 | -50.3361 | -43.3273 | -49.4422 | -76.4032 | -49.8049 | -53.0239 | -50.0819 | -43.6434 | -49.356 | -72.063 | -49.6717 | -43.1479 | 69 | -51.9911 | -59.6208 | -54.8045 | -51.3973 | -49.9496 | -57.9054 | -54.4258 | -49.6794 | 69 | -48.4893 | -42.0508 | -47.8496 | -74.9066 | -48.3083 | -51.4225 | -48.5853 | -42.042 | -47.9387 | -74.8018 | -48.3014 | -51.5204 | -48.7435 | -41.7347 | -47.7634 | -70.5664 | -48.1751 | -41.5465 | -48.8395 | -41.7259 | -47.8525 | -70.4616 | -48.1682 | -41.6444
70 | -1.592 | 0 | -1.5169 | 0 | -1.6194 | 0 | -1.5197 | 0 | -73.3728 | -4.8335 | -62.2748 | -8.0879 | -52.6387 | 44.8362 | -60.2715 | -124.1459 | -73.8041 | 46.5814 | -56.1523 | -2.8559 | -78.5614 | 57.8037 | -61.1774 | 33.3096 | -50.5785 | 51.7401 | -59.0317 | -115.5992 | -65.0862 | 111.8954 | -58.037 | -1.2836 | -33.5597 | -50.8927 | -45.0405 | -32.563 | -34.3854 | -13.4407 | -27.4556 | 12.7128 | -41.7411 | -8.5274 | -36.9112 | -29.8555 | -34.9505 | -7.2201 | -32.4733 | 87.6775 | -53.1775 | -50.2214 | -43.2096 | -49.3337 | -75.7791 | -49.5065 | -52.9505 | -49.9475 | -43.549 | -49.2357 | -73.9622 | -49.4436 | -43.3453 | 70 | -52.1574 | -59.8841 | -54.0263 | -51.0162 | -50.2094 | -58.0308 | -54.4566 | -49.7329 | 70 | -48.3555 | -41.957 | -47.7417 | -74.2622 | -47.9896 | -51.3311 | -48.4306 | -41.9296 | -47.814 | -74.1597 | -47.9868 | -51.4308 | -48.6294 | -41.6176 | -47.6437 | -72.4453 | -47.9267 | -41.7259 | -48.7045 | -41.5902 | -47.716 | -72.3428 | -47.9239 | -41.8256
71 | -1.5998 | 0 | -1.519 | 0 | -1.6241 | 0 | -1.5366 | 0 | -78.6727 | -83.4397 | -63.3915 | -28.7855 | -52.9461 | 21.4498 | -60.0842 | -134.3466 | -71.8818 | 9.5218 | -55.312 | -21.7416 | -78.8919 | 152.2265 | -62.9843 | 23.087 | -51.4352 | 37.4667 | -59.1359 | -129.6622 | -65.4045 | 97.5954 | -57.7067 | -18.53 | -32.5946 | -25.0001 | -40.6996 | 35.2881 | -30.6616 | -15.0849 | -28.1773 | 2.6342 | -33.8638 | -2.9558 | -35.7909 | -5.2651 | -30.8835 | -18.9185 | -31.9589 | 80.9895 | -53.0155 | -50.1324 | -43.2058 | -49.1015 | -73.289 | -49.0855 | -52.7885 | -49.8233 | -43.51 | -49.0034 | -75.2338 | -49.0499 | -43.7014 | 71 | -52.5602 | -59.7502 | -53.5834 | -50.9246 | -51.1341 | -58.1783 | -54.6613 | -50.3765 | 71 | -48.2235 | -41.9102 | -47.5017 | -71.77 | -47.5665 | -51.1644 | -48.3043 | -41.8859 | -47.5649 | -71.6649 | -47.5489 | -51.2519 | -48.5326 | -41.606 | -47.4036 | -73.7148 | -47.5309 | -42.0773 | -48.6134 | -41.5817 | -47.4668 | -73.6097 | -47.5133 | -42.1648
72 | -1.6039 | 0 | -1.5218 | 0 | -1.6565 | 0 | -1.5379 | 0 | -72.6798 | -150.7439 | -65.1693 | -53.6644 | -53.3137 | -2.2878 | -59.9701 | -146.4277 | -69.7077 | -23.4192 | -55.4987 | -44.1642 | -70.8944 | 159.7859 | -65.7216 | 18.9814 | -52.4614 | 21.9231 | -59.4936 | -144.3568 | -65.954 | 84.2345 | -58.6181 | -31.678 | -29.9243 | -16.8481 | -34.3704 | 36.6534 | -28.5379 | -24.3993 | -29.0852 | -5.3759 | -30.5081 | -14.326 | -32.8432 | 3.5292 | -29.0796 | -33.3949 | -31.6236 | 72.8371 | -52.7957 | -50.1179 | -43.1629 | -48.7957 | -70.8074 | -48.5437 | -52.5218 | -49.7854 | -43.5023 | -48.6858 | -74.3577 | -48.5628 | -44.2376 | 72 | -52.9923 | -59.3262 | -53.8402 | -51.1983 | -52.202 | -58.3597 | -55.5813 | -51.3655 | 72 | -48.1815 | -41.8984 | -47.1918 | -69.2856 | -47.0219 | -50.8653 | -48.2636 | -41.8458 | -47.2578 | -69.1509 | -47.0058 | -50.9839 | -48.514 | -41.559 | -47.0819 | -72.8359 | -47.041 | -42.5811 | -48.5961 | -41.5064 | -47.1479 | -72.7012 | -47.0249 | -42.6997
73 | -1.6067 | 0 | -1.5366 | 0 | -1.6675 | 0 | -1.5522 | 0 | -67.7894 | -177.2717 | -67.915 | -87.0176 | -54.247 | -26.3692 | -60.0835 | -160.6944 | -67.9217 | -49.1646 | -55.7148 | -66.3933 | -66.5306 | 151.1803 | -68.9464 | 31.851 | -54.0935 | 8.7883 | -60.202 | -160.9785 | -66.761 | 74.044 | -60.1299 | -49.9505 | -28.1901 | -19.7111 | -30.9095 | 25.9648 | -27.6776 | -36.054 | -30.4552 | -10.3365 | -29.0291 | -27.0094 | -30.2016 | -0.4311 | -28.4466 | -48.7546 | -31.232 | 65.6816 | -52.5527 | -50.1055 | -43.1658 | -48.4941 | -68.6152 | -47.9688 | -52.2163 | -49.7847 | -43.5169 | -48.3491 | -71.939 | -48.0699 | -44.6978 | 73 | -53.8839 | -58.8316 | -54.1737 | -51.8015 | -53.7202 | -58.5771 | -56.8771 | -52.9434 | 73 | -48.178 | -41.9102 | -46.8874 | -67.0786 | -46.4322 | -50.5488 | -48.2481 | -41.8494 | -46.9419 | -66.9477 | -46.4166 | -50.6641 | -48.4988 | -41.5591 | -46.7424 | -70.4024 | -46.5333 | -43.0303 | -48.5689 | -41.4983 | -46.7969 | -70.2715 | -46.5177 | -43.1456
74 | -1.6305 | 0 | -1.5589 | 0 | -1.6756 | 0 | -1.5702 | 0 | -64.5037 | 163.395 | -70.4685 | -142.0044 | -55.2606 | -53.9194 | -60.7367 | -177.9664 | -66.7587 | -71.9443 | -56.5475 | -90.0737 | -63.624 | 137.8862 | -68.3591 | 62.5326 | -56.4656 | -1.6916 | -61.7121 | -178.685 | -67.8414 | 66.1403 | -63.9344 | -62.3645 | -27.1634 | -26.4919 | -28.6881 | 11.615 | -27.4382 | -48.4521 | -31.7376 | -12.5342 | -28.6944 | -41.0388 | -28.5308 | -9.5887 | -28.7105 | -65.5424 | -31.2522 | 56.7551 | -52.2078 | -50.1175 | -43.2521 | -48.2351 | -66.743 | -47.5159 | -51.8636 | -49.8514 | -43.5992 | -48.0667 | -69.3245 | -47.6639 | -44.8816 | 74 | -54.6567 | -58.5096 | -55.0195 | -52.6733 | -55.4721 | -58.9528 | -59.1212 | -55.4897 | 74 | -48.2209 | -41.9687 | -46.6046 | -65.1841 | -45.957 | -50.188 | -48.2925 | -41.9236 | -46.6649 | -65.0674 | -45.9457 | -50.2934 | -48.487 | -41.6216 | -46.4362 | -67.7656 | -46.105 | -43.206 | -48.5586 | -41.5765 | -46.4965 | -67.6489 | -46.0937 | -43.3114
75 | -1.6313 | 0 | -1.5698 | 0 | -1.6762 | 0 | -1.5578 | 0 | -62.0113 | 145.5676 | -68.2937 | 152.7455 | -56.2949 | -83.0164 | -62.3397 | 162.6095 | -66.2956 | -91.0225 | -58.9568 | -115.6595 | -61.3031 | 121.729 | -64.5459 | 74.0495 | -59.9981 | -8.5644 | -64.4154 | 161.807 | -68.5327 | 56.6532 | -69.6526 | -62.6802 | -27.0233 | -33.8965 | -27.4346 | -2.9802 | -28.043 | -61.0496 | -32.9608 | -9.0958 | -29.5524 | -55.1949 | -27.5308 | -21.8193 | -29.8428 | -83.6132 | -31.7108 | 46.4979 | -51.8321 | -50.1064 | -43.3818 | -48.0821 | -65.3086 | -47.2704 | -51.4644 | -49.9614 | -43.6821 | -47.9253 | -67.2456 | -47.4653 | -44.6597 | 75 | -55.0523 | -58.3939 | -56.9829 | -54.1418 | -56.7938 | -59.0561 | -60.8555 | -59.0345 | 75 | -48.3301 | -42.0508 | -46.4508 | -63.7388 | -45.7006 | -49.7882 | -48.3916 | -42.0059 | -46.5243 | -63.6324 | -45.7126 | -49.9066 | -48.4751 | -41.7505 | -46.294 | -65.6758 | -45.8955 | -42.9835 | -48.5366 | -41.7056 | -46.3675 | -65.5694 | -45.9075 | -43.1019
76 | -1.6547 | 0 | -1.5928 | 0 | -1.6815 | 0 | -1.5628 | 0 | -60.0266 | 125.929 | -64.3729 | 110.77 | -57.1333 | -115.5464 | -65.2436 | 140.4949 | -65.7533 | -105.6642 | -61.4647 | -143.7827 | -59.4752 | 102.7617 | -61.4111 | 70.1253 | -66.6316 | 2.9178 | -69.5636 | 139.6507 | -69.8725 | 42.5022 | -70.7119 | 3.492 | -27.4362 | -40.427 | -26.6462 | -18.2757 | -29.3594 | -72.8907 | -33.3327 | -2.0031 | -31.0746 | -68.0225 | -26.9154 | -35.688 | -31.6978 | -102.5483 | -32.5348 | 35.311 | -51.398 | -50.0766 | -43.5224 | -48.0699 | -64.191 | -47.3227 | -51.0381 | -50.1308 | -43.7993 | -47.9014 | -65.5615 | -47.5526 | -44.1925 | 76 | -54.8225 | -58.0723 | -58.6073 | -55.3543 | -56.844 | -58.7225 | -60.3714 | -63.9249 | 76 | -48.4761 | -42.1446 | -46.4152 | -62.5982 | -45.7299 | -49.3566 | -48.538 | -42.1178 | -46.5071 | -62.5095 | -45.7599 | -49.4753 | -48.4219 | -41.8677 | -46.2467 | -63.9687 | -45.9598 | -42.511 | -48.4838 | -41.8409 | -46.3386 | -63.88 | -45.9898 | -42.6297
77 | -1.6711 | 0 | -1.6066 | 0 | -1.6836 | 0 | -1.586 | 0 | -58.6552 | 102.5674 | -61.4295 | 81.2505 | -56.6772 | -151.4048 | -70.4612 | 115.8598 | -64.7581 | -119.2179 | -64.2778 | 175.9147 | -58.0918 | 79.5951 | -59.0791 | 61.0411 | -68.1105 | 78.5557 | -82.6516 | 91.2362 | -74.2072 | 25.5178 | -65.3716 | 22.6737 | -28.325 | -44.5461 | -26.4584 | -34.4264 | -31.4324 | -83.3456 | -32.6981 | 1.595 | -34.5642 | -77.5675 | -26.9241 | -50.5166 | -34.9939 | -125.3613 | -34.0526 | 23.2431 | -51.0271 | -50.0377 | -43.574 | -48.2537 | -63.5446 | -47.6236 | -50.6594 | -50.2266 | -43.8742 | -48.0851 | -64.2588 | -47.8633 | -43.5442 | 77 | -53.7349 | -57.4782 | -59.2705 | -55.4409 | -55.3129 | -57.972 | -58.1476 | -63.1627 | 77 | -48.5555 | -42.2031 | -46.5826 | -61.938 | -46.017 | -48.9758 | -48.62 | -42.1906 | -46.6677 | -61.861 | -46.0376 | -49.0734 | -48.3666 | -41.9029 | -46.414 | -62.6522 | -46.2567 | -41.8606 | -48.4311 | -41.8904 | -46.4991 | -62.5752 | -46.2773 | -41.9582
78 | -1.6884 | 0 | -1.6069 | 0 | -1.7206 | 0 | -1.5862 | 0 | -58.3003 | 74.4792 | -59.3941 | 57.2751 | -54.9693 | 172.0439 | -80.7308 | 63.3445 | -63.042 | -137.4765 | -64.5385 | 119.7473 | -57.5764 | 50.4059 | -57.2877 | 49.3878 | -58.1654 | 98.8484 | -74.4975 | -49.4357 | -83.7619 | 117.7453 | -61.9444 | 21.1442 | -29.4941 | -43.9448 | -26.7147 | -50.1307 | -34.9585 | -89.3655 | -31.8847 | 2.1975 | -41.3939 | -71.6078 | -27.4715 | -66.3461 | -40.5558 | -161.6319 | -36.6868 | 10.5918 | -51.0801 | -49.9673 | -43.2339 | -48.5703 | -63.5917 | -48.1938 | -50.6068 | -50.2362 | -43.6629 | -48.3432 | -63.6166 | -48.3768 | -42.882 | 78 | -52.3557 | -57.025 | -58.2107 | -53.944 | -52.8901 | -57.4788 | -55.9483 | -56.6375 | 78 | -48.5478 | -41.9745 | -46.8819 | -61.9848 | -46.5869 | -48.8862 | -48.6293 | -41.9423 | -46.9841 | -61.8711 | -46.6076 | -49.0206 | -48.2789 | -41.5455 | -46.6548 | -62.0097 | -46.7699 | -41.1614 | -48.3604 | -41.5133 | -46.757 | -61.896 | -46.7906 | -41.2958
79 | -1.703 | 0 | -1.6233 | 0 | -1.7174 | 0 | -1.5967 | 0 | -59.8355 | 44.0874 | -57.9914 | 35.7067 | -52.7489 | 134.7089 | -77.0708 | -50.8688 | -62.0306 | -163.0287 | -61.4897 | 74.7182 | -58.6342 | 18.2517 | -55.9924 | 35.3826 | -52.517 | 84.6668 | -68.1832 | -66.2861 | -70.1789 | 120.02 | -59.0256 | 13.1037 | -30.4474 | -38.0339 | -27.4767 | -66.409 | -40.1331 | -76.3024 | -30.9554 | -2.6666 | -43.0671 | 9.3661 | -28.5868 | -83.3824 | -44.7865 | 109.5945 | -42.2194 | -2.1269 | -51.9443 | -49.8236 | -42.5553 | -49.0537 | -65.2451 | -48.8392 | -51.342 | -50.1627 | -43.0819 | -48.7209 | -64.2991 | -48.9987 | -42.205 | 79 | -51.0035 | -57.7346 | -56.3502 | -51.7742 | -50.2286 | -57.9117 | -54.0674 | -51.5808 | 79 | -48.4597 | -41.3789 | -47.3507 | -63.6218 | -47.2159 | -49.6246 | -48.5394 | -41.3645 | -47.457 | -63.5277 | -47.2425 | -49.7453 | -48.1206 | -40.8523 | -47.0179 | -62.6758 | -47.3754 | -40.4876 | -48.2003 | -40.8379 | -47.1242 | -62.5817 | -47.402 | -40.6083
80 | -1.7209 | 0 | -1.6087 | 0 | -1.7398 | 0 | -1.6201 | 0 | -63.3899 | 19.5751 | -57.1153 | 14.9614 | -51.2177 | 100.2442 | -71.8747 | -70.7781 | -62.3733 | 169.2367 | -58.2501 | 45.3429 | -61.1237 | -10.0867 | -55.3729 | 21.2254 | -49.6046 | 61.9142 | -64.5687 | -77.1305 | -66.3475 | 94.0724 | -56.9068 | 6.3553 | -30.3996 | -27.6067 | -28.8271 | -82.8187 | -40.6115 | -28.2314 | -30.2832 | -9.9347 | -34.7997 | 26.5207 | -30.505 | -101.6342 | -38.8315 | 45.398 | -69.7404 | 122.7772 | -53.047 | -49.6821 | -42.1162 | -49.5431 | -68.4884 | -49.5883 | -52.4212 | -50.1383 | -42.6037 | -49.1399 | -66.343 | -49.7359 | -41.614 | 80 | -50.0191 | -59.5779 | -54.5542 | -50.1637 | -48.3484 | -58.6866 | -52.7655 | -48.7865 | 80 | -48.4174 | -40.8828 | -47.8222 | -66.8797 | -47.9796 | -50.6814 | -48.5296 | -40.8639 | -47.923 | -66.7486 | -47.9682 | -50.8011 | -47.9612 | -40.3953 | -47.419 | -64.7343 | -48.1272 | -39.8742 | -48.0734 | -40.3764 | -47.5198 | -64.6032 | -48.1158 | -39.9939
81 | -1.7014 | 0 | -1.6478 | 0 | -1.7632 | 0 | -1.6375 | 0 | -68.3957 | 2.4617 | -56.7155 | -4.495 | -50.323 | 73.1413 | -68.5561 | -74.6463 | -63.3604 | 145.3738 | -54.8105 | 19.6936 | -64.4303 | -34.3997 | -55.2249 | 7.8466 | -48.1902 | 42.3429 | -61.9038 | -86.194 | -65.076 | 72.8354 | -54.6348 | -4.2058 | -29.0613 | -19.2001 | -31.0367 | -97.3096 | -35.8146 | -12.8907 | -29.8527 | -17.6819 | -30.373 | 17.0002 | -33.6795 | -124.3598 | -35.254 | 14.7248 | -41.3273 | 147.5086 | -53.6487 | -49.5415 | -41.9329 | -50.051 | -72.7542 | -50.3774 | -53.2415 | -50.1382 | -42.3499 | -49.5618 | -68.5306 | -50.4312 | -41.1684 | 81 | -49.3711 | -61.2761 | -52.539 | -48.8446 | -47.3205 | -58.8062 | -51.4951 | -47.2307 | 81 | -48.4368 | -40.6485 | -48.3496 | -71.1064 | -48.7296 | -51.4783 | -48.4904 | -40.5867 | -48.4135 | -70.991 | -48.7399 | -51.604 | -47.8401 | -40.2315 | -47.8604 | -66.8828 | -48.7834 | -39.4052 | -47.8937 | -40.1697 | -47.9243 | -66.7674 | -48.7937 | -39.5309
82 | -1.7133 | 0 | -1.6457 | 0 | -1.7838 | 0 | -1.6426 | 0 | -77.0021 | -5.6463 | -56.7395 | -22.9073 | -49.6507 | 47.4951 | -65.3004 | -77.6422 | -64.609 | 120.9354 | -52.4945 | -0.6508 | -68.1722 | -59.0913 | -55.2344 | -3.5819 | -47.6309 | 25.2323 | -59.5046 | -96.022 | -64.9452 | 56.1856 | -52.272 | -19.6366 | -27.2599 | -19.3073 | -34.6526 | -110.8881 | -32.9559 | -19.7126 | -29.801 | -26.892 | -27.7216 | 3.2021 | -38.8021 | -157.9196 | -33.5437 | -9.6266 | -35.6777 | 133.6071 | -53.7873 | -49.3864 | -41.8862 | -50.3772 | -79.0334 | -50.8434 | -53.6418 | -49.9947 | -42.2445 | -49.7746 | -70.8332 | -50.7213 | -40.9191 | 82 | -48.8686 | -61.7976 | -50.9452 | -47.7433 | -46.903 | -57.9767 | -49.9812 | -46.289 | 82 | -48.2814 | -40.5312 | -48.6639 | -77.3877 | -49.1977 | -51.858 | -48.349 | -40.4607 | -48.7346 | -77.2496 | -49.2008 | -51.9992 | -47.6731 | -40.1729 | -48.0613 | -69.1875 | -49.0756 | -39.1353 | -47.7407 | -40.1024 | -48.132 | -69.0494 | -49.0787 | -39.2765
83 | -1.7321 | 0 | -1.6524 | 0 | -1.8182 | 0 | -1.666 | 0 | -82.8694 | 128.2048 | -57.0744 | -40.1697 | -49.1881 | 24.9003 | -61.7561 | -84.5033 | -65.7445 | 92.8315 | -50.6758 | -21.5538 | -72.6155 | -93.1235 | -55.4648 | -13.8315 | -47.2168 | 9.5984 | -57.2 | -106.6899 | -64.8176 | 40.4725 | -50.9382 | -37.0346 | -25.8306 | -24.7809 | -41.8025 | -113.9604 | -31.4772 | -31.385 | -30.1043 | -35.6661 | -26.218 | -11.9548 | -42.4674 | 120.5691 | -33.3582 | -34.6548 | -32.0926 | 120.4259 | -53.6887 | -49.1631 | -41.8466 | -50.4661 | -98.3489 | -50.6435 | -53.7422 | -49.7205 | -42.2048 | -49.6954 | -73.2501 | -50.4393 | -41.0118 | 83 | -48.5318 | -60.2734 | -49.5126 | -46.8025 | -46.6001 | -56.4016 | -48.9266 | -45.6276 | 83 | -47.9884 | -40.4727 | -48.734 | -96.6965 | -48.9911 | -51.924 | -48.0681 | -40.3866 | -48.8001 | -96.5307 | -48.9775 | -52.0762 | -47.431 | -40.1145 | -47.9633 | -71.5977 | -48.7869 | -39.1936 | -47.5107 | -40.0284 | -48.0294 | -71.4319 | -48.7733 | -39.3458
84 | -1.7371 | 0 | -1.6376 | 0 | -1.8436 | 0 | -1.6801 | 0 | -72.3079 | 128.735 | -57.6756 | -55.2251 | -49.011 | 5.6878 | -58.596 | -99.4399 | -67.7182 | 62.7735 | -49.0481 | -44.8453 | -76.2458 | -154.5256 | -55.7293 | -23.0302 | -47.1572 | -5.2407 | -55.0901 | -122.3675 | -65.2564 | 25.4937 | -50.0603 | -56.232 | -24.9111 | -33.9714 | -46.3032 | -24.972 | -31.3614 | -45.8842 | -30.3305 | -45.6489 | -25.4199 | -27.5382 | -36.9207 | 57.3419 | -33.8414 | -61.3249 | -29.8157 | 105.7699 | -53.385 | -48.8722 | -41.8282 | -49.8811 | -79.0412 | -49.505 | -53.5986 | -49.2303 | -42.1864 | -49.0595 | -75.036 | -49.3006 | -41.529 | 84 | -48.4394 | -57.933 | -48.0855 | -45.9899 | -46.5875 | -54.6608 | -48.0596 | -45.316 | 84 | -47.4932 | -40.4493 | -48.144 | -77.4036 | -47.8674 | -51.755 | -47.5927 | -40.3428 | -48.201 | -77.1976 | -47.8249 | -51.9185 | -47.1351 | -40.0911 | -47.3224 | -73.3984 | -47.663 | -39.6854 | -47.2346 | -39.9846 | -47.3794 | -73.1924 | -47.6205 | -39.8489
85 | -1.7542 | 0 | -1.6553 | 0 | -1.8598 | 0 | -1.6833 | 0 | -68.4798 | 114.6228 | -58.1395 | -70.1842 | -48.9871 | -15.7683 | -56.2946 | -119.7368 | -69.5461 | 21.3127 | -48.2119 | -67.5403 | -74.4042 | 143.3597 | -55.9867 | -31.693 | -47.4808 | -19.8466 | -53.5474 | -141.6985 | -66.781 | 12.1098 | -49.3779 | -76.9492 | -24.4762 | -44.6085 | -37.0058 | -9.5151 | -31.9313 | -59.7653 | -30.6456 | -53.9757 | -25.2377 | -43.459 | -32.8407 | 29.0583 | -35.5873 | -92.4177 | -28.3281 | 91.3043 | -53.0004 | -48.4549 | -41.8258 | -48.8051 | -72.1918 | -47.8806 | -53.2412 | -48.5902 | -42.2034 | -48.0186 | -73.7217 | -47.7895 | -42.5566 | 85 | -48.4456 | -55.8501 | -47.2179 | -45.5546 | -46.9 | -53.312 | -47.3334 | -45.2854 | 85 | -46.836 | -40.4492 | -47.0509 | -70.5365 | -46.2253 | -51.3814 | -46.9349 | -40.3436 | -47.1218 | -70.332 | -46.1973 | -51.5579 | -46.7007 | -40.0716 | -46.2644 | -72.0664 | -46.1342 | -40.6968 | -46.7996 | -39.966 | -46.3353 | -71.8619 | -46.1062 | -40.8733
86 | -1.7717 | 0 | -1.6767 | 0 | -1.8653 | 0 | -1.6874 | 0 | -66.7881 | 101.3801 | -58.6179 | -86.8796 | -49.3216 | -35.8351 | -54.9917 | -143.3068 | -70.8363 | -26.9594 | -47.8049 | -89.7074 | -71.5279 | 106.3687 | -56.4564 | -41.0487 | -47.9553 | -33.0108 | -52.7097 | -163.315 | -69.2327 | 3.0962 | -49.732 | -100.1814 | -24.6339 | -56.2741 | -32.5736 | -22.2852 | -33.9156 | -72.7395 | -31.0144 | -63.1499 | -25.6617 | -59.7755 | -30.2661 | 6.2898 | -37.4354 | -133.0643 | -27.5499 | 76.2023 | -52.5179 | -48.0269 | -41.8083 | -47.5453 | -68.4984 | -46.2847 | -52.7197 | -47.9708 | -42.2327 | -46.8525 | -70.6298 | -46.338 | -43.9134 | 86 | -48.7697 | -54.6088 | -46.753 | -45.4744 | -47.3649 | -52.5586 | -47.3859 | -45.7237 | 86 | -46.1991 | -40.461 | -45.7736 | -66.8217 | -44.608 | -50.8544 | -46.2941 | -40.3674 | -45.8579 | -66.6331 | -44.5973 | -51.0323 | -46.2552 | -40.0366 | -45.0808 | -68.9531 | -44.6613 | -42.0481 | -46.3502 | -39.943 | -45.1651 | -68.7645 | -44.6506 | -42.226
87 | -1.788 | 0 | -1.6933 | 0 | -1.8759 | 0 | -1.7035 | 0 | -66.3187 | 89.432 | -59.2808 | -107.991 | -49.7151 | -56.8098 | -54.6737 | -167.9687 | -71.2086 | -73.211 | -47.9908 | -112.2921 | -69.608 | 80.8634 | -57.2263 | -49.4684 | -48.5755 | -44.3656 | -52.7197 | 174.1117 | -72.4807 | 16.0666 | -51.0064 | -122.8739 | -25.3868 | -67.9731 | -30.0924 | -38.8086 | -37.4685 | -80.9898 | -31.4448 | -73.1672 | -26.6576 | -74.5922 | -28.747 | -12.3312 | -38.3606 | 170.3319 | -26.9918 | 61.7206 | -51.9917 | -47.6743 | -41.8129 | -46.4917 | -66.2456 | -45.1313 | -52.1386 | -47.4189 | -42.2606 | -45.9745 | -67.8456 | -45.2548 | -45.3024 | 87 | -49.1752 | -54.2967 | -46.8885 | -45.7453 | -47.99 | -52.587 | -48.1897 | -46.6015 | 87 | -45.6309 | -40.4726 | -44.7037 | -64.5523 | -43.438 | -50.2627 | -45.7256 | -40.3847 | -44.7882 | -64.3697 | -43.4278 | -50.4351 | -45.8863 | -40.0249 | -44.1865 | -66.1523 | -43.5615 | -43.4265 | -45.981 | -39.937 | -44.271 | -65.9697 | -43.5513 | -43.5989
88 | -1.7919 | 0 | -1.7032 | 0 | -1.8609 | 0 | -1.7165 | 0 | -66.3145 | 82.6348 | -60.6315 | -135.9196 | -50.5718 | -76.8152 | -55.3409 | 167.5947 | -70.1501 | -114.0791 | -48.9101 | -133.3596 | -68.4233 | 60.5114 | -58.5176 | -55.1482 | -49.6534 | -56.2482 | -53.5662 | 152.3283 | -70.2443 | 37.6821 | -52.9362 | -144.2213 | -26.9517 | -79.0811 | -28.6 | -56.5734 | -43.4562 | -69.4725 | -31.8718 | -83.9052 | -28.7543 | -89.5895 | -27.9712 | -30.8668 | -36.0801 | 124.3709 | -27.0207 | 47.6594 | -51.5446 | -47.3625 | -41.8521 | -45.8063 | -64.8454 | -44.3898 | -51.5938 | -47.189 | -42.2646 | -45.3751 | -66.3165 | -44.5914 | -46.3809 | 88 | -50.0592 | -54.8761 | -47.7883 | -46.6323 | -49.0723 | -53.3371 | -49.6289 | -47.9557 | 88 | -45.3971 | -40.4727 | -44.0144 | -63.1422 | -42.6866 | -49.7329 | -45.4858 | -40.4037 | -44.0898 | -62.9845 | -42.6733 | -49.8773 | -45.5706 | -40.0602 | -43.5832 | -64.6133 | -42.8882 | -44.52 | -45.6593 | -39.9912 | -43.6586 | -64.4556 | -42.8749 | -44.6644
89 | -1.8051 | 0 | -1.7241 | 0 | -1.8522 | 0 | -1.7384 | 0 | -66.5702 | 78.2517 | -62.75 | -172.5117 | -51.7339 | -100.1846 | -56.9444 | 144.1842 | -70.0404 | -140.1306 | -50.0399 | -153.3659 | -67.6213 | 41.9947 | -59.8623 | -53.6212 | -51.1619 | -62.0483 | -55.186 | 132.607 | -66.9025 | 33.7674 | -56.1613 | -164.0974 | -29.7244 | -86.9272 | -27.6605 | -74.68 | -43.7302 | -5.711 | -32.1722 | -94.9217 | -32.5034 | -103.2299 | -27.701 | -48.6896 | -33.5163 | 90.6734 | -27.2771 | 31.9472 | -51.1672 | -47.221 | -41.9122 | -45.4523 | -64.2297 | -44.0491 | -51.1577 | -47.0749 | -42.2778 | -45.1265 | -65.5601 | -44.2897 | -46.8876 | 89 | -51.2729 | -56.3072 | -49.0447 | -47.7687 | -50.5268 | -54.6767 | -51.8828 | -49.8813 | 89 | -45.2698 | -40.4727 | -43.6472 | -62.5056 | -42.325 | -49.3055 | -45.3508 | -40.4256 | -43.7139 | -62.3775 | -42.3107 | -49.4193 | -45.4159 | -40.1071 | -43.3214 | -63.836 | -42.5656 | -45.0354 | -45.4969 | -40.06 | -43.3881 | -63.7079 | -42.5513 | -45.1492
90 | -1.8133 | 0 | -1.7443 | 0 | -1.8494 | 0 | -1.7362 | 0 | -66.4942 | 75.5077 | -64.5682 | 137.2051 | -52.9907 | -123.0452 | -59.6301 | 123.0701 | -69.6535 | -158.3217 | -51.8565 | -172.6858 | -66.9088 | 25.4477 | -60.1417 | -45.5821 | -52.8482 | -66.9587 | -57.572 | 116.3196 | -64.5992 | 20.9549 | -60.0292 | 178.9041 | -34.3625 | -83.0875 | -27.2468 | -93.3674 | -37.6947 | 9.6694 | -32.3685 | -106.1857 | -40.4049 | -100.5261 | -28.024 | -67.1642 | -31.6108 | 64.8366 | -28.0037 | 16.2224 | -50.8905 | -47.1713 | -42.0102 | -45.328 | -64.035 | -43.9877 | -50.8146 | -47.072 | -42.2859 | -45.0997 | -65.3927 | -44.2634 | -46.779 | 90 | -52.5212 | -58.4729 | -50.991 | -49.3358 | -51.9642 | -56.3835 | -54.306 | -51.8507 | 90 | -45.2587 | -40.4726 | -43.5147 | -62.2907 | -42.2434 | -48.9652 | -45.3277 | -40.4365 | -43.5918 | -62.1856 | -42.2515 | -49.0784 | -45.358 | -40.1969 | -43.2864 | -63.6484 | -42.5191 | -44.9296 | -45.427 | -40.1608 | -43.3635 | -63.5433 | -42.5272 | -45.0428
91 | -1.8107 | 0 | -1.7447 | 0 | -1.8376 | 0 | -1.733 | 0 | -65.8075 | 73.3091 | -63.6 | 81.4166 | -55.1872 | -150.643 | -63.7253 | 104.5993 | -69.6615 | -172.1421 | -53.8716 | 170.5246 | -66.0314 | 8.0123 | -58.8913 | -40.4654 | -54.242 | -66.4537 | -60.6882 | 104.772 | -63.298 | 3.8403 | -66.4592 | 152.8776 | -37.7883 | -31.4566 | -27.2981 | -113.4905 | -33.8636 | 4.7768 | -32.4983 | -121.2491 | -39.6677 | -4.4793 | -28.6635 | -85.4183 | -30.3938 | 39.0797 | -29.0091 | -1.8925 | -50.6058 | -47.1947 | -42.0897 | -45.3753 | -64.012 | -44.1401 | -50.483 | -47.1305 | -42.2599 | -45.1822 | -65.3463 | -44.3923 | -46.1694 | 91 | -54.2853 | -60.9975 | -53.0442 | -51.4041 | -52.7527 | -58.0388 | -56.252 | -53.5074 | 91 | -45.3198 | -40.4492 | -43.5646 | -62.2673 | -42.3954 | -48.6454 | -45.3858 | -40.4223 | -43.6423 | -62.1744 | -42.4071 | -48.75 | -45.384 | -40.279 | -43.3715 | -63.6016 | -42.6476 | -44.3318 | -45.45 | -40.2521 | -43.4492 | -63.5087 | -42.6593 | -44.4364
92 | -1.8084 | 0 | -1.7484 | 0 | -1.8526 | 0 | -1.7346 | 0 | -64.9624 | 66.0076 | -61.0296 | 38.8276 | -57.4519 | 176.7556 | -70.0357 | 94.3637 | -69.1228 | 179.6129 | -56.3333 | 151.0495 | -64.8585 | -9.1721 | -57.2467 | -43.5094 | -55.2276 | -64.7409 | -64.204 | 102.0595 | -62.7727 | -15.1149 | -78.6042 | 68.9624 | -31.7241 | -1.1625 | -27.6952 | -133.4541 | -31.6864 | -5.458 | -32.5717 | -136.0668 | -31.7702 | -0.4572 | -29.9418 | -105.6826 | -29.699 | 16.5361 | -30.8625 | -20.8234 | -50.3165 | -47.2215 | -42.2047 | -45.5665 | -63.8986 | -44.4949 | -50.182 | -47.3955 | -42.2459 | -45.432 | -65.3265 | -44.7237 | -45.3366 | 92 | -55.3671 | -62.6717 | -54.929 | -53.7194 | -52.8295 | -59.0845 | -56.4231 | -54.5066 | 92 | -45.5871 | -40.4375 | -43.7581 | -62.1502 | -42.7465 | -48.3294 | -45.6471 | -40.3933 | -43.8319 | -62.046 | -42.7603 | -48.4474 | -45.4131 | -40.3963 | -43.6236 | -63.5781 | -42.9753 | -43.484 | -45.4731 | -40.3521 | -43.6974 | -63.4739 | -42.9891 | -43.602
93 | -1.8581 | 0 | -1.7476 | 0 | -1.8853 | 0 | -1.7566 | 0 | -64.1946 | 51.952 | -58.8386 | 7.6407 | -58.5517 | 134.6957 | -80.099 | 120.6045 | -67.8201 | 172.1926 | -59.3817 | 124.5447 | -63.2924 | -28.4255 | -55.9601 | -51.0152 | -55.1148 | -58.7764 | -67.3432 | 108.3569 | -63.1613 | -37.3454 | -67.897 | -0.2919 | -27.048 | -5.5847 | -28.5316 | -153.6597 | -29.9332 | -19.3284 | -32.5694 | -150.6424 | -27.5596 | -13.5129 | -31.8558 | -126.7722 | -29.5653 | -6.9118 | -33.2727 | -42.5596 | -50.0462 | -47.3285 | -42.3599 | -45.8822 | -63.4642 | -44.9848 | -49.853 | -47.7213 | -42.2605 | -45.7593 | -64.9741 | -45.2056 | -44.4512 | 93 | -55.1102 | -62.5521 | -56.0741 | -55.6639 | -52.1585 | -59.4469 | -55.4035 | -54.2887 | 93 | -45.8632 | -40.4024 | -44.0241 | -61.7166 | -43.2372 | -47.9677 | -45.9737 | -40.3752 | -44.1256 | -61.5789 | -43.2282 | -48.0964 | -45.4704 | -40.5018 | -43.9012 | -63.2265 | -43.458 | -42.5659 | -45.5809 | -40.4746 | -44.0027 | -63.0888 | -43.449 | -42.6946
94 | -1.8881 | 0 | -1.7608 | 0 | -1.895 | 0 | -1.7708 | 0 | -64.1545 | 26.5066 | -57.2451 | -17.9766 | -57.1182 | 94.7481 | -79.6256 | -162.3944 | -65.8469 | 162.0151 | -63.8417 | 77.0258 | -60.987 | -51.7913 | -55.1015 | -60.0752 | -55.644 | -55.5064 | -69.6415 | 115.5496 | -64.5388 | -60.8846 | -61.3793 | -26.1062 | -24.1082 | -16.7399 | -29.9473 | -175.4012 | -29.0171 | -33.4458 | -32.6854 | -167.4052 | -24.7979 | -29.849 | -34.4967 | -151.648 | -29.7271 | -32.1341 | -36.7166 | -74.9282 | -49.8251 | -47.3851 | -42.5423 | -46.3563 | -62.9813 | -45.6077 | -49.5029 | -48.0708 | -42.2319 | -46.2569 | -64.1514 | -45.7309 | -43.6248 | 94 | -53.7555 | -61.8356 | -56.3647 | -55.8257 | -51.7964 | -59.0067 | -54.0608 | -54.1953 | 94 | -46.1827 | -40.3438 | -44.4682 | -61.2205 | -43.8469 | -47.6079 | -46.31 | -40.3369 | -44.5855 | -61.0863 | -43.8369 | -47.7321 | -45.497 | -40.6542 | -44.3688 | -62.3906 | -43.9701 | -41.7298 | -45.6243 | -40.6473 | -44.4861 | -62.2564 | -43.9601 | -41.854
95 | -1.9379 | 0 | -1.7723 | 0 | -1.8991 | 0 | -1.7927 | 0 | -66.3812 | -22.2535 | -56.2266 | -40.8337 | -54.6185 | 59.1139 | -77.2636 | -126.0889 | -63.4873 | 142.7867 | -61.6455 | 11.7765 | -58.5222 | -85.7095 | -54.357 | -70.1157 | -55.371 | -39.5796 | -74.7865 | 122.4341 | -68.8949 | -83.5443 | -57.9864 | -43.0506 | -22.2898 | -30.3492 | -31.3605 | 161.7076 | -28.6733 | -48.5131 | -32.3493 | 175.6448 | -23.1551 | -47.7668 | -38.1314 | 174.5423 | -30.3379 | -60.3631 | -39.1812 | -122.9745 | -50.1296 | -47.5064 | -42.3694 | -46.9655 | -62.9695 | -46.4009 | -49.5262 | -48.3952 | -42.0121 | -46.866 | -63.6473 | -46.4303 | -42.9139 | 95 | -52.1703 | -61.5686 | -55.1038 | -53.3864 | -50.9824 | -58.0478 | -52.7655 | -53.3515 | 95 | -46.4573 | -40.0742 | -45.0276 | -61.1972 | -44.6286 | -47.6271 | -46.6229 | -40.113 | -45.1728 | -61.0704 | -44.6082 | -47.7335 | -45.5685 | -40.4315 | -44.9281 | -61.875 | -44.658 | -41.0148 | -45.7341 | -40.4703 | -45.0733 | -61.7482 | -44.6376 | -41.1212
96 | -1.9591 | 0 | -1.774 | 0 | -1.9341 | 0 | -1.7799 | 0 | -70.2478 | -123.2114 | -55.8365 | -62.7471 | -52.2417 | 28.8129 | -69.8787 | -92.6921 | -62.7191 | 115.1312 | -57.2781 | -31.2142 | -57.7571 | -126.4156 | -53.8897 | -81.9778 | -51.6994 | -36.8593 | -74.4763 | -131.7032 | -74.5056 | -55.6843 | -54.9371 | -56.9796 | -21.1228 | -44.8693 | -34.0529 | 138.1472 | -28.7299 | -65.2738 | -32.5709 | 160.3542 | -22.0391 | -65.0499 | -40.6148 | 123.5026 | -30.9269 | -91.6654 | -38.0836 | -176.178 | -51.3657 | -47.6117 | -41.7461 | -47.7915 | -64.9243 | -47.3773 | -50.5982 | -48.7231 | -41.5294 | -47.5279 | -64.6255 | -47.2309 | -42.3473 | 96 | -50.6194 | -61.3551 | -53.3889 | -50.7706 | -49.0235 | -57.5766 | -51.3504 | -49.9976 | 96 | -46.764 | -39.5703 | -45.8324 | -63.1503 | -45.6033 | -48.6641 | -46.9491 | -39.5953 | -46.0116 | -62.9902 | -45.5974 | -48.8183 | -45.6526 | -39.787 | -45.5688 | -62.8515 | -45.4569 | -40.4132 | -45.8377 | -39.812 | -45.748 | -62.6914 | -45.451 | -40.5674
97 | -1.9759 | 0 | -1.7972 | 0 | -1.9697 | 0 | -1.7878 | 0 | -65.7564 | 158.2126 | -56.1408 | -82.0344 | -50.8278 | 0.2566 | -63.2319 | -99.8194 | -63.0934 | 92.4266 | -53.2729 | -59.3826 | -58.439 | -161.4745 | -53.8308 | -93.8548 | -49.5662 | -49.9929 | -63.9721 | -133.3709 | -71.1278 | -41.2125 | -52.1907 | -73.08 | -20.2911 | -59.29 | -38.041 | 108.5083 | -29.2265 | -82.5398 | -33.0259 | 145.2732 | -21.3817 | -82.5892 | -39.6723 | 71.4674 | -31.0701 | -129.4221 | -35.6233 | 149.0273 | -52.1662 | -47.6943 | -41.4466 | -48.6037 | -68.0647 | -48.3544 | -51.8792 | -49.0752 | -41.3236 | -48.055 | -65.9651 | -47.8877 | -42.09 | 97 | -49.6011 | -59.0962 | -51.1841 | -48.709 | -47.7931 | -57.1889 | -49.7558 | -47.6533 | 97 | -47.0993 | -39.3477 | -46.6278 | -66.2675 | -46.5572 | -49.9095 | -47.278 | -39.3539 | -46.8159 | -66.095 | -46.5666 | -50.0914 | -45.7184 | -39.4707 | -46.0791 | -64.1679 | -46.0905 | -40.1203 | -45.8971 | -39.4769 | -46.2672 | -63.9954 | -46.0999 | -40.3022
98 | -1.995 | 0 | -1.7936 | 0 | -1.9949 | 0 | -1.8056 | 0 | -62.5924 | 121.0163 | -56.8513 | -96.7911 | -49.8652 | -23.3124 | -58.6454 | -118.6595 | -63.8047 | 70.5125 | -50.5377 | -84.9672 | -59.4781 | 169.4371 | -53.9818 | -104.2853 | -48.2902 | -65.2017 | -58.6868 | -152.8165 | -69.5988 | -53.7855 | -50.7001 | -93.0328 | -19.8983 | -73.9984 | -44.1343 | 63.672 | -30.438 | -100.4851 | -33.4612 | 130.5571 | -20.9646 | -100.0601 | -37.4837 | 34.3844 | -30.9086 | -163.7984 | -33.9197 | 123.0705 | -52.1979 | -47.5789 | -41.4188 | -48.9635 | -71.2486 | -48.7898 | -52.5827 | -49.1863 | -41.3075 | -48.0983 | -66.4694 | -48.0223 | -42.3419 | 98 | -48.8838 | -56.3209 | -49.1129 | -47.0847 | -47.0006 | -55.8663 | -48.5817 | -46.2994 | 98 | -47.1913 | -39.3125 | -46.9685 | -69.455 | -46.9962 | -50.5878 | -47.3927 | -39.3126 | -47.1579 | -69.2537 | -46.9842 | -50.7771 | -45.5839 | -39.4238 | -46.1033 | -64.6758 | -46.2287 | -40.347 | -45.7853 | -39.4239 | -46.2927 | -64.4745 | -46.2167 | -40.5363
99 | -1.9923 | 0 | -1.8203 | 0 | -2.0329 | 0 | -1.8093 | 0 | -60.9636 | 94.6789 | -57.3006 | -107.0355 | -49.2697 | -42.2247 | -55.8168 | -142.0839 | -64.7912 | 54.5114 | -48.823 | -107.8702 | -60.6243 | 143.808 | -54.0539 | -114.5299 | -48.0546 | -78.1296 | -55.4765 | -175.951 | -69.9013 | -72.8427 | -49.624 | -117.1554 | -19.8882 | -89.3548 | -47.0173 | -49.7902 | -32.4587 | -122.1389 | -34.0332 | 122.6342 | -20.8921 | -117.849 | -35.9314 | 9.0178 | -30.2915 | 161.2699 | -32.6658 | 105.9513 | -51.8965 | -47.3239 | -41.4044 | -48.4746 | -73.3418 | -48.0856 | -52.7266 | -48.7633 | -41.3283 | -47.4336 | -65.8594 | -47.3649 | -43.0832 | 99 | -48.3881 | -54.2563 | -47.5461 | -45.9729 | -46.8933 | -54.1998 | -47.5276 | -45.7418 | 99 | -46.771 | -39.336 | -46.4823 | -71.5215 | -46.2653 | -50.6937 | -46.943 | -39.2954 | -46.6653 | -71.3089 | -46.2763 | -50.9173 | -45.3316 | -39.4121 | -45.4413 | -64.0391 | -45.5446 | -41.0503 | -45.5036 | -39.3715 | -45.6243 | -63.8265 | -45.5556 | -41.2739
100 | -1.9844 | 0 | -1.8214 | 0 | -2.0654 | 0 | -1.8255 | 0 | -60.4975 | 71.4885 | -57.2104 | -117.9656 | -48.9456 | -61.8059 | -54.3738 | -167.5062 | -66.3535 | 37.0026 | -47.6517 | -132.7188 | -62.2435 | 120.9111 | -54.2022 | -125.6547 | -47.8097 | -90.842 | -53.7483 | 159.5685 | -72.8446 | -95.8274 | -49.3722 | -138.3483 | -20.2708 | -104.5057 | -39.1393 | -97.1273 | -36.0731 | -143.1259 | -35.3528 | 112.9467 | -21.1836 | -135.5798 | -34.9336 | -12.6542 | -29.7405 | 130.9139 | -32.466 | 90.6112 | -51.4171 | -46.9462 | -41.4317 | -47.382 | -72.2921 | -46.7001 | -52.4308 | -47.9834 | -41.3555 | -46.3878 | -64.6496 | -46.374 | -44.1629 | 100 | -48.0853 | -53.2093 | -46.4348 | -45.2069 | -46.787 | -53.1273 | -47.0832 | -45.5027 | 100 | -45.999 | -39.3711 | -45.3976 | -70.4707 | -44.8787 | -50.3654 | -46.162 | -39.2901 | -45.5565 | -70.2267 | -44.8746 | -50.6053 | -44.9618 | -39.4473 | -44.4034 | -62.8282 | -44.5526 | -42.0975 | -45.1248 | -39.3663 | -44.5623 | -62.5842 | -44.5485 | -42.3374
101 | -1.9874 | 0 | -1.839 | 0 | -2.0673 | 0 | -1.8408 | 0 | -60.7801 | 49.8065 | -57.0461 | -132.8531 | -48.678 | -81.0218 | -54.0911 | 167.6347 | -67.6431 | 24.6088 | -47.3795 | -154.6595 | -64.2334 | 99.9693 | -54.6737 | -138.6336 | -48.1111 | -103.545 | -53.1008 | 136.1463 | -78.1138 | -86.3053 | -49.9195 | -161.5116 | -21.0814 | -119.7215 | -34.7374 | -128.1203 | -42.3528 | -162.4982 | -36.6576 | 110.9223 | -21.7979 | -153.9039 | -35.0183 | -31.3243 | -29.5261 | 103.0665 | -32.546 | 77.2557 | -50.9621 | -46.581 | -41.4464 | -46.3176 | -70.1183 | -45.4286 | -51.8742 | -47.1649 | -41.4523 | -45.4523 | -63.4914 | -45.3759 | -45.2704 | 101 | -47.8601 | -53.0927 | -46.1698 | -44.9467 | -47.1591 | -52.7658 | -47.3299 | -45.9089 | 101 | -45.1775 | -39.4649 | -44.3302 | -68.2793 | -43.5896 | -49.8069 | -45.3259 | -39.385 | -44.4768 | -68.051 | -43.5878 | -50.0334 | -44.5936 | -39.459 | -43.4649 | -61.6524 | -43.5369 | -43.2031 | -44.742 | -39.3791 | -43.6115 | -61.4241 | -43.5351 | -43.4296
102 | -1.9919 | 0 | -1.8454 | 0 | -2.0696 | 0 | -1.8568 | 0 | -61.9644 | 29.2295 | -57.3862 | -152.7462 | -49.0295 | -98.6812 | -54.8504 | 144.0109 | -68.5855 | 15.3668 | -47.5115 | -174.8012 | -67.0998 | 79.8467 | -55.711 | -151.5283 | -48.4987 | -114.817 | -53.2829 | 114.3639 | -80.3145 | -25.4227 | -50.9167 | 175.8749 | -22.5094 | -134.603 | -32.4062 | -151.1222 | -60.8498 | 12.4819 | -37.9833 | 111.1671 | -22.8731 | -172.1915 | -35.2011 | -45.5686 | -29.7059 | 77.7184 | -33.373 | 64.6401 | -50.5818 | -46.3098 | -41.4627 | -45.488 | -68.7966 | -44.4856 | -51.2673 | -46.5149 | -41.5271 | -44.7439 | -62.7087 | -44.6125 | -46.3627 | 102 | -48.249 | -53.9279 | -46.4141 | -45.1744 | -47.6931 | -53.098 | -48.103 | -46.5294 | 102 | -44.523 | -39.5352 | -43.4961 | -66.9512 | -42.6402 | -49.1977 | -44.6695 | -39.4575 | -43.6312 | -66.727 | -42.6288 | -49.4105 | -44.3179 | -39.4708 | -42.752 | -60.8633 | -42.7671 | -44.2931 | -44.4644 | -39.3931 | -42.8871 | -60.6391 | -42.7557 | -44.5059
103 | -1.9599 | 0 | -1.8686 | 0 | -2.0723 | 0 | -1.8666 | 0 | -63.983 | 9.0198 | -58.5959 | -175.7108 | -49.5385 | -115.965 | -56.495 | 122.7288 | -69.304 | 1.8952 | -48.0808 | 165.8005 | -71.4288 | 59.5382 | -57.5196 | -162.5166 | -49.0753 | -125.9106 | -54.0357 | 95.6087 | -73.1804 | -13.5425 | -53.2015 | 155.4766 | -24.5409 | -149.0283 | -30.6314 | -173.245 | -42.094 | -18.2596 | -38.2854 | 123.3907 | -24.6463 | 169.8029 | -36.0157 | -57.9363 | -30.4096 | 52.7158 | -34.9841 | 54.5468 | -50.273 | -46.0431 | -41.4775 | -44.9839 | -68.3707 | -43.8907 | -50.728 | -46.084 | -41.5653 | -44.3179 | -62.3335 | -44.1426 | -47.1898 | 103 | -48.8933 | -55.5935 | -47.1716 | -45.7194 | -48.4725 | -53.9056 | -49.7867 | -47.6433 | 103 | -44.1241 | -39.6054 | -43.024 | -66.5021 | -42.0221 | -48.6557 | -44.2154 | -39.493 | -43.1173 | -66.2984 | -42.0241 | -48.8614 | -44.0832 | -39.5176 | -42.358 | -60.4649 | -42.274 | -45.1175 | -44.1745 | -39.4052 | -42.4513 | -60.2612 | -42.276 | -45.3232
104 | -1.9631 | 0 | -1.8697 | 0 | -2.0724 | 0 | -1.884 | 0 | -66.9878 | -12.6381 | -60.9544 | 157.619 | -50.2656 | -133.2248 | -59.1093 | 104.0936 | -70.114 | -10.3977 | -49.0411 | 147.3774 | -81.1547 | 31.0421 | -60.0985 | -167.9986 | -49.7632 | -136.7436 | -55.1641 | 80.0883 | -69.3364 | -28.0281 | -55.5913 | 141.5764 | -27.8245 | -162.2752 | -29.4162 | 164.3986 | -37.911 | -36.5028 | -37.0915 | 130.3401 | -27.2185 | 152.0471 | -37.1978 | -69.6394 | -31.9967 | 27.3442 | -37.6611 | 43.9855 | -50.0397 | -45.8909 | -41.4925 | -44.5866 | -68.3014 | -43.5276 | -50.2954 | -45.7443 | -41.6154 | -44.0493 | -62.3931 | -43.8497 | -47.8346 | 104 | -49.8257 | -58.1669 | -48.386 | -46.5807 | -49.3758 | -54.9905 | -51.6862 | -48.7171 | 104 | -43.7812 | -39.6523 | -42.6235 | -66.4317 | -41.6579 | -48.223 | -43.8746 | -39.543 | -42.7026 | -66.229 | -41.6436 | -48.4114 | -43.9278 | -39.5294 | -42.0862 | -60.5234 | -41.98 | -45.7622 | -44.0212 | -39.4201 | -42.1653 | -60.3207 | -41.9657 | -45.9506
105 | -1.9911 | 0 | -1.8857 | 0 | -2.066 | 0 | -1.8942 | 0 | -71.9766 | -45.5083 | -64.7278 | 119.9182 | -51.5466 | -150.8709 | -63.3803 | 89.0508 | -71.0177 | -24.1176 | -50.4914 | 131.1477 | -78.5641 | -138.0513 | -62.9407 | -160.0676 | -50.9945 | -146.4072 | -56.4163 | 67.5506 | -67.0312 | -44.199 | -58.6682 | 122.3577 | -33.8066 | -166.7706 | -28.7222 | 143.9195 | -34.9019 | -53.2606 | -35.6628 | 134.2767 | -31.633 | 135.6774 | -38.752 | -75.6863 | -34.2213 | -3.7198 | -42.1981 | 41.7042 | -49.88 | -45.7439 | -41.5401 | -44.341 | -68.5168 | -43.3064 | -49.9326 | -45.4996 | -41.663 | -43.9131 | -62.7256 | -43.6793 | -48.0783 | 105 | -51.3053 | -62.2061 | -50.1206 | -47.9552 | -50.7184 | -56.0305 | -53.8203 | -50.218 | 105 | -43.5085 | -39.6719 | -42.3499 | -66.6311 | -41.4207 | -47.8666 | -43.6139 | -39.597 | -42.4468 | -66.4508 | -41.4122 | -48.0384 | -43.7528 | -39.549 | -41.922 | -60.8399 | -41.7936 | -46.0123 | -43.8582 | -39.4741 | -42.0189 | -60.6596 | -41.7851 | -46.1841
106 | -2.0096 | 0 | -1.8941 | 0 | -2.0705 | 0 | -1.9045 | 0 | -75.7345 | -123.1455 | -68.0748 | 50.8729 | -53.1465 | -167.7826 | -71.0646 | 86.8831 | -72.7983 | -42.6725 | -52.2238 | 116.1193 | -69.9694 | -163.1209 | -63.4489 | -138.2968 | -52.5352 | -156.518 | -57.6325 | 58.0015 | -65.5976 | -61.2102 | -64.5023 | 116.3892 | -41.2935 | -100.5162 | -28.2791 | 125.0434 | -33.312 | -72.7329 | -33.6698 | 136.4284 | -42.9129 | 126.8079 | -40.2708 | -84.0883 | -36.5527 | -47.3126 | -48.8214 | 82.6939 | -49.7556 | -45.643 | -41.5352 | -44.1697 | -68.6189 | -43.2524 | -49.7027 | -45.3869 | -41.658 | -43.812 | -63.3433 | -43.6135 | -48.0594 | 106 | -52.986 | -68.0282 | -52.0574 | -49.6294 | -52.1249 | -56.7755 | -55.9663 | -52.0703 | 106 | -43.3773 | -39.6484 | -42.1601 | -66.7248 | -41.3583 | -47.6322 | -43.4928 | -39.5875 | -42.2652 | -66.5484 | -41.3479 | -47.7982 | -43.6334 | -39.5256 | -41.8024 | -61.4492 | -41.7194 | -45.9889 | -43.7489 | -39.4647 | -41.9075 | -61.2728 | -41.709 | -46.1549
107 | -2.0275 | 0 | -1.9119 | 0 | -2.0702 | 0 | -1.9267 | 0 | -70.3346 | 175.1298 | -64.1225 | -17.3613 | -55.2652 | 173.897 | -75.1609 | 176.7394 | -74.7208 | -63.5652 | -54.4875 | 101.3753 | -65.6378 | 177.6416 | -60.9404 | -125.7406 | -54.0479 | -160.2737 | -58.4953 | 49.8951 | -64.9105 | -79.0585 | -73.7689 | 86.2308 | -31.8878 | -60.2223 | -28.4186 | 105.408 | -32.1164 | -88.4185 | -32.2275 | 130.8317 | -37.6137 | -92.0933 | -41.7619 | -87.2909 | -36.2263 | -101.2733 | -42.447 | 144.9572 | -49.6446 | -45.5216 | -41.5649 | -44.1056 | -68.3165 | -43.2638 | -49.5096 | -45.3514 | -41.6291 | -43.8064 | -64.2439 | -43.6014 | -47.7269 | 107 | -54.6161 | -68.0471 | -54.0057 | -51.8263 | -52.9966 | -56.9682 | -56.4563 | -53.6631 | 107 | -43.3239 | -39.6016 | -42.0781 | -66.4046 | -41.3519 | -47.4394 | -43.4395 | -39.5589 | -42.1789 | -66.2463 | -41.3371 | -47.5829 | -43.4941 | -39.5374 | -41.7789 | -62.332 | -41.6895 | -45.6567 | -43.6097 | -39.4947 | -41.8797 | -62.1737 | -41.6747 | -45.8002
108 | -2.0539 | 0 | -1.9268 | 0 | -2.0711 | 0 | -1.9132 | 0 | -65.6917 | 149.3504 | -60.021 | -53.7448 | -58.1749 | 150.0541 | -67.3697 | -167.9524 | -78.5264 | -92.3907 | -57.3705 | 89.9072 | -62.7334 | 159.27 | -58.194 | -128.0342 | -55.4611 | -162.8779 | -59.0142 | 40.6799 | -64.6156 | -97.0023 | -73.673 | -75.4887 | -26.8492 | -69.1079 | -29.0139 | 87.7466 | -31.2074 | -105.1389 | -31.0834 | 124.0459 | -29.5123 | -104.0301 | -42.3201 | -91.7721 | -33.5878 | -140.3109 | -37.7911 | 145.1747 | -49.5424 | -45.4758 | -41.5679 | -44.0971 | -67.6401 | -43.386 | -49.3838 | -45.3758 | -41.6086 | -43.8682 | -65.1065 | -43.661 | -47.1887 | 108 | -55.5484 | -63.3073 | -55.2136 | -54.7257 | -53.1049 | -56.7096 | -55.5077 | -54.9051 | 108 | -43.3219 | -39.5547 | -42.0432 | -65.7133 | -41.4592 | -47.3127 | -43.449 | -39.5375 | -42.1839 | -65.569 | -41.4728 | -47.4706 | -43.4219 | -39.514 | -41.8143 | -63.1797 | -41.7342 | -45.1176 | -43.549 | -39.4968 | -41.955 | -63.0354 | -41.7478 | -45.2755
109 | -2.0604 | 0 | -1.9468 | 0 | -2.0739 | 0 | -1.9115 | 0 | -62.7971 | 131.4558 | -57.2382 | -80.5602 | -62.6527 | 123.333 | -64.2505 | -173.6248 | -80.2251 | -136.5504 | -60.7417 | 62.3126 | -60.8847 | 141.4843 | -56.1736 | -137.2883 | -57.088 | -165.0683 | -59.3774 | 27.047 | -64.3567 | -114.479 | -66.6351 | -94.6499 | -23.7515 | -81.8096 | -30.2602 | 69.6327 | -30.2477 | -119.4003 | -30.1222 | 119.6067 | -25.4193 | -121.3125 | -43.0488 | -102.3793 | -30.4202 | -168.9485 | -34.3479 | 139.9866 | -49.4336 | -45.467 | -41.5511 | -44.1993 | -66.8008 | -43.6232 | -49.2867 | -45.5349 | -41.5565 | -44.0054 | -66.0054 | -43.8044 | -46.578 | 109 | -55.2917 | -60.4075 | -55.0758 | -58.553 | -52.853 | -56.3142 | -54.2198 | -55.9534 | 109 | -43.4745 | -39.4961 | -42.1389 | -64.854 | -41.6764 | -47.2128 | -43.5881 | -39.4826 | -42.2878 | -64.7269 | -41.7117 | -47.3752 | -43.4066 | -39.4907 | -41.945 | -64.0586 | -41.8576 | -44.5041 | -43.5202 | -39.4772 | -42.0939 | -63.9315 | -41.8929 | -44.6665
110 | -2.0861 | 0 | -1.9446 | 0 | -2.0716 | 0 | -1.9107 | 0 | -60.7378 | 115.0139 | -55.4929 | -102.8544 | -69.6903 | 70.1292 | -62.852 | -178.0972 | -78.6166 | 159.568 | -68.7172 | 23.7452 | -59.6375 | 124.5608 | -54.8037 | -148.8576 | -59.3397 | -161.7556 | -59.9553 | 8.2835 | -64.4309 | -133.974 | -62.0299 | -95.9488 | -21.7649 | -96.2549 | -31.9968 | 53.2944 | -29.6016 | -133.6247 | -29.416 | 111.1006 | -22.8165 | -137.6672 | -44.0119 | -124.9695 | -28.3213 | 170.4601 | -32.1662 | 130.9353 | -49.3026 | -45.457 | -41.5886 | -44.4354 | -65.8807 | -43.9726 | -49.1789 | -45.8607 | -41.5001 | -44.2532 | -66.4407 | -43.9896 | -45.9074 | 110 | -54.2318 | -58.6136 | -54.5893 | -65.926 | -52.5494 | -56.0944 | -53.0579 | -56.6729 | 110 | -43.7746 | -39.414 | -42.3493 | -63.9361 | -42.028 | -47.1073 | -43.9161 | -39.4285 | -42.5247 | -63.8091 | -42.0619 | -47.2682 | -43.3709 | -39.5025 | -42.1671 | -64.4961 | -42.045 | -43.8358 | -43.5124 | -39.517 | -42.3425 | -64.3691 | -42.0789 | -43.9967
111 | -2.1087 | 0 | -1.9621 | 0 | -2.0719 | 0 | -1.9283 | 0 | -59.217 | 101.2529 | -54.4036 | -122.6832 | -67.2293 | -22.4987 | -61.604 | -177.5987 | -74.9538 | 116.8326 | -68.7199 | -83.2661 | -58.9265 | 109.2549 | -53.78 | -161.0326 | -60.3498 | -153.0791 | -61.0814 | -16.4228 | -64.865 | -154.9538 | -58.1289 | -110.4565 | -20.3747 | -111.1009 | -35.2234 | 39.3902 | -28.7133 | -147.2208 | -29.0788 | 103.6247 | -20.9342 | -154.1523 | -44.4983 | -152.542 | -26.6336 | 154.5595 | -30.6914 | 124.4201 | -49.1561 | -45.4457 | -41.6465 | -44.7459 | -65.1483 | -44.4808 | -49.0558 | -46.2712 | -41.4642 | -44.5871 | -66.2121 | -44.2985 | -45.4269 | 111 | -52.9976 | -57.1654 | -53.5132 | -64.4915 | -51.9443 | -56.2229 | -51.8668 | -55.5481 | 111 | -44.1625 | -39.3555 | -42.6372 | -63.1862 | -42.5187 | -46.9839 | -44.3091 | -39.3923 | -42.8176 | -63.0764 | -42.5525 | -47.1275 | -43.337 | -39.5378 | -42.4784 | -64.25 | -42.3364 | -43.355 | -43.4836 | -39.5746 | -42.6588 | -64.1402 | -42.3702 | -43.4986
112 | -2.1394 | 0 | -1.9638 | 0 | -2.0906 | 0 | -1.9535 | 0 | -58.0407 | 88.8007 | -53.7016 | -140.3442 | -62.471 | -60.7087 | -59.4937 | -178.0643 | -71.6351 | 88.7269 | -61.187 | -119.9024 | -58.1652 | 96.2023 | -52.9058 | -173.9954 | -61.2224 | -136.2249 | -62.8681 | -49.0599 | -65.7858 | -176.36 | -55.7257 | -127.4679 | -19.3987 | -126.7185 | -40.7975 | 40.0271 | -27.7947 | -161.9059 | -28.6562 | 98.9962 | -19.6262 | -170.4509 | -44.3226 | 166.7986 | -25.4743 | 139.7636 | -29.5945 | 116.234 | -49.0759 | -45.3941 | -41.6304 | -45.1696 | -64.6306 | -45.0035 | -49.0107 | -46.7274 | -41.4011 | -45.0224 | -65.2841 | -44.6453 | -45.1599 | 112 | -51.9379 | -55.5872 | -52.1122 | -58.5524 | -51.3064 | -56.3709 | -50.8019 | -54.3248 | 112 | -44.588 | -39.2617 | -43.0302 | -62.6668 | -43.0397 | -46.9201 | -44.7636 | -39.3105 | -43.2161 | -62.54 | -43.05 | -47.0572 | -43.2547 | -39.491 | -42.883 | -63.3203 | -42.6815 | -43.0693 | -43.4303 | -39.5398 | -43.0689 | -63.1935 | -42.6918 | -43.2064
113 | -2.1544 | 0 | -1.9733 | 0 | -2.1051 | 0 | -1.9693 | 0 | -56.9684 | 74.9412 | -53.3688 | -157.0654 | -57.8784 | -85.2098 | -57.2438 | 175.249 | -69.3101 | 62.7545 | -56.522 | -139.1658 | -57.283 | 81.3042 | -52.2382 | 171.1761 | -58.0738 | -125.8706 | -64.945 | -92.0364 | -66.9793 | 160.4206 | -53.9928 | -143.0265 | -18.7755 | -141.8096 | -44.7564 | 110.2314 | -27.0472 | -175.6832 | -28.6097 | 93.788 | -18.7483 | 173.7013 | -42.1617 | 133.5022 | -24.6714 | 127.1368 | -28.8879 | 107.7647 | -49.0621 | -45.4048 | -41.5518 | -45.4996 | -64.5582 | -45.5025 | -49.1608 | -47.07 | -41.299 | -45.3874 | -64.3171 | -44.9996 | -45.0684 | 113 | -50.8388 | -53.9649 | -50.596 | -54.0072 | -50.2685 | -56.2158 | -49.8797 | -52.4061 | 113 | -44.9156 | -39.1446 | -43.3452 | -62.5849 | -43.5292 | -47.0557 | -45.0967 | -39.1939 | -43.5303 | -62.4531 | -43.5332 | -47.1915 | -43.2504 | -39.3974 | -43.233 | -62.3438 | -43.0263 | -42.9633 | -43.4315 | -39.4467 | -43.4181 | -62.212 | -43.0303 | -43.0991
114 | -2.1614 | 0 | -1.9975 | 0 | -2.1258 | 0 | -1.9751 | 0 | -56.4091 | 59.3596 | -53.2152 | -172.4778 | -56.0453 | -106.0632 | -55.5981 | 162.6579 | -67.5918 | 42.2118 | -53.5429 | -158.958 | -56.7193 | 63.4853 | -51.9174 | 155.3387 | -55.9517 | -134.3589 | -65.9294 | -140.048 | -69.4179 | 137.7305 | -52.5689 | -161.8049 | -18.5637 | -156.5417 | -37.9738 | 124.108 | -26.5431 | 170.4547 | -28.3991 | 85.5656 | -18.2539 | 158.5882 | -40.3381 | 98.2213 | -24.2445 | 115.3922 | -28.4968 | 100.6659 | -49.0629 | -45.535 | -41.4534 | -45.6645 | -64.5824 | -45.828 | -49.3373 | -47.3016 | -41.2239 | -45.5053 | -63.5053 | -45.3133 | -45.1238 | 114 | -50.2038 | -52.8269 | -49.2271 | -51.4979 | -49.5471 | -56.0238 | -49.129 | -50.8676 | 114 | -45.1402 | -39.0625 | -43.5031 | -62.5849 | -43.8305 | -47.2115 | -45.3041 | -39.0981 | -43.6894 | -62.4566 | -43.8529 | -47.3622 | -43.3736 | -39.292 | -43.3439 | -61.5078 | -43.3158 | -42.998 | -43.5375 | -39.3276 | -43.5302 | -61.3795 | -43.3382 | -43.1487
115 | -2.1593 | 0 | -2.003 | 0 | -2.1524 | 0 | -1.9851 | 0 | -56.3225 | 43.6336 | -53.1106 | 172.697 | -54.906 | -125.0516 | -54.7787 | 148.8009 | -66.5917 | 21.8933 | -52.0474 | -176.8166 | -56.7649 | 45.1836 | -51.8608 | 138.8125 | -54.9733 | -144.6028 | -65.1026 | 179.0565 | -71.367 | 116.8116 | -52.1987 | 179.3064 | -18.4282 | -170.8733 | -33.5517 | 119.744 | -26.0309 | 158.0454 | -28.6781 | 80.761 | -18.0172 | 143.4084 | -38.0748 | 70.9077 | -24.066 | 105.7014 | -28.3154 | 95.0751 | -49.0216 | -45.6555 | -41.3928 | -45.6818 | -64.717 | -45.8898 | -49.4366 | -47.3165 | -41.2218 | -45.4405 | -62.7374 | -45.4845 | -45.3022 | 115 | -49.8091 | -52.307 | -48.4 | -50.136 | -49.28 | -56.0413 | -48.9105 | -50.3235 | 115 | -45.1572 | -39.0625 | -43.5225 | -62.714 | -43.8868 | -47.2842 | -45.3135 | -39.0694 | -43.6967 | -62.5646 | -43.9047 | -47.4515 | -43.4962 | -39.2335 | -43.2812 | -60.7344 | -43.4815 | -43.1498 | -43.6525 | -39.2404 | -43.4554 | -60.585 | -43.4994 | -43.3171
116 | -2.1588 | 0 | -2.0239 | 0 | -2.1713 | 0 | -1.9976 | 0 | -56.8469 | 28.4606 | -53.1041 | 157.2181 | -54.0442 | -144.0584 | -54.5521 | 134.869 | -65.4869 | 1.589 | -51.3779 | 167.4205 | -57.3282 | 27.0826 | -52.0747 | 122.2303 | -54.3673 | -156.7675 | -63.905 | 150.5887 | -73.8375 | 79.9747 | -52.3558 | 166.8468 | -18.6697 | 174.4817 | -30.9664 | 105.4839 | -25.737 | 145.2375 | -28.7957 | 74.4088 | -18.0237 | 129.7823 | -37.2756 | 48.8472 | -24.1451 | 97.56 | -28.404 | 88.6539 | -48.9548 | -45.7741 | -41.3631 | -45.5798 | -64.8317 | -45.821 | -49.4106 | -47.1654 | -41.2096 | -45.2582 | -62.0921 | -45.5854 | -45.4943 | 116 | -49.6254 | -52.3245 | -48.0465 | -49.3912 | -49.3143 | -56.386 | -49.058 | -50.2169 | 116 | -45.0066 | -39.0508 | -43.421 | -62.8078 | -43.7971 | -47.2393 | -45.1415 | -39.0383 | -43.5822 | -62.6604 | -43.8234 | -47.413 | -43.6153 | -39.2043 | -43.0994 | -60.0682 | -43.5615 | -43.323 | -43.7502 | -39.1918 | -43.2606 | -59.9208 | -43.5878 | -43.4967
117 | -2.1417 | 0 | -2.0509 | 0 | -2.195 | 0 | -2.0031 | 0 | -57.9063 | 14.5491 | -53.286 | 140.5734 | -53.8989 | -162.947 | -54.877 | 122.8612 | -64.9759 | -18.9959 | -50.7773 | 152.328 | -58.3899 | 9.6626 | -52.5372 | 104.6349 | -54.3614 | -168.5603 | -62.7855 | 129.9639 | -76.3006 | 43.6377 | -52.8032 | 148.4535 | -19.1264 | 160.8197 | -29.5217 | 91.0958 | -25.6279 | 133.9142 | -29.456 | 69.5388 | -18.4111 | 115.5761 | -36.3454 | 24.4337 | -24.3733 | 89.8279 | -28.5907 | 81.4445 | -48.8784 | -45.8155 | -41.3344 | -45.4213 | -65.0852 | -45.6279 | -49.3028 | -46.8961 | -41.2159 | -45.0274 | -61.6091 | -45.6208 | -45.7282 | 117 | -49.8352 | -52.8479 | -47.8763 | -48.9435 | -49.7113 | -56.9923 | -49.4515 | -50.4911 | 117 | -44.7544 | -39.0742 | -43.2796 | -63.0343 | -43.577 | -47.1078 | -44.8452 | -39.0209 | -43.4182 | -62.8902 | -43.6248 | -47.2997 | -43.6738 | -39.1927 | -42.8857 | -59.5582 | -43.5699 | -43.5332 | -43.7646 | -39.1394 | -43.0243 | -59.4141 | -43.6177 | -43.7251
118 | -2.1292 | 0 | -2.0502 | 0 | -2.2195 | 0 | -2.0076 | 0 | -59.6029 | 2.0785 | -53.757 | 122.149 | -54.1414 | 179.5578 | -55.5846 | 113.0457 | -64.5769 | -34.5453 | -50.6154 | 136.9662 | -60.0224 | -6.4068 | -53.3442 | 86.3454 | -54.8788 | 177.85 | -61.7895 | 114.4706 | -76.9105 | -10.8512 | -53.1719 | 136.3125 | -19.9133 | 147.5701 | -28.7169 | 75.4256 | -25.79 | 122.3716 | -30.2278 | 63.8062 | -19.1173 | 102.5405 | -36.3775 | -0.7661 | -24.6824 | 84.3566 | -29.0974 | 78.128 | -48.8309 | -45.7932 | -41.3279 | -45.2449 | -65.5184 | -45.4143 | -49.1439 | -46.5867 | -41.2269 | -44.7337 | -61.265 | -45.5984 | -45.9338 | 118 | -50.3813 | -53.7589 | -48.054 | -48.9005 | -50.5175 | -57.7533 | -49.9526 | -50.9208 | 118 | -44.4575 | -39.0977 | -43.1157 | -63.4682 | -43.3641 | -46.9244 | -44.5365 | -39.0074 | -43.2373 | -63.2989 | -43.4067 | -47.1363 | -43.664 | -39.1987 | -42.6045 | -59.2148 | -43.5482 | -43.7143 | -43.743 | -39.1084 | -42.7261 | -59.0455 | -43.5908 | -43.9262
119 | -2.139 | 0 | -2.0685 | 0 | -2.2387 | 0 | -2.0281 | 0 | -62.1769 | -5.8148 | -54.7407 | 102.2437 | -54.8591 | 161.751 | -56.5805 | 106.7917 | -64.0724 | -53.2854 | -51.0177 | 123.0739 | -62.5398 | -21.4591 | -54.5656 | 66.3898 | -56.0808 | 165.9767 | -60.7824 | 100.8467 | -75.6343 | -54.4541 | -53.6123 | 122.4308 | -21.071 | 135.5831 | -28.61 | 61.0243 | -26.1719 | 112.46 | -31.448 | 60.1948 | -20.2652 | 90.9789 | -36.1292 | -27.1298 | -25.1781 | 79.5228 | -29.737 | 74.6505 | -48.7906 | -45.707 | -41.3378 | -45.0406 | -66.0875 | -45.2226 | -48.963 | -46.1684 | -41.2601 | -44.4591 | -61.1544 | -45.5239 | -46.0229 | 119 | -51.4091 | -54.9554 | -48.7078 | -49.367 | -51.859 | -58.4781 | -50.6134 | -51.6458 | 119 | -44.0294 | -39.1211 | -42.9016 | -64.019 | -43.1541 | -46.7243 | -44.0999 | -39.0214 | -43.0125 | -63.8488 | -43.1945 | -46.9349 | -43.568 | -39.1988 | -42.3201 | -59.0859 | -43.4554 | -43.7842 | -43.6385 | -39.0991 | -42.431 | -58.9157 | -43.4958 | -43.9948
120 | -2.147 | 0 | -2.0667 | 0 | -2.2415 | 0 | -2.0257 | 0 | -65.6347 | -4.8884 | -56.3565 | 78.8411 | -55.846 | 145.3673 | -57.5785 | 104.0393 | -64.2277 | -73.411 | -51.5511 | 110.0603 | -66.6535 | -32.4767 | -56.3503 | 44.0697 | -56.4299 | 155.5327 | -59.7674 | 87.517 | -73.1963 | -92.191 | -55.2835 | 109.8754 | -22.6181 | 126.4786 | -29.1361 | 47.3694 | -26.9505 | 104.1961 | -33.3587 | 62.5021 | -21.8896 | 81.947 | -37.0647 | -59.9136 | -25.6893 | 76.6579 | -30.5548 | 77.6983 | -48.7421 | -45.5106 | -41.3224 | -44.8398 | -66.6757 | -45.0145 | -48.7699 | -45.7375 | -41.2798 | -44.1488 | -61.1996 | -45.4915 | -46.0253 | 120 | -52.8486 | -56.2025 | -49.5636 | -50.01 | -53.1799 | -58.7975 | -51.9827 | -52.7691 | 120 | -43.5905 | -39.1328 | -42.6928 | -64.609 | -42.9478 | -46.5284 | -43.6708 | -39.0383 | -42.8141 | -64.4342 | -42.9888 | -46.7442 | -43.3636 | -39.1754 | -42.0018 | -59.1329 | -43.4248 | -43.7838 | -43.4439 | -39.0809 | -42.1231 | -58.9581 | -43.4658 | -43.9996
121 | -2.1414 | 0 | -2.0841 | 0 | -2.2495 | 0 | -2.02 | 0 | -68.772 | 22.6983 | -58.93 | 49.8608 | -57.7814 | 125.6391 | -58.2478 | 105.1932 | -64.3911 | -91.0661 | -52.244 | 97.2506 | -74.1778 | -23.1021 | -58.9967 | 16.7597 | -58.871 | 139.7588 | -58.8207 | 71.8213 | -71.1047 | -124.0247 | -55.473 | 98.0312 | -24.8352 | 121.5284 | -30.5004 | 34.0902 | -28.3253 | 100.4706 | -35.61 | 72.2845 | -24.1811 | 75.186 | -37.5049 | -91.711 | -26.4529 | 74.8817 | -30.4248 | 75.4444 | -48.6892 | -45.2336 | -41.2935 | -44.6346 | -67.2322 | -44.8351 | -48.5997 | -45.2612 | -41.286 | -43.8732 | -61.5021 | -45.355 | -45.9743 | 121 | -55.1162 | -57.0038 | -50.5843 | -50.9716 | -55.8587 | -58.4535 | -52.6698 | -53.7568 | 121 | -43.1198 | -39.1446 | -42.4932 | -65.1481 | -42.751 | -46.3502 | -43.1771 | -39.0365 | -42.6146 | -64.9827 | -42.8151 | -46.5797 | -43.0922 | -39.1521 | -41.7318 | -59.418 | -43.2709 | -43.7248 | -43.1495 | -39.044 | -41.8532 | -59.2526 | -43.335 | -43.9543
122 | -2.1574 | 0 | -2.0953 | 0 | -2.2511 | 0 | -2.0114 | 0 | -66.3429 | 54.1633 | -62.5636 | 5.4881 | -60.1981 | 110.4737 | -58.2882 | 107.1624 | -64.8206 | -111.7853 | -53.6913 | 85.3874 | -73.2368 | 62.4934 | -62.723 | -22.6329 | -61.7265 | 132.6499 | -58.1334 | 54.0923 | -69.7999 | -146.9202 | -56.6916 | 82.1372 | -27.6256 | 121.5985 | -31.9758 | 21.5685 | -29.9384 | 98.3734 | -35.8946 | 86.6943 | -27.2853 | 79.9633 | -37.26 | -131.8889 | -27.3333 | 77.7605 | -30.9473 | 82.7241 | -48.5951 | -44.8954 | -41.2861 | -44.4467 | -67.6928 | -44.6845 | -48.4117 | -44.7589 | -41.2902 | -43.6266 | -61.8532 | -45.2394 | -45.9051 | 122 | -57.5903 | -56.8935 | -51.9986 | -52.5498 | -59.0183 | -57.7234 | -53.7538 | -55.348 | 122 | -42.6015 | -39.1328 | -42.2893 | -65.5975 | -42.5892 | -46.1606 | -42.6636 | -39.0391 | -42.4353 | -65.4417 | -42.6731 | -46.4003 | -42.738 | -39.1287 | -41.4692 | -59.7579 | -43.1441 | -43.654 | -42.8001 | -39.035 | -41.6152 | -59.6021 | -43.228 | -43.8937
123 | -2.1727 | 0 | -2.0911 | 0 | -2.264 | 0 | -2.0357 | 0 | -62.634 | 59.0531 | -63.6933 | -67.4087 | -62.4597 | 91.8906 | -58.0637 | 106.8751 | -64.8547 | -132.985 | -55.6779 | 77.8195 | -65.7054 | 68.0439 | -65.0553 | -90.9374 | -64.4419 | 119.9381 | -57.7633 | 33.026 | -68.2167 | -172.6588 | -58.5773 | 68.0207 | -29.1858 | 145.3974 | -35.5137 | 15.4832 | -31.1894 | 115.3793 | -34.6503 | 108.9587 | -29.1436 | 104.6857 | -35.1669 | -170.2118 | -27.7682 | 87.5231 | -30.4046 | 87.143 | -48.4737 | -44.5686 | -41.2663 | -44.2276 | -67.6417 | -44.5803 | -48.2552 | -44.3734 | -41.3055 | -43.4348 | -62.388 | -45.1 | -45.8941 | 123 | -58.1246 | -56.1367 | -53.2843 | -54.4372 | -60.2658 | -56.7918 | -54.7192 | -57.2171 | 123 | -42.2007 | -39.1328 | -42.0549 | -65.5506 | -42.4892 | -45.9912 | -42.2823 | -39.0415 | -42.1919 | -65.3777 | -42.5446 | -46.2195 | -42.3959 | -39.0936 | -41.2621 | -60.2969 | -43.0089 | -43.6301 | -42.4775 | -39.0023 | -41.3991 | -60.124 | -43.0643 | -43.8584
124 | -2.1968 | 0 | -2.0853 | 0 | -2.2619 | 0 | -2.0603 | 0 | -59.782 | 54.1098 | -59.9602 | -124.731 | -66.8285 | 74.2044 | -57.9299 | 105.197 | -65.1096 | -158.6553 | -58.3247 | 76.8723 | -61.4626 | 57.603 | -61.6508 | -153.0505 | -69.9675 | 104.2809 | -58.0606 | 9.5807 | -68.2912 | 163.1768 | -60.4183 | 55.3633 | -27.5223 | 165.081 | -38.8569 | 25.2328 | -29.8383 | 131.8074 | -31.9603 | 115.7385 | -26.8923 | 127.7207 | -33.3698 | 159.2782 | -26.8881 | 99.8478 | -29.2114 | 84.9779 | -48.3508 | -44.293 | -41.2318 | -44.093 | -67.3195 | -44.5548 | -48.1439 | -44.0978 | -41.271 | -43.3939 | -62.9251 | -44.9221 | -45.8446 | 124 | -56.4431 | -55.2717 | -53.8821 | -57.0188 | -58.2431 | -56.1525 | -55.0102 | -59.3661 | 124 | -41.901 | -39.0742 | -41.8962 | -65.2342 | -42.4695 | -45.882 | -42.0125 | -39.0091 | -42.0327 | -65.0576 | -42.4945 | -46.0836 | -42.0962 | -39.035 | -41.1971 | -60.8398 | -42.8368 | -43.5827 | -42.2077 | -38.9699 | -41.3336 | -60.6632 | -42.8618 | -43.7843
125 | -2.2073 | 0 | -2.0858 | 0 | -2.2524 | 0 | -2.0738 | 0 | -57.7084 | 45.7883 | -56.6786 | -158.6629 | -77.2456 | 77.1323 | -58.0745 | 104.0253 | -65.8111 | 178.4827 | -59.8882 | 74.535 | -58.6909 | 44.1185 | -58.2005 | 169.8001 | -82.1257 | -177.3547 | -58.8331 | -18.0612 | -66.6713 | 139.8075 | -62.9623 | 27.678 | -24.3998 | 170.7806 | -41.0147 | 63.7173 | -26.8244 | 139.1518 | -29.836 | 115.4498 | -23.5804 | 132.9777 | -31.8787 | 134.543 | -24.9719 | 106.4435 | -28.5127 | 82.7947 | -48.2108 | -44.1313 | -41.1603 | -44.0233 | -66.7772 | -44.5336 | -48.0624 | -43.9946 | -41.2346 | -43.4178 | -63.371 | -44.7836 | -45.8228 | 125 | -54.1315 | -54.5404 | -53.2491 | -58.8363 | -55.4192 | -55.4132 | -54.7792 | -61.3853 | 125 | -41.7873 | -39.0273 | -41.816 | -64.6914 | -42.4478 | -45.81 | -41.9088 | -38.9822 | -41.9495 | -64.5248 | -42.4598 | -45.9886 | -41.924 | -38.953 | -41.2105 | -61.2852 | -42.6978 | -43.5704 | -42.0455 | -38.9079 | -41.344 | -61.1186 | -42.7098 | -43.749
126 | -2.2331 | 0 | -2.0885 | 0 | -2.2465 | 0 | -2.0894 | 0 | -56.0796 | 34.6769 | -54.5875 | 174.4821 | -73.0109 | -170.8651 | -58.1818 | 106.2547 | -66.1654 | 152.4031 | -63.7859 | 68.3089 | -56.647 | 29.3618 | -55.8552 | 142.7179 | -70.1467 | -155.1588 | -60.1039 | -50.7971 | -65.9038 | 117.4353 | -69.3607 | -19.7075 | -21.7588 | 165.8198 | -36.8744 | 77.545 | -23.9514 | 134.9804 | -28.2366 | 109.8989 | -20.8306 | 129.782 | -30.7183 | 116.0361 | -22.7062 | 106.5101 | -28.0002 | 79.9105 | -48.0846 | -44.1255 | -41.1159 | -44.0026 | -66.0612 | -44.6684 | -48.0416 | -44.0239 | -41.2018 | -43.5963 | -63.7643 | -44.684 | -45.7696 | 126 | -52.2231 | -53.7387 | -52.6636 | -61.4873 | -53.1355 | -54.6885 | -54.3306 | -63.285 | 126 | -41.7908 | -38.9687 | -41.7695 | -63.9727 | -42.5799 | -45.7951 | -41.9354 | -38.9553 | -41.9132 | -63.8147 | -42.579 | -45.9522 | -41.8924 | -38.8828 | -41.3632 | -61.6758 | -42.5955 | -43.5231 | -42.037 | -38.8694 | -41.5069 | -61.5178 | -42.5946 | -43.6802
127 | -2.251 | 0 | -2.0984 | 0 | -2.2621 | 0 | -2.096 | 0 | -54.8541 | 22.9654 | -53.4206 | 152.0697 | -65.9994 | 173.016 | -57.7131 | 111.0029 | -66.5205 | 126.0987 | -70.2172 | 101.8439 | -55.0976 | 14.0976 | -54.3922 | 118.4648 | -69.1277 | -161.9243 | -61.4186 | -91.4515 | -65.2743 | 92.6151 | -69.5023 | -112.2737 | -19.7161 | 156.8918 | -34.1438 | 73.8441 | -21.7105 | 126.1316 | -27.2211 | 103.8391 | -18.8736 | 119.9361 | -29.8383 | 92.5522 | -20.6928 | 98.9465 | -27.6265 | 73.2676 | -48.0008 | -44.2231 | -41.1104 | -44.0476 | -65.4031 | -44.8481 | -48.0515 | -44.2074 | -41.1846 | -43.8288 | -64.0906 | -44.6879 | -45.7494 | 127 | -50.9308 | -52.8515 | -51.9808 | -62.4476 | -51.6421 | -53.8614 | -53.4962 | -62.7469 | 127 | -41.9564 | -38.9336 | -41.7966 | -63.3047 | -42.7497 | -45.7894 | -42.109 | -38.9225 | -41.9516 | -63.141 | -42.7521 | -45.9555 | -41.9721 | -38.8594 | -41.5778 | -61.9922 | -42.5895 | -43.4873 | -42.1247 | -38.8483 | -41.7328 | -61.8285 | -42.5919 | -43.6534
128 | -2.2722 | 0 | -2.1051 | 0 | -2.2951 | 0 | -2.099 | 0 | -53.9444 | 10.5517 | -52.7791 | 131.9314 | -63.4204 | 147.5239 | -56.4426 | 114.5197 | -66.0953 | 97.424 | -63.4434 | 157.9536 | -53.9781 | -1.5277 | -53.5548 | 97.0249 | -66.7081 | -166.0005 | -61.4113 | -137.4039 | -64.654 | 71.8459 | -64.6625 | -152.4719 | -18.202 | 145.9752 | -32.7949 | 64.7549 | -20.0636 | 114.4919 | -26.5734 | 95.8115 | -17.4529 | 108.6818 | -29.6614 | 74.4405 | -19.1808 | 89.4423 | -27.6717 | 65.4924 | -47.9372 | -44.4358 | -41.0965 | -44.113 | -64.7731 | -45.0335 | -48.0699 | -44.4397 | -41.1589 | -44.0816 | -63.9684 | -44.7326 | -45.6647 | 128 | -50.1052 | -51.8398 | -50.9721 | -59.3809 | -50.6422 | -52.9532 | -52.616 | -60.469 | 128 | -42.1675 | -38.8867 | -41.8408 | -62.668 | -42.9284 | -45.7748 | -42.3346 | -38.8638 | -42.014 | -62.478 | -42.9345 | -45.9709 | -42.1636 | -38.8243 | -41.8094 | -61.8633 | -42.6275 | -43.3696 | -42.3307 | -38.8014 | -41.9826 | -61.6733 | -42.6336 | -43.5657
129 | -2.2884 | 0 | -2.1246 | 0 | -2.3098 | 0 | -2.1081 | 0 | -53.276 | -2.4777 | -52.5621 | 113.5771 | -60.9194 | 118.6422 | -54.8269 | 113.3122 | -65.7901 | 68.2978 | -57.5621 | 153.7014 | -53.1753 | -16.8263 | -53.1186 | 76.7553 | -66.7612 | 173.7065 | -59.7758 | -178.4064 | -63.8758 | 50.2059 | -60.0928 | -179.5437 | -17.0807 | 133.9797 | -32.2719 | 52.0929 | -18.911 | 100.9053 | -26.3977 | 88.9303 | -16.4881 | 97.234 | -30.4322 | 60.863 | -18.2027 | 79.8195 | -28.5505 | 59.2891 | -47.8747 | -44.6146 | -41.0892 | -44.2028 | -64.1833 | -45.2006 | -48.0895 | -44.7122 | -41.1516 | -44.2691 | -63.8238 | -44.8177 | -45.5969 | 129 | -49.564 | -50.8314 | -49.7521 | -55.4885 | -50.0431 | -52.023 | -51.606 | -57.9606 | 129 | -42.4238 | -38.8632 | -41.9144 | -62.0587 | -43.076 | -45.7797 | -42.5876 | -38.8418 | -42.0947 | -61.8735 | -43.0925 | -45.9814 | -42.3262 | -38.8008 | -41.9807 | -61.6992 | -42.6931 | -43.2871 | -42.49 | -38.7794 | -42.161 | -61.514 | -42.7096 | -43.4888
130 | -2.3092 | 0 | -2.1301 | 0 | -2.343 | 0 | -2.114 | 0 | -52.8493 | -15.8161 | -52.6409 | 95.6147 | -59.9862 | 94.1911 | -53.2611 | 108.0788 | -65.4469 | 42.3454 | -55.0727 | 140.3918 | -52.6367 | -32.0722 | -52.9377 | 56.8903 | -71.6361 | 152.8037 | -57.6715 | 149.3848 | -63.7133 | 29.6479 | -58.1179 | 149.8005 | -16.3001 | 121.4435 | -32.9198 | 38.1896 | -18.2171 | 87.3308 | -26.5847 | 82.8232 | -15.8915 | 85.366 | -31.7055 | 47.7915 | -17.6149 | 68.3896 | -30.0809 | 54.1005 | -47.8137 | -44.847 | -41.1101 | -44.2747 | -63.7434 | -45.3509 | -48.048 | -44.9914 | -41.1256 | -44.4387 | -63.3683 | -44.9211 | -45.4186 | 130 | -49.342 | -49.9167 | -48.7703 | -53.5672 | -49.7461 | -51.2011 | -50.7903 | -56.9115 | 130 | -42.6822 | -38.8164 | -41.9655 | -61.6133 | -43.2208 | -45.705 | -42.8613 | -38.7826 | -42.1607 | -61.4004 | -43.2369 | -45.934 | -42.5378 | -38.8009 | -42.1295 | -61.2382 | -42.791 | -43.0756 | -42.7169 | -38.7671 | -42.3247 | -61.0253 | -42.8071 | -43.3046
131 | -2.3397 | 0 | -2.1232 | 0 | -2.3617 | 0 | -2.1083 | 0 | -52.6686 | -29.428 | -52.9925 | 78.4102 | -58.836 | 77.7785 | -51.9193 | 100.4616 | -65.1788 | 17.9173 | -53.8479 | 130.5646 | -52.3091 | -46.9342 | -53.1772 | 36.6781 | -83.9318 | 122.0265 | -55.7413 | 123.4907 | -63.5825 | 8.8746 | -57.2651 | 129.9091 | -15.8844 | 108.9098 | -35.0444 | 23.8739 | -17.9843 | 73.1136 | -27.3999 | 79.6981 | -15.5846 | 72.4324 | -34.3826 | 40.7747 | -17.4434 | 56.168 | -32.3624 | 54.9937 | -47.76 | -45.0102 | -41.1288 | -44.3499 | -63.385 | -45.4595 | -47.9826 | -45.2602 | -41.1327 | -44.5021 | -62.9514 | -45.0688 | -45.1049 | 131 | -49.3044 | -49.1576 | -48.0767 | -52.4156 | -49.7096 | -50.467 | -50.2897 | -56.3462 | 131 | -42.9205 | -38.793 | -42.0102 | -61.2618 | -43.3363 | -45.6209 | -43.137 | -38.771 | -42.2416 | -61.0233 | -43.3512 | -45.8743 | -42.6705 | -38.7891 | -42.1624 | -60.8282 | -42.9456 | -42.7432 | -42.887 | -38.7671 | -42.3938 | -60.5897 | -42.9605 | -42.9966
132 | -2.3689 | 0 | -2.1312 | 0 | -2.3867 | 0 | -2.1074 | 0 | -52.6609 | -43.0457 | -53.6596 | 60.6985 | -57.7968 | 56.0178 | -50.8912 | 90.6357 | -64.9887 | -7.3759 | -53.0145 | 117.2783 | -52.2555 | -61.6771 | -53.7199 | 16.1575 | -73.2649 | -14.3042 | -54.14 | 100.9517 | -63.5799 | -11.3105 | -55.5998 | 113.0425 | -15.7196 | 96.0765 | -40.0495 | 12.9983 | -18.1542 | 59.0672 | -28.1922 | 81.5036 | -15.5256 | 59.4318 | -35.8606 | 45.4844 | -17.4417 | 43.3053 | -33.7555 | 67.0537 | -47.6938 | -45.1055 | -41.158 | -44.4399 | -63.0297 | -45.543 | -47.9086 | -45.4375 | -41.1384 | -44.5101 | -62.5101 | -45.2461 | -44.7661 | 132 | -49.4365 | -48.5759 | -47.5831 | -51.5658 | -49.8959 | -49.896 | -49.6435 | -54.8945 | 132 | -43.0686 | -38.7695 | -42.071 | -60.8985 | -43.4118 | -45.5219 | -43.3063 | -38.7517 | -42.3325 | -60.643 | -43.4356 | -45.8012 | -42.7366 | -38.7891 | -42.1412 | -60.3789 | -43.1149 | -42.3794 | -42.9743 | -38.7713 | -42.4027 | -60.1234 | -43.1387 | -42.6587
133 | -2.3892 | 0 | -2.1512 | 0 | -2.3977 | 0 | -2.1105 | 0 | -52.911 | -56.7892 | -54.7339 | 42.3199 | -56.9705 | 27.5977 | -50.1907 | 79.9205 | -65.1675 | -31.633 | -52.3842 | 103.4379 | -52.3668 | -75.7007 | -54.6363 | -5.8151 | -64.8411 | -39.1594 | -52.8966 | 79.9255 | -63.5816 | -33.2311 | -54.3793 | 89.2089 | -15.8889 | 83.5336 | -57.9123 | 122.7403 | -18.7902 | 45.3155 | -28.773 | 90.9425 | -15.8836 | 46.5757 | -37.7689 | 72.7467 | -18.0299 | 31.0953 | -34.2682 | 98.5695 | -47.6317 | -45.1165 | -41.1665 | -44.5419 | -62.7919 | -45.636 | -47.8114 | -45.5657 | -41.147 | -44.4949 | -62.0262 | -45.5071 | -44.4135 | 133 | -49.7937 | -48.2419 | -47.2798 | -50.9213 | -50.1931 | -49.4426 | -49.1295 | -53.5512 | 133 | -43.1765 | -38.7578 | -42.1527 | -60.6407 | -43.4848 | -45.4137 | -43.4145 | -38.7493 | -42.4314 | -60.3942 | -43.5255 | -45.7009 | -42.7273 | -38.7773 | -42.1057 | -59.875 | -43.3559 | -42.0158 | -42.9653 | -38.7688 | -42.3844 | -59.6285 | -43.3966 | -42.303
134 | -2.3867 | 0 | -2.1566 | 0 | -2.4057 | 0 | -2.118 | 0 | -53.3821 | -70.5852 | -56.3322 | 22.101 | -56.4911 | 1.4052 | -49.8274 | 69.2815 | -65.4501 | -55.0862 | -52.1802 | 86.6547 | -52.6829 | -89.248 | -56.0147 | -29.6647 | -60.9491 | -55.8307 | -51.9467 | 60.1772 | -64.302 | -53.9471 | -54.4255 | 67.56 | -16.4357 | 70.9224 | -37.9813 | 153.8286 | -19.9955 | 31.734 | -28.1855 | 101.3299 | -16.6244 | 34.2569 | -34.1672 | 87.8728 | -19.1277 | 19.8334 | -30.7614 | 115.6305 | -47.5551 | -45.019 | -41.2031 | -44.641 | -62.6449 | -45.7964 | -47.6879 | -45.562 | -41.1328 | -44.4535 | -61.5863 | -45.7729 | -44.1517 | 134 | -50.3811 | -48.1587 | -47.2618 | -50.6643 | -50.6055 | -49.1541 | -49.0308 | -53.2016 | 134 | -43.1753 | -38.7461 | -42.2543 | -60.4883 | -43.6398 | -45.2822 | -43.4054 | -38.7271 | -42.523 | -60.2392 | -43.6784 | -45.5699 | -42.6323 | -38.8164 | -42.0668 | -59.4297 | -43.6163 | -41.746 | -42.8624 | -38.7974 | -42.3355 | -59.1806 | -43.6549 | -42.0337
135 | -2.3903 | 0 | -2.1489 | 0 | -2.4105 | 0 | -2.149 | 0 | -54.1357 | -84.6542 | -58.9084 | -2.2801 | -56.0433 | -22.7307 | -49.7386 | 58.5241 | -66.1946 | -78.1107 | -52.8907 | 73.3483 | -53.252 | -102.1345 | -57.9862 | -57.8386 | -58.9257 | -68.3976 | -51.3247 | 40.4342 | -65.1971 | -74.7246 | -54.7343 | 48.4652 | -17.3034 | 58.7435 | -32.1383 | 135.2523 | -21.8067 | 19.3419 | -26.4299 | 107.6114 | -17.7409 | 22.0465 | -30.7366 | 86.1661 | -20.8349 | 10.1372 | -27.3275 | 111.5898 | -47.477 | -44.8597 | -41.2184 | -44.727 | -62.4809 | -45.9183 | -47.5395 | -45.4496 | -41.1013 | -44.3872 | -61.2817 | -46.1176 | -44.0351 | 135 | -51.174 | -48.3212 | -47.6838 | -51.042 | -51.1919 | -49.0649 | -49.0929 | -53.0587 | 135 | -43.0593 | -38.711 | -42.3367 | -60.332 | -43.7694 | -45.129 | -43.3007 | -38.6908 | -42.578 | -60.0704 | -43.7693 | -45.3905 | -42.4694 | -38.8281 | -41.9969 | -59.1328 | -43.9687 | -41.6246 | -42.7108 | -38.8079 | -42.2382 | -58.8712 | -43.9686 | -41.8861
136 | -2.3952 | 0 | -2.177 | 0 | -2.3957 | 0 | -2.1755 | 0 | -55.2451 | -98.5378 | -62.9094 | -36.7905 | -56.5527 | -44.3458 | -49.8941 | 48.9325 | -67.0038 | -105.5843 | -54.6476 | 62.1113 | -54.1139 | -113.9542 | -60.3808 | -94.0635 | -56.8364 | -84.9002 | -51.0089 | 21.2536 | -66.5283 | -95.1449 | -55.3924 | 22.9581 | -18.6586 | 47.9776 | -28.6018 | 120.8269 | -24.9817 | 10.5317 | -24.4291 | 106.9418 | -19.5014 | 11.0209 | -28.2931 | 78.3891 | -23.6157 | 4.1479 | -24.9266 | 106.3979 | -47.3996 | -44.6807 | -41.2232 | -44.8136 | -62.5324 | -46.1495 | -47.3997 | -45.2355 | -41.0944 | -44.3567 | -60.9934 | -46.4465 | -44.0317 | 136 | -52.4319 | -48.7176 | -48.4807 | -52.3354 | -51.633 | -49.1983 | -49.3062 | -52.8539 | 136 | -42.8403 | -38.6992 | -42.4184 | -60.3554 | -43.9725 | -45.004 | -43.0585 | -38.6987 | -42.6381 | -60.1367 | -43.974 | -45.2242 | -42.2855 | -38.828 | -41.9615 | -58.8164 | -44.2695 | -41.636 | -42.5037 | -38.8275 | -42.1812 | -58.5977 | -44.271 | -41.8562
137 | -2.3676 | 0 | -2.1962 | 0 | -2.3723 | 0 | -2.1831 | 0 | -56.8109 | -112.5849 | -66.8234 | -104.5734 | -56.8546 | -68.9392 | -50.1954 | 40.2142 | -67.9767 | -132.7644 | -56.2325 | 54.5014 | -55.3006 | -124.1132 | -62.0554 | -145.2757 | -55.4755 | -94.7919 | -51.0081 | 2.2272 | -68.2159 | -117.8557 | -56.8225 | 3.3908 | -20.6468 | 40.068 | -26.2738 | 105.1451 | -30.2358 | 13.8023 | -22.6608 | 102.3484 | -22.0879 | 2.5916 | -26.491 | 65.5565 | -27.1292 | 10.6847 | -23.136 | 96.2994 | -47.3601 | -44.4659 | -41.219 | -44.8796 | -62.6374 | -46.3565 | -47.2665 | -44.9856 | -41.0669 | -44.3642 | -60.8486 | -46.634 | -44.1059 | 137 | -53.6101 | -49.2799 | -49.1547 | -53.3691 | -51.9327 | -49.5742 | -49.7347 | -52.9554 | 137 | -42.618 | -38.6993 | -42.512 | -60.4412 | -44.1603 | -44.8942 | -42.7894 | -38.6946 | -42.6965 | -60.2651 | -44.1734 | -45.0834 | -42.0983 | -38.8514 | -41.9966 | -58.6524 | -44.4378 | -41.7336 | -42.2697 | -38.8467 | -42.1811 | -58.4763 | -44.4509 | -41.9228
138 | -2.3515 | 0 | -2.2104 | 0 | -2.375 | 0 | -2.2159 | 0 | -59.1602 | -125.5999 | -62.9461 | -174.7775 | -57.7269 | -87.9818 | -50.6539 | 32.2696 | -69.2405 | -167.5 | -58.1615 | 56.4365 | -56.8659 | -131.1349 | -60.7221 | 160.9898 | -55.4262 | -110.1938 | -51.313 | -17.1996 | -72.0899 | -138.9745 | -58.7097 | -27.0554 | -23.2819 | 37.4103 | -24.814 | 88.2515 | -33.6533 | 68.6064 | -21.2925 | 94.3079 | -25.9254 | 1.6095 | -25.3021 | 51.7362 | -29.0034 | 41.9067 | -21.8392 | 84.6907 | -47.3469 | -44.3396 | -41.2146 | -44.9133 | -62.8469 | -46.5623 | -47.1753 | -44.754 | -41.039 | -44.4135 | -60.7807 | -46.7188 | -44.2609 | 138 | -54.6743 | -50.0285 | -49.7319 | -54.7705 | -52.3872 | -50.2179 | -50.1847 | -53.6912 | 138 | -42.4025 | -38.6875 | -42.5618 | -60.6365 | -44.3519 | -44.8003 | -42.5436 | -38.664 | -42.6974 | -60.4719 | -44.3464 | -44.9594 | -41.9881 | -38.8631 | -42.062 | -58.5703 | -44.5084 | -41.8859 | -42.1292 | -38.8396 | -42.1976 | -58.4057 | -44.5029 | -42.045
139 | -2.3444 | 0 | -2.2255 | 0 | -2.3753 | 0 | -2.2424 | 0 | -62.8139 | -137.5401 | -58.7491 | 149.6677 | -59.5184 | -110.6593 | -51.2074 | 25.4891 | -69.7318 | 158.1783 | -59.1663 | 62.3067 | -58.6518 | -132.12 | -58.0828 | 121.2486 | -55.2806 | -117.9633 | -51.9728 | -36.9459 | -77.542 | -179.1264 | -60.6059 | -61.7355 | -26.5313 | 48.952 | -23.9809 | 72.4506 | -27.292 | 96.5279 | -20.3273 | 85.5003 | -30.4964 | 24.923 | -24.6601 | 36.8474 | -25.8991 | 64.8227 | -21.1472 | 72.2538 | -47.3501 | -44.2812 | -41.2034 | -44.8931 | -62.9908 | -46.7265 | -47.0966 | -44.5667 | -41.0436 | -44.4637 | -60.7372 | -46.6839 | -44.4018 | 139 | -55.2663 | -50.8606 | -49.9489 | -56.1345 | -52.3037 | -51.1177 | -50.568 | -54.1433 | 139 | -42.2223 | -38.6992 | -42.5487 | -60.7653 | -44.501 | -44.7213 | -42.3412 | -38.6683 | -42.6507 | -60.6155 | -44.4841 | -44.8542 | -41.9368 | -38.859 | -42.1193 | -58.5117 | -44.4584 | -42.0265 | -42.0557 | -38.8281 | -42.2213 | -58.3619 | -44.4415 | -42.1594
140 | -2.3539 | 0 | -2.2477 | 0 | -2.3823 | 0 | -2.2561 | 0 | -70.1402 | -142.5277 | -56.0885 | 125.1211 | -62.6264 | -132.0212 | -51.9779 | 20.194 | -69.5507 | 123.3673 | -60.5326 | 79.52 | -60.1074 | -124.8622 | -55.8161 | 91.388 | -54.8539 | -127.4072 | -53.0302 | -57.7747 | -80.6593 | 84.7251 | -60.3346 | -94.2481 | -26.8236 | 75.1403 | -23.6563 | 55.9822 | -23.0185 | 91.5993 | -19.6526 | 75.074 | -28.1673 | 65.7776 | -24.38 | 22.0434 | -22.3647 | 64.3979 | -20.5289 | 58.4557 | -47.3723 | -44.2647 | -41.2129 | -44.8684 | -63.1887 | -46.8975 | -47.0602 | -44.48 | -41.0766 | -44.5915 | -60.736 | -46.6206 | -44.5496 | 140 | -55.0804 | -51.8379 | -50.1379 | -58.12 | -51.6326 | -52.2466 | -50.6938 | -53.7624 | 140 | -42.1261 | -38.7227 | -42.5145 | -60.941 | -44.6498 | -44.6779 | -42.2323 | -38.6943 | -42.6123 | -60.8064 | -44.6414 | -44.8041 | -41.9108 | -38.859 | -42.2376 | -58.4883 | -44.3729 | -42.1673 | -42.017 | -38.8306 | -42.3354 | -58.3537 | -44.3645 | -42.2935
141 | -2.3602 | 0 | -2.2638 | 0 | -2.4103 | 0 | -2.2688 | 0 | -74.4133 | -25.273 | -54.4417 | 104.5312 | -65.4855 | -176.203 | -52.789 | 17.1881 | -68.4895 | 93.8767 | -59.9153 | 91.4225 | -59.9187 | -112.0112 | -54.1765 | 66.1724 | -55.1701 | -135.3674 | -54.5343 | -80.7516 | -72.7547 | 24.3281 | -59.7038 | -131.7479 | -24.0899 | 89.5228 | -24.0232 | 39.4894 | -20.518 | 80.9048 | -19.3176 | 63.9414 | -24.0871 | 73.5043 | -24.7251 | 7.2904 | -20.073 | 55.6533 | -20.3864 | 44.831 | -47.4352 | -44.3278 | -41.2191 | -44.8141 | -63.2282 | -46.9841 | -47.0763 | -44.4611 | -41.1062 | -44.713 | -60.6701 | -46.5314 | -44.7302 | 141 | -54.0726 | -52.6447 | -50.0537 | -58.4041 | -51.0335 | -53.3798 | -50.7503 | -53.8044 | 141 | -42.1009 | -38.746 | -42.4539 | -60.9644 | -44.7203 | -44.666 | -42.1973 | -38.6959 | -42.5453 | -60.8179 | -44.7153 | -44.8075 | -41.9676 | -38.8589 | -42.3528 | -58.4063 | -44.2676 | -42.3199 | -42.064 | -38.8088 | -42.4442 | -58.2598 | -44.2626 | -42.4614
142 | -2.3931 | 0 | -2.2784 | 0 | -2.448 | 0 | -2.2736 | 0 | -63.7414 | -19.0419 | -53.4307 | 86.1569 | -66.5448 | 117.4278 | -53.4863 | 17.1019 | -67.3891 | 64.04 | -58.5254 | 97.6207 | -58.1119 | -103.5622 | -53.0245 | 43.8287 | -55.7202 | -134.5647 | -56.5532 | -107.9602 | -69.2611 | -2.2091 | -58.7856 | -164.3579 | -21.339 | 89.2157 | -24.8207 | 22.5916 | -18.8749 | 67.2305 | -19.38 | 53.1033 | -21.2585 | 67.3242 | -25.6967 | -7.225 | -18.6425 | 43.9468 | -20.7612 | 30.4323 | -47.5123 | -44.4709 | -41.2402 | -44.817 | -63.149 | -47.1272 | -47.1027 | -44.5105 | -41.186 | -44.8331 | -60.5441 | -46.5105 | -44.8735 | 142 | -52.8544 | -52.9363 | -49.8197 | -57.4273 | -50.3587 | -54.1177 | -50.6967 | -53.8508 | 142 | -42.1174 | -38.7929 | -42.4239 | -60.8706 | -44.8488 | -44.6547 | -42.2321 | -38.738 | -42.5434 | -60.701 | -44.8536 | -44.8291 | -42.0778 | -38.8471 | -42.44 | -58.2657 | -44.2321 | -42.4255 | -42.1925 | -38.7922 | -42.5595 | -58.0961 | -44.2369 | -42.5999
143 | -2.3992 | 0 | -2.2701 | 0 | -2.4968 | 0 | -2.2685 | 0 | -58.7527 | -31.1711 | -52.9322 | 69.7531 | -62.9272 | 53.6861 | -53.8248 | 19.7519 | -66.3046 | 40.3121 | -57.1103 | 95.1023 | -55.8719 | -104.2756 | -52.3605 | 22.3909 | -55.3968 | -130.4165 | -58.9712 | -143.0755 | -66.2115 | -22.2343 | -58.0616 | 167.3658 | -19.3794 | 82.4897 | -26.6881 | 4.9634 | -17.9742 | 53.2469 | -19.7735 | 42.4259 | -19.4213 | 56.4617 | -27.392 | -21.0296 | -17.7805 | 30.2672 | -21.4624 | 16.1495 | -47.5507 | -44.6603 | -41.258 | -44.8202 | -63.0351 | -47.2228 | -47.1294 | -44.6179 | -41.2508 | -44.9654 | -60.3716 | -46.5007 | -44.9929 | 143 | -51.5907 | -52.4323 | -49.5152 | -55.704 | -49.4768 | -53.8789 | -50.6364 | -53.2901 | 143 | -42.2187 | -38.8516 | -42.421 | -60.765 | -44.9527 | -44.6326 | -42.3478 | -38.754 | -42.5517 | -60.5383 | -44.9543 | -44.8609 | -42.2611 | -38.8588 | -42.5662 | -58.1015 | -44.2306 | -42.4961 | -42.3902 | -38.7612 | -42.6969 | -57.8748 | -44.2322 | -42.7244
144 | -2.4312 | 0 | -2.2719 | 0 | -2.5273 | 0 | -2.2656 | 0 | -55.5908 | -45.7697 | -52.8334 | 53.6852 | -59.0993 | 12.181 | -53.4281 | 23.2986 | -65.5331 | 19.0034 | -55.4467 | 85.645 | -53.8563 | -110.4791 | -52.1665 | 1.7268 | -55.105 | -127.1226 | -60.3734 | 168.4701 | -64.2096 | -40.3015 | -56.2818 | 134.9361 | -18.0688 | 72.2733 | -29.8421 | -15.3838 | -17.5781 | 38.6641 | -20.6185 | 32.1694 | -18.2336 | 43.5748 | -30.1301 | -31.8738 | -17.5996 | 15.7683 | -22.6345 | 1.6119 | -47.5408 | -44.8665 | -41.2665 | -44.8338 | -62.7439 | -47.2766 | -47.1196 | -44.7422 | -41.3531 | -45.0532 | -60.1626 | -46.5312 | -45.0706 | 144 | -50.3629 | -51.2026 | -48.9954 | -53.6018 | -48.77 | -52.6664 | -50.2947 | -52.3506 | 144 | -42.311 | -38.9219 | -42.4026 | -60.472 | -45.0047 | -44.5923 | -42.4703 | -38.8258 | -42.5682 | -60.2166 | -45.011 | -44.854 | -42.4353 | -38.8353 | -42.622 | -57.8907 | -44.2593 | -42.5433 | -42.5946 | -38.7392 | -42.7876 | -57.6353 | -44.2656 | -42.805
145 | -2.475 | 0 | -2.2621 | 0 | -2.5442 | 0 | -2.292 | 0 | -53.4111 | -61.1811 | -53.0609 | 39.4194 | -55.6241 | -10.9753 | -52.4956 | 23.8301 | -64.9528 | 1.978 | -54.5547 | 76.6259 | -52.1219 | -119.7752 | -52.2042 | -18.0346 | -54.0662 | -126.4073 | -58.9881 | 119.1149 | -63.2911 | -62.2137 | -55.9784 | 117.6741 | -17.3304 | 61.1014 | -35.9539 | -41.77 | -17.7016 | 24.4382 | -22.0348 | 22.563 | -17.8292 | 29.951 | -34.7875 | -31.9856 | -17.83 | 1.3914 | -24.4826 | -12.1884 | -47.4606 | -45.0201 | -41.322 | -44.859 | -62.2731 | -47.3013 | -47.0863 | -44.8724 | -41.4203 | -45.1019 | -59.8324 | -46.5325 | -45.123 | 145 | -49.1221 | -49.7848 | -48.5155 | -51.8294 | -47.9383 | -51.0425 | -50.0848 | -51.6027 | 145 | -42.3974 | -38.9453 | -42.384 | -60.011 | -45.0392 | -44.5421 | -42.6103 | -38.8761 | -42.567 | -59.7289 | -45.0093 | -44.7943 | -42.5451 | -38.847 | -42.6269 | -57.5703 | -44.2704 | -42.5788 | -42.758 | -38.7778 | -42.8099 | -57.2882 | -44.2405 | -42.831
146 | -2.5027 | 0 | -2.2621 | 0 | -2.5274 | 0 | -2.2982 | 0 | -51.7436 | -77.5138 | -53.5546 | 26.4649 | -53.0963 | -29.3811 | -51.4281 | 21.0838 | -65.0474 | -16.0469 | -54.2691 | 67.9441 | -50.7456 | -131.0357 | -52.67 | -37.8567 | -52.0872 | -126.8576 | -56.4423 | 82.5559 | -62.9634 | -76.9313 | -55.355 | 95.6828 | -17.0587 | 49.2418 | -41.4643 | -159.0358 | -18.4571 | 10.5199 | -24.0707 | 15.3331 | -17.8341 | 15.6402 | -40.1159 | 6.5866 | -18.7789 | -14.5854 | -27.3286 | -27.4096 | -47.3043 | -45.1711 | -41.3614 | -44.9293 | -61.7575 | -47.3196 | -47.016 | -44.9883 | -41.4598 | -45.1606 | -59.3754 | -46.5625 | -45.1651 | 146 | -47.9571 | -48.476 | -48.1388 | -50.4785 | -46.9866 | -49.5091 | -49.7509 | -50.1756 | 146 | -42.4856 | -38.9571 | -42.4266 | -59.4954 | -45.0575 | -44.4886 | -42.7262 | -38.9324 | -42.6311 | -59.2301 | -45.0214 | -44.7178 | -42.6684 | -38.8587 | -42.6579 | -57.1133 | -44.3004 | -42.6377 | -42.909 | -38.834 | -42.8624 | -56.848 | -44.2643 | -42.8669
147 | -2.5177 | 0 | -2.2684 | 0 | -2.4948 | 0 | -2.2812 | 0 | -50.5101 | -93.9914 | -54.2804 | 14.2449 | -51.2697 | -47.1233 | -50.4856 | 14.9202 | -65.9752 | -28.3622 | -54.6597 | 62.6625 | -49.648 | -144.1013 | -53.4913 | -57.1069 | -50.3096 | -133.4727 | -54.1395 | 54.625 | -62.7605 | -92.4539 | -56.2191 | 73.3676 | -17.2459 | 37.679 | -31.923 | 143.7643 | -19.6729 | -2.2819 | -27.0055 | 13.6439 | -18.2757 | 1.4646 | -33.8354 | 47.611 | -20.3013 | -29.9205 | -32.0806 | -37.9581 | -47.1231 | -45.2909 | -41.3997 | -45.045 | -61.3301 | -47.3846 | -46.8465 | -45.0729 | -41.4395 | -45.1903 | -58.8661 | -46.612 | -45.2735 | 147 | -46.9704 | -47.4264 | -47.9333 | -49.5321 | -46.085 | -48.1733 | -49.6983 | -49.1258 | 147 | -42.5552 | -38.9218 | -42.5273 | -59.0617 | -45.1162 | -44.3517 | -42.8045 | -38.9447 | -42.7638 | -58.8353 | -45.1034 | -44.5653 | -42.7732 | -38.882 | -42.6726 | -56.5977 | -44.3436 | -42.7787 | -43.0225 | -38.9049 | -42.9091 | -56.3713 | -44.3308 | -42.9923
148 | -2.5151 | 0 | -2.2832 | 0 | -2.487 | 0 | -2.2918 | 0 | -49.6191 | -111.2983 | -55.2876 | 2.9516 | -50.0214 | -65.964 | -49.7867 | 7.6216 | -66.7307 | -33.3501 | -56.0322 | 54.4291 | -48.8548 | -157.6399 | -54.7034 | -77.7973 | -49.0534 | -140.6198 | -52.4033 | 31.7845 | -63.1956 | -106.9288 | -57.0612 | 54.7698 | -17.7649 | 26.5168 | -27.038 | 120.8822 | -21.6441 | -13.7146 | -30.3981 | 27.9542 | -19.3899 | -13.7608 | -29.5819 | 44.0825 | -22.8066 | -47.0535 | -42.6489 | -45.0846 | -46.9152 | -45.4002 | -41.4283 | -45.177 | -60.884 | -47.4823 | -46.6621 | -45.1706 | -41.351 | -45.2051 | -58.291 | -46.7448 | -45.4184 | 148 | -46.2293 | -46.649 | -47.9707 | -48.9769 | -45.4003 | -47.1565 | -49.5455 | -48.2734 | 148 | -42.6555 | -38.8359 | -42.6619 | -58.6008 | -45.1991 | -44.1751 | -42.8874 | -38.864 | -42.8852 | -58.397 | -45.1905 | -44.3703 | -42.8851 | -38.9132 | -42.69 | -56.0078 | -44.4616 | -42.9314 | -43.117 | -38.9413 | -42.9133 | -55.804 | -44.453 | -43.1266
149 | -2.4987 | 0 | -2.3206 | 0 | -2.4935 | 0 | -2.3295 | 0 | -49.0919 | -128.6004 | -56.7612 | -7.3895 | -48.7417 | -84.9834 | -49.3185 | -1.0941 | -66.355 | -33.5565 | -57.9681 | 53.1277 | -48.3369 | -172.1974 | -56.4597 | -100.3756 | -47.9047 | -147.2515 | -51.1307 | 11.2486 | -64.8263 | -118.3714 | -57.7992 | 36.1203 | -18.7629 | 16.6862 | -24.1169 | 101.9459 | -24.4974 | -20.3416 | -31.2 | 61.1704 | -21.1619 | -29.2687 | -26.5203 | 32.0371 | -26.8814 | -64.6373 | -39.2696 | 86.0407 | -46.7299 | -45.4653 | -41.4237 | -45.2846 | -60.5229 | -47.6059 | -46.4299 | -45.2474 | -41.2175 | -45.1721 | -57.6721 | -46.8216 | -45.4956 | 149 | -45.5604 | -46.1518 | -48.1238 | -48.1848 | -44.7983 | -46.4392 | -49.3452 | -47.4018 | 149 | -42.7487 | -38.7188 | -42.7859 | -58.2023 | -45.2853 | -43.9364 | -42.9268 | -38.724 | -42.9551 | -58.0294 | -45.2764 | -44.1004 | -42.9666 | -38.925 | -42.6734 | -55.3515 | -44.501 | -43.0021 | -43.1447 | -38.9302 | -42.8426 | -55.1786 | -44.4921 | -43.1661
150 | -2.4978 | 0 | -2.3564 | 0 | -2.5059 | 0 | -2.3234 | 0 | -48.9138 | -146.8185 | -58.8835 | -16.0153 | -47.7597 | -104.287 | -49.0472 | -10.0483 | -65.4244 | -40.2326 | -59.7691 | 59.8157 | -48.1127 | 172.3685 | -59.0211 | -127.9444 | -46.7914 | -156.2868 | -50.3075 | -9.0207 | -66.1123 | -121.3749 | -58.9258 | 17.3175 | -20.2335 | 8.6074 | -22.3122 | 85.1047 | -28.4694 | -14.8259 | -27.7085 | 79.935 | -23.9005 | -44.9374 | -24.5396 | 17.4315 | -35.1747 | -89.8581 | -31.4993 | 76.476 | -46.5782 | -45.5012 | -41.3994 | -45.379 | -60.2189 | -47.7239 | -46.1962 | -45.2364 | -41.0525 | -45.1493 | -57.1884 | -46.8809 | -45.6022 | 150 | -45.1025 | -45.9207 | -48.2971 | -47.4251 | -44.2446 | -46.0199 | -49.2629 | -46.4859 | 150 | -42.7386 | -38.5547 | -42.8812 | -57.8625 | -45.3675 | -43.6903 | -42.88 | -38.5466 | -43.0556 | -57.713 | -45.4005 | -43.8728 | -43.0034 | -38.9016 | -42.6515 | -54.832 | -44.5245 | -43.0963 | -43.1448 | -38.8935 | -42.8259 | -54.6825 | -44.5575 | -43.2788
151 | -2.5021 | 0 | -2.3682 | 0 | -2.4885 | 0 | -2.3198 | 0 | -49.1006 | -164.7986 | -61.7831 | -16.7355 | -47.1465 | -121.5239 | -48.9844 | -19.0702 | -64.4154 | -44.6926 | -59.3308 | 74.425 | -48.2102 | 156.602 | -62.2827 | -167.1532 | -46.1077 | -167.0458 | -49.8532 | -27.7854 | -67.8898 | -116.7794 | -62.7784 | -2.8169 | -22.2402 | 4.2074 | -21.2637 | 69.513 | -31.2834 | 14.7086 | -25.0138 | 82.2973 | -28.1539 | -65.0712 | -23.5029 | 1.2282 | -38.6661 | 118.1593 | -28.5246 | 62.5219 | -46.5433 | -45.437 | -41.3568 | -45.4378 | -60.0667 | -47.812 | -45.9698 | -45.1721 | -40.8576 | -45.0909 | -56.755 | -46.8635 | -45.6437 | 151 | -44.914 | -45.9693 | -48.397 | -46.8154 | -43.9583 | -45.9165 | -49.4072 | -45.9871 | 151 | -42.67 | -38.3555 | -42.9357 | -57.6985 | -45.4438 | -43.4813 | -42.8039 | -38.3691 | -43.118 | -57.5782 | -45.4922 | -43.65 | -42.9349 | -38.8547 | -42.5888 | -54.3868 | -44.4953 | -43.1552 | -43.0688 | -38.8683 | -42.7711 | -54.2665 | -44.5437 | -43.3239
152 | -2.5117 | 0 | -2.394 | 0 | -2.4968 | 0 | -2.3346 | 0 | -49.6544 | 176.9759 | -64.8463 | -1.1014 | -46.9618 | -139.5511 | -49.133 | -28.3924 | -63.4084 | -54.1696 | -57.3679 | 86.863 | -48.6655 | 140.3055 | -63.8467 | 132.276 | -45.8407 | -176.2545 | -49.775 | -46.9153 | -66.416 | -101.8431 | -67.5221 | -13.8607 | -24.4536 | 5.8157 | -20.8402 | 53.7244 | -28.5231 | 38.7525 | -22.9476 | 76.1684 | -38.3834 | -92.2135 | -22.8995 | -16.9226 | -28.9433 | 81.4461 | -26.2798 | 45.5968 | -46.5886 | -45.3632 | -41.2844 | -45.4245 | -59.9831 | -47.9023 | -45.8159 | -45.0632 | -40.6796 | -45.0893 | -56.4721 | -46.8483 | -45.6523 | 152 | -45.0467 | -46.2904 | -48.4253 | -46.494 | -43.9721 | -46.1337 | -49.5385 | -45.7737 | 152 | -42.5515 | -38.1679 | -42.9128 | -57.5891 | -45.5083 | -43.3191 | -42.6692 | -38.1828 | -43.0899 | -57.4863 | -45.5677 | -43.4813 | -42.8515 | -38.7727 | -42.5776 | -54.0781 | -44.4543 | -43.1555 | -42.9692 | -38.7876 | -42.7547 | -53.9753 | -44.5137 | -43.3177
153 | -2.4998 | 0 | -2.4143 | 0 | -2.5001 | 0 | -2.3765 | 0 | -50.6338 | 158.4064 | -64.4369 | 28.3932 | -46.8634 | -158.6307 | -49.5374 | -37.0945 | -62.4587 | -68.2598 | -55.6167 | 84.6089 | -49.6059 | 123.6551 | -60.8826 | 78.1816 | -45.2273 | 174.1424 | -50.0596 | -65.7845 | -63.6308 | -97.8874 | -81.2977 | 43.8037 | -26.0841 | 17.018 | -20.8492 | 38.5968 | -25.6128 | 39.734 | -21.5326 | 68.8028 | -37.2831 | 113.1289 | -22.7388 | -33.9114 | -24.8717 | 62.0264 | -25.4367 | 26.3362 | -46.7496 | -45.3197 | -41.1436 | -45.4215 | -60.1207 | -47.9408 | -45.7425 | -45.0079 | -40.4685 | -45.0628 | -56.3011 | -46.8165 | -45.6793 | 153 | -45.2882 | -46.9178 | -48.4687 | -46.2157 | -43.7907 | -46.727 | -49.7114 | -45.164 | 153 | -42.5081 | -37.9687 | -42.9217 | -57.7064 | -45.5265 | -43.2424 | -42.5936 | -37.9684 | -43.045 | -57.6206 | -45.5643 | -43.366 | -42.8199 | -38.6438 | -42.563 | -53.8868 | -44.4022 | -43.1792 | -42.9054 | -38.6435 | -42.6863 | -53.801 | -44.44 | -43.3028
154 | -2.4908 | 0 | -2.4085 | 0 | -2.5255 | 0 | -2.3844 | 0 | -52.1513 | 138.6292 | -61.0807 | 39.8022 | -47.2677 | -174.0111 | -50.2086 | -44.9061 | -62.2026 | -80.1214 | -53.6278 | 80.0766 | -51.1616 | 106.618 | -57.659 | 43.3329 | -44.9085 | 161.6368 | -50.7305 | -85.1508 | -61.0687 | -103.0361 | -66.4902 | 139.1954 | -25.8458 | 29.7541 | -21.1782 | 23.4672 | -23.583 | 31.1238 | -20.6847 | 59.7153 | -28.8684 | 85.8963 | -23.138 | -52.3323 | -22.9956 | 45.6811 | -25.1528 | 6.8853 | -46.9899 | -45.2983 | -40.9706 | -45.3688 | -60.4665 | -47.9663 | -45.7484 | -45.0099 | -40.3033 | -45.057 | -56.307 | -46.795 | -45.6465 | 154 | -45.912 | -47.8977 | -48.3422 | -46.2526 | -43.8024 | -47.7245 | -49.8336 | -44.7753 | 154 | -42.5191 | -37.8125 | -42.878 | -58.058 | -45.5578 | -43.2229 | -42.6014 | -37.7778 | -42.9844 | -57.941 | -45.5819 | -43.364 | -42.8075 | -38.4798 | -42.5662 | -53.8985 | -44.3865 | -43.121 | -42.8898 | -38.4451 | -42.6726 | -53.7815 | -44.4106 | -43.2621
155 | -2.5072 | 0 | -2.4078 | 0 | -2.5534 | 0 | -2.388 | 0 | -54.4458 | 117.6962 | -58.3283 | 37.2562 | -48.091 | 166.0206 | -51.1206 | -51.0164 | -62.4156 | -96.1686 | -52.0341 | 74.1898 | -53.56 | 89.9223 | -55.2242 | 18.3974 | -44.7392 | 152.5345 | -51.9153 | -104.9138 | -58.9768 | -115.984 | -62.0786 | 120.2829 | -24.683 | 34.729 | -22.1651 | 9.1111 | -22.7141 | 19.2354 | -20.2022 | 50.7546 | -25.8451 | 68.5108 | -23.83 | -72.154 | -22.285 | 29.1658 | -25.2691 | -16.3065 | -47.2978 | -45.3262 | -40.7703 | -45.3037 | -60.9226 | -47.9649 | -45.8707 | -45.0553 | -40.1967 | -45.0738 | -56.5034 | -46.8229 | -45.5984 | 155 | -46.865 | -49.2475 | -48.1092 | -46.5065 | -43.8734 | -49.1703 | -49.9755 | -44.502 | 155 | -42.5481 | -37.6895 | -42.7965 | -58.5148 | -45.5571 | -43.3173 | -42.6475 | -37.6433 | -42.9157 | -58.3692 | -45.5769 | -43.4827 | -42.819 | -38.2631 | -42.5666 | -54.0956 | -44.4151 | -43.045 | -42.9184 | -38.2169 | -42.6858 | -53.95 | -44.4349 | -43.2104
156 | -2.5093 | 0 | -2.3947 | 0 | -2.5744 | 0 | -2.4026 | 0 | -57.9733 | 92.4401 | -56.4819 | 29.7674 | -49.2651 | 148.8163 | -52.1514 | -54.1881 | -63.2774 | -110.1818 | -51.0217 | 62.5976 | -57.4976 | 73.5382 | -53.5281 | -2.9707 | -45.0367 | 140.7024 | -53.6542 | -126.45 | -57.4422 | -130.5772 | -58.2802 | 102.2431 | -23.771 | 32.9026 | -23.8519 | -4.2926 | -22.7119 | 5.8885 | -20.2374 | 42.0381 | -24.1525 | 53.5655 | -25.0734 | -93.597 | -22.2765 | 13.8904 | -25.7623 | -42.172 | -47.5134 | -45.3064 | -40.5908 | -45.2204 | -61.5636 | -47.8865 | -46.0001 | -45.1115 | -40.1343 | -45.0959 | -56.9062 | -46.8264 | -45.5084 | 156 | -48.0447 | -50.884 | -47.8928 | -46.9427 | -44.2511 | -51.0279 | -49.8992 | -44.6036 | 156 | -42.6022 | -37.625 | -42.7111 | -59.1689 | -45.4918 | -43.4257 | -42.7168 | -37.5599 | -42.8178 | -58.9892 | -45.4839 | -43.5975 | -42.7971 | -38.0815 | -42.5866 | -54.5115 | -44.4317 | -42.934 | -42.9117 | -38.0164 | -42.6933 | -54.3318 | -44.4238 | -43.1058
157 | -2.4971 | 0 | -2.3737 | 0 | -2.5691 | 0 | -2.4057 | 0 | -63.5329 | 49.5031 | -55.2542 | 19.9395 | -50.9787 | 130.717 | -53.0325 | -54.4409 | -63.7981 | -124.6959 | -50.4475 | 52.4773 | -65.7785 | 61.2956 | -52.3826 | -22.5132 | -45.3156 | 130.935 | -56.2456 | -150.884 | -56.4789 | -146.3586 | -56.2241 | 89.2436 | -23.1649 | 27.5225 | -26.2877 | -14.1987 | -23.3565 | -7.4194 | -20.2998 | 34.8142 | -23.6289 | 39.293 | -26.7042 | -117.0114 | -23.0039 | -1.2012 | -26.2009 | -70.7066 | -47.6975 | -45.389 | -40.4264 | -45.1585 | -62.2561 | -47.7523 | -46.1862 | -45.1941 | -40.1104 | -45.0924 | -57.5182 | -46.8386 | -45.515 | 157 | -49.4278 | -52.3397 | -47.7012 | -47.5894 | -44.5041 | -53.1089 | -49.7729 | -44.6799 | 157 | -42.697 | -37.6133 | -42.6614 | -59.8824 | -45.3786 | -43.6171 | -42.8204 | -37.5413 | -42.7528 | -59.687 | -45.3466 | -43.7805 | -42.8919 | -37.9293 | -42.5953 | -55.1445 | -44.4649 | -42.9459 | -43.0153 | -37.8573 | -42.6867 | -54.9491 | -44.4329 | -43.1093
158 | -2.4974 | 0 | -2.3687 | 0 | -2.5722 | 0 | -2.4229 | 0 | -64.3046 | -41.5034 | -54.451 | 10.853 | -53.2293 | 109.2563 | -53.422 | -51.3835 | -65.5026 | -144.4843 | -50.3814 | 42.9171 | -69.7158 | -150.0681 | -51.6374 | -41.0246 | -45.9588 | 122.2424 | -59.8964 | 175.8223 | -56.035 | -162.5375 | -55.3987 | 73.3995 | -23.4736 | 19.5848 | -30.3936 | -19.5499 | -24.9477 | -21.1325 | -20.8058 | 28.0366 | -23.8258 | 26.5135 | -29.3125 | -145.8461 | -24.5429 | -15.0722 | -26.3723 | -102.1988 | -47.7044 | -45.4156 | -40.3682 | -45.1536 | -62.6848 | -47.6031 | -46.2633 | -45.291 | -40.1928 | -45.0758 | -58.3023 | -46.8652 | -45.6588 | 158 | -50.598 | -52.8395 | -47.6207 | -48.4786 | -44.9047 | -54.4098 | -49.6786 | -45.1237 | 158 | -42.7936 | -37.6954 | -42.6562 | -60.3161 | -45.2344 | -43.6911 | -42.9223 | -37.6206 | -42.7307 | -60.1126 | -45.1802 | -43.8404 | -42.9182 | -37.8708 | -42.5784 | -55.9336 | -44.4965 | -43.0866 | -43.0469 | -37.796 | -42.6529 | -55.7301 | -44.4423 | -43.2359
159 | -2.524 | 0 | -2.3828 | 0 | -2.5824 | 0 | -2.4407 | 0 | -58.1639 | -90.4205 | -53.9297 | 2.7641 | -56.3837 | 85.8883 | -53.2345 | -49.7977 | -68.0569 | -165.5482 | -50.8788 | 31.6822 | -58.8162 | -160.5169 | -51.3159 | -58.6865 | -46.9428 | 116.2498 | -63.3555 | 119.8059 | -55.9309 | -178.5364 | -54.9024 | 59.2418 | -24.3642 | 12.9805 | -35.6368 | 2.4389 | -27.7624 | -35.4007 | -21.4685 | 22.219 | -25.0147 | 15.7978 | -32.0468 | 177.3025 | -27.2433 | -26.3633 | -25.6684 | -132.0656 | -47.4372 | -45.4728 | -40.3832 | -45.1794 | -62.5817 | -47.4377 | -46.3945 | -45.4418 | -40.3131 | -45.1015 | -59.1406 | -46.8754 | -46.0207 | 159 | -51.0393 | -51.9172 | -47.7051 | -49.7371 | -45.3885 | -53.6378 | -49.5538 | -45.8497 | 159 | -42.9178 | -37.7891 | -42.6554 | -60.1989 | -45.0549 | -43.8121 | -43.059 | -37.7307 | -42.7387 | -59.9993 | -44.997 | -43.9538 | -42.9488 | -37.8592 | -42.5775 | -56.7578 | -44.4926 | -43.4383 | -43.09 | -37.8008 | -42.6608 | -56.5582 | -44.4347 | -43.58
160 | -2.5231 | 0 | -2.3843 | 0 | -2.5726 | 0 | -2.4541 | 0 | -54.0689 | -117.6148 | -53.4379 | -4.6608 | -63.1125 | 47.6503 | -52.7116 | -49.7262 | -72.8029 | 160.4945 | -51.7247 | 21.0656 | -54.2937 | -175.3468 | -51.3345 | -75.5103 | -47.7279 | 113.2909 | -61.568 | 56.1274 | -56.1271 | 164.6759 | -54.684 | 42.9168 | -26.1016 | 10.5745 | -33.8312 | 50.4674 | -33.1275 | -42.9849 | -22.0966 | 18.9647 | -27.2406 | 10.7914 | -33.2803 | 121.8589 | -31.8445 | -29.9502 | -25.0934 | -161.7175 | -47.0951 | -45.5568 | -40.5112 | -45.263 | -61.8646 | -47.299 | -46.2789 | -45.6547 | -40.5153 | -45.1265 | -59.6226 | -46.8304 | -46.5539 | 160 | -50.4876 | -50.3027 | -47.7964 | -51.3887 | -45.5364 | -51.6386 | -49.4111 | -46.437 | 160 | -43.1316 | -37.9922 | -42.7399 | -59.4803 | -44.9147 | -43.7063 | -43.2704 | -37.9427 | -42.8089 | -59.292 | -44.8449 | -43.8248 | -43.0337 | -37.9881 | -42.6034 | -57.2383 | -44.4461 | -43.9813 | -43.1725 | -37.9386 | -42.6724 | -57.05 | -44.3763 | -44.0998
161 | -2.5113 | 0 | -2.4084 | 0 | -2.5704 | 0 | -2.4468 | 0 | -51.2445 | -139.098 | -52.8375 | -12.8668 | -65.6094 | -55.6631 | -52.0866 | -52.0083 | -73.7081 | 75.2748 | -52.7513 | 11.2413 | -51.4553 | 168.1566 | -51.6011 | -92.2946 | -48.6382 | 111.1531 | -57.9429 | 18.4759 | -56.7365 | 148.3766 | -55.2018 | 33.3045 | -29.1849 | 14.7354 | -29.613 | 59.0168 | -48.0929 | -14.4783 | -22.9213 | 15.9741 | -30.0907 | 20.5531 | -32.1861 | 74.3277 | -38.1363 | 4.5092 | -24.3054 | 170.8843 | -46.5567 | -45.6952 | -40.7455 | -45.3926 | -60.5254 | -47.2616 | -45.9709 | -45.9337 | -40.7496 | -45.1975 | -59.3537 | -46.8165 | -47.3291 | 161 | -48.8652 | -48.6214 | -47.7741 | -52.499 | -45.567 | -49.6343 | -49.3775 | -47.2534 | 161 | -43.4224 | -38.2383 | -42.8813 | -58.117 | -44.8532 | -43.4005 | -43.5253 | -38.1792 | -42.9458 | -57.955 | -44.8148 | -43.5241 | -43.1839 | -38.2342 | -42.6862 | -56.9453 | -44.4081 | -44.7587 | -43.2868 | -38.1751 | -42.7507 | -56.7833 | -44.3697 | -44.8823
162 | -2.5328 | 0 | -2.4288 | 0 | -2.5741 | 0 | -2.4451 | 0 | -49.1604 | -160.8081 | -52.3601 | -23.5886 | -58.2694 | -92.4653 | -51.5415 | -56.2725 | -66.4746 | 28.1339 | -54.8065 | 5.6342 | -49.3502 | 151.2419 | -52.2129 | -108.7501 | -49.2956 | 112.3385 | -55.3957 | -6.7264 | -57.7902 | 130.2932 | -55.8454 | 25.5231 | -30.5219 | 42.4555 | -26.5259 | 51.5853 | -35.2106 | 85.2397 | -23.6359 | 15.0762 | -31.3634 | 44.7632 | -30.1125 | 36.5672 | -34.8642 | 49.9143 | -23.7946 | 150.5083 | -45.9403 | -45.863 | -41.1537 | -45.495 | -58.8544 | -47.3122 | -45.3702 | -46.246 | -41.0172 | -45.253 | -57.9639 | -46.8202 | -48.1648 | 162 | -47.1153 | -47.1287 | -47.9247 | -52.992 | -45.3191 | -47.9145 | -49.394 | -47.9514 | 162 | -43.7132 | -38.4844 | -42.9622 | -56.4256 | -44.8834 | -42.7961 | -43.8172 | -38.4431 | -43.0499 | -56.2803 | -44.8671 | -42.9251 | -43.3302 | -38.6209 | -42.7202 | -55.5351 | -44.3914 | -45.5907 | -43.4342 | -38.5796 | -42.8079 | -55.3898 | -44.3751 | -45.7197
163 | -2.5561 | 0 | -2.4436 | 0 | -2.6017 | 0 | -2.4392 | 0 | -47.6243 | 176.5352 | -52.2865 | -34.7328 | -53.152 | -105.6651 | -51.0348 | -61.4479 | -60.7642 | 0.6275 | -58.1779 | 13.1329 | -47.7544 | 131.4478 | -53.3704 | -126.5393 | -50.055 | 111.8756 | -53.7508 | -28.3317 | -59.7198 | 106.2388 | -56.9819 | 30.5143 | -28.4319 | 65.8084 | -25.0226 | 40.2093 | -29.7157 | 75.7111 | -24.5043 | 11.3582 | -27.9003 | 62.7845 | -28.1628 | 8.8701 | -29.3328 | 52.6457 | -23.413 | 128.303 | -45.3107 | -46.1055 | -41.6731 | -45.6271 | -57.0568 | -47.5274 | -44.6311 | -46.4611 | -41.2162 | -45.2327 | -55.9436 | -46.9064 | -49.1339 | 163 | -45.5242 | -45.8503 | -48.1508 | -51.427 | -45.0519 | -46.5652 | -49.657 | -48.8792 | 163 | -43.905 | -38.6601 | -43.071 | -54.6132 | -45.0838 | -42.0294 | -44.0175 | -38.6145 | -43.1879 | -54.4551 | -45.0882 | -42.1919 | -43.5494 | -39.117 | -42.6766 | -53.5 | -44.4628 | -46.5322 | -43.6619 | -39.0714 | -42.7935 | -53.3419 | -44.4672 | -46.6947
164 | -2.5801 | 0 | -2.4618 | 0 | -2.6169 | 0 | -2.4504 | 0 | -46.7586 | 150.4762 | -52.8035 | -47.6592 | -49.0821 | -123.3714 | -50.6233 | -68.5418 | -56.7083 | -26.5905 | -59.6052 | 54.4789 | -46.6641 | 108.4446 | -55.4218 | -146.5708 | -50.9852 | 122.769 | -52.9246 | -47.6861 | -64.0787 | 65.713 | -56.3386 | 39.086 | -24.9186 | 68.6874 | -24.1555 | 27.09 | -26.8798 | 62.1238 | -25.2392 | 12.0204 | -24.9634 | 62.67 | -27.2331 | -15.2679 | -27.0242 | 44.906 | -23.6033 | 112.4275 | -45.0711 | -46.2731 | -42.037 | -45.8328 | -55.4421 | -47.8473 | -43.9344 | -46.406 | -40.9356 | -45.2508 | -53.8446 | -46.9333 | -48.9968 | 164 | -44.124 | -44.9635 | -48.2385 | -48.0736 | -44.8949 | -45.6787 | -49.8747 | -49.7123 | 164 | -43.8259 | -38.3555 | -43.2527 | -52.9803 | -45.3855 | -41.3175 | -43.9442 | -38.3187 | -43.3824 | -52.8252 | -45.3969 | -41.484 | -43.693 | -39.4569 | -42.6707 | -51.3828 | -44.4715 | -46.3799 | -43.8113 | -39.4201 | -42.8004 | -51.2277 | -44.4829 | -46.5464
165 | -2.6296 | 0 | -2.4837 | 0 | -2.655 | 0 | -2.455 | 0 | -46.9918 | 121.3987 | -54.3206 | -58.5822 | -45.6266 | -146.5492 | -50.4856 | -77.3971 | -53.6773 | -58.4122 | -54.8413 | 73.1108 | -46.6576 | 80.5553 | -59.7905 | -168.5315 | -48.4749 | 138.5076 | -52.7987 | -64.9561 | -68.3253 | -48.0087 | -54.9095 | 43.6887 | -22.8539 | 62.5333 | -23.9486 | 13.5234 | -25.8506 | 48.8746 | -26.2234 | 11.8702 | -23.2345 | 52.9252 | -26.4342 | -38.8023 | -26.3136 | 30.3131 | -24.6196 | 95.4493 | -45.6789 | -46.1236 | -41.5358 | -46.1867 | -54.5695 | -48.19 | -43.7688 | -46.1042 | -39.9382 | -45.3313 | -52.4446 | -46.8893 | -47.3434 | 165 | -42.919 | -44.7859 | -47.9806 | -44.5665 | -44.3361 | -45.6886 | -50.21 | -47.549 | 165 | -43.4746 | -37.3086 | -43.5571 | -52.0858 | -45.7063 | -41.1138 | -43.6205 | -37.2832 | -43.7317 | -51.9145 | -45.735 | -41.3138 | -43.494 | -38.9062 | -42.7017 | -49.9609 | -44.4056 | -44.6884 | -43.6399 | -38.8808 | -42.8763 | -49.7896 | -44.4343 | -44.8884
166 | -2.6562 | 0 | -2.4891 | 0 | -2.6666 | 0 | -2.4823 | 0 | -48.7482 | 93.1718 | -56.8823 | -57.5098 | -43.3543 | -173.3403 | -50.758 | -86.3167 | -52.3328 | -92.5462 | -51.739 | 68.6553 | -48.1546 | 51.9149 | -72.7933 | 177.4441 | -44.612 | 132.5143 | -53.0147 | -79.5644 | -60.3131 | -123.1463 | -53.5064 | 41.9212 | -21.5829 | 53.4954 | -24.2988 | -0.9368 | -25.7187 | 37.0729 | -27.2694 | 13.7596 | -22.24 | 43.2645 | -26.4275 | -61.0024 | -26.534 | 19.331 | -25.7389 | 82.6368 | -47.4852 | -45.7094 | -40.4101 | -46.5789 | -54.9969 | -48.3188 | -44.5126 | -45.8775 | -38.9297 | -45.5243 | -52.2626 | -46.9009 | -45.4136 | 166 | -42.1054 | -45.5935 | -47.6576 | -42.3109 | -43.0168 | -46.7325 | -50.2192 | -43.9828 | 166 | -43.2213 | -36.2735 | -43.9227 | -52.5078 | -45.8297 | -41.846 | -43.3884 | -36.2631 | -44.0966 | -52.3303 | -45.8365 | -42.0303 | -43.0532 | -37.7539 | -42.8681 | -49.7735 | -44.4118 | -42.747 | -43.2203 | -37.7435 | -43.042 | -49.596 | -44.4186 | -42.9313
167 | -2.6763 | 0 | -2.4813 | 0 | -2.6881 | 0 | -2.4862 | 0 | -51.7021 | 70.2068 | -57.5063 | -39.495 | -42.1861 | 162.2429 | -51.4495 | -93.8076 | -52.243 | -121.5846 | -49.599 | 57.4277 | -50.9595 | 27.3552 | -65.1838 | -32.6681 | -42.4786 | 115.4795 | -53.6724 | -94.3531 | -56.5536 | -160.1847 | -52.3461 | 39.9726 | -20.992 | 44.6298 | -25.4542 | -16.2077 | -26.8627 | 28.4245 | -28.5209 | 18.8274 | -21.8449 | 33.0168 | -26.7913 | -83.1908 | -27.9375 | 9.437 | -28.171 | 73.9679 | -49.7702 | -45.4029 | -39.6411 | -46.9343 | -56.5437 | -48.567 | -45.868 | -45.8991 | -38.5279 | -45.7859 | -53.0789 | -46.9459 | -43.7906 | 167 | -41.6126 | -47.0145 | -47.0103 | -41.1136 | -41.8821 | -48.3797 | -49.8203 | -41.9011 | 167 | -43.2228 | -35.8516 | -44.258 | -54.0624 | -46.0857 | -43.1799 | -43.4178 | -35.8398 | -44.4481 | -53.8556 | -46.0808 | -43.3818 | -42.7266 | -36.9648 | -43.1096 | -50.5976 | -44.4646 | -41.1025 | -42.9216 | -36.953 | -43.2997 | -50.3908 | -44.4597 | -41.3044
168 | -2.6673 | 0 | -2.4678 | 0 | -2.7236 | 0 | -2.4897 | 0 | -55.2228 | 52.6919 | -55.0662 | -31.7308 | -41.7928 | 140.0851 | -52.0176 | -98.4715 | -52.8583 | -146.503 | -48.0269 | 45.1747 | -54.7238 | 6.0635 | -57.8959 | -51.1609 | -41.5198 | 99.5801 | -54.8152 | -108.457 | -55.007 | 173.2758 | -51.0353 | 34.5191 | -21.0055 | 35.4036 | -27.4329 | -31.4597 | -28.7952 | 27.9493 | -29.7219 | 29.9462 | -22.1414 | 21.9225 | -27.7287 | -106.6392 | -30.6619 | 6.2789 | -31.7502 | 78.8555 | -51.413 | -45.2391 | -39.3391 | -47.2763 | -58.6318 | -48.9188 | -47.1631 | -45.9618 | -38.554 | -45.9756 | -54.335 | -47.3603 | -42.6502 | 168 | -41.4088 | -48.3964 | -45.9947 | -40.5994 | -41.2225 | -50.0759 | -48.9272 | -40.888 | 168 | -43.2945 | -35.8867 | -44.609 | -56.164 | -46.451 | -44.4395 | -43.494 | -35.8304 | -44.7866 | -55.9082 | -46.4291 | -44.6734 | -42.5718 | -36.6718 | -43.3083 | -51.8672 | -44.8925 | -39.9266 | -42.7713 | -36.6155 | -43.4859 | -51.6114 | -44.8706 | -40.1605
169 | -2.6551 | 0 | -2.4636 | 0 | -2.7592 | 0 | -2.4904 | 0 | -59.2354 | 36.9541 | -52.626 | -37.4013 | -41.9443 | 120.6393 | -52.3941 | -103.3401 | -54.0019 | -166.6002 | -46.6426 | 32.0603 | -59.6577 | -15.3047 | -54.4081 | -69.5995 | -41.002 | 84.2472 | -56.9219 | -122.9 | -54.4774 | 152.4494 | -49.9429 | 25.6208 | -21.7554 | 26.0486 | -30.5156 | -48.0132 | -31.0726 | 41.2788 | -29.6706 | 45.3139 | -23.1624 | 11.0654 | -29.0674 | -129.8417 | -33.9721 | 23.244 | -33.3461 | 110.2381 | -52.0339 | -44.9467 | -39.28 | -47.6823 | -61.112 | -49.3881 | -48.0144 | -45.7006 | -38.7996 | -46.0066 | -55.7175 | -48.0991 | -42.0608 | 169 | -41.5141 | -49.6122 | -44.8295 | -40.4792 | -40.7519 | -51.7522 | -48.0168 | -40.3107 | 169 | -43.0455 | -36.1445 | -45.0272 | -58.6484 | -46.9245 | -45.2552 | -43.237 | -36.0404 | -45.1919 | -58.3528 | -46.8977 | -45.524 | -42.2916 | -36.6249 | -43.3515 | -53.2539 | -45.6355 | -39.3016 | -42.4831 | -36.5208 | -43.5162 | -52.9583 | -45.6087 | -39.5704
170 | -2.6441 | 0 | -2.4775 | 0 | -2.8115 | 0 | -2.5118 | 0 | -64.227 | 14.072 | -51.0238 | -50.9016 | -42.1573 | 100.7894 | -52.8248 | -111.135 | -55.2086 | 173.6179 | -46.4092 | 21.3945 | -67.2378 | -52.3999 | -52.3514 | -88.3211 | -41.1319 | 69.5053 | -61.044 | -135.4376 | -54.2675 | 135.7078 | -49.544 | 16.5132 | -23.1966 | 19.944 | -36.0625 | -65.797 | -29.8624 | 64.1084 | -27.7249 | 57.6493 | -25.3417 | 2.8261 | -30.7562 | -152.8994 | -33.9186 | 56.3824 | -30.1433 | 136.1217 | -51.8954 | -44.538 | -39.316 | -48.0594 | -63.9344 | -49.9364 | -48.5009 | -45.1904 | -39.0934 | -45.8642 | -57.0829 | -49.1631 | -41.9723 | 170 | -41.6034 | -50.65 | -44.4396 | -40.6185 | -40.8058 | -53.262 | -47.5172 | -40.3665 | 170 | -42.5463 | -36.4493 | -45.4153 | -61.4569 | -47.4589 | -45.6894 | -42.7129 | -36.2819 | -45.5476 | -61.1229 | -47.4246 | -45.9891 | -41.8939 | -36.6719 | -43.2201 | -54.6054 | -46.6856 | -39.1608 | -42.0605 | -36.5045 | -43.3524 | -54.2714 | -46.6513 | -39.4605
171 | -2.6493 | 0 | -2.4766 | 0 | -2.869 | 0 | -2.5234 | 0 | -69.8484 | -46.0091 | -50.4846 | -68.0404 | -42.7047 | 83.8291 | -53.8219 | -120.5378 | -56.6008 | 157.5501 | -46.5252 | 8.5274 | -68.3536 | -155.1293 | -51.3116 | -107.0699 | -41.6184 | 56.597 | -71.0767 | -121.7199 | -54.4348 | 121.1024 | -48.6774 | 9.0435 | -25.5726 | 22.2277 | -55.2256 | -133.4203 | -26.8652 | 71.9757 | -25.4812 | 61.1097 | -29.1793 | 7.1173 | -33.2532 | -177.8205 | -29.6559 | 71.4813 | -26.0762 | 134.5757 | -51.457 | -43.9979 | -39.4266 | -48.25 | -67.5547 | -50.2987 | -48.6641 | -44.3885 | -39.4188 | -45.5352 | -58.4571 | -50.4549 | -42.2641 | 171 | -42.0278 | -51.9121 | -44.5162 | -41.074 | -41.1674 | -54.1726 | -46.7713 | -40.6524 | 171 | -41.7392 | -36.7695 | -45.6007 | -65.0781 | -47.8221 | -45.7951 | -41.9119 | -36.5498 | -45.7266 | -64.6857 | -47.7753 | -46.1407 | -41.3486 | -36.7773 | -42.8859 | -55.9805 | -47.9783 | -39.3951 | -41.5213 | -36.5576 | -43.0118 | -55.5881 | -47.9315 | -39.7407
172 | -2.654 | 0 | -2.4884 | 0 | -2.8976 | 0 | -2.5495 | 0 | -65.3998 | -117.2359 | -51.1098 | -84.0926 | -43.6241 | 64.9356 | -56.0955 | -129.3118 | -58.4247 | 140.705 | -46.6258 | 3.4604 | -61.6296 | 163.4416 | -51.1579 | -125.0055 | -42.2474 | 45.1717 | -64.9351 | -24.3686 | -54.56 | 110.5281 | -48.0077 | -0.7985 | -28.0475 | 40.7034 | -39.1926 | 104.5868 | -24.4827 | 68.4799 | -23.6217 | 57.2259 | -32.1048 | 46.7902 | -37.0632 | 155.3062 | -26.7612 | 69.1765 | -23.3924 | 125.1584 | -50.8711 | -43.4835 | -39.525 | -47.9063 | -72.7071 | -50.0226 | -48.5938 | -43.6789 | -39.7165 | -45.043 | -59.918 | -51.2961 | -42.9176 | 172 | -42.8867 | -53.7852 | -44.9553 | -41.7656 | -41.6782 | -53.4606 | -46.234 | -41.028 | 172 | -41.0249 | -37.0625 | -45.2523 | -70.2187 | -47.5342 | -45.6962 | -41.1905 | -36.8189 | -45.3568 | -69.8095 | -47.4731 | -46.0443 | -40.8295 | -36.871 | -42.389 | -57.4296 | -48.8077 | -40.02 | -40.9951 | -36.6274 | -42.4935 | -57.0204 | -48.7466 | -40.3681
173 | -2.6584 | 0 | -2.5016 | 0 | -2.8923 | 0 | -2.5724 | 0 | -60.3454 | -147.0638 | -52.7835 | -94.6776 | -44.7293 | 49.5751 | -60.142 | -125.8497 | -60.0928 | 125.1871 | -46.8556 | -2.1976 | -57.8945 | 142.2389 | -51.7216 | -139.6927 | -43.1832 | 33.8141 | -58.2628 | -31.8817 | -54.7743 | 99.6981 | -47.1587 | -10.0368 | -26.3595 | 70.1773 | -33.1842 | 85.0303 | -22.7612 | 61.1928 | -22.2385 | 50.7448 | -26.7437 | 77.3932 | -42.0257 | 112.93 | -24.1899 | 61.8461 | -21.5658 | 113.0426 | -50.2476 | -43.1267 | -39.6115 | -47.0367 | -82.1382 | -49.0056 | -48.4195 | -43.2361 | -39.9553 | -44.5953 | -61.318 | -50.7986 | -43.8654 | 173 | -43.9959 | -55.4208 | -45.7084 | -42.5757 | -42.4872 | -51.9067 | -45.6137 | -41.511 | 173 | -40.5777 | -37.2969 | -44.3783 | -79.6366 | -46.504 | -45.5272 | -40.7345 | -37.063 | -44.4643 | -79.2459 | -46.4332 | -45.8471 | -40.4683 | -36.9531 | -41.9369 | -58.8164 | -48.297 | -40.9731 | -40.6251 | -36.7192 | -42.0229 | -58.4257 | -48.2262 | -41.293
174 | -2.6948 | 0 | -2.5017 | 0 | -2.8779 | 0 | -2.5863 | 0 | -57.1541 | -168.1024 | -54.7375 | -94.5827 | -46.3339 | 33.3078 | -61.6391 | -90.955 | -61.7707 | 107.8815 | -46.7088 | -8.2373 | -55.5068 | 125.2346 | -52.6975 | -148.1079 | -44.3259 | 24.4448 | -54.8342 | -45.2284 | -54.9619 | 88.7485 | -46.556 | -21.3559 | -22.5753 | 78.7246 | -30.6258 | 71.4899 | -21.5703 | 52.098 | -21.3394 | 41.6311 | -22.649 | 75.8701 | -51.7223 | -17.5166 | -22.846 | 50.5753 | -20.9619 | 101.0408 | -49.7322 | -43.0068 | -39.7182 | -46.0876 | -79.4353 | -47.9209 | -48.2048 | -43.1045 | -40.1323 | -44.1853 | -62.8689 | -49.2295 | -45.2727 | 174 | -45.4447 | -54.8459 | -45.9549 | -43.4427 | -43.4563 | -50.3201 | -45.1203 | -42.0605 | 174 | -40.4097 | -37.4375 | -43.3928 | -76.9336 | -45.4192 | -45.3269 | -40.6028 | -37.2544 | -43.5013 | -76.5574 | -45.3346 | -45.6185 | -40.312 | -37.0234 | -41.4905 | -60.3672 | -46.7278 | -42.3948 | -40.5051 | -36.8403 | -41.599 | -59.991 | -46.6432 | -42.6864
175 | -2.7404 | 0 | -2.5015 | 0 | -2.8468 | 0 | -2.5992 | 0 | -55.161 | 173.9109 | -55.0682 | -84.1101 | -48.2946 | 22.6837 | -58.0105 | -75.407 | -63.2354 | 90.9905 | -46.9727 | -16.3017 | -53.9517 | 108.6263 | -53.1934 | -150.9312 | -45.4293 | 18.6742 | -53.0329 | -59.4186 | -55.1135 | 77.4633 | -46.9217 | -31.4555 | -19.4762 | 74.6601 | -29.9135 | 59.9048 | -20.9685 | 41.7333 | -20.8725 | 31.8159 | -19.5914 | 65.8284 | -38.8504 | -79.9274 | -21.9269 | 36.5927 | -20.5144 | 87.0742 | -49.2358 | -43.0694 | -39.8341 | -45.2397 | -72.2593 | -46.9249 | -47.9351 | -43.2726 | -40.2872 | -43.8452 | -64.314 | -47.6358 | -47.3352 | 175 | -46.7841 | -52.9217 | -46.0603 | -44.5145 | -44.2637 | -49.1792 | -45.2168 | -42.8364 | 175 | -40.5322 | -37.5468 | -42.4993 | -69.7578 | -44.4234 | -45.0883 | -40.7711 | -37.4404 | -42.6405 | -69.4125 | -44.3257 | -45.3359 | -40.329 | -37.0937 | -41.1048 | -61.8125 | -45.1343 | -44.4884 | -40.5679 | -36.9873 | -41.246 | -61.4672 | -45.0366 | -44.736
176 | -2.8002 | 0 | -2.4996 | 0 | -2.8212 | 0 | -2.5954 | 0 | -53.9681 | 156.4319 | -53.4881 | -80.2893 | -50.7399 | 5.6401 | -55.5207 | -81.2168 | -64.4357 | 67.9111 | -47.2108 | -22.0897 | -52.9993 | 92.4028 | -52.7688 | -153.1945 | -46.9476 | 13.0188 | -52.1771 | -73.1755 | -55.2371 | 65.9225 | -47.157 | -41.9385 | -17.2287 | 65.7368 | -29.1526 | 52.5278 | -20.641 | 31.5306 | -20.9222 | 22.0522 | -17.5523 | 53.092 | -34.6689 | -111.3706 | -21.619 | 22.4834 | -20.5219 | 74.2875 | -48.8472 | -43.2314 | -39.9643 | -44.6011 | -68.648 | -46.0439 | -47.6754 | -43.6494 | -40.4174 | -43.5933 | -65.3238 | -46.3525 | -50.6142 | 176 | -47.7152 | -51.4415 | -45.8019 | -45.5594 | -45.1579 | -48.5188 | -45.1446 | -43.7229 | 176 | -40.8492 | -37.6172 | -41.8009 | -66.1484 | -43.5443 | -44.8542 | -41.1498 | -37.5962 | -42.0057 | -65.8268 | -43.4485 | -45.08 | -40.4312 | -37.1641 | -40.7931 | -62.8242 | -43.8529 | -47.793 | -40.7318 | -37.1431 | -40.9979 | -62.5026 | -43.7571 | -48.0188
177 | -2.8393 | 0 | -2.524 | 0 | -2.7835 | 0 | -2.598 | 0 | -53.4001 | 140.3562 | -51.9789 | -86.4051 | -54.5335 | 0.7532 | -54.4783 | -92.1809 | -65.5567 | 38.2013 | -48.3868 | -28.9155 | -52.4915 | 75.8151 | -51.8432 | -159.4464 | -48.104 | 12.4458 | -51.9879 | -83.8021 | -55.5913 | 52.1006 | -48.485 | -46.7358 | -15.6948 | 54.7063 | -29.8653 | 48.0982 | -20.9803 | 20.4609 | -21.4868 | 11.643 | -16.1258 | 39.2494 | -31.2717 | -137.2826 | -22.1105 | 6.8396 | -21.1993 | 61.829 | -48.5318 | -43.4162 | -40.0971 | -44.1099 | -66.1685 | -45.2873 | -47.4068 | -44.1741 | -40.5736 | -43.4068 | -66.0553 | -45.2913 | -53.3498 | 177 | -48.4067 | -50.7495 | -46.1253 | -47.3761 | -45.5831 | -48.3205 | -45.6795 | -44.8935 | 177 | -41.3348 | -37.7343 | -41.2706 | -63.6445 | -42.7633 | -44.6233 | -41.6501 | -37.7901 | -41.5119 | -63.385 | -42.6893 | -44.8088 | -40.5769 | -37.2578 | -40.5675 | -63.5313 | -42.7673 | -50.5663 | -40.8922 | -37.3136 | -40.8088 | -63.2718 | -42.6933 | -50.7518
178 | -2.8878 | 0 | -2.5247 | 0 | -2.7677 | 0 | -2.6051 | 0 | -53.3274 | 124.922 | -51.1324 | -96.6954 | -59.7152 | 11.2728 | -54.773 | -102.11 | -65.3366 | 4.8765 | -50.081 | -27.6177 | -52.3322 | 59.5358 | -50.949 | -169.8261 | -48.743 | 16.2351 | -52.0763 | -90.8016 | -55.9127 | 36.8526 | -49.6328 | -44.453 | -14.7283 | 42.6236 | -30.7502 | 49.5593 | -22.0454 | 9.1439 | -22.5993 | 0.1347 | -15.3143 | 24.4801 | -28.7351 | -161.2783 | -23.5357 | -9.4539 | -22.5874 | 51.3102 | -48.2239 | -43.5411 | -40.255 | -43.7474 | -64.1106 | -44.6583 | -47.1029 | -44.8419 | -40.7628 | -43.3021 | -66.3958 | -44.4161 | -49.0293 | 178 | -48.7223 | -50.8236 | -46.8085 | -49.5173 | -45.6481 | -48.3542 | -46 | -45.7183 | 178 | -41.9541 | -37.875 | -40.8596 | -61.5859 | -42.1336 | -44.3352 | -42.3172 | -37.9951 | -41.1423 | -61.3429 | -42.0532 | -44.4978 | -40.6533 | -37.3672 | -40.4143 | -63.8711 | -41.8914 | -46.2616 | -41.0164 | -37.4873 | -40.697 | -63.6281 | -41.811 | -46.4242
179 | -2.9138 | 0 | -2.5343 | 0 | -2.7701 | 0 | -2.6053 | 0 | -53.7167 | 110.3763 | -51.0282 | -107.2198 | -61.904 | 55.1908 | -56.0519 | -106.5963 | -63.5474 | -27.4325 | -50.7671 | -17.0902 | -52.4304 | 42.578 | -50.3888 | 177.6806 | -48.7643 | 18.9309 | -52 | -92.9574 | -56.6204 | 19.2742 | -49.6307 | -34.4858 | -14.162 | 30.3747 | -30.7841 | 58.9768 | -24.0019 | 1.9044 | -24.6013 | -6.8048 | -14.8848 | 9.255 | -27.1468 | 174.7961 | -26.0685 | -25.3929 | -24.8597 | 43.0871 | -47.9171 | -43.649 | -40.4919 | -43.4952 | -62.2061 | -44.1451 | -46.7101 | -45.7233 | -41.0349 | -43.2999 | -66.4757 | -43.692 | -44.7739 | 179 | -48.9325 | -51.4428 | -47.2689 | -50.2375 | -45.5053 | -48.4767 | -45.7937 | -45.7911 | 179 | -42.8095 | -38.1211 | -40.5814 | -59.6718 | -41.6108 | -43.94 | -43.189 | -38.2648 | -40.8899 | -59.436 | -41.5398 | -44.1048 | -40.7352 | -37.5781 | -40.3861 | -63.9414 | -41.1577 | -42.0038 | -41.1147 | -37.7218 | -40.6946 | -63.7056 | -41.0867 | -42.1686
180 | -2.9127 | 0 | -2.558 | 0 | -2.7871 | 0 | -2.6032 | 0 | -54.3982 | 96.4583 | -51.2895 | -113.7506 | -59.4387 | 76.7952 | -57.1762 | -97.2198 | -60.6933 | -54.2726 | -48.9415 | -1.6867 | -52.5816 | 24.7187 | -50.1854 | 163.8957 | -48.7105 | 22.9839 | -51.2232 | -94.6814 | -57.4088 | -3.0899 | -47.3853 | -31.135 | -14.0109 | 17.9962 | -29.6669 | 68.0668 | -26.9323 | 3.0137 | -27.6354 | -11.4005 | -14.9556 | -6.0519 | -25.7868 | 151.89 | -32.2696 | -31.9401 | -28.6585 | 43.3708 | -47.5424 | -43.7402 | -40.7603 | -43.3431 | -60.0775 | -43.7636 | -46.1713 | -46.8574 | -41.4479 | -43.4057 | -64.7963 | -43.0957 | -42.3222 | 180 | -49.1359 | -51.9377 | -46.5547 | -48.312 | -45.4427 | -48.2739 | -44.5117 | -44.7454 | 180 | -43.9447 | -38.5352 | -40.4304 | -57.5195 | -41.2056 | -43.3842 | -44.2994 | -38.6608 | -40.7399 | -57.2904 | -41.1604 | -43.5681 | -40.8275 | -37.8476 | -40.493 | -62.2383 | -40.5377 | -39.5351 | -41.1822 | -37.9732 | -40.8025 | -62.0092 | -40.4925 | -39.719
181 | -2.8973 | 0 | -2.5687 | 0 | -2.8471 | 0 | -2.5824 | 0 | -55.0889 | 79.4609 | -51.2749 | -116.151 | -57.531 | 83.0724 | -55.381 | -84.6115 | -57.5712 | -77.7948 | -45.677 | -1.8469 | -52.5 | 4.6877 | -50.244 | 149.7821 | -48.2471 | 24.098 | -49.9484 | -100.0018 | -58.8062 | -33.3586 | -45.1728 | -40.1727 | -14.2792 | 5.8638 | -27.499 | 69.6402 | -28.9373 | 27.1391 | -32.4342 | 8.8615 | -15.4066 | -22.0936 | -24.8626 | 129.5851 | -43.1566 | 25.6422 | -32.222 | 76.3317 | -47.0335 | -43.7884 | -41.2137 | -43.4593 | -57.5843 | -43.679 | -45.4047 | -48.1049 | -41.995 | -43.7484 | -61.1273 | -42.7338 | -41.1243 | 181 | -49.0939 | -51.1102 | -44.27 | -45.1466 | -45.2216 | -47.6804 | -43.0136 | -43.3089 | 181 | -45.2076 | -39.0977 | -40.562 | -55.0156 | -41.1103 | -42.5576 | -45.5362 | -39.1479 | -40.8769 | -54.7372 | -41.0966 | -42.8223 | -40.8911 | -38.3164 | -40.8511 | -58.5586 | -40.1651 | -38.2772 | -41.2197 | -38.3666 | -41.166 | -58.2802 | -40.1514 | -38.5419
182 | -2.888 | 0 | -2.5841 | 0 | -2.9345 | 0 | -2.6052 | 0 | -55.3026 | 50.5614 | -50.0904 | -119.4313 | -55.3821 | 94.7234 | -52.4688 | -89.927 | -54.156 | -102.8174 | -43.1435 | -12.2144 | -51.4366 | -23.8498 | -50.5888 | 134.7543 | -48.5048 | 28.5687 | -49.0357 | -110.662 | -59.3298 | -85.3044 | -43.6728 | -55.8442 | -15.0027 | -5.9794 | -25.5361 | 65.18 | -26.5556 | 48.936 | -31.8477 | 52.6373 | -16.4167 | -38.2988 | -24.3509 | 106.821 | -32.2717 | 75.0723 | -28.7854 | 109.1339 | -46.5566 | -43.7586 | -41.9465 | -43.9941 | -54.8574 | -43.993 | -44.3614 | -48.4306 | -42.6107 | -44.42 | -56.4747 | -42.7626 | -41.2586 | 182 | -48.0578 | -49.0469 | -41.9417 | -42.5785 | -45.2251 | -46.8117 | -41.9284 | -42.3506 | 182 | -45.5426 | -39.7227 | -41.1061 | -52.2733 | -41.4089 | -41.4269 | -45.8465 | -39.6762 | -41.3889 | -51.9229 | -41.3878 | -41.7562 | -40.8706 | -39.0585 | -41.532 | -53.8906 | -40.1785 | -38.3241 | -41.1745 | -39.012 | -41.8148 | -53.5402 | -40.1574 | -38.6534
183 | -2.8757 | 0 | -2.6161 | 0 | -3.029 | 0 | -2.6051 | 0 | -54.7429 | -17.6957 | -48.722 | -132.814 | -49.205 | 103.1369 | -50.9306 | -109.6037 | -50.6303 | -140.2598 | -41.6951 | -26.5471 | -49.4945 | -73.0058 | -51.8906 | 120.2225 | -46.0107 | 42.6668 | -49.0128 | -121.0714 | -56.3602 | -168.8008 | -43.2919 | -75.1847 | -16.3293 | -16.6669 | -24.1612 | 56.159 | -23.3374 | 50.4643 | -26.6095 | 66.9764 | -18.2453 | -55.1853 | -24.1474 | 85.3426 | -27.1702 | 66.9466 | -24.6785 | 111.4881 | -47.3308 | -43.5094 | -41.7584 | -45.3426 | -52.8777 | -44.9586 | -43.5692 | -46.5017 | -41.7742 | -45.2997 | -52.8231 | -43.2556 | -41.486 | 183 | -45.4083 | -46.9733 | -40.4975 | -40.5383 | -43.6894 | -45.8338 | -41.8122 | -41.2942 | 183 | -43.626 | -38.8985 | -42.4669 | -50.2616 | -42.3425 | -40.5402 | -43.8856 | -38.7452 | -42.7375 | -49.8487 | -42.3535 | -40.9641 | -40.6337 | -38.8827 | -42.424 | -50.207 | -40.6395 | -38.457 | -40.8933 | -38.7294 | -42.6946 | -49.7941 | -40.6505 | -38.8809
184 | -2.813 | 0 | -2.628 | 0 | -3.086 | 0 | -2.6306 | 0 | -53.3749 | -109.7671 | -48.4896 | -148.1846 | -44.2154 | 72.2994 | -51.9184 | -131.1351 | -50.7332 | 171.8946 | -41.1662 | -42.536 | -50.0106 | -137.5001 | -52.128 | 118.5613 | -42.1796 | 24.6087 | -48.6822 | -129.634 | -54.7422 | 113.0349 | -44.5976 | -92.4924 | -18.4519 | -23.7581 | -23.5347 | 45.8611 | -21.3964 | 42.3594 | -23.3622 | 61.6424 | -21.4437 | -70.852 | -24.6247 | 64.7425 | -24.5514 | 56.2773 | -21.8016 | 105.4003 | -53.2333 | -42.6054 | -39.9418 | -48.2489 | -55.5966 | -46.8124 | -45.8623 | -44.8204 | -40.063 | -46.874 | -54.3428 | -43.9024 | -40.5898 | 184 | -42.4687 | -47.1056 | -40.1305 | -39.1087 | -41.1554 | -45.7063 | -42.6469 | -40.0618 | 184 | -42.0074 | -37.25 | -45.4359 | -52.9686 | -44.1844 | -42.7763 | -42.1924 | -36.977 | -45.6183 | -52.5106 | -44.1818 | -43.2317 | -39.7924 | -37.1288 | -44.061 | -51.7148 | -41.2744 | -37.5038 | -39.9774 | -36.8558 | -44.2434 | -51.2568 | -41.2718 | -37.9592
185 | -2.761 | 0 | -2.6198 | 0 | -3.1106 | 0 | -2.638 | 0 | -52.3484 | -160.9495 | -48.4356 | -164.83 | -43.364 | 45.1515 | -54.7634 | -147.7974 | -53.1842 | 142.2211 | -41.4863 | -55.949 | -51.5559 | 177.7515 | -51.0601 | 102.5398 | -41.4656 | 2.9681 | -49.2008 | -140.0354 | -56.1107 | 68.5131 | -46.8337 | -97.2647 | -21.103 | -21.8782 | -23.1455 | 35.3357 | -20.105 | 32.691 | -21.113 | 52.6824 | -26.6104 | -84.0471 | -25.2795 | 42.9093 | -23.1208 | 44.0443 | -19.9407 | 95.4409 | -55.1626 | -42.0871 | -39.8312 | -51.6978 | -60.7251 | -48.9308 | -48.5143 | -43.8567 | -40.3079 | -48.9831 | -59.2722 | -45.4895 | -40.1184 | 185 | -41.7882 | -48.5492 | -40.5211 | -39.1396 | -40.6459 | -46.6841 | -43.9162 | -40.2439 | 185 | -41.0957 | -37.5469 | -48.9368 | -58.1053 | -46.311 | -45.4037 | -41.2369 | -37.1973 | -49.0598 | -57.6145 | -46.2928 | -45.8763 | -39.3261 | -37.0702 | -46.2221 | -56.6524 | -42.8697 | -37.0078 | -39.4673 | -36.7206 | -46.3451 | -56.1616 | -42.8515 | -37.4804
186 | -2.7569 | 0 | -2.6081 | 0 | -3.1177 | 0 | -2.6597 | 0 | -51.4903 | 172.5032 | -49.191 | 175.8103 | -43.2546 | 25.6867 | -60.9183 | -150.1219 | -55.2818 | 124.6504 | -41.9045 | -64.4988 | -51.9482 | 147.5944 | -51.0422 | 78.7763 | -41.6141 | -13.5751 | -50.0974 | -143.4719 | -57.9311 | 44.5038 | -48.1401 | -88.7956 | -23.3255 | -5.6273 | -23.3236 | 24.2537 | -19.5333 | 21.2247 | -19.7297 | 39.9677 | -42.8963 | -65.5916 | -26.4236 | 19.8535 | -22.2183 | 30.6195 | -18.6439 | 83.2867 | -53.2486 | -41.8598 | -40.1435 | -54.858 | -64.3346 | -51.3481 | -49.6785 | -43.1451 | -40.8077 | -50.4636 | -63.7058 | -47.9185 | -39.9029 | 186 | -41.7778 | -49.6384 | -41.1151 | -39.4033 | -40.7982 | -47.5022 | -44.8161 | -40.6593 | 186 | -40.3882 | -38.0508 | -52.1011 | -61.7265 | -48.74 | -46.5608 | -40.537 | -37.69 | -52.1983 | -61.2169 | -48.6884 | -47.0188 | -39.1029 | -37.3866 | -47.7067 | -61.0977 | -45.3104 | -36.7852 | -39.2517 | -37.0258 | -47.8039 | -60.5881 | -45.2588 | -37.2432
187 | -2.7566 | 0 | -2.6041 | 0 | -3.0895 | 0 | -2.66 | 0 | -50.7475 | 153.8082 | -51.0518 | 155.3704 | -43.5564 | 6.7321 | -63.5143 | -73.652 | -56.9725 | 110.896 | -42.0856 | -69.5618 | -51.7258 | 123.4175 | -51.7658 | 51.5886 | -41.9353 | -27.0284 | -50.0586 | -142.1051 | -59.6304 | 31.4592 | -46.9215 | -80.1263 | -22.3716 | 18.0106 | -24.0151 | 13.6757 | -19.252 | 11.012 | -18.8339 | 28.0663 | -28.4203 | 51.7006 | -28.3569 | -5.7244 | -21.7065 | 17.2554 | -17.9525 | 70.9283 | -52.0336 | -41.8315 | -40.4283 | -55.0883 | -66.1547 | -53.7534 | -50.1783 | -42.6832 | -41.1707 | -50.733 | -65.5494 | -51.3238 | -39.7692 | 187 | -42.1925 | -49.6369 | -41.5392 | -39.6672 | -41.1113 | -47.5263 | -44.3366 | -40.683 | 187 | -39.9266 | -38.4141 | -52.3317 | -63.5506 | -51.1493 | -47.0888 | -40.0791 | -38.0812 | -52.4283 | -63.0652 | -51.0934 | -47.5183 | -39.0749 | -37.6717 | -47.9764 | -62.9453 | -48.7197 | -36.6797 | -39.2274 | -37.3388 | -48.073 | -62.4599 | -48.6638 | -37.1092
188 | -2.7954 | 0 | -2.6058 | 0 | -3.0494 | 0 | -2.6727 | 0 | -50.1533 | 137.3828 | -54.3672 | 136.7032 | -44.0806 | -9.4249 | -55.3637 | -62.7761 | -58.1646 | 99.3806 | -41.7587 | -74.548 | -51.4031 | 101.7981 | -53.1568 | 21.3157 | -42.3954 | -38.5851 | -49.1787 | -143.0194 | -60.8743 | 26.1514 | -45.1203 | -83.0249 | -19.5591 | 25.4223 | -25.43 | 2.8508 | -19.4166 | -0.9819 | -18.4633 | 13.7984 | -22.1864 | 36.7215 | -30.977 | -38.3655 | -21.7394 | 0.6742 | -17.7541 | 57.5521 | -51.3048 | -41.8969 | -40.6664 | -52.9415 | -66.6642 | -55.1117 | -50.4144 | -42.4908 | -41.4478 | -49.9925 | -64.3597 | -56.354 | -39.7174 | 188 | -42.8075 | -48.5117 | -41.3509 | -39.6938 | -41.569 | -46.9597 | -43.2171 | -40.4973 | 188 | -39.6954 | -38.6524 | -50.1461 | -64.0584 | -52.5059 | -47.365 | -39.885 | -38.3984 | -50.2688 | -63.6148 | -52.439 | -47.7417 | -39.1015 | -37.871 | -47.1971 | -61.7539 | -53.7482 | -36.668 | -39.2911 | -37.617 | -47.3198 | -61.3103 | -53.6813 | -37.0447
189 | -2.8631 | 0 | -2.5926 | 0 | -3.0147 | 0 | -2.6678 | 0 | -49.8486 | 121.0809 | -60.3375 | 122.1598 | -44.6548 | -24.9915 | -51.4279 | -75.9529 | -58.8156 | 87.1328 | -41.3594 | -81.4276 | -51.191 | 81.4122 | -54.7654 | -12.8581 | -43.066 | -49.3717 | -47.8495 | -149.3126 | -60.9795 | 23.9015 | -43.6157 | -91.8008 | -17.082 | 22.8258 | -27.7867 | -1.5945 | -20.0355 | -11.8798 | -18.6297 | 0.0499 | -18.8489 | 21.1888 | -34.4376 | -87.9148 | -22.3932 | -16.6126 | -17.9986 | 44.7975 | -50.858 | -42.0263 | -40.863 | -50.9987 | -66.1901 | -54.5966 | -50.5691 | -42.3702 | -41.6678 | -48.7098 | -62.5262 | -64.9131 | -39.7296 | 189 | -43.4181 | -47.2431 | -40.9019 | -39.6386 | -42.1967 | -46.0542 | -41.9901 | -40.2847 | 189 | -39.5071 | -38.8047 | -48.1356 | -63.5975 | -52.004 | -47.5544 | -39.7776 | -38.6531 | -48.3309 | -63.1754 | -51.9288 | -47.9013 | -39.1632 | -37.9999 | -45.8467 | -59.9336 | -62.3205 | -36.7149 | -39.4337 | -37.8483 | -46.042 | -59.5115 | -62.2453 | -37.0618
190 | -2.9227 | 0 | -2.5946 | 0 | -2.9854 | 0 | -2.6781 | 0 | -49.9706 | 105.0181 | -76.659 | -173.1247 | -45.663 | -37.0014 | -49.2492 | -92.5563 | -58.9949 | 71.3926 | -41.0168 | -91.1771 | -51.2295 | 60.4145 | -55.8926 | -53.1892 | -44.0199 | -58.4614 | -46.8334 | -161.3389 | -60.0494 | 16.0483 | -42.6999 | -105.7366 | -15.3147 | 14.5876 | -31.2357 | 1.4323 | -21.1321 | -22.9956 | -19.111 | -14.7884 | -16.8097 | 4.3544 | -33.7866 | -150.1096 | -23.69 | -35.5921 | -18.7383 | 32.0301 | -50.5632 | -42.079 | -41.028 | -49.2702 | -65.571 | -52.7782 | -50.6766 | -42.2706 | -41.8328 | -47.4071 | -61.2 | -65.2706 | -39.9347 | 190 | -44.2905 | -46.3422 | -40.4079 | -39.6846 | -43.0331 | -45.3378 | -41.1344 | -40.2539 | 190 | -39.3479 | -38.9101 | -46.3475 | -62.9764 | -50.1836 | -47.6912 | -39.676 | -38.8474 | -46.5921 | -62.5856 | -50.1001 | -47.9985 | -39.1563 | -38.1053 | -44.4844 | -58.6054 | -62.676 | -36.9493 | -39.4844 | -38.0426 | -44.729 | -58.2146 | -62.5925 | -37.2566
191 | -2.9699 | 0 | -2.6179 | 0 | -2.9673 | 0 | -2.6849 | 0 | -50.5727 | 87.8759 | -60.7166 | -115.5073 | -46.8446 | -49.5788 | -48.2425 | -109.7391 | -59.0128 | 50.0681 | -40.9772 | -101.9016 | -51.5619 | 38.1067 | -55.9521 | -96.7497 | -45.1966 | -65.4849 | -46.5497 | -176.0305 | -59.1544 | 0.8377 | -42.4766 | -120.8956 | -14.1021 | 4.1199 | -33.8934 | 30.5307 | -22.8446 | -32.3136 | -20.1008 | -29.934 | -15.4822 | -12.5796 | -30.1869 | 162.1026 | -25.7774 | -57.521 | -20.0396 | 20.5308 | -50.3404 | -42.1078 | -41.1573 | -47.7545 | -64.4303 | -50.7523 | -50.6062 | -42.1587 | -42.009 | -46.1843 | -60.5163 | -56.2446 | -40.7524 | 191 | -45.1867 | -46.0192 | -40.1915 | -39.9231 | -44.0075 | -45.1817 | -40.9039 | -40.5564 | 191 | -39.1888 | -39.0391 | -44.7846 | -61.8124 | -48.1344 | -47.6389 | -39.5408 | -39.0417 | -45.0696 | -61.463 | -48.0674 | -47.9213 | -39.1379 | -38.1874 | -43.2144 | -57.8984 | -53.6267 | -37.7851 | -39.4899 | -38.19 | -43.4994 | -57.549 | -53.5597 | -38.0675
192 | -3.008 | 0 | -2.632 | 0 | -2.923 | 0 | -2.7029 | 0 | -51.9214 | 68.4514 | -55.5601 | -131.6961 | -48.2694 | -61.1238 | -48.2832 | -127.0508 | -59.1256 | 20.4731 | -41.3266 | -113.0204 | -52.25 | 12.9626 | -55.0365 | -138.8268 | -46.5255 | -68.1417 | -47.069 | 167.7055 | -58.7762 | -21.7055 | -42.9921 | -136.1286 | -13.3528 | -7.0352 | -30.8175 | 60.3535 | -25.3794 | -37.7727 | -22.0046 | -45.8061 | -14.7371 | -29.5979 | -27.2813 | 131.4551 | -29.4788 | -88.5118 | -22.1927 | 11.8563 | -50.003 | -42.0401 | -41.2539 | -46.3115 | -62.7139 | -48.9307 | -50.2414 | -42.0207 | -42.2345 | -45.0343 | -60.6593 | -51.673 | -42.8605 | 192 | -46.1798 | -46.4789 | -40.395 | -40.4674 | -45.0378 | -45.6992 | -41.3677 | -41.3199 | 192 | -39.0127 | -39.2265 | -43.3035 | -60.0819 | -46.2987 | -47.3184 | -39.3887 | -39.3115 | -43.6086 | -59.7909 | -46.2278 | -47.5385 | -39.0321 | -38.2459 | -42.0263 | -58.0273 | -49.041 | -39.9375 | -39.4081 | -38.3309 | -42.3314 | -57.7363 | -48.9701 | -40.1576
193 | -3.0363 | 0 | -2.6636 | 0 | -2.8769 | 0 | -2.6903 | 0 | -54.6213 | 45.6731 | -53.322 | -151.2895 | -49.8077 | -67.3074 | -49.5158 | -141.0899 | -59.2975 | -18.8402 | -42.3119 | -123.5186 | -53.2328 | -15.8708 | -53.8122 | -177.6683 | -47.3893 | -67.7381 | -48.6928 | 153.3447 | -59.1233 | -52.0049 | -44.3266 | -147.1674 | -12.9568 | -18.7982 | -26.908 | 64.1784 | -28.8691 | -31.8995 | -24.806 | -63.7564 | -14.3537 | -46.7571 | -25.0422 | 107.1982 | -33.4214 | -144.8238 | -25.1502 | 7.3797 | -49.4564 | -41.8885 | -41.2705 | -44.9681 | -60.6283 | -47.3924 | -49.5347 | -41.9394 | -42.4972 | -44.0308 | -61.9956 | -48.5137 | -46.7753 | 193 | -47.315 | -48.0119 | -41.2752 | -41.5273 | -45.6624 | -47.1028 | -42.6284 | -42.4878 | 193 | -38.9031 | -39.4609 | -41.9318 | -57.9647 | -44.7288 | -46.6578 | -39.2758 | -39.6203 | -42.2778 | -57.7514 | -44.7021 | -46.8444 | -38.8522 | -38.2342 | -40.9945 | -59.332 | -45.8501 | -43.8984 | -39.2249 | -38.3936 | -41.3405 | -59.1187 | -45.8234 | -44.085
194 | -3.0238 | 0 | -2.6822 | 0 | -2.8586 | 0 | -2.7111 | 0 | -60.223 | 9.6267 | -52.83 | -171.2211 | -51.0324 | -71.4928 | -51.6868 | -144.5013 | -58.7823 | -67.3221 | -44.0016 | -129.4887 | -54.2499 | -52.6514 | -52.8136 | 144.9053 | -47.2654 | -68.8595 | -51.7384 | 148.3047 | -60.9816 | -89.8646 | -46.0738 | -147.9496 | -12.9242 | -30.569 | -24.2561 | 56.8432 | -30.735 | -6.8052 | -29.8315 | -86.7669 | -14.2773 | -64.1344 | -23.6151 | 84.1178 | -31.876 | 146.5618 | -28.7013 | 20.0535 | -48.5776 | -41.7764 | -41.1526 | -43.9334 | -58.529 | -46.2915 | -48.476 | -42.0968 | -42.6762 | -43.3481 | -65.8812 | -46.1732 | -52.6005 | 194 | -48.5244 | -50.4311 | -42.8576 | -43.0977 | -45.5658 | -49.4856 | -44.3618 | -43.5396 | 194 | -39.073 | -39.6524 | -40.9096 | -55.8468 | -43.6093 | -45.6174 | -39.4146 | -39.8176 | -41.2223 | -55.6704 | -43.5804 | -45.7649 | -38.7526 | -38.1288 | -40.3243 | -63.199 | -43.491 | -49.7419 | -39.0942 | -38.294 | -40.637 | -63.0226 | -43.4621 | -49.8894
195 | -2.9958 | 0 | -2.701 | 0 | -2.8596 | 0 | -2.7307 | 0 | -64.5138 | -99.3359 | -53.93 | 173.7807 | -52.2767 | -76.1565 | -52.2151 | -132.2762 | -57.7491 | -116.5624 | -45.3022 | -124.4252 | -54.5338 | -96.6733 | -52.4172 | 106.8057 | -46.8208 | -70.8009 | -53.5611 | 166.9979 | -64.8803 | -144.0872 | -45.9832 | -143.0861 | -13.1846 | -42.1088 | -22.4669 | 46.1764 | -28.3508 | 14.1123 | -39.3145 | -160.097 | -14.5561 | -81.6961 | -22.696 | 62.6363 | -28.3454 | 105.0178 | -28.9992 | 51.824 | -47.5731 | -41.877 | -40.937 | -43.4392 | -56.9321 | -45.8204 | -47.3602 | -42.693 | -42.7067 | -43.1971 | -76.5765 | -44.6531 | -56.127 | 195 | -49.8634 | -50.9488 | -44.0288 | -44.3067 | -45.2222 | -50.8354 | -44.5158 | -43.341 | 195 | -39.6972 | -39.7109 | -40.4434 | -54.2311 | -43.1194 | -44.5006 | -39.992 | -39.8471 | -40.7085 | -54.0725 | -43.0897 | -44.6295 | -38.8812 | -37.9412 | -40.2013 | -73.8755 | -41.9521 | -53.2674 | -39.176 | -38.0774 | -40.4664 | -73.7169 | -41.9224 | -53.3963
196 | -2.9577 | 0 | -2.712 | 0 | -2.8913 | 0 | -2.7416 | 0 | -56.3926 | -162.5529 | -55.7586 | 172.3477 | -54.4042 | -78.8703 | -50.0573 | -130.6119 | -56.9755 | -159.7792 | -44.5974 | -118.5909 | -53.6285 | -140.8521 | -52.5894 | 68.9355 | -46.8301 | -78.201 | -50.8592 | 176.4405 | -67.9562 | 137.3024 | -44.2204 | -147.5324 | -13.7137 | -53.0829 | -21.2418 | 33.7333 | -25.3042 | 15.004 | -31.2916 | 103.305 | -15.1978 | -99.4807 | -22.1341 | 41.6519 | -25.999 | 76.8816 | -25.4951 | 66.551 | -46.79 | -42.2662 | -40.8287 | -43.7471 | -56.1377 | -46.0787 | -46.5011 | -43.7312 | -42.5827 | -43.6886 | -68.1026 | -44.0241 | -52.6682 | 196 | -50.6664 | -48.4862 | -43.2588 | -43.9439 | -45.1436 | -48.9614 | -42.8773 | -42.31 | 196 | -40.7735 | -39.625 | -40.7894 | -53.4257 | -43.3667 | -43.6098 | -41.0192 | -39.6914 | -41.0055 | -53.2464 | -43.3371 | -43.7595 | -39.3085 | -37.871 | -40.7309 | -65.3906 | -41.3121 | -49.7769 | -39.5542 | -37.9374 | -40.947 | -65.2113 | -41.2825 | -49.9266
197 | -2.9084 | 0 | -2.7004 | 0 | -2.9436 | 0 | -2.7328 | 0 | -52.312 | 170.4104 | -55.2978 | -179.6289 | -58.0879 | -75.3356 | -48.6351 | -143.5594 | -57.11 | 166.9508 | -43.1162 | -122.4227 | -52.1549 | -177.562 | -53.0779 | 32.835 | -46.8224 | -86.3318 | -48.8289 | 165.4873 | -66.6375 | 57.4221 | -43.3937 | -163.1742 | -14.6574 | -63.2543 | -20.6352 | 20.1451 | -23.3828 | 5.1787 | -25.6803 | 76.503 | -16.2281 | -118.11 | -22.0988 | 22.0666 | -24.8891 | 55.9716 | -22.6278 | 64.4612 | -46.2746 | -42.8849 | -40.9669 | -44.8175 | -56.1027 | -46.9396 | -46.0168 | -44.9124 | -42.4865 | -44.8684 | -62.6106 | -44.1467 | -49.7243 | 197 | -49.8389 | -46.6735 | -41.8415 | -42.8155 | -44.9762 | -47.1219 | -41.9523 | -41.7537 | 197 | -42.004 | -39.5781 | -41.9091 | -53.4023 | -44.2392 | -43.0732 | -42.212 | -39.5429 | -42.0847 | -53.1591 | -44.2068 | -43.284 | -39.9765 | -38.0585 | -41.96 | -59.9102 | -41.4463 | -46.7807 | -40.1845 | -38.0233 | -42.1356 | -59.667 | -41.4139 | -46.9915
198 | -2.8727 | 0 | -2.6918 | 0 | -2.9684 | 0 | -2.7374 | 0 | -50.1651 | 150.626 | -53.2722 | 176.5988 | -59.7088 | -48.2243 | -48.7822 | -160.0304 | -57.9499 | 143.5376 | -42.364 | -132.8373 | -50.8067 | 153.7182 | -53.3663 | 0.0003 | -47.0766 | -91.9856 | -48.4062 | 150.2066 | -65.6162 | 5.6104 | -43.8966 | -179.7755 | -15.8888 | -71.8049 | -20.5506 | 5.8905 | -22.4522 | -8.7954 | -22.5934 | 57.6799 | -17.6812 | -136.8166 | -22.2957 | 1.2889 | -24.862 | 34.1764 | -20.7761 | 54.4312 | -46.0784 | -43.3902 | -41.2711 | -46.4768 | -56.3792 | -48.1519 | -45.8792 | -45.8278 | -42.5681 | -46.4574 | -60.2621 | -44.8161 | -47.831 | 198 | -48.1237 | -46.1142 | -41.1937 | -42.1684 | -44.8792 | -46.3803 | -42.2322 | -42.1718 | 198 | -42.9551 | -39.6954 | -43.6041 | -53.6874 | -45.4601 | -42.9108 | -43.136 | -39.5997 | -43.7394 | -53.4108 | -45.4145 | -43.1418 | -40.5175 | -38.3984 | -43.5847 | -57.5703 | -42.1243 | -44.8626 | -40.6984 | -38.3027 | -43.72 | -57.2937 | -42.0787 | -45.0936
199 | -2.8518 | 0 | -2.6854 | 0 | -2.9916 | 0 | -2.7359 | 0 | -48.9333 | 134.4015 | -51.8766 | 162.267 | -57.6124 | -34.7664 | -50.2856 | -174.8143 | -58.6255 | 128.582 | -42.3866 | -142.799 | -49.8334 | 129.7007 | -53.2142 | -29.354 | -47.2834 | -97.2763 | -49.1042 | 137.4622 | -66.0359 | -36.433 | -45.2867 | 163.312 | -17.3934 | -77.3963 | -20.9485 | -8.4427 | -22.3648 | -23.4608 | -20.7276 | 41.1463 | -19.6518 | -157.5999 | -23.0891 | -18.8763 | -25.6163 | 15.1456 | -19.6171 | 42.264 | -46.0447 | -43.7064 | -41.6642 | -48.4353 | -56.5017 | -49.3626 | -45.8494 | -46.2651 | -42.7619 | -48.2947 | -58.8807 | -45.769 | -46.5142 | 199 | -46.7761 | -46.2856 | -41.3326 | -42.159 | -44.7039 | -46.3958 | -43.3102 | -43.1387 | 199 | -43.4133 | -39.9101 | -45.5835 | -53.8163 | -46.6772 | -42.8578 | -43.5797 | -39.7703 | -45.6994 | -53.5101 | -46.6267 | -43.1135 | -40.8546 | -38.8124 | -45.4429 | -56.1953 | -43.0836 | -43.5226 | -41.021 | -38.6726 | -45.5588 | -55.8891 | -43.0331 | -43.7783
200 | -2.8223 | 0 | -2.6891 | 0 | -2.9953 | 0 | -2.7496 | 0 | -48.2974 | 120.413 | -51.2841 | 144.1004 | -54.9244 | -34.9775 | -53.1981 | 178.4098 | -58.5698 | 119.9302 | -43.0077 | -151.118 | -49.2305 | 109.7571 | -52.5892 | -54.6545 | -47.6384 | -103.0695 | -50.4139 | 130.9087 | -68.213 | -88.5228 | -47.9466 | 149.9173 | -19.0104 | -78.7342 | -21.8823 | -23.3392 | -22.8289 | -39.1685 | -19.5693 | 24.4174 | -22.4853 | -178.8579 | -24.202 | -39.6493 | -27.3342 | -2.9908 | -19.0623 | 29.0531 | -46.0484 | -43.8547 | -42.1152 | -50.6148 | -56.2672 | -50.3429 | -45.8415 | -46.3508 | -43.0488 | -50.3805 | -57.5876 | -46.843 | -45.7053 | 200 | -45.9418 | -46.7823 | -42.058 | -42.6251 | -44.6001 | -46.7407 | -45.1364 | -44.7598 | 200 | -43.5285 | -40.2265 | -47.7925 | -53.5781 | -47.6538 | -42.8462 | -43.6617 | -40.0535 | -47.8652 | -53.2719 | -47.5933 | -43.0919 | -41.0324 | -39.2929 | -47.5582 | -54.8985 | -44.1539 | -42.71 | -41.1656 | -39.1199 | -47.6309 | -54.5923 | -44.0934 | -42.9557
201 | -2.8036 | 0 | -2.6783 | 0 | -3.0244 | 0 | -2.7354 | 0 | -48.21 | 108.0141 | -51.3007 | 123.3377 | -53.3119 | -40.468 | -56.9398 | -168.7722 | -57.0411 | 113.9878 | -43.8884 | -155.386 | -48.9745 | 93.2821 | -51.6823 | -76.595 | -48.3338 | -107.3217 | -51.4347 | 132.1505 | -68.3346 | -178.207 | -51.6366 | 147.3649 | -20.4473 | -75.4146 | -23.5248 | -37.8342 | -24.2513 | -55.0645 | -19.1207 | 9.7096 | -26.736 | 156.1658 | -25.8345 | -61.0483 | -30.5562 | -22.4091 | -18.9402 | 15.1782 | -46.1587 | -43.9306 | -42.6981 | -53.0727 | -55.518 | -51.0087 | -45.69 | -46.2627 | -43.3466 | -52.5689 | -55.9087 | -47.9423 | -45.7576 | 201 | -45.6579 | -47.1896 | -42.9859 | -43.2342 | -44.6689 | -46.9904 | -46.812 | -46.6387 | 201 | -43.4591 | -40.543 | -50.2691 | -52.8397 | -48.3304 | -42.6656 | -43.5844 | -40.3222 | -50.3373 | -52.4936 | -48.2733 | -42.9546 | -41.127 | -39.8945 | -49.7653 | -53.2304 | -45.264 | -42.7332 | -41.2523 | -39.6737 | -49.8335 | -52.8843 | -45.2069 | -43.0222
202 | -2.8137 | 0 | -2.661 | 0 | -3.0272 | 0 | -2.7525 | 0 | -48.2907 | 102.226 | -51.8107 | 98.3923 | -51.7719 | -38.8729 | -56.3736 | -136.1186 | -53.8564 | 98.1905 | -44.4836 | -156.2498 | -48.535 | 81.1133 | -50.6473 | -95.4059 | -49.063 | -105.7481 | -50.9935 | 137.3907 | -61.5048 | 102.22 | -54.6376 | 169.8775 | -21.0657 | -68.3323 | -26.0445 | -52.9786 | -26.5194 | -71.055 | -19.1449 | -5.5054 | -33.8788 | 109.5095 | -28.4892 | -84.7994 | -36.9548 | -45.5745 | -19.231 | 0.1121 | -46.7274 | -43.9803 | -43.3996 | -55.8641 | -54.618 | -51.0467 | -45.2977 | -46.0272 | -43.345 | -54.2001 | -54.0907 | -49.0506 | -48.5376 | 202 | -45.5186 | -46.7279 | -43.5153 | -43.3367 | -44.5549 | -46.4447 | -46.988 | -47.8113 | 202 | -43.2135 | -40.5313 | -53.0504 | -51.957 | -48.3857 | -42.2705 | -43.3662 | -40.3178 | -53.1116 | -51.5908 | -48.2942 | -42.5452 | -41.1666 | -40.5859 | -51.3864 | -51.4297 | -46.3896 | -45.5104 | -41.3193 | -40.3724 | -51.4476 | -51.0635 | -46.2981 | -45.7851
203 | -2.8353 | 0 | -2.6619 | 0 | -3.0406 | 0 | -2.7579 | 0 | -46.7427 | 95.9076 | -52.8475 | 65.3187 | -48.4522 | -44.116 | -52.7096 | -124.3455 | -52.4104 | 63.3468 | -44.2908 | -155.4787 | -47.075 | 62.7906 | -49.4089 | -112.1239 | -47.5527 | -105.2671 | -49.4039 | 136.5644 | -58.7763 | 28.0522 | -52.0316 | -167.4664 | -20.6557 | -62.2105 | -30.3594 | -68.3559 | -30.4787 | -87.6898 | -19.599 | -20.16 | -33.0212 | -1.2014 | -32.4179 | -109.2112 | -47.9068 | -159.657 | -20.0645 | -15.1409 | -48.7868 | -44.0288 | -42.8236 | -58.3689 | -56.4665 | -50.5992 | -45.9665 | -45.7711 | -42.5424 | -54.1189 | -55.0564 | -50.1226 | -49.4415 | 203 | -43.9101 | -44.9121 | -43.2074 | -42.4219 | -43.1303 | -44.8935 | -45.3472 | -45.9933 | 203 | -42.9358 | -39.7071 | -55.5336 | -53.8046 | -47.9373 | -42.9259 | -43.1092 | -39.5018 | -55.611 | -53.4259 | -47.8413 | -43.2086 | -41.1935 | -39.9883 | -51.2836 | -52.3945 | -47.4607 | -46.4009 | -41.3669 | -39.783 | -51.361 | -52.0158 | -47.3647 | -46.6836
204 | -2.8558 | 0 | -2.6869 | 0 | -3.0502 | 0 | -2.744 | 0 | -46.159 | 76.0763 | -54.3858 | 23.5994 | -47.3332 | -63.55 | -49.1436 | -130.32 | -54.3607 | 38.8647 | -43.592 | -158.2568 | -47.3347 | 35.7119 | -48.0976 | -128.6774 | -47.1685 | -122.5394 | -47.6006 | 127.7734 | -61.7382 | -22.6217 | -48.467 | -167.9671 | -19.5505 | -60.3041 | -40.1919 | -75.3418 | -39.1302 | -97.8063 | -20.4413 | -33.6253 | -27.1264 | -43.9233 | -39.4173 | -153.6329 | -35.2398 | 132.4263 | -21.4741 | -31.2681 | -49.351 | -43.765 | -42.2776 | -58.726 | -61.1947 | -50.1634 | -48.0619 | -45.1947 | -42.5628 | -53.5307 | -58.5385 | -51.1088 | -47.1111 | 204 | -43.3407 | -43.973 | -42.2509 | -41.8128 | -42.7439 | -44.3749 | -43.2693 | -44.6729 | 204 | -42.3389 | -39.707 | -55.8702 | -58.5078 | -47.4765 | -45.0117 | -42.5078 | -39.5126 | -55.982 | -58.1445 | -47.4194 | -45.3179 | -40.9092 | -39.4218 | -50.6749 | -55.8516 | -48.4219 | -44.0609 | -41.0781 | -39.2274 | -50.7867 | -55.4883 | -48.3648 | -44.3671
205 | -2.883 | 0 | -2.7077 | 0 | -3.0665 | 0 | -2.72 | 0 | -46.83 | 57.61 | -54.4776 | -25.3797 | -47.7352 | -78.5191 | -46.8907 | -145.6257 | -55.5992 | 25.9851 | -42.676 | -163.4096 | -48.6729 | 12.2646 | -46.857 | -145.5659 | -48.2598 | -135.9441 | -45.9809 | 113.3048 | -64.8899 | -47.2571 | -45.9041 | 178.2135 | -18.4645 | -63.3242 | -40.2935 | 66.7389 | -42.6349 | 31.5272 | -21.7535 | -46.0003 | -23.2617 | -69.0308 | -40.909 | 98.8647 | -30.6649 | 113.5111 | -23.4417 | -48.8776 | -49.0319 | -43.4297 | -42.4923 | -55.4186 | -62.9889 | -49.3555 | -49.5671 | -44.2696 | -43.0041 | -51.6217 | -58.7233 | -51.6407 | -45.635 | 205 | -43.8551 | -43.5689 | -41.0775 | -41.3312 | -43.0871 | -44.0751 | -41.4551 | -43.8793 | 205 | -41.3866 | -40.1211 | -52.5356 | -60.2812 | -46.6478 | -46.5006 | -41.5619 | -39.9376 | -52.6986 | -59.9224 | -46.6355 | -46.8471 | -40.5467 | -39.6093 | -48.7387 | -56.0156 | -48.933 | -42.5685 | -40.722 | -39.4258 | -48.9017 | -55.6568 | -48.9207 | -42.915
206 | -2.8847 | 0 | -2.7251 | 0 | -3.0874 | 0 | -2.7118 | 0 | -48.181 | 39.8182 | -52.6768 | -71.3115 | -48.3181 | -90.0557 | -45.7058 | -164.2725 | -55.6982 | 9.4567 | -41.6875 | -172.8909 | -50.6266 | -12.5303 | -45.6776 | -163.806 | -49.5773 | -145.138 | -44.8291 | 93.6984 | -65.6068 | -67.2769 | -44.7482 | 159.5963 | -17.5733 | -69.0422 | -31.1161 | 60.9095 | -32.6966 | 24.9361 | -23.6776 | -56.9916 | -20.9723 | -90.111 | -34.1208 | 48.6964 | -28.3751 | 97.982 | -26.6073 | -70.5818 | -48.6509 | -43.0171 | -42.8613 | -51.2837 | -63.0532 | -48.3061 | -50.522 | -43.1382 | -43.4512 | -49.1587 | -58.0728 | -51.4507 | -44.7847 | 206 | -44.5185 | -43.4897 | -39.9965 | -40.6943 | -43.3037 | -43.7858 | -40.2939 | -43.4865 | 206 | -40.2535 | -40.5665 | -48.399 | -60.3281 | -45.581 | -47.4346 | -40.4131 | -40.3638 | -48.5719 | -59.9658 | -45.5943 | -47.8102 | -40.1324 | -39.9766 | -46.274 | -55.3477 | -48.7256 | -41.6973 | -40.292 | -39.7739 | -46.4469 | -54.9854 | -48.7389 | -42.0729
207 | -2.9225 | 0 | -2.745 | 0 | -3.1079 | 0 | -2.7248 | 0 | -50.5769 | 19.5878 | -50.5648 | -109.3353 | -48.499 | -98.0713 | -45.5168 | 174.1377 | -55.7554 | -14.7733 | -41.1186 | 173.6136 | -53.3558 | -44.063 | -44.7432 | 176.2926 | -50.8935 | -146.0487 | -44.2003 | 69.7937 | -64.7394 | -105.0264 | -44.5094 | 137.3218 | -16.973 | -76.9203 | -27.1939 | 48.1639 | -28.9838 | 8.2106 | -26.8649 | -66.5667 | -19.3874 | -109.8672 | -30.2851 | 20.4436 | -27.3344 | 87.393 | -31.24 | -99.4681 | -48.0106 | -42.3422 | -43.1686 | -47.741 | -62.5223 | -47.1626 | -50.6121 | -41.854 | -43.8756 | -46.6981 | -58.1981 | -50.3422 | -44.6878 | 207 | -44.9942 | -44.0353 | -39.4253 | -40.2651 | -43.3435 | -43.6684 | -39.7074 | -43.5772 | 207 | -38.9315 | -40.9531 | -44.8185 | -59.7773 | -44.4176 | -47.5042 | -39.109 | -40.7677 | -45.0162 | -59.4144 | -44.4378 | -47.8873 | -39.4197 | -40.2461 | -43.7756 | -55.4531 | -47.5972 | -41.5799 | -39.5972 | -40.0607 | -43.9733 | -55.0902 | -47.6174 | -41.963
208 | -2.9338 | 0 | -2.7632 | 0 | -3.1139 | 0 | -2.7621 | 0 | -55.3305 | -6.7778 | -49.1871 | -142.1873 | -47.9398 | -106.016 | -46.6985 | 151.0596 | -56.6678 | -46.1056 | -41.1586 | 157.2023 | -56.3724 | -95.5779 | -44.3456 | 153.6512 | -50.3878 | -143.3807 | -44.3192 | 41.6446 | -63.908 | -152.7906 | -45.5419 | 111.6337 | -16.4272 | -85.003 | -25.0216 | 34.0115 | -27.0366 | -14.4748 | -30.4336 | -62.1481 | -18.3167 | -127.9818 | -27.5409 | -3.7104 | -27.0691 | 77.507 | -37.9559 | -161.867 | -47.0289 | -41.4655 | -43.1447 | -44.982 | -61.5523 | -46.192 | -49.4781 | -40.6842 | -44.0432 | -44.5992 | -59.7789 | -48.7624 | -45.3772 | 208 | -45.0781 | -45.7722 | -39.5849 | -40.2315 | -43.168 | -44.0119 | -39.9281 | -44.2637 | 208 | -37.7504 | -41.1094 | -42.0482 | -58.7891 | -43.4288 | -46.3642 | -37.921 | -40.9293 | -42.2199 | -58.4384 | -43.4299 | -46.716 | -38.5317 | -40.2109 | -41.6654 | -57.0157 | -45.9992 | -42.2633 | -38.7023 | -40.0308 | -41.8371 | -56.665 | -46.0003 | -42.6151
209 | -2.9534 | 0 | -2.775 | 0 | -3.0911 | 0 | -2.7814 | 0 | -65.428 | -94.5088 | -49.0632 | -171.0761 | -47.171 | -115.1364 | -49.9402 | 127.9628 | -59.3091 | -81.7517 | -42.3322 | 139.3399 | -55.0519 | -164.5203 | -44.8804 | 130.3203 | -49.4626 | -146.5964 | -45.4175 | 10.6796 | -63.1481 | 154.5049 | -48.2138 | 85.1815 | -16.1773 | -94.6466 | -23.6646 | 21.1928 | -26.8091 | -36.3315 | -34.7621 | -35.0203 | -17.5092 | -145.8237 | -26.0055 | -25.653 | -26.609 | 75.7556 | -33.4244 | 115.8728 | -45.8414 | -40.6692 | -42.7776 | -43.2906 | -60.4 | -45.6536 | -47.8101 | -40.013 | -43.7659 | -43.1422 | -61.5093 | -47.6224 | -46.4597 | 209 | -44.9653 | -49.3563 | -40.9154 | -41.0345 | -43.2839 | -44.9035 | -41.1737 | -45.7042 | 209 | -37.0596 | -40.8125 | -40.3372 | -57.625 | -42.8786 | -44.719 | -37.238 | -40.6748 | -40.5092 | -57.3089 | -42.8722 | -45.0287 | -37.7158 | -39.8242 | -40.1888 | -58.7343 | -44.8474 | -43.3686 | -37.8942 | -39.6865 | -40.3608 | -58.4182 | -44.841 | -43.6783
210 | -2.9721 | 0 | -2.7825 | 0 | -3.0407 | 0 | -2.7817 | 0 | -55.1647 | 168.6204 | -50.3801 | 167.0296 | -46.5919 | -127.8408 | -57.7367 | 115.4175 | -63.5581 | -130.8255 | -44.7973 | 124.802 | -51.0342 | 150.3082 | -46.5565 | 108.3415 | -48.5384 | -156.3621 | -47.3288 | -21.9277 | -62.146 | 102.9105 | -53.4203 | 60.9341 | -15.9911 | -104.1966 | -22.9108 | 6.4886 | -26.7404 | -61.1719 | -31.9076 | -0.9844 | -17.0985 | -162.6106 | -24.586 | -46.1002 | -26.7606 | 68.0799 | -28.9074 | 79.6921 | -44.8489 | -40.2633 | -42.2651 | -42.4504 | -59.4192 | -45.7438 | -46.2668 | -39.8219 | -43.2573 | -42.4075 | -61.3528 | -46.736 | -47.4559 | 210 | -44.6693 | -52.8657 | -43.5675 | -42.5576 | -43.5675 | -45.6882 | -43.4539 | -47.1759 | 210 | -36.8498 | -40.2852 | -39.4783 | -56.6367 | -42.9613 | -43.2261 | -37.0394 | -40.2166 | -39.6687 | -56.3785 | -42.9621 | -43.4851 | -37.2912 | -39.293 | -39.4354 | -58.5703 | -43.9535 | -44.4152 | -37.4808 | -39.2244 | -39.6258 | -58.3121 | -43.9543 | -44.6742
211 | -2.9885 | 0 | -2.7805 | 0 | -3.0004 | 0 | -2.7921 | 0 | -49.793 | 139.1572 | -52.2942 | 158.166 | -46.8576 | -143.2899 | -61.6404 | -149.7956 | -67.0726 | 154.507 | -48.5756 | 121.7112 | -48.061 | 119.1992 | -49.7333 | 92.2477 | -48.7122 | -170.7025 | -49.9616 | -56.1672 | -61.8956 | 54.3179 | -63.5742 | 77.447 | -16.0109 | -114.8734 | -22.679 | -7.2769 | -27.3926 | -88.7547 | -28.1935 | 2.9209 | -16.7927 | -179.6184 | -23.9375 | -67.5204 | -27.2192 | 67.2832 | -26.3849 | 58.0977 | -44.2258 | -40.3403 | -41.9651 | -42.3899 | -59.3235 | -46.5512 | -45.3352 | -40.2152 | -42.8049 | -42.4055 | -59.1165 | -46.5668 | -48.1421 | 211 | -44.3177 | -49.4425 | -46.8902 | -44.5973 | -44.0107 | -45.7901 | -46.7446 | -48.3752 | 211 | -37.2267 | -39.8164 | -39.4014 | -56.543 | -43.7707 | -42.3348 | -37.4347 | -39.8045 | -39.5978 | -56.3231 | -43.7591 | -42.5431 | -37.3518 | -38.9766 | -39.417 | -56.336 | -43.7863 | -45.1417 | -37.5598 | -38.9647 | -39.6134 | -56.1161 | -43.7747 | -45.35
212 | -3.0019 | 0 | -2.7588 | 0 | -2.9826 | 0 | -2.8188 | 0 | -47.0974 | 118.3106 | -52.7376 | 160.3839 | -47.7601 | -159.9809 | -53.8132 | -145.8505 | -65.6773 | 99.4475 | -51.0417 | 138.2251 | -46.1372 | 95.1936 | -53.8944 | 90.7636 | -49.4257 | 174.4052 | -52.6083 | -89.1146 | -62.1479 | 13.4911 | -59.8977 | 136.5342 | -16.1473 | -126.0012 | -22.8847 | -21.1605 | -27.7991 | -118.1953 | -25.8085 | -4.5026 | -16.7487 | 164.3587 | -23.455 | -87.029 | -27.7032 | 71.4011 | -25.1206 | 38.262 | -43.9424 | -40.7951 | -41.9081 | -42.876 | -59.7588 | -47.7209 | -44.8174 | -40.9748 | -42.5917 | -42.8682 | -57.7041 | -46.8772 | -48.5851 | 212 | -43.8108 | -46.2094 | -47.6076 | -46.0403 | -43.9978 | -45.1666 | -49.7519 | -48.8447 | 212 | -37.9729 | -39.5898 | -39.8741 | -57 | -44.9621 | -41.8348 | -38.216 | -39.6091 | -40.0572 | -56.7762 | -44.9021 | -41.9986 | -37.7932 | -38.9062 | -39.8663 | -54.9453 | -44.1184 | -45.6025 | -38.0363 | -38.9255 | -40.0494 | -54.7215 | -44.0584 | -45.7663
213 | -3.0028 | 0 | -2.7493 | 0 | -2.9924 | 0 | -2.8374 | 0 | -45.5526 | 101.0088 | -51.7105 | 157.5895 | -49.0113 | -175.1828 | -50.9976 | -156.4494 | -64.4564 | 69.4857 | -50.2156 | 153.3441 | -44.8393 | 74.463 | -56.4373 | 112.1402 | -50.7401 | 157.5152 | -54.2392 | -120.5998 | -62.8889 | -23.504 | -56.3703 | 129.9277 | -16.4094 | -135.7538 | -23.402 | -34.73 | -27.8376 | -152.4754 | -24.102 | -15.7818 | -16.9948 | 149.2092 | -23.2412 | -105.5503 | -27.2766 | 76.9396 | -24.5345 | 17.6593 | -43.8625 | -41.3322 | -42.0497 | -43.593 | -60.2805 | -49.1643 | -44.5852 | -41.8674 | -42.5926 | -43.5969 | -57.2141 | -47.4533 | -48.829 | 213 | -43.2656 | -44.4188 | -46.1604 | -46.4916 | -43.6132 | -44.3066 | -50.7854 | -49.487 | 213 | -38.8646 | -39.5898 | -40.5902 | -57.5312 | -46.415 | -41.5928 | -39.1181 | -39.6002 | -40.7556 | -57.2881 | -46.3269 | -41.7478 | -38.3294 | -39.0469 | -40.5941 | -54.4648 | -44.704 | -45.8366 | -38.5829 | -39.0573 | -40.7595 | -54.2217 | -44.6159 | -45.9916
214 | -3.0075 | 0 | -2.7556 | 0 | -2.9935 | 0 | -2.8364 | 0 | -44.6103 | 85.4631 | -50.7769 | 146.6039 | -50.133 | 170.1366 | -49.8043 | -166.8303 | -64.0856 | 53.0583 | -48.7368 | 152.9004 | -44.0718 | 55.9722 | -55.0576 | 130.5062 | -52.2258 | 142.3008 | -54.4535 | -149.1142 | -63.9943 | -59.9298 | -55.8157 | 116.0582 | -16.8295 | -147.1553 | -24.4214 | -47.3106 | -27.1515 | 171.2225 | -23.5218 | -28.7926 | -17.3955 | 134.5636 | -23.3686 | -124.3674 | -25.6491 | 80.4299 | -24.4938 | -2.0019 | -43.9157 | -41.9349 | -42.2771 | -44.4353 | -60.5681 | -50.7162 | -44.5095 | -42.7474 | -42.6911 | -44.4861 | -57.3611 | -48.0756 | -48.9353 | 214 | -42.7859 | -43.4253 | -44.9216 | -46.2959 | -43.1634 | -43.6509 | -50.3022 | -50.4531 | 214 | -39.7399 | -39.6836 | -41.4278 | -57.8125 | -47.9606 | -41.516 | -39.9918 | -39.6976 | -41.5989 | -57.5746 | -47.8798 | -41.6731 | -38.9274 | -39.2696 | -41.4786 | -54.6055 | -45.32 | -45.9418 | -39.1793 | -39.2836 | -41.6497 | -54.3676 | -45.2392 | -46.0989
215 | -3.0005 | 0 | -2.7519 | 0 | -3.0163 | 0 | -2.8169 | 0 | -44.096 | 71.3134 | -50.5183 | 131.0573 | -51.3356 | 158.8118 | -49.1489 | -173.9369 | -63.3326 | 40.7227 | -48.1294 | 146.3967 | -43.6162 | 38.7694 | -53.1089 | 134.0151 | -53.3358 | 125.2054 | -53.6169 | -174.0509 | -64.7232 | -99.1629 | -57.163 | 101.7465 | -17.4125 | -158.1596 | -25.5821 | -59.3089 | -26.212 | 140.0977 | -23.0242 | -40.158 | -18.0543 | 121.0177 | -23.7004 | -141.3934 | -23.9608 | 78.7866 | -25.1344 | -24.6338 | -44.0058 | -42.4616 | -42.5278 | -45.3026 | -60.4589 | -52.3756 | -44.5175 | -43.6413 | -42.8403 | -45.494 | -57.7831 | -48.7584 | -49.0867 | 215 | -42.5831 | -42.8761 | -44.3862 | -46.345 | -42.7559 | -43.1718 | -49.5242 | -51.6129 | 215 | -40.6408 | -39.8398 | -42.3021 | -57.707 | -49.6237 | -41.5012 | -40.8894 | -39.824 | -42.4857 | -57.4426 | -49.5587 | -41.7006 | -39.4611 | -39.5273 | -42.4935 | -55.0312 | -46.0065 | -46.0704 | -39.7097 | -39.5115 | -42.6771 | -54.7668 | -45.9415 | -46.2698
216 | -3.0048 | 0 | -2.7599 | 0 | -3.0488 | 0 | -2.8253 | 0 | -43.9046 | 58.1799 | -51.2147 | 113.261 | -52.4705 | 147.3503 | -48.6752 | 179.862 | -62.7504 | 31.6179 | -47.9318 | 139.322 | -43.4831 | 21.8511 | -51.639 | 131.4965 | -54.7146 | 111.1611 | -52.3012 | 162.9845 | -64.5466 | -140.7053 | -60.7847 | 93.4075 | -18.2044 | -169.0028 | -27.1001 | -70.4147 | -25.2889 | 112.3806 | -23.0257 | -52.2858 | -19.0723 | 108.381 | -24.3617 | -155.8866 | -22.8371 | 69.6136 | -25.7056 | -47.8076 | -44.1348 | -42.8457 | -42.8016 | -46.2716 | -60.0059 | -54.1933 | -44.6075 | -44.4863 | -43.0438 | -46.6192 | -58.377 | -49.4472 | -49.3417 | 216 | -42.6828 | -42.6128 | -44.2914 | -46.5184 | -42.5904 | -42.9175 | -48.6717 | -53.4077 | 216 | -41.4815 | -40.039 | -43.2668 | -57.246 | -51.4334 | -41.5587 | -41.7264 | -39.995 | -43.4463 | -56.9571 | -51.368 | -41.7822 | -39.8409 | -39.7968 | -43.6144 | -55.6171 | -46.6873 | -46.2929 | -40.0858 | -39.7528 | -43.7939 | -55.3282 | -46.6219 | -46.5164
217 | -3.0171 | 0 | -2.7777 | 0 | -3.0736 | 0 | -2.8195 | 0 | -43.9863 | 45.7637 | -53.0814 | 92.7394 | -54.6564 | 141.6674 | -48.0785 | 174.9433 | -61.6989 | 26.5095 | -48.2454 | 131.8762 | -43.6921 | 5.6507 | -50.4967 | 127.0443 | -56.0345 | 96.6449 | -50.9644 | 141.0702 | -63.4971 | -179.7054 | -65.6657 | 112.291 | -19.3023 | -179.2411 | -28.6421 | -79.8961 | -24.9025 | 86.0336 | -23.232 | -62.6435 | -20.4219 | 97.2222 | -25.3351 | -168.1017 | -22.2564 | 60.3142 | -26.431 | -73.0413 | -44.2699 | -43.097 | -43.0639 | -47.2308 | -59.4261 | -56.1244 | -44.766 | -45.2181 | -43.2788 | -47.848 | -58.7699 | -50.1791 | -49.8859 | 217 | -43.1625 | -42.5044 | -44.5024 | -47.1949 | -42.6643 | -42.908 | -47.6449 | -54.9346 | 217 | -42.201 | -40.2617 | -44.2137 | -56.6484 | -53.3467 | -41.6924 | -42.4404 | -40.2052 | -44.4113 | -56.3525 | -53.3049 | -41.9465 | -40.0799 | -40.0468 | -44.8309 | -55.9922 | -47.4014 | -46.8123 | -40.3193 | -39.9903 | -45.0285 | -55.6963 | -47.3596 | -47.0664
218 | -2.9886 | 0 | -2.7909 | 0 | -3.1061 | 0 | -2.8051 | 0 | -44.3179 | 33.0274 | -57.3736 | 65.0584 | -56.7041 | 137.253 | -47.4168 | 167.5797 | -60.2809 | 21.8968 | -48.903 | 124.9854 | -44.2541 | -10.3173 | -49.5467 | 122.485 | -58.5952 | 81.287 | -49.8671 | 117.7998 | -62.2889 | 145.2583 | -63.4913 | 151.3864 | -20.6605 | 171.1537 | -30.5415 | -90.226 | -24.7247 | 62.9076 | -23.6809 | -73.4416 | -22.2328 | 88.512 | -26.2856 | -176.9697 | -22.3543 | 50.7323 | -26.6674 | -105.0888 | -44.4002 | -43.1646 | -43.387 | -48.1151 | -59.0174 | -58.2623 | -44.9901 | -45.7194 | -43.5199 | -49.1425 | -58.4784 | -50.9186 | -51.0002 | 218 | -43.8756 | -42.5131 | -44.8371 | -47.9732 | -43.0077 | -43.1471 | -46.6038 | -56.1621 | 218 | -42.7308 | -40.5313 | -45.1265 | -56.2265 | -55.4714 | -41.884 | -42.9285 | -40.4138 | -45.31 | -55.9113 | -55.4572 | -42.185 | -40.176 | -40.3984 | -46.1539 | -55.6875 | -48.1277 | -47.8941 | -40.3737 | -40.2809 | -46.3374 | -55.3723 | -48.1135 | -48.1951
219 | -2.9616 | 0 | -2.7997 | 0 | -3.1248 | 0 | -2.7999 | 0 | -44.9856 | 20.9909 | -67.0261 | -15.6573 | -59.8731 | 132.9629 | -46.81 | 158.4399 | -58.368 | 15.8112 | -50.1357 | 122.5731 | -45.2717 | -25.5806 | -48.4864 | 117.1685 | -61.4225 | 63.6597 | -49.0887 | 93.361 | -61.8893 | 114.4334 | -58.6284 | 148.0774 | -22.5764 | 164.2135 | -32.1762 | -99.8564 | -25.2709 | 37.7748 | -24.1438 | -81.1746 | -24.5582 | 83.7493 | -27.1566 | 178.5465 | -22.9055 | 40.5784 | -26.4681 | -134.2371 | -44.5262 | -42.9451 | -43.7701 | -48.7137 | -58.9051 | -59.8435 | -45.2723 | -45.574 | -43.7975 | -50.1981 | -57.4989 | -51.7811 | -53.1439 | 219 | -44.8207 | -42.6737 | -45.1236 | -49.1442 | -43.5071 | -43.697 | -45.5477 | -55.6236 | 219 | -42.6124 | -40.8359 | -45.7521 | -56.1054 | -57.0438 | -42.1475 | -42.7743 | -40.6727 | -45.9138 | -55.7803 | -57.0436 | -42.4724 | -39.9835 | -40.8085 | -47.2365 | -54.6992 | -48.9814 | -50.0191 | -40.1454 | -40.6453 | -47.3982 | -54.3741 | -48.9812 | -50.344
220 | -2.9727 | 0 | -2.8034 | 0 | -3.1771 | 0 | -2.7955 | 0 | -46.093 | 9.5177 | -57.4346 | -118.9232 | -63.7103 | 121.39 | -46.7411 | 146.4138 | -56.8427 | 2.4377 | -50.9092 | 126.0026 | -46.913 | -40.276 | -47.398 | 109.3593 | -65.6569 | 24.0373 | -48.8117 | 67.2163 | -62.2271 | 89.4251 | -55.7921 | 128.2633 | -24.7209 | 162.5232 | -34.0966 | -115.1272 | -26.5702 | 10.9133 | -24.4591 | -91.3288 | -27.5996 | 88.3639 | -27.7685 | 178.9898 | -24.5737 | 33.7363 | -25.7121 | -159.5927 | -44.5884 | -42.4114 | -44.3007 | -48.6314 | -59.4517 | -59.1926 | -45.5221 | -44.7201 | -44.1641 | -50.0963 | -56.3034 | -53.2123 | -57.2664 | 220 | -45.7158 | -43.2027 | -45.0731 | -49.7447 | -44.1079 | -44.6722 | -44.6868 | -54.5522 | 220 | -41.7474 | -41.1914 | -45.6587 | -56.6483 | -56.3892 | -42.345 | -41.9167 | -40.987 | -45.8359 | -56.2746 | -56.3971 | -42.7266 | -39.4387 | -41.328 | -47.1236 | -53.5 | -50.4089 | -54.0893 | -39.608 | -41.1236 | -47.3008 | -53.1263 | -50.4168 | -54.4709
221 | -2.9842 | 0 | -2.8104 | 0 | -3.2042 | 0 | -2.8102 | 0 | -47.7465 | -0.1744 | -51.6025 | -149.6433 | -74.1141 | 130.8982 | -47.3766 | 133.4335 | -55.9067 | -14.2291 | -50.7373 | 128.5965 | -49.4749 | -52.8141 | -46.5964 | 99.4019 | -68.3885 | -33.4555 | -49.1004 | 38.0313 | -63.0795 | 74.6709 | -54.7133 | 100.0946 | -26.85 | 171.9097 | -35.5603 | -131.3524 | -28.7817 | -22.5386 | -24.558 | -96.9861 | -29.363 | 111.2019 | -27.2639 | 179.4447 | -26.8223 | 35.3367 | -24.7379 | 177.9943 | -44.5837 | -41.6846 | -44.8279 | -47.7947 | -60.4118 | -56.833 | -45.6229 | -43.3839 | -44.5272 | -48.6346 | -55.6425 | -55.7433 | -66.2076 | 221 | -46.2425 | -44.2408 | -44.7304 | -49.5688 | -44.7722 | -46.1836 | -44.251 | -53.963 | 221 | -40.3997 | -41.543 | -44.8105 | -57.6014 | -54.0226 | -42.4187 | -40.5735 | -41.323 | -44.9845 | -57.2076 | -54.0228 | -42.8127 | -38.7004 | -41.8437 | -45.6504 | -52.8321 | -52.9329 | -63.0034 | -38.8742 | -41.6237 | -45.8244 | -52.4383 | -52.9331 | -63.3974
222 | -2.9799 | 0 | -2.8292 | 0 | -3.2374 | 0 | -2.8266 | 0 | -50.2925 | -7.8397 | -48.6305 | -173.6617 | -69.7361 | -156.9114 | -49.0961 | 120.8124 | -55.5484 | -31.8524 | -50.3426 | 120.1342 | -53.6496 | -58.8407 | -46.3162 | 88.1781 | -67.0048 | -87.2611 | -49.9679 | 5.8748 | -63.0886 | 65.8792 | -55.4128 | 66.2925 | -27.0345 | -170.5716 | -36.9988 | -157.1508 | -31.0369 | -71.4266 | -24.4796 | -105.2514 | -27.6464 | 132.4261 | -26.6223 | 178.274 | -28.2542 | 50.099 | -24.0243 | 159.4384 | -44.497 | -40.9559 | -45.175 | -46.579 | -61.2744 | -54.62 | -45.63 | -42.0538 | -44.7455 | -46.841 | -55.4464 | -60.3389 | -66.6978 | 222 | -46.3522 | -46.1173 | -44.5269 | -49.1597 | -45.5486 | -48.2737 | -44.4004 | -54.4783 | 222 | -39.0739 | -41.7656 | -43.5991 | -58.4452 | -51.7908 | -42.3926 | -39.2246 | -41.5081 | -43.7524 | -58.037 | -51.7934 | -42.8034 | -37.976 | -42.1951 | -43.8611 | -52.6172 | -57.5097 | -63.4604 | -38.1267 | -41.9376 | -44.0144 | -52.209 | -57.5123 | -63.8712
223 | -2.995 | 0 | -2.8475 | 0 | -3.2168 | 0 | -2.8471 | 0 | -54.0383 | -2.9328 | -47.3275 | 165.9066 | -60.6113 | -156.4271 | -52.3887 | 115.2212 | -55.4997 | -48.9308 | -51.593 | 106.1959 | -59.8893 | -33.9161 | -46.6699 | 78.2484 | -68.387 | -152.4152 | -51.3283 | -30.6474 | -62.5675 | 54.5043 | -57.7558 | 22.7507 | -24.7622 | -161.8848 | -37.2114 | 168.3624 | -30.4644 | -134.7634 | -24.0336 | -115.6763 | -24.4769 | 139.0824 | -25.5352 | 173.4336 | -27.0433 | 68.0736 | -23.3921 | 144.7564 | -44.398 | -40.4275 | -45.2877 | -45.4918 | -61.8472 | -53.2204 | -45.3904 | -41.0801 | -44.8543 | -45.3436 | -55.242 | -70.8066 | -58.1538 | 223 | -46.3231 | -49.0191 | -45.0581 | -49.7401 | -46.4399 | -50.4845 | -45.1471 | -56.243 | 223 | -38.0851 | -41.8593 | -42.4968 | -58.9997 | -50.3729 | -42.1736 | -38.2326 | -41.6375 | -42.6447 | -58.6304 | -50.3733 | -42.5433 | -37.4325 | -42.2927 | -42.3486 | -52.3945 | -67.9591 | -54.937 | -37.58 | -42.0709 | -42.4965 | -52.0252 | -67.9595 | -55.3067
224 | -3.0387 | 0 | -2.8606 | 0 | -3.199 | 0 | -2.8609 | 0 | -56.1792 | 28.6676 | -46.936 | 151.4722 | -55.6448 | -177.1451 | -56.3561 | 135.1479 | -55.723 | -64.7409 | -54.6266 | 94.4325 | -56.4895 | 20.3327 | -47.2829 | 72.8532 | -66.6941 | 131.2039 | -52.6545 | -70.0862 | -62.4769 | 39.822 | -59.8712 | -38.3802 | -22.4026 | -163.8376 | -36.2076 | 134.5571 | -27.2983 | -179.5333 | -23.6312 | -126.9194 | -21.9639 | 135.1996 | -24.4863 | 165.7627 | -24.6062 | 73.2248 | -22.8882 | 132.7803 | -44.3173 | -40.2104 | -45.2455 | -44.8447 | -62.3056 | -52.5581 | -45.0833 | -40.6052 | -44.8747 | -44.4387 | -54.9505 | -69.3904 | -54.2651 | 224 | -45.9542 | -51.3066 | -45.8487 | -50.5308 | -46.7464 | -50.8426 | -45.9944 | -57.4243 | 224 | -37.5665 | -41.836 | -41.806 | -59.445 | -49.6975 | -41.8843 | -37.7446 | -41.6757 | -41.9838 | -59.1066 | -49.6972 | -42.2224 | -37.1717 | -42.2068 | -41.4 | -52.0899 | -66.5298 | -51.0661 | -37.3498 | -42.0465 | -41.5778 | -51.7515 | -66.5295 | -51.4042
225 | -3.0574 | 0 | -2.8641 | 0 | -3.1764 | 0 | -2.8465 | 0 | -52.8903 | 52.1552 | -46.6675 | 140.6651 | -53.4638 | 169.6645 | -54.5224 | 169.5802 | -56.2439 | -80.3728 | -60.6106 | 111.8178 | -51.1732 | 23.0906 | -47.3626 | 71.029 | -60.5814 | 91.8843 | -53.0964 | -109.2506 | -62.897 | 25.9162 | -58.3308 | -97.7578 | -20.4629 | -172.5396 | -34.5308 | 104.6513 | -24.254 | 148.3613 | -23.0942 | -141.0004 | -20.075 | 126.8084 | -23.8781 | 156.1811 | -22.5355 | 69.5046 | -22.5402 | 122.6068 | -44.2387 | -40.2229 | -45.1742 | -44.5669 | -62.7114 | -52.4065 | -44.7469 | -40.5123 | -44.8933 | -43.9618 | -54.6141 | -62.36 | -51.9536 | 225 | -45.0606 | -49.5685 | -45.8605 | -51.1082 | -45.7086 | -48.8446 | -46.0687 | -55.4415 | 225 | -37.4549 | -41.8359 | -41.5095 | -59.8473 | -49.5424 | -41.5705 | -37.6482 | -41.7169 | -41.7204 | -59.535 | -49.56 | -41.9004 | -37.1655 | -42.1168 | -40.9044 | -51.75 | -59.4959 | -48.7772 | -37.3588 | -41.9978 | -41.1153 | -51.4377 | -59.5135 | -49.1071
226 | -3.097 | 0 | -2.8727 | 0 | -3.1691 | 0 | -2.855 | 0 | -49.467 | 53.2191 | -46.2908 | 133.1875 | -51.814 | 146.8771 | -50.731 | 176.2656 | -57.0184 | -95.6431 | -58.9633 | 171.5876 | -47.892 | 13.9059 | -46.7442 | 68.7049 | -56.1902 | 65.3236 | -52.4363 | -144.7252 | -63.7776 | 12.6264 | -55.9131 | -135.1677 | -19.133 | 176.8884 | -33.3825 | 79.4903 | -22.3743 | 125.0466 | -22.9405 | -155.0181 | -18.7592 | 116.7657 | -23.5003 | 146.9823 | -21.1217 | 61.6245 | -22.3526 | 115.1364 | -44.2355 | -40.4304 | -45.1786 | -44.5402 | -63.5793 | -52.5866 | -44.486 | -40.6457 | -45.0306 | -43.7946 | -54.4 | -59.634 | -50.4035 | 226 | -43.8317 | -46.6267 | -44.787 | -50.0691 | -43.9995 | -46.5027 | -45.3118 | -52.6874 | 226 | -37.5487 | -41.9336 | -41.4432 | -60.7066 | -49.7139 | -41.3169 | -37.773 | -41.8615 | -41.6852 | -60.4102 | -49.7316 | -41.631 | -37.3334 | -42.0816 | -40.6976 | -51.5273 | -56.7613 | -47.2344 | -37.5577 | -42.0095 | -40.9396 | -51.2309 | -56.779 | -47.5485
227 | -3.1284 | 0 | -2.8814 | 0 | -3.173 | 0 | -2.8917 | 0 | -47.0583 | 46.0142 | -45.7324 | 124.178 | -50.3246 | 127.4438 | -48.1141 | 170.2935 | -57.898 | -110.5823 | -53.5751 | -178.9326 | -45.7275 | 2.071 | -46.0031 | 61.8403 | -53.6541 | 47.3835 | -51.173 | -172.6445 | -65.6452 | 1.1835 | -54.1448 | -159.2991 | -18.1102 | 163.3238 | -32.2188 | 57.1202 | -21.1361 | 104.0322 | -22.6783 | -171.3531 | -17.8922 | 105.0757 | -23.6872 | 137.0769 | -20.1418 | 50.9131 | -22.0488 | 107.5059 | -44.209 | -40.8092 | -45.1982 | -44.6074 | -64.5645 | -52.8835 | -44.3072 | -40.966 | -45.1909 | -43.8267 | -54.3032 | -58.2512 | -49.4428 | 227 | -42.5429 | -44.3478 | -43.3214 | -48.1552 | -42.5059 | -44.6028 | -44.367 | -50.7396 | 227 | -37.8376 | -42.0625 | -41.479 | -61.6831 | -50.0021 | -41.1342 | -38.0846 | -42.0179 | -41.7157 | -61.3915 | -49.9918 | -41.4155 | -37.6808 | -42.0698 | -40.6983 | -51.4218 | -55.3698 | -46.2698 | -37.9278 | -42.0252 | -40.935 | -51.1302 | -55.3595 | -46.5511
228 | -3.1417 | 0 | -2.8888 | 0 | -3.1676 | 0 | -2.9108 | 0 | -45.377 | 35.9612 | -45.2595 | 113.8604 | -49.1805 | 109.0545 | -46.3278 | 161.0252 | -59.2272 | -124.9669 | -50.363 | 170.3498 | -44.1831 | -11.4518 | -45.46 | 52.154 | -51.5542 | 28.7592 | -49.7477 | 163.5558 | -67.8106 | -1.6896 | -53.2192 | 179.4461 | -17.5251 | 149.6729 | -32.0119 | 33.8408 | -20.5088 | 85.4471 | -22.5606 | 171.9765 | -17.3794 | 92.9705 | -24.1732 | 129.0216 | -19.7761 | 38.3392 | -21.919 | 101.9413 | -44.146 | -41.2374 | -45.27 | -44.7437 | -65.7241 | -53.2218 | -44.1153 | -41.3356 | -45.4151 | -43.9044 | -54.3458 | -57.445 | -48.8282 | 228 | -41.4961 | -42.718 | -42.0566 | -46.484 | -41.331 | -43.1042 | -43.5845 | -49.2364 | 228 | -38.1939 | -42.2734 | -41.602 | -62.8353 | -50.333 | -40.9477 | -38.4468 | -42.2475 | -41.8329 | -62.5565 | -50.311 | -41.2045 | -38.0957 | -42.1283 | -40.7627 | -51.457 | -54.5562 | -45.6606 | -38.3486 | -42.1024 | -40.9936 | -51.1782 | -54.5342 | -45.9174
229 | -3.1697 | 0 | -2.9048 | 0 | -3.1761 | 0 | -2.8985 | 0 | -44.1547 | 24.363 | -45.031 | 102.4681 | -48.525 | 93.7821 | -45.1797 | 151.2355 | -61.0202 | -139.5028 | -48.6777 | 157.5116 | -43.1262 | -25.3077 | -45.316 | 41.0299 | -50.2749 | 10.6048 | -48.4208 | 142.3246 | -70.1703 | 3.0376 | -52.5888 | 161.7776 | -17.2368 | 135.3723 | -32.3118 | 9.4045 | -20.4057 | 68.2092 | -22.9075 | 154.2078 | -17.2273 | 80.2851 | -25.1977 | 122.4475 | -19.8894 | 24.7476 | -21.7375 | 96.2236 | -44.0448 | -41.695 | -45.4152 | -44.9237 | -66.2909 | -53.6169 | -43.9673 | -41.7699 | -45.6892 | -44.0962 | -54.5376 | -56.8675 | -48.4852 | 229 | -40.7645 | -41.5771 | -41.2322 | -45.4677 | -40.5812 | -41.9952 | -43.0717 | -48.2413 | 229 | -38.6002 | -42.5195 | -41.754 | -63.3861 | -50.7121 | -40.7912 | -38.8651 | -42.5131 | -42.0252 | -63.1148 | -50.7184 | -41.0688 | -38.5253 | -42.2455 | -40.9265 | -51.6328 | -53.9627 | -45.3091 | -38.7902 | -42.2391 | -41.1977 | -51.3615 | -53.969 | -45.5867
230 | -3.1699 | 0 | -2.9198 | 0 | -3.1822 | 0 | -2.9106 | 0 | -43.3313 | 12.8653 | -45.2154 | 90.3178 | -47.936 | 77.0292 | -44.3846 | 140.6608 | -63.6343 | -154.8608 | -47.7443 | 143.2542 | -42.4138 | -39.5751 | -45.5979 | 28.5594 | -48.9359 | -6.7284 | -47.2735 | 122.4859 | -71.4472 | 26.462 | -52.0887 | 144.5255 | -17.3232 | 121.2008 | -33.0509 | -21.1769 | -20.8527 | 52.317 | -23.6386 | 135.9254 | -17.4699 | 67.8679 | -26.2585 | 121.9565 | -20.4831 | 10.8999 | -21.6812 | 91.1664 | -43.9074 | -42.1581 | -45.556 | -45.0949 | -65.7902 | -54.2011 | -43.7792 | -42.2565 | -45.959 | -44.3573 | -54.7753 | -56.401 | -48.2883 | 230 | -40.3332 | -40.7932 | -40.7915 | -44.772 | -40.1013 | -41.1823 | -42.8007 | -47.2056 | 230 | -39.0866 | -42.7891 | -41.925 | -62.8704 | -51.2813 | -40.597 | -39.3367 | -42.7768 | -42.1843 | -62.608 | -51.2905 | -40.8686 | -38.9882 | -42.3861 | -41.1874 | -51.8555 | -53.4812 | -45.1061 | -39.2383 | -42.3738 | -41.4467 | -51.5931 | -53.4904 | -45.3777
231 | -3.1813 | 0 | -2.921 | 0 | -3.1751 | 0 | -2.9337 | 0 | -42.7942 | 0.225 | -45.9257 | 77.7011 | -47.6538 | 60.0664 | -43.847 | 130.5131 | -66.3771 | -170.2248 | -47.4593 | 130.103 | -42.0094 | -53.1677 | -46.4649 | 15.8462 | -47.727 | -23.1983 | -46.3749 | 102.9933 | -68.9184 | 46.1702 | -51.6963 | 130.2319 | -17.7006 | 106.9464 | -34.0959 | -59.8789 | -21.9167 | 38.2841 | -24.7244 | 117.0755 | -18.0586 | 54.6113 | -27.1089 | 125.1065 | -21.7214 | -3.4386 | -21.5878 | 85.3403 | -43.6937 | -42.5611 | -45.8368 | -45.2719 | -64.3187 | -55.0025 | -43.5695 | -42.7571 | -46.3024 | -44.6632 | -55.1163 | -56.0891 | -48.1758 | 231 | -40.2106 | -40.2678 | -40.7191 | -44.5168 | -39.8968 | -40.6485 | -42.8086 | -46.2393 | 231 | -39.5758 | -43.1211 | -42.0906 | -61.3977 | -52.0815 | -40.3944 | -39.8361 | -43.1273 | -42.3382 | -61.1436 | -52.0688 | -40.6358 | -39.3798 | -42.6555 | -41.4819 | -52.1953 | -53.1681 | -45.0007 | -39.6401 | -42.6617 | -41.7295 | -51.9412 | -53.1554 | -45.2421
232 | -3.1698 | 0 | -2.9086 | 0 | -3.1616 | 0 | -2.9437 | 0 | -42.5195 | -12.5367 | -47.2769 | 66.8816 | -47.1903 | 41.8817 | -43.5784 | 120.0364 | -69.1511 | 168.7015 | -47.558 | 118.2633 | -41.8349 | -67.8126 | -48.0584 | 3.4016 | -46.6302 | -38.1322 | -45.7228 | 83.733 | -65.4043 | 51.0998 | -51.4464 | 117.0899 | -18.4968 | 93.2361 | -33.3638 | -105.2369 | -23.7484 | 26.0612 | -26.6583 | 96.0994 | -19.0497 | 41.9908 | -26.6673 | 135.2105 | -24.4245 | -19.987 | -21.8007 | 81.4753 | -43.5641 | -42.9265 | -46.2276 | -45.4704 | -62.8024 | -56.0593 | -43.4047 | -43.1889 | -46.6073 | -45.0649 | -55.3774 | -55.8999 | -48.0218 | 232 | -40.278 | -40.0012 | -40.9617 | -44.3456 | -39.8757 | -40.3337 | -43.047 | -45.3489 | 232 | -40.0191 | -43.4375 | -42.3006 | -59.8938 | -53.1507 | -40.2431 | -40.2803 | -43.4457 | -42.5267 | -59.6408 | -53.1156 | -40.461 | -39.7567 | -43.0578 | -41.8951 | -52.4688 | -52.9913 | -44.8602 | -40.0179 | -43.066 | -42.1212 | -52.2158 | -52.9562 | -45.0781
233 | -3.154 | 0 | -2.9125 | 0 | -3.145 | 0 | -2.9551 | 0 | -42.526 | -26.2537 | -49.5004 | 58.596 | -46.5658 | 26.0073 | -43.5117 | 109.5903 | -72.6228 | 149.0774 | -48.4346 | 108.986 | -41.9917 | -82.2762 | -50.8432 | -8.3502 | -45.9054 | -49.577 | -45.3953 | 64.175 | -62.9952 | 45.9448 | -51.624 | 106.3696 | -19.6444 | 81.1318 | -31.0395 | -148.4283 | -26.4195 | 21.7108 | -29.7707 | 71.5627 | -20.7876 | 29.7744 | -25.2188 | 138.4245 | -28.6746 | -34.7257 | -21.9694 | 78.436 | -43.4156 | -43.0329 | -46.7147 | -45.7026 | -61.521 | -57.7782 | -43.2504 | -43.4008 | -46.8375 | -45.6007 | -55.4399 | -55.9008 | -47.7295 | 233 | -40.4979 | -39.9783 | -41.5424 | -44.3836 | -40.1267 | -40.3344 | -43.5668 | -44.8078 | 233 | -40.2468 | -43.6835 | -42.5486 | -58.6085 | -54.8657 | -40.1054 | -40.4883 | -43.6925 | -42.7475 | -58.376 | -54.8231 | -40.2953 | -39.8789 | -43.5607 | -42.4467 | -52.5274 | -52.9883 | -44.5845 | -40.1204 | -43.5697 | -42.6456 | -52.2949 | -52.9457 | -44.7744
234 | -3.1492 | 0 | -2.9359 | 0 | -3.1485 | 0 | -2.9578 | 0 | -42.8439 | -40.0558 | -53.0021 | 59.2539 | -46.3119 | 9.4778 | -43.6722 | 99.2181 | -75.3848 | 92.9954 | -49.6762 | 102.5567 | -42.4686 | -97.2165 | -56.4046 | -14.8111 | -45.3315 | -62.3439 | -45.4396 | 44.3496 | -61.1649 | 37.0118 | -51.7828 | 91.5291 | -21.3598 | 70.9415 | -28.1204 | 179.9608 | -29.7773 | 31.458 | -35.0693 | 32.1089 | -23.3744 | 17.817 | -23.4652 | 136.1981 | -39.515 | -51.1495 | -22.2027 | 77.0386 | -43.3511 | -42.9072 | -47.2043 | -45.9309 | -60.6643 | -60.3084 | -43.1449 | -43.3573 | -46.95 | -46.2468 | -55.2795 | -56.1969 | -47.3146 | 234 | -40.9507 | -40.2267 | -42.3125 | -44.6621 | -40.5439 | -40.6558 | -44.2597 | -44.3537 | 234 | -40.2081 | -43.8008 | -42.7817 | -57.7284 | -57.3725 | -39.9964 | -40.4214 | -43.8015 | -42.9731 | -57.5158 | -57.3506 | -40.1871 | -39.758 | -44.0551 | -43.0976 | -52.3436 | -53.261 | -44.1661 | -39.9713 | -44.0558 | -43.289 | -52.131 | -53.2391 | -44.3568
235 | -3.1337 | 0 | -2.9535 | 0 | -3.1623 | 0 | -2.9422 | 0 | -43.5445 | -54.0292 | -56.7234 | 85.6099 | -45.9154 | -7.1676 | -44.0931 | 89.7126 | -71.5338 | 45.0942 | -50.8825 | 99.6825 | -43.3125 | -111.4871 | -66.2285 | 74.3821 | -44.6973 | -73.8203 | -45.9513 | 24.3427 | -59.5381 | 28.5825 | -52.0632 | 77.6547 | -23.5553 | 64.4421 | -25.6822 | 154.7699 | -30.1834 | 59.8998 | -36.4167 | -62.3404 | -27.6565 | 6.7984 | -21.9356 | 130.125 | -35.4405 | 122.348 | -22.3364 | 77.9586 | -43.3979 | -42.5833 | -47.5196 | -46.1401 | -60.2847 | -63.4935 | -43.1215 | -43.0373 | -46.9111 | -46.9769 | -55.0316 | -56.5959 | -46.8117 | 235 | -41.4295 | -40.7962 | -43.0756 | -44.7051 | -40.9268 | -41.3577 | -44.9677 | -43.8472 | 235 | -39.9036 | -43.7774 | -43.0064 | -57.3312 | -60.54 | -39.9592 | -40.0838 | -43.7488 | -43.1979 | -57.1224 | -60.5513 | -40.1793 | -39.4496 | -44.3859 | -43.8432 | -52.0781 | -53.6424 | -43.6494 | -39.6298 | -44.3573 | -44.0347 | -51.8693 | -53.6537 | -43.8695
236 | -3.1208 | 0 | -2.9686 | 0 | -3.1799 | 0 | -2.9523 | 0 | -44.7335 | -68.2885 | -53.7102 | 122.7322 | -45.8656 | -23.5041 | -44.8463 | 80.5485 | -68.412 | 7.8248 | -52.0651 | 99.363 | -44.6666 | -124.9175 | -52.8747 | 104.0157 | -44.3847 | -85.2208 | -46.8591 | 4.4086 | -58.2868 | 17.4871 | -53.2011 | 62.5429 | -26.0688 | 65.3914 | -23.7928 | 132.8659 | -27.067 | 73.7079 | -29.3274 | -114.5887 | -36.7597 | 10.8691 | -20.7867 | 120.3657 | -27.5508 | 104.5024 | -22.1386 | 80.4398 | -43.5771 | -42.1673 | -47.4715 | -46.4131 | -60.3349 | -65.4837 | -43.1718 | -42.5823 | -46.7341 | -47.5936 | -54.871 | -56.9065 | -46.2785 | 236 | -41.9526 | -41.7698 | -43.6418 | -44.9123 | -41.2067 | -42.4995 | -45.1493 | -43.6952 | 236 | -39.4615 | -43.6133 | -43.2923 | -57.3663 | -62.5151 | -39.9919 | -39.6137 | -43.5542 | -43.4608 | -57.155 | -62.5314 | -40.2195 | -39.0465 | -44.3507 | -44.4728 | -51.9024 | -53.9379 | -43.0986 | -39.1987 | -44.2916 | -44.6413 | -51.6911 | -53.9542 | -43.3262
237 | -3.1251 | 0 | -2.9865 | 0 | -3.2106 | 0 | -2.9562 | 0 | -46.5303 | -80.5482 | -49.1694 | 128.0971 | -46.107 | -40.1102 | -45.8965 | 73.8258 | -65.0712 | -20.4689 | -53.1268 | 99.9632 | -46.6078 | -136.0852 | -47.4413 | 91.3768 | -44.2577 | -97.6403 | -48.2611 | -15.403 | -57.3136 | 4.2852 | -55.1771 | 42.9885 | -27.6428 | 77.5412 | -22.44 | 113.4089 | -24.1133 | 70.3545 | -25.3094 | -141.1444 | -35.5901 | 123.8485 | -19.9769 | 108.6897 | -23.8247 | 87.1816 | -21.263 | 82.8592 | -43.8059 | -41.8581 | -47.1086 | -46.6184 | -60.5285 | -64.7761 | -43.2951 | -42.2614 | -46.5743 | -48.0099 | -54.7834 | -56.9724 | -45.7429 | 237 | -42.3028 | -43.1635 | -43.6957 | -45.2744 | -41.1137 | -44.132 | -44.4388 | -43.7254 | 237 | -39.1363 | -43.4492 | -43.4933 | -57.542 | -61.7896 | -40.0845 | -39.2749 | -43.3637 | -43.6622 | -57.3179 | -61.8199 | -40.3389 | -38.733 | -43.9835 | -44.8848 | -51.7969 | -53.9859 | -42.5323 | -38.8716 | -43.898 | -45.0537 | -51.5728 | -54.0162 | -42.7867
238 | -3.1441 | 0 | -3.002 | 0 | -3.2244 | 0 | -2.968 | 0 | -49.1169 | -90.8449 | -46.0002 | 120.6972 | -46.7611 | -58.0269 | -47.166 | 70.115 | -62.7319 | -40.799 | -54.3528 | 102.1706 | -49.1483 | -142.203 | -44.2848 | 76.3947 | -44.4856 | -110.0993 | -50.191 | -35.8811 | -56.8673 | -10.2115 | -58.1187 | 24.0952 | -27.1668 | 91.1322 | -21.471 | 94.7136 | -22.1963 | 60.218 | -22.1478 | -161.7164 | -27.8836 | 128.8981 | -19.614 | 96.37 | -21.9792 | 71.4166 | -20.2262 | 82.2235 | -44.0596 | -41.7078 | -46.8697 | -46.8096 | -60.8604 | -63.6492 | -43.4512 | -42.1229 | -46.5348 | -48.2364 | -54.7755 | -56.8221 | -45.2763 | 238 | -42.3319 | -44.9495 | -43.1883 | -45.9715 | -40.7033 | -46.2354 | -43.1519 | -44.0673 | 238 | -38.9788 | -43.3907 | -43.6655 | -57.8584 | -60.6472 | -40.2268 | -39.1209 | -43.3104 | -43.8416 | -57.636 | -60.6812 | -40.4832 | -38.5637 | -43.7256 | -45.0923 | -51.7735 | -53.8201 | -42.0519 | -38.7058 | -43.6453 | -45.2684 | -51.5511 | -53.8541 | -42.3083
239 | -3.1508 | 0 | -3.014 | 0 | -3.2428 | 0 | -3.0121 | 0 | -52.6886 | -94.552 | -43.9041 | 109.908 | -47.689 | -75.8923 | -48.3805 | 70.9334 | -62.2337 | -59.4287 | -55.0536 | 112.9979 | -52.1109 | -139.3952 | -42.2439 | 61.0362 | -44.8299 | -120.1102 | -52.8193 | -59.4414 | -56.7143 | -23.1183 | -62.8605 | 7.9215 | -25.4349 | 94.3891 | -20.9575 | 77.0275 | -21.1123 | 47.6355 | -20.096 | 178.9452 | -24.1262 | 117.4945 | -19.6904 | 83.2349 | -20.911 | 55.2805 | -19.0955 | 78.4915 | -44.2765 | -41.773 | -46.7358 | -46.9328 | -61.1514 | -62.8893 | -43.551 | -42.2115 | -46.6585 | -48.2542 | -54.7757 | -56.6117 | -44.9469 | 239 | -41.9991 | -46.8821 | -42.3401 | -46.8305 | -40.0574 | -48.6947 | -41.8447 | -44.4935 | 239 | -39.0607 | -43.5077 | -43.782 | -58.1374 | -59.8753 | -40.3082 | -39.1975 | -43.4157 | -43.9207 | -57.9086 | -59.8772 | -40.5389 | -38.6222 | -43.585 | -45.1034 | -51.7617 | -53.5977 | -41.7041 | -38.759 | -43.493 | -45.2421 | -51.5329 | -53.5996 | -41.9348
240 | -3.1444 | 0 | -3.0219 | 0 | -3.2594 | 0 | -3.0489 | 0 | -57.3285 | -79.7964 | -42.4489 | 98.002 | -49.2945 | -92.4439 | -49.1706 | 75.5118 | -61.6215 | -78.3472 | -54.8171 | 127.3996 | -54.1239 | -121.7518 | -40.8546 | 45.627 | -45.5464 | -128.0068 | -56.4246 | -92.9017 | -56.9114 | -36.0009 | -76.2598 | -36.5692 | -23.955 | 89.4523 | -20.8634 | 59.6151 | -20.6079 | 34.3568 | -18.5667 | 161.5156 | -21.9869 | 106.592 | -20.1328 | 70.0811 | -20.5551 | 40.0939 | -18.0269 | 72.3274 | -44.4368 | -41.9359 | -46.7176 | -47.0461 | -61.3704 | -62.7133 | -43.6 | -42.4387 | -46.857 | -48.139 | -54.8246 | -56.3137 | -44.78 | 240 | -41.5173 | -48.3438 | -41.4085 | -48.027 | -39.4351 | -50.8707 | -40.7346 | -45.2368 | 240 | -39.2943 | -43.7126 | -43.9017 | -58.3485 | -59.6914 | -40.3406 | -39.4168 | -43.5976 | -43.9972 | -58.111 | -59.6644 | -40.5511 | -38.7915 | -43.5732 | -44.9946 | -51.8027 | -53.2918 | -41.5206 | -38.914 | -43.4582 | -45.0901 | -51.5652 | -53.2648 | -41.7311
241 | -3.1544 | 0 | -3.0364 | 0 | -3.2597 | 0 | -3.0953 | 0 | -58.0492 | -36.0387 | -41.4708 | 86.1565 | -51.7208 | -110.1365 | -49.1731 | 82.3479 | -61.5743 | -93.2974 | -53.4445 | 136.1364 | -53.1285 | -101.4097 | -39.9298 | 30.8631 | -46.3543 | -133.1584 | -59.6482 | -149.5917 | -57.3876 | -48.6526 | -67.5065 | 165.9004 | -23.0283 | 80.1013 | -21.21 | 42.8416 | -20.84 | 20.2844 | -17.4187 | 145.0039 | -20.8255 | 95.1941 | -21.1057 | 56.6605 | -21.0193 | 24.2671 | -17.1464 | 64.2094 | -44.5509 | -42.2001 | -46.7627 | -47.1955 | -61.4845 | -62.9891 | -43.6262 | -42.7949 | -47.1544 | -48.0012 | -54.8684 | -55.998 | -44.6281 | 241 | -40.9926 | -48.4284 | -40.5604 | -49.2268 | -38.8724 | -51.093 | -39.8762 | -45.994 | 241 | -39.6405 | -44 | -44.0411 | -58.4481 | -59.9527 | -40.3665 | -39.7585 | -43.8947 | -44.1002 | -58.2248 | -59.8938 | -40.5309 | -39.0457 | -43.6083 | -44.8468 | -51.832 | -52.9616 | -41.3684 | -39.1637 | -43.503 | -44.9059 | -51.6087 | -52.9027 | -41.5328
242 | -3.1588 | 0 | -3.0277 | 0 | -3.2776 | 0 | -3.1295 | 0 | -53.3996 | -18.7419 | -40.8727 | 73.6943 | -55.4994 | -125.0455 | -48.315 | 86.6566 | -62.0888 | -111.6658 | -51.4855 | 139.6167 | -50.5 | -95.2019 | -39.3732 | 15.9782 | -47.0218 | -133.6042 | -57.0273 | 147.3902 | -58.0585 | -59.1118 | -59.5815 | 142.2841 | -22.8158 | 67.6714 | -22.058 | 26.3826 | -21.6154 | 6.2713 | -16.7391 | 128.9388 | -20.4655 | 84.1052 | -22.7467 | 44.0214 | -22.3165 | 8.6241 | -16.6391 | 54.5186 | -44.589 | -42.5109 | -46.896 | -47.4015 | -61.3937 | -63.8429 | -43.5706 | -43.305 | -47.5143 | -47.8519 | -54.9886 | -55.6292 | -44.4703 | 242 | -40.497 | -47.005 | -39.8448 | -49.7716 | -38.4076 | -49.0452 | -39.2588 | -46.4748 | 242 | -40.1462 | -44.3555 | -44.2427 | -58.366 | -60.8152 | -40.293 | -40.2773 | -44.2367 | -44.272 | -58.1161 | -60.7134 | -40.4411 | -39.3521 | -43.7372 | -44.6931 | -51.9609 | -52.6015 | -41.1927 | -39.4832 | -43.6184 | -44.7224 | -51.711 | -52.4997 | -41.3408
243 | -3.1995 | 0 | -3.027 | 0 | -3.2805 | 0 | -3.1492 | 0 | -49.8848 | -22.3086 | -40.6076 | 62.1225 | -63.7694 | -130.4124 | -47.0245 | 87.3787 | -62.676 | -129.5717 | -49.7652 | 138.531 | -48.2054 | -99.2579 | -39.1557 | 1.58 | -47.0456 | -130.8191 | -53.0317 | 111.3738 | -59.2054 | -68.018 | -56.1916 | 128.6708 | -23.2645 | 54.1628 | -23.5891 | 10.3793 | -23.2544 | -6.0637 | -16.3977 | 113.1919 | -20.4751 | 74.4971 | -25.1985 | 33.8465 | -24.6809 | -6.2813 | -16.2961 | 43.8496 | -44.5532 | -42.8926 | -47.0655 | -47.6352 | -61.1235 | -65.5137 | -43.4997 | -43.9211 | -47.9534 | -47.8161 | -55.1169 | -55.2688 | -44.2154 | 243 | -40.104 | -45.1358 | -39.3055 | -49.3872 | -38.0599 | -46.7176 | -38.8996 | -46.3174 | 243 | -40.7216 | -44.7539 | -44.4357 | -58.0965 | -62.4867 | -40.2192 | -40.8941 | -44.6729 | -44.486 | -57.843 | -62.3645 | -40.3505 | -39.6931 | -43.866 | -44.6166 | -52.0899 | -52.2418 | -40.9349 | -39.8656 | -43.785 | -44.6669 | -51.8364 | -52.1196 | -41.0662
244 | -3.198 | 0 | -3.0129 | 0 | -3.2726 | 0 | -3.176 | 0 | -47.4938 | -32.245 | -40.6033 | 50.5998 | -65.1712 | 0.5931 | -45.6566 | 83.8678 | -63.5561 | -147.8088 | -48.4473 | 133.8719 | -46.466 | -107.8648 | -39.3076 | -13.0802 | -46.5278 | -129.618 | -50.0624 | 86.0217 | -60.4337 | -76.1156 | -53.9007 | 115.1099 | -24.5366 | 40.7889 | -26.1453 | -4.3105 | -25.9263 | -14.5712 | -16.371 | 97.8415 | -21.1422 | 67.162 | -29.5258 | 28.6872 | -28.9932 | -21.6232 | -16.3684 | 32.6361 | -44.375 | -43.2948 | -47.2905 | -47.9024 | -60.4961 | -68.3417 | -43.4036 | -44.5694 | -48.362 | -47.9192 | -55.2317 | -54.9405 | -43.8794 | 244 | -39.7822 | -43.4261 | -38.9105 | -48.2267 | -37.9024 | -44.7722 | -38.8202 | -45.6507 | 244 | -41.3714 | -45.164 | -44.7044 | -57.4832 | -65.3288 | -40.131 | -41.5565 | -45.0894 | -44.7264 | -57.2235 | -65.1657 | -40.2276 | -40.0968 | -44.0925 | -44.7212 | -52.2188 | -51.9276 | -40.6068 | -40.2819 | -44.0179 | -44.7432 | -51.9591 | -51.7645 | -40.7034
245 | -3.1774 | 0 | -3.0124 | 0 | -3.2603 | 0 | -3.1723 | 0 | -45.8054 | -44.8504 | -40.8815 | 40.266 | -55.4151 | -3.5709 | -44.4623 | 77.1614 | -64.8208 | -160.8351 | -47.4931 | 127.9498 | -45.1811 | -118.8005 | -39.8353 | -26.9619 | -45.6176 | -129.8862 | -47.9093 | 64.8726 | -62.4482 | -82.1095 | -52.4261 | 99.4321 | -26.8999 | 27.4957 | -30.6836 | -16.7829 | -29.8706 | -10.6784 | -16.6306 | 83.4002 | -22.1454 | 63.0719 | -35.5362 | 56.3004 | -40.1661 | -31.5512 | -16.7471 | 20.2584 | -44.1166 | -43.6575 | -47.6214 | -48.2182 | -59.683 | -72.2083 | -43.2975 | -45.1822 | -48.7789 | -48.2233 | -55.3522 | -54.7056 | -43.4297 | 245 | -39.5556 | -42.0488 | -38.6892 | -46.7748 | -37.9149 | -43.2713 | -39.0043 | -44.7211 | 245 | -42.0048 | -45.6015 | -45.0408 | -56.6706 | -69.1959 | -40.0372 | -42.1698 | -45.5186 | -45.0459 | -56.4227 | -69.036 | -40.1252 | -40.4801 | -44.444 | -45.0459 | -52.3398 | -51.6932 | -40.1694 | -40.6451 | -44.3611 | -45.051 | -52.0919 | -51.5333 | -40.2574
246 | -3.1835 | 0 | -3.0151 | 0 | -3.2555 | 0 | -3.1621 | 0 | -44.6327 | -59.2346 | -41.4005 | 30.3519 | -51.1433 | -17.31 | -43.5578 | 68.4165 | -66.3555 | -176.8636 | -46.8475 | 119.8845 | -44.2725 | -131.0965 | -40.7956 | -41.1014 | -44.5735 | -134.5126 | -46.3953 | 44.5392 | -65.1911 | -81.8536 | -51.671 | 83.9613 | -31.3703 | 18.5841 | -41.8706 | -3.8553 | -32.2899 | 20.577 | -17.3268 | 69.6444 | -23.6004 | 64.516 | -32.6898 | 113.1213 | -35.4518 | 124.5808 | -17.5017 | 9.0196 | -43.8107 | -43.9612 | -48.1666 | -48.506 | -58.7951 | -72.6526 | -43.1596 | -45.6578 | -49.2304 | -48.687 | -55.269 | -54.689 | -42.9328 | 246 | -39.4106 | -41.039 | -38.6271 | -45.439 | -38.0817 | -42.1734 | -39.4692 | -43.7681 | 246 | -42.4743 | -46.0469 | -45.3225 | -55.78 | -69.6375 | -39.9041 | -42.6427 | -45.9749 | -45.3439 | -55.5396 | -69.4905 | -39.9975 | -40.7777 | -44.9831 | -45.5035 | -52.2539 | -51.6739 | -39.6773 | -40.9461 | -44.9111 | -45.5249 | -52.0135 | -51.5269 | -39.7707
247 | -3.1953 | 0 | -3.034 | 0 | -3.248 | 0 | -3.144 | 0 | -43.8613 | -73.7814 | -42.2571 | 22.3935 | -48.4299 | -31.601 | -42.9505 | 58.9599 | -68.0925 | 168.3887 | -46.4971 | 112.432 | -43.6457 | -144.1992 | -42.3344 | -53.578 | -43.7963 | -140.5473 | -45.4043 | 25.2238 | -69.2825 | -67.9109 | -51.2023 | 67.6928 | -41.3376 | 43.8772 | -34.9881 | 104.1633 | -28.82 | 44.5488 | -18.439 | 57.3034 | -24.6073 | 73.0338 | -27.085 | 116.9841 | -27.4681 | 112.2725 | -18.7515 | -2.4015 | -43.478 | -44.1763 | -49.0495 | -48.724 | -58.0014 | -68.3638 | -43.0027 | -45.8964 | -49.7617 | -49.2449 | -54.9715 | -54.8339 | -42.4176 | 247 | -39.3958 | -40.3644 | -38.7757 | -44.3283 | -38.4364 | -41.4192 | -40.2313 | -43.0608 | 247 | -42.7011 | -46.5664 | -45.5287 | -54.9674 | -65.3298 | -39.7547 | -42.8624 | -46.5137 | -45.58 | -54.7534 | -65.2198 | -39.8587 | -40.981 | -45.8542 | -46.0496 | -51.9375 | -51.7999 | -39.1696 | -41.1423 | -45.8015 | -46.1009 | -51.7235 | -51.6899 | -39.2736
248 | -3.2228 | 0 | -3.0401 | 0 | -3.276 | 0 | -3.1163 | 0 | -43.4229 | -89.7119 | -43.4345 | 16.2748 | -46.5904 | -46.5842 | -42.6032 | 48.2037 | -69.5223 | 153.7956 | -46.3784 | 105.689 | -43.3171 | -158.7081 | -44.6948 | -64.8962 | -43.1092 | -147.543 | -44.8772 | 5.8947 | -68.4189 | -23.2813 | -51.3843 | 51.0157 | -34.3638 | 127.3526 | -27.9322 | 97.6938 | -25.4613 | 43.242 | -20.0738 | 47.0291 | -24.1355 | 85.2329 | -23.9653 | 108.1238 | -23.8234 | 98.4354 | -20.6595 | -15.598 | -43.1794 | -44.3098 | -50.3347 | -48.9059 | -57.3708 | -65.1575 | -42.7628 | -45.901 | -50.3517 | -49.7823 | -54.2862 | -55.3112 | -41.9419 | 248 | -39.4792 | -39.9786 | -39.0909 | -43.462 | -38.881 | -41.0093 | -41.3238 | -42.4958 | 248 | -42.6782 | -47.1289 | -45.6831 | -54.3307 | -62.1174 | -39.4868 | -42.8609 | -47.0757 | -45.7896 | -54.0948 | -62.0412 | -39.6465 | -41.087 | -47.1119 | -46.5595 | -51.2461 | -52.2711 | -38.6659 | -41.2697 | -47.0587 | -46.666 | -51.0102 | -52.1949 | -38.8256
249 | -3.2403 | 0 | -3.0707 | 0 | -3.3025 | 0 | -3.0957 | 0 | -43.3721 | -107.3816 | -44.9082 | 14.5378 | -45.2867 | -62.1697 | -42.5431 | 37.0861 | -69.0824 | 127.8976 | -46.4929 | 99.3104 | -43.28 | -174.4601 | -48.7075 | -70.2886 | -42.6015 | -154.4527 | -44.7946 | -13.1603 | -62.2725 | -8.2337 | -51.6081 | 34.1489 | -28.0373 | 122.519 | -24.2976 | 84.0559 | -23.3587 | 32.9738 | -22.5133 | 39.4194 | -22.5547 | 91.6221 | -21.9331 | 95.8977 | -21.724 | 84.9814 | -23.7442 | -26.4511 | -42.9873 | -44.4768 | -52.0006 | -49.1123 | -57.2255 | -63.1955 | -42.52 | -45.6579 | -50.7364 | -50.2465 | -53.2231 | -56.1814 | -41.5075 | 249 | -39.6696 | -39.9223 | -39.5703 | -42.8275 | -39.3783 | -40.9293 | -42.7143 | -42.0459 | 249 | -42.4176 | -47.4961 | -45.872 | -54.1548 | -60.1248 | -39.2175 | -42.5872 | -47.4339 | -46.0166 | -53.923 | -60.0998 | -39.4243 | -41.2365 | -48.7603 | -47.0062 | -50.1524 | -53.1107 | -38.205 | -41.4061 | -48.6981 | -47.1508 | -49.9206 | -53.0857 | -38.4118
250 | -3.2797 | 0 | -3.1022 | 0 | -3.3327 | 0 | -3.0691 | 0 | -43.8547 | -126.2896 | -46.3957 | 19.7499 | -44.2534 | -75.1214 | -42.7381 | 26.2304 | -65.6019 | 95.8839 | -46.4293 | 95.2827 | -43.7009 | 169.3726 | -55.2086 | -45.5938 | -41.8391 | -160.2085 | -45.1628 | -31.527 | -58.1354 | -17.7406 | -52.2946 | 14.0013 | -24.778 | 108.0286 | -22.0629 | 68.9943 | -22.0791 | 18.4938 | -25.6958 | 40.9635 | -21.0275 | 91.3488 | -20.6417 | 82.609 | -20.6017 | 72.0308 | -29.4999 | -27.6712 | -43.0304 | -44.671 | -53.4032 | -49.4483 | -57.6241 | -61.9328 | -42.3991 | -45.2077 | -50.3617 | -50.653 | -52.0905 | -57.4929 | -41.116 | 250 | -39.9289 | -40.2377 | -40.0472 | -42.1764 | -39.5413 | -41.27 | -44.0485 | -41.3722 | 250 | -41.928 | -47.082 | -46.1686 | -54.5219 | -58.8306 | -39.0664 | -42.1055 | -47.029 | -46.3792 | -54.2914 | -58.8637 | -39.33 | -41.3913 | -50.1235 | -47.3733 | -48.9883 | -54.3907 | -37.7833 | -41.5688 | -50.0705 | -47.5839 | -48.7578 | -54.4238 | -38.0469
251 | -3.2945 | 0 | -3.1101 | 0 | -3.3567 | 0 | -3.0652 | 0 | -44.9743 | -145.7534 | -46.7148 | 31.4941 | -43.1487 | -87.9067 | -43.1689 | 15.9934 | -62.3973 | 59.9229 | -46.5077 | 92.9488 | -44.7149 | 152.5988 | -51.5053 | 14.4213 | -41.0838 | -168.101 | -45.9463 | -49.1925 | -55.4613 | -34.6908 | -53.3085 | -4.7384 | -22.9164 | 91.9122 | -20.6897 | 54.6218 | -21.6615 | 3.4264 | -27.8752 | 62.9848 | -19.7506 | 87.8347 | -20.0493 | 68.0507 | -20.1041 | 60.4629 | -38.2629 | 23.2001 | -43.3781 | -44.9411 | -53.8164 | -49.9406 | -58.7844 | -61.2302 | -42.5007 | -44.7708 | -49.271 | -50.9226 | -51.1921 | -58.9544 | -40.8237 | 251 | -39.9332 | -40.937 | -40.3687 | -41.4658 | -39.2535 | -42.073 | -44.298 | -40.6841 | 251 | -41.4763 | -45.9765 | -46.6461 | -55.6743 | -58.1201 | -39.144 | -41.6607 | -45.9143 | -46.8754 | -55.4277 | -58.165 | -39.4355 | -41.6466 | -50.5219 | -47.6281 | -48.082 | -55.8443 | -37.467 | -41.831 | -50.4597 | -47.8574 | -47.8354 | -55.8892 | -37.7585
252 | -3.3252 | 0 | -3.128 | 0 | -3.3665 | 0 | -3.0722 | 0 | -46.8535 | -164.7079 | -45.3826 | 41.8111 | -42.3083 | -101.9739 | -43.8585 | 6.2718 | -60.1834 | 29.0504 | -46.4186 | 91.3668 | -46.31 | 137.8722 | -45.7203 | 17.5824 | -40.4187 | -177.7223 | -47.0728 | -67.8477 | -53.9718 | -51.1638 | -55.4027 | -29.4814 | -22.0418 | 73.9979 | -19.8645 | 39.7229 | -21.867 | -14.0156 | -26.5078 | 86.2922 | -18.9201 | 82.508 | -19.9173 | 53.1744 | -20.2529 | 49.7767 | -29.6716 | 79.6639 | -43.9233 | -45.2947 | -53.6478 | -50.4506 | -60.5405 | -60.8494 | -42.7569 | -44.5697 | -48.1729 | -50.9756 | -50.667 | -59.9876 | -40.775 | 252 | -39.6511 | -42.0256 | -40.32 | -40.8333 | -38.5082 | -43.2775 | -43.0721 | -40.1011 | 252 | -41.2445 | -44.8477 | -47.1254 | -57.4125 | -57.7214 | -39.3904 | -41.4417 | -44.8064 | -47.3784 | -57.174 | -57.7772 | -39.6847 | -41.9695 | -50.3226 | -47.6504 | -47.539 | -56.8596 | -37.4085 | -42.1667 | -50.2813 | -47.9034 | -47.3005 | -56.9154 | -37.7028
253 | -3.3305 | 0 | -3.1313 | 0 | -3.3657 | 0 | -3.0962 | 0 | -49.6393 | 176.9625 | -43.2886 | 44.1653 | -41.7486 | -117.4925 | -44.7538 | -2.3221 | -58.5183 | -0.1374 | -46.3118 | 89.6346 | -48.4474 | 124.7443 | -42.2161 | 8.4231 | -40.144 | 171.6567 | -48.6629 | -86.9908 | -53.1624 | -66.9633 | -59.6356 | -60.224 | -21.9577 | 55.5298 | -19.6189 | 25.129 | -22.766 | -32.9649 | -23.5641 | 92.2938 | -18.463 | 77.3373 | -20.3028 | 37.9953 | -20.926 | 41.1851 | -24.6947 | 74.9143 | -44.5282 | -45.8797 | -53.4774 | -50.8797 | -62.743 | -60.743 | -43.0532 | -44.6274 | -47.2602 | -50.8384 | -50.4126 | -59.8774 | -40.7743 | 253 | -39.0442 | -43.3971 | -39.8404 | -40.3791 | -37.6683 | -44.8504 | -41.2653 | -39.8862 | 253 | -41.2969 | -43.9297 | -47.5492 | -59.6117 | -57.6117 | -39.6875 | -41.4961 | -43.8945 | -47.7835 | -59.3773 | -57.6468 | -39.957 | -42.5492 | -50.1469 | -47.5079 | -47.2813 | -56.7461 | -37.4086 | -42.7484 | -50.1117 | -47.7422 | -47.0469 | -56.7812 | -37.6781
254 | -3.3434 | 0 | -3.1317 | 0 | -3.3788 | 0 | -3.1414 | 0 | -53.9445 | 158.5847 | -41.3856 | 40.1148 | -41.6624 | -133.6885 | -45.9533 | -9.6403 | -57.2737 | -27.5708 | -45.9908 | 86.3066 | -51.309 | 114.1898 | -39.841 | -4.2529 | -40.1417 | 161.4762 | -50.8576 | -107.6312 | -52.7292 | -81.6264 | -63.2269 | -126.2552 | -22.5908 | 34.0854 | -19.7661 | 10.848 | -24.4963 | -53.6937 | -21.2148 | 87.5284 | -18.3178 | 72.8213 | -21.1919 | 22.2757 | -21.9255 | 36.2394 | -21.8116 | 63.271 | -45.091 | -46.4006 | -53.3847 | -51.2785 | -65.7551 | -61.0842 | -43.3583 | -44.9101 | -46.8161 | -50.6825 | -50.3661 | -59.1054 | -40.7992 | 254 | -38.3889 | -45.0451 | -39.0922 | -40.2117 | -36.8211 | -46.7902 | -39.4918 | -39.8885 | 254 | -41.5667 | -43.4727 | -47.9351 | -62.6234 | -57.9525 | -39.9795 | -41.7784 | -43.4373 | -48.1371 | -62.3763 | -57.9428 | -40.2169 | -43.0572 | -50.0413 | -47.3391 | -47.2344 | -55.9737 | -37.4204 | -43.2689 | -50.0059 | -47.5411 | -46.9873 | -55.964 | -37.6578
255 | -3.3642 | 0 | -3.1082 | 0 | -3.3715 | 0 | -3.1649 | 0 | -62.2023 | 140.3884 | -39.8535 | 32.9879 | -41.8363 | -150.6977 | -47.4919 | -14.0779 | -56.4713 | -54.3697 | -45.7853 | 82.2414 | -55.2918 | 111.2637 | -38.1834 | -17.2685 | -40.4103 | 151.7225 | -53.89 | -133.3338 | -52.4535 | -93.6468 | -59.2202 | 165.2104 | -24.2364 | 10.4068 | -20.4957 | -2.5927 | -27.5856 | -79.6997 | -19.5698 | 79.5393 | -18.3461 | 70.1573 | -22.733 | 7.4672 | -22.9382 | 37.9205 | -20.1046 | 51.2601 | -45.6573 | -46.8151 | -53.1243 | -51.6065 | -70.669 | -61.5378 | -43.5574 | -45.3402 | -46.5322 | -50.6355 | -50.5066 | -58.1684 | -40.7099 | 255 | -37.707 | -46.8462 | -38.308 | -40.2611 | -36.0928 | -48.9538 | -38.035 | -40.0937 | 255 | -41.976 | -43.168 | -48.2423 | -67.5608 | -58.4296 | -40.1859 | -42.232 | -43.1607 | -48.4416 | -67.2975 | -58.3729 | -40.3925 | -43.4509 | -49.7601 | -47.2713 | -47.3984 | -55.0602 | -37.3384 | -43.7069 | -49.7528 | -47.4706 | -47.1351 | -55.0035 | -37.545
256 | -3.37 | 0 | -3.0957 | 0 | -3.387 | 0 | -3.1929 | 0 | -69.1593 | -52.2819 | -38.6904 | 23.3895 | -42.4653 | -167.4412 | -49.1243 | -13.0843 | -56.389 | -80.0876 | -45.5343 | 77.6061 | -59.6948 | 130.495 | -36.9709 | -31.1983 | -40.8037 | 143.162 | -57.5827 | -173.9564 | -52.2634 | -105.8224 | -55.3834 | 136.5802 | -26.669 | -24.3909 | -21.7642 | -15.0017 | -32.183 | -121.7866 | -18.8009 | 67.8579 | -18.3903 | 68.3868 | -25.1153 | -8.0153 | -23.4619 | 43.0332 | -19.15 | 37.5407 | -46.0432 | -46.9009 | -52.7394 | -51.7932 | -85.4143 | -61.7993 | -43.6738 | -45.8362 | -46.3973 | -50.705 | -50.8144 | -57.3245 | -40.4872 | 256 | -37.167 | -48.341 | -37.5599 | -40.6076 | -35.4509 | -50.577 | -36.8717 | -40.365 | 256 | -42.4662 | -43.0273 | -48.4232 | -82.3186 | -58.7036 | -40.2868 | -42.7405 | -43.0103 | -48.6003 | -82.0273 | -58.6064 | -40.4809 | -43.5309 | -49.3694 | -47.335 | -47.7187 | -54.2288 | -37.1002 | -43.8052 | -49.3524 | -47.5121 | -47.4274 | -54.1316 | -37.2943
257 | -3.3892 | 0 | -3.0845 | 0 | -3.3892 | 0 | -3.2134 | 0 | -57.7248 | -70.689 | -37.8178 | 12.9354 | -43.5397 | 176.7419 | -50.076 | -6.4632 | -56.9166 | -105.3177 | -45.3344 | 72.0347 | -59.0213 | 165.9991 | -36.2088 | -45.2512 | -41.2437 | 136.2356 | -58.488 | 124.2474 | -52.3542 | -117.0963 | -52.7498 | 115.1226 | -28.5747 | -78.1676 | -23.7341 | -25.0199 | -33.7514 | 160.5751 | -18.3502 | 57.2091 | -18.1183 | 70.319 | -29.1868 | -24.039 | -23.1438 | 50.2464 | -18.9566 | 24.0412 | -46.2077 | -46.4577 | -52.2312 | -51.8874 | -73.5945 | -61.4382 | -43.7095 | -46.2642 | -46.3462 | -50.8618 | -51.272 | -56.5767 | -40.1262 | 257 | -36.7524 | -48.6809 | -36.8955 | -41.2162 | -35.0066 | -50.7137 | -36.0885 | -40.6438 | 257 | -42.875 | -42.957 | -48.4982 | -70.51 | -58.3537 | -40.3203 | -43.1797 | -42.957 | -48.674 | -70.2053 | -58.2248 | -40.4961 | -43.0685 | -48.842 | -47.4726 | -48.1875 | -53.4922 | -36.737 | -43.3732 | -48.842 | -47.6484 | -47.8828 | -53.3633 | -36.9128
258 | -3.4274 | 0 | -3.087 | 0 | -3.4033 | 0 | -3.216 | 0 | -53.6558 | -85.6098 | -37.213 | 2.0907 | -45.2553 | 162.5378 | -49.7547 | 1.0244 | -58.1161 | -132.3241 | -45.4374 | 67.4938 | -55.5791 | 174.6311 | -35.7898 | -60.2874 | -41.6198 | 130.1099 | -55.0707 | 76.266 | -52.4882 | -128.3721 | -51.2557 | 97.7175 | -26.2106 | -136.0215 | -26.7385 | -28.6368 | -29.0517 | 106.368 | -18.4019 | 46.7846 | -17.5211 | 71.4267 | -37.2515 | -46.2148 | -22.1189 | 53.1267 | -19.274 | 9.0935 | -46.1516 | -45.6593 | -51.8084 | -51.9367 | -66.3313 | -60.5929 | -43.6651 | -46.6299 | -46.3024 | -51.0167 | -51.8721 | -55.9189 | -39.6365 | 258 | -36.4955 | -47.8427 | -36.3988 | -42.2219 | -34.7459 | -49.3864 | -35.6186 | -40.8621 | 258 | -43.2025 | -42.875 | -48.5093 | -63.2443 | -57.5059 | -40.2618 | -43.5429 | -42.8991 | -48.7207 | -62.928 | -57.3769 | -40.4491 | -42.2319 | -48.381 | -47.5893 | -48.7851 | -52.8319 | -36.2332 | -42.5723 | -48.4051 | -47.8007 | -48.4688 | -52.7029 | -36.4205
259 | -3.4591 | 0 | -3.089 | 0 | -3.4122 | 0 | -3.2131 | 0 | -51.4035 | -100.2533 | -36.9072 | -9.8776 | -47.8722 | 150.938 | -48.7611 | 3.0103 | -59.9075 | -162.2594 | -45.6454 | 63.4882 | -53.225 | 168.9242 | -35.7471 | -74.1391 | -41.926 | 124.9064 | -51.7696 | 47.6346 | -52.7275 | -138.636 | -49.7434 | 81.7022 | -22.4955 | -172.7541 | -30.1372 | -17.087 | -25.5238 | 76.513 | -18.9525 | 36.9065 | -16.6057 | 70.4008 | -40.7872 | 139.1996 | -20.911 | 52.6245 | -20.2102 | -5.7525 | -46.0598 | -44.8323 | -51.5706 | -52.095 | -62.4075 | -59.6604 | -43.6202 | -46.7794 | -46.3224 | -51.0773 | -52.5695 | -55.3029 | -39.0674 | 259 | -36.4322 | -46.6633 | -36.1191 | -43.5067 | -34.7471 | -47.7602 | -35.4743 | -40.9623 | 259 | -43.3203 | -42.8633 | -48.6359 | -59.3185 | -56.5714 | -40.208 | -43.6904 | -42.9102 | -48.8819 | -58.9953 | -56.4473 | -40.4071 | -41.3732 | -48.1115 | -47.6182 | -49.4805 | -52.2139 | -35.6552 | -41.7433 | -48.1584 | -47.8642 | -49.1573 | -52.0898 | -35.8543
260 | -3.496 | 0 | -3.0942 | 0 | -3.4366 | 0 | -3.2034 | 0 | -49.9871 | -115.215 | -36.9264 | -21.4002 | -51.8665 | 145.376 | -47.753 | 0.2693 | -62.4904 | 162.4527 | -46.4085 | 60.5617 | -51.7519 | 159.2669 | -36.0416 | -88.5296 | -42.2015 | 120.938 | -49.4503 | 25.7924 | -52.948 | -148.5286 | -48.8585 | 67.5326 | -19.5567 | 161.2272 | -30.4382 | 13.8618 | -23.3852 | 53.1382 | -19.9417 | 28.8471 | -15.4523 | 68.8469 | -30.6481 | 116.525 | -20.0691 | 48.1804 | -22.0527 | -20.4878 | -45.8306 | -44.2355 | -51.5371 | -52.2642 | -59.8345 | -59.0402 | -43.5902 | -46.6631 | -46.4179 | -51.1762 | -53.2582 | -54.8233 | -38.4473 | 260 | -36.5862 | -45.6273 | -36.1515 | -45.2384 | -35.0071 | -46.3635 | -35.636 | -41.0616 | 260 | -43.1671 | -42.9219 | -48.7682 | -56.7403 | -55.946 | -40.1536 | -43.5689 | -42.9813 | -49.0608 | -56.3979 | -55.8368 | -40.3868 | -40.7395 | -48.0411 | -47.6802 | -50.164 | -51.7291 | -35.0107 | -41.1413 | -48.1005 | -47.9728 | -49.8216 | -51.6199 | -35.2439
261 | -3.5415 | 0 | -3.0962 | 0 | -3.4595 | 0 | -3.19 | 0 | -49.1581 | -130.2934 | -37.2758 | -33.3257 | -57.48 | 166.2757 | -46.916 | -5.1005 | -64.9595 | 114.3811 | -47.0887 | 59.2849 | -50.9645 | 147.0097 | -36.6958 | -101.9122 | -42.3489 | 116.7616 | -47.8182 | 6.3908 | -53.1808 | -159.4434 | -48.0605 | 54.7669 | -17.4786 | 139.6522 | -27.1811 | 27.5771 | -22.2512 | 30.8007 | -21.3966 | 23.3581 | -14.5708 | 61.8914 | -26.8948 | 98.8862 | -19.7045 | 39.7633 | -24.9248 | -37.6159 | -45.7389 | -43.9146 | -51.7467 | -52.4654 | -57.8873 | -58.6138 | -43.6158 | -46.3345 | -46.5806 | -51.2954 | -53.9517 | -54.5298 | -37.8687 | 261 | -36.9643 | -44.8412 | -36.437 | -46.6444 | -35.5248 | -45.325 | -36.0878 | -41.0423 | 261 | -42.793 | -43.0391 | -48.9239 | -54.7911 | -55.5176 | -40.1563 | -43.2383 | -43.1211 | -49.2754 | -54.4278 | -55.4238 | -40.4258 | -40.3731 | -48.2052 | -47.7539 | -50.8555 | -51.4336 | -34.4092 | -40.8184 | -48.2872 | -48.1054 | -50.4922 | -51.3398 | -34.6787
262 | -3.585 | 0 | -3.134 | 0 | -3.4733 | 0 | -3.1955 | 0 | -48.8012 | -145.2253 | -37.9607 | -43.5921 | -54.8672 | -144.85 | -46.2801 | -11.4948 | -65.2943 | 54.0882 | -47.7596 | 62.4548 | -50.5443 | 134.465 | -37.7037 | -113.9963 | -42.3605 | 113.2752 | -46.7521 | -10.6029 | -53.3689 | -168.4399 | -47.8354 | 43.3799 | -16.0381 | 120.6047 | -24.4153 | 25.15 | -21.9578 | 9.822 | -23.0681 | 24.8836 | -13.8146 | 55.3031 | -24.5335 | 83.2511 | -19.567 | 35.2 | -30.4317 | -57.3205 | -45.6359 | -43.8581 | -52.3097 | -52.6906 | -56.3234 | -58.3346 | -43.6418 | -45.9694 | -46.9054 | -51.4035 | -54.7668 | -54.3444 | -37.3318 | 262 | -37.5358 | -44.3151 | -36.9847 | -46.9236 | -36.2604 | -44.6155 | -36.8347 | -41.0163 | 262 | -42.3844 | -43.3204 | -49.1056 | -53.1894 | -55.2006 | -40.1685 | -42.8354 | -43.4321 | -49.4951 | -52.8501 | -55.1391 | -40.4463 | -40.2731 | -48.7247 | -47.8185 | -51.6328 | -51.2104 | -33.8585 | -40.7241 | -48.8364 | -48.208 | -51.2935 | -51.1489 | -34.1363
263 | -3.6139 | 0 | -3.1484 | 0 | -3.4897 | 0 | -3.1954 | 0 | -48.8475 | -160.7102 | -39.0095 | -52.8133 | -49.8697 | -141.8345 | -45.7344 | -19.865 | -62.5576 | 9.5757 | -47.3593 | 65.9705 | -50.5258 | 120.6901 | -39.179 | -124.5998 | -42.2636 | 109.6904 | -46.1381 | -27.2933 | -53.4386 | -178.8632 | -47.8858 | 34.265 | -15.203 | 101.6711 | -22.409 | 15.5946 | -22.2817 | -13.379 | -24.2236 | 31.7562 | -13.3224 | 47.4131 | -23.277 | 68.066 | -19.8576 | 30.1022 | -44.5476 | -135.0417 | -45.5448 | -44.0854 | -53.0533 | -52.8222 | -55.0331 | -58.0463 | -43.6679 | -45.728 | -47.403 | -51.4179 | -55.6874 | -54.0639 | -36.8405 | 263 | -38.2693 | -43.9473 | -37.6779 | -45.342 | -37.2343 | -44.234 | -37.9206 | -40.9593 | 263 | -42.1141 | -43.7891 | -49.2083 | -51.8847 | -54.8979 | -40.1782 | -42.5796 | -43.9133 | -49.6268 | -51.5434 | -54.8509 | -40.4725 | -40.4715 | -49.4394 | -47.804 | -52.539 | -50.9155 | -33.3508 | -40.937 | -49.5636 | -48.2225 | -52.1977 | -50.8685 | -33.6451
264 | -3.6306 | 0 | -3.1628 | 0 | -3.493 | 0 | -3.1925 | 0 | -49.2899 | -176.2436 | -40.4638 | -59.5011 | -46.5386 | -150.973 | -45.3776 | -28.1405 | -60.319 | -22.6284 | -46.3985 | 68.3852 | -50.7877 | 106.4084 | -41.2275 | -132.1595 | -41.9986 | 105.6404 | -45.9051 | -43.4903 | -53.5603 | 169.5054 | -48.2441 | 25.7995 | -14.7965 | 84.3016 | -21.2693 | 3.994 | -23.2936 | -38.2998 | -23.9594 | 41.7962 | -13.1645 | 39.2705 | -22.7105 | 53.6498 | -20.3651 | 28.5503 | -31.3936 | 115.6305 | -45.4889 | -44.6316 | -53.9294 | -52.9303 | -53.9772 | -57.5535 | -43.6941 | -45.743 | -48.1267 | -51.2683 | -56.8894 | -53.6336 | -36.4571 | 264 | -39.0715 | -43.7992 | -38.4839 | -43.3691 | -38.3317 | -44.1544 | -39.3541 | -40.8352 | 264 | -42.1124 | -44.4961 | -49.2997 | -50.8144 | -54.3907 | -40.2011 | -42.5802 | -44.6337 | -49.7378 | -50.4842 | -54.361 | -40.5016 | -41.001 | -50.2988 | -47.6377 | -53.7266 | -50.4708 | -32.9641 | -41.4688 | -50.4364 | -48.0758 | -53.3964 | -50.4411 | -33.2646
265 | -3.6353 | 0 | -3.1783 | 0 | -3.5064 | 0 | -3.2017 | 0 | -50.1004 | 168.7907 | -42.2048 | -61.343 | -44.3327 | -164.4475 | -45.034 | -37.8607 | -59.7151 | -46.0192 | -44.8074 | 65.7717 | -51.3627 | 91.1388 | -44.0166 | -133.9411 | -41.7207 | 100.0522 | -46.0763 | -59.7993 | -53.7755 | 156.0232 | -49.021 | 21.1776 | -14.875 | 67.1297 | -20.6643 | -8.9155 | -24.9919 | -67.5942 | -22.5831 | 48.1401 | -13.3263 | 30.562 | -22.7464 | 39.3608 | -20.8046 | 27.4387 | -25.3372 | 95.1974 | -45.434 | -45.434 | -54.8168 | -53.0395 | -53.0864 | -56.8051 | -43.6861 | -46.1079 | -49.1548 | -51.0025 | -58.5845 | -52.9517 | -36.2009 | 265 | -39.7128 | -43.7453 | -39.044 | -41.4875 | -39.4213 | -44.4153 | -41.1425 | -40.7568 | 265 | -42.4726 | -45.5195 | -49.4042 | -49.9081 | -53.6268 | -40.1797 | -42.9296 | -45.6484 | -49.8378 | -49.58 | -53.6034 | -40.4844 | -41.7987 | -51.1815 | -47.3672 | -55.4062 | -49.7734 | -32.6945 | -42.2557 | -51.3104 | -47.8008 | -55.0781 | -49.75 | -32.9992
266 | -3.6137 | 0 | -3.1828 | 0 | -3.516 | 0 | -3.23 | 0 | -51.3715 | 154.0004 | -43.7622 | -55.4839 | -42.8906 | -178.548 | -44.843 | -48.923 | -60.4185 | -68.0533 | -43.6599 | 60.4171 | -52.2105 | 75.4746 | -47.0107 | -120.8522 | -41.3968 | 94.5048 | -46.6484 | -75.0992 | -54.1395 | 139.3357 | -49.6399 | 21.7034 | -15.5408 | 51.6343 | -20.734 | -22.3613 | -27.1973 | -108.7593 | -21.0127 | 48.7934 | -13.8178 | 22.4162 | -23.3566 | 26.3581 | -20.8217 | 30.7992 | -22.2314 | 79.6296 | -45.4034 | -46.4905 | -55.346 | -53.2471 | -52.2589 | -55.6155 | -43.6672 | -46.8364 | -50.6137 | -50.6516 | -60.6711 | -51.9848 | -36.0817 | 266 | -39.968 | -43.8735 | -39.2852 | -40.2064 | -40.0695 | -45.0167 | -42.8064 | -40.594 | 266 | -43.2227 | -47 | -49.6334 | -49.0761 | -52.4327 | -40.1512 | -43.6536 | -47.0977 | -50.0171 | -48.7429 | -52.3855 | -40.4372 | -42.8768 | -51.7323 | -47.0379 | -57.4883 | -48.802 | -32.5657 | -43.3077 | -51.83 | -47.4216 | -57.1551 | -48.7548 | -32.8517
267 | -3.5666 | 0 | -3.1905 | 0 | -3.5486 | 0 | -3.2735 | 0 | -53.0863 | 139.0559 | -44.1296 | -44.6951 | -42.0622 | 165.9882 | -44.8356 | -62.4271 | -63.4334 | -85.2591 | -42.9285 | 50.5836 | -53.1901 | 58.2679 | -47.0168 | -92.1471 | -41.2474 | 86.4962 | -47.7125 | -91.4847 | -55.0538 | 117.9117 | -49.8761 | 25.774 | -16.8311 | 33.5993 | -21.2131 | -35.6414 | -27.8075 | -161.1805 | -19.7796 | 40.379 | -14.7525 | 17.029 | -24.6343 | 13.5301 | -20.2598 | 35.0898 | -20.5583 | 64.2911 | -45.3642 | -47.3317 | -55.2989 | -53.665 | -51.4775 | -54.0348 | -43.6515 | -47.9158 | -52.6838 | -50.4718 | -60.8311 | -50.7947 | -36.1143 | 267 | -39.7571 | -44.1783 | -39.121 | -39.4461 | -40.0127 | -46.046 | -43.2699 | -40.5332 | 267 | -44.3492 | -49.1172 | -50.0984 | -48.287 | -50.8443 | -40.1029 | -44.7253 | -49.1352 | -50.3915 | -47.9289 | -50.7613 | -40.378 | -43.7651 | -51.7323 | -46.9052 | -57.6406 | -47.6042 | -32.5657 | -44.1412 | -51.7503 | -47.1983 | -57.2825 | -47.5212 | -32.8408
268 | -3.5394 | 0 | -3.1835 | 0 | -3.5905 | 0 | -3.2996 | 0 | -55.283 | 125.9439 | -43.1298 | -35.3047 | -41.5885 | 150.2721 | -45.1956 | -76.5718 | -71.628 | -64.4342 | -43.2653 | 41.9406 | -54.0895 | 38.7626 | -43.6432 | -79.4033 | -41.2084 | 78.5358 | -49.3547 | -107.7845 | -56.7397 | 87.7342 | -48.6535 | 31.5527 | -19.3179 | 17.9922 | -22.4878 | -48.829 | -25.6292 | 152.2803 | -19.1469 | 34.1761 | -15.8855 | 13.6012 | -26.7075 | 2.7858 | -19.1716 | 34.6614 | -19.6083 | 49.1957 | -45.2361 | -47.2329 | -54.4865 | -54.3611 | -50.6814 | -52.2211 | -43.5624 | -49.192 | -55.7855 | -50.5233 | -57.0155 | -49.6608 | -36.3671 | 268 | -39.1731 | -44.7806 | -38.9955 | -39.3336 | -39.1069 | -47.5399 | -41.6459 | -40.3875 | 268 | -45.6526 | -52.2461 | -50.8217 | -47.4979 | -49.0376 | -39.9719 | -46.0085 | -52.195 | -51.0615 | -47.0909 | -48.9215 | -40.2628 | -43.6935 | -50.9471 | -46.9839 | -53.832 | -46.4773 | -32.7766 | -44.0494 | -50.896 | -47.2237 | -53.425 | -46.3612 | -33.0675
269 | -3.5298 | 0 | -3.1899 | 0 | -3.6469 | 0 | -3.3188 | 0 | -57.5234 | 112.3259 | -41.5126 | -32.4369 | -41.746 | 133.5012 | -46.0037 | -92.9602 | -60.7684 | 2.1585 | -44.3506 | 34.5904 | -54.2641 | 15.4428 | -40.5935 | -80.9569 | -41.5125 | 70.8409 | -51.9022 | -125.0148 | -59.3434 | 37.3358 | -46.7139 | 28.2565 | -23.9932 | 3.0322 | -24.4479 | -59.7484 | -23.1364 | 118.3877 | -18.8521 | 23.8131 | -17.1058 | 16.5597 | -30.0641 | -3.1329 | -18.045 | 30.6983 | -19.3722 | 36.3687 | -45.0901 | -45.9846 | -52.9925 | -55.3792 | -49.844 | -50.4886 | -43.3344 | -49.8618 | -58.4907 | -50.9048 | -52.5298 | -48.7446 | -36.7283 | 269 | -38.5619 | -45.5746 | -38.7808 | -39.8106 | -37.9166 | -49.4452 | -39.3933 | -40.3121 | 269 | -46.332 | -54.9609 | -51.8494 | -46.6541 | -47.2987 | -39.6875 | -46.6719 | -54.8438 | -52.0604 | -46.1971 | -47.1698 | -40.0156 | -42.4548 | -49.4627 | -47.375 | -49.3399 | -45.5547 | -33.0814 | -42.7947 | -49.3456 | -47.586 | -48.8829 | -45.4258 | -33.4095
270 | -3.5647 | 0 | -3.2121 | 0 | -3.6935 | 0 | -3.3185 | 0 | -58.9566 | 86.6998 | -39.8489 | -34.8941 | -42.5905 | 119.5698 | -47.2091 | -108.2186 | -52.4239 | -23.821 | -45.8877 | 38.2675 | -53.0758 | -17.0563 | -38.285 | -88.8902 | -41.9287 | 67.8101 | -56.2241 | -148.0875 | -58.2458 | -47.3649 | -44.8975 | 19.7214 | -39.2966 | 4.6901 | -27.6422 | -66.579 | -21.2344 | 92.5928 | -19.0657 | 13.5713 | -17.6359 | 26.6454 | -34.9732 | 6.2822 | -17.0981 | 23.9157 | -19.7842 | 24.7291 | -45.1943 | -44.2343 | -51.0665 | -56.4834 | -49.2177 | -49.0077 | -42.7433 | -49.0958 | -53.7054 | -51.2355 | -48.7668 | -48.4005 | -35.9623 | 270 | -37.9619 | -45.8487 | -38.2877 | -40.6261 | -36.6256 | -50.551 | -37.3711 | -40.087 | 270 | -45.5311 | -50.1407 | -52.9187 | -46.0056 | -45.7956 | -39.0498 | -45.8837 | -50.0119 | -53.1649 | -45.5242 | -45.6892 | -39.4248 | -40.6696 | -47.5018 | -47.6708 | -45.5547 | -45.1884 | -32.2688 | -41.0222 | -47.373 | -47.917 | -45.0733 | -45.082 | -32.6438
271 | -3.6392 | 0 | -3.2134 | 0 | -3.7555 | 0 | -3.3429 | 0 | -58.8537 | 21.7072 | -38.4108 | -40.7622 | -43.5934 | 114.3468 | -48.7529 | -127.1293 | -48.0758 | -64.715 | -44.8717 | 45.7402 | -51.4749 | -64.2424 | -36.5838 | -100.3096 | -41.2452 | 66.2763 | -66.8755 | 145.2808 | -53.3215 | -119.9242 | -43.8231 | 4.9691 | -26.6452 | 141.2944 | -31.9711 | -56.4349 | -19.844 | 72.2122 | -19.8118 | 4.8035 | -16.707 | 36.1252 | -37.4219 | 39.0661 | -16.5267 | 14.6926 | -20.4318 | 10.762 | -46.68 | -42.4135 | -49.5979 | -57.9222 | -49.9378 | -48.2807 | -42.1587 | -47.0524 | -48.9712 | -51.7056 | -46.7447 | -48.9469 | -35.4736 | 271 | -37.2307 | -45.1995 | -37.2106 | -40.3686 | -35.203 | -49.2154 | -35.8292 | -39.1652 | 271 | -43.4132 | -45.332 | -54.283 | -46.7244 | -45.0673 | -38.4032 | -43.839 | -45.2157 | -54.5793 | -46.1823 | -44.9378 | -38.8158 | -38.7743 | -45.9587 | -48.0664 | -43.5313 | -45.7335 | -31.7181 | -39.2001 | -45.8424 | -48.3627 | -42.9892 | -45.604 | -32.1307
272 | -3.7164 | 0 | -3.2096 | 0 | -3.7933 | 0 | -3.321 | 0 | -56.2979 | -52.9997 | -37.0741 | -47.5221 | -43.0619 | 108.1098 | -51.7596 | -147.1664 | -47.7922 | -105.3624 | -43.3277 | 41.0832 | -51.5999 | -112.1712 | -35.3889 | -113.6561 | -40.1918 | 57.1596 | -60.2052 | 26.546 | -51.7362 | -171.9999 | -43.7097 | -5.0256 | -19.4918 | 128.1939 | -33.2962 | -20.1335 | -19.059 | 54.1004 | -20.9704 | -2.3458 | -14.9213 | 37.9449 | -34.4011 | 72.6463 | -16.2733 | 3.2095 | -21.8855 | -1.6028 | -49.5145 | -40.84 | -49.9371 | -60.2156 | -53.364 | -48.3711 | -42.7798 | -44.8272 | -47.7965 | -53.7961 | -47.6949 | -49.3949 | -35.8734 | 272 | -36.0571 | -45.9109 | -36.0329 | -39.488 | -34.07 | -48.3633 | -34.78 | -38.3879 | 272 | -41.1108 | -44.0801 | -56.4992 | -50.1544 | -45.1615 | -38.9865 | -41.6176 | -44.0032 | -56.8946 | -49.5707 | -45.0501 | -39.4588 | -37.1236 | -46.2207 | -50.0797 | -44.4853 | -46.1853 | -32.0801 | -37.6304 | -46.1438 | -50.4751 | -43.9016 | -46.0739 | -32.5524
273 | -3.8167 | 0 | -3.2191 | 0 | -3.8069 | 0 | -3.2894 | 0 | -54.4294 | -101.789 | -35.9741 | -57.9775 | -42.9755 | 94.5941 | -55.8381 | -159.8792 | -49.3493 | -136.3104 | -42.8928 | 33.5241 | -52.9958 | -147.978 | -34.7337 | -127.427 | -40.1152 | 44.9129 | -55.1644 | 3.5496 | -52.3361 | 151.9822 | -44.0296 | -12.7157 | -15.8652 | 112.5665 | -29.7991 | 0.4961 | -18.6803 | 35.3749 | -22.7154 | -8.5729 | -13.2378 | 34.5369 | -30.304 | 77.9178 | -16.4423 | -8.2653 | -24.7007 | -10.5007 | -50.4823 | -39.9064 | -51.204 | -60.6734 | -58.4464 | -48.5312 | -43.889 | -43.1747 | -48.2816 | -55.4018 | -50.0542 | -49.2677 | -36.6159 | 273 | -35.1329 | -47.4885 | -35.1333 | -39.4543 | -33.5791 | -48.5695 | -34.2158 | -38.4539 | 273 | -39.358 | -44.4649 | -56.8567 | -55.2273 | -45.3121 | -40.0821 | -39.9556 | -44.4747 | -57.384 | -54.6395 | -45.2418 | -40.5996 | -36.0897 | -47.3873 | -51.5851 | -46.8351 | -46.0486 | -32.809 | -36.6873 | -47.3971 | -52.1124 | -46.2473 | -45.9783 | -33.3265
274 | -3.9081 | 0 | -3.2297 | 0 | -3.8098 | 0 | -3.2774 | 0 | -53.7338 | -133.2122 | -35.2089 | -69.6761 | -43.6266 | 81.7239 | -59.7166 | -164.9879 | -51.6852 | -157.2466 | -42.9865 | 25.4375 | -54.976 | -172.2651 | -34.4368 | -141.2574 | -40.5344 | 33.3768 | -52.3271 | -5.1073 | -53.6579 | 126.6105 | -44.0877 | -19.2408 | -13.5619 | 97.2722 | -26.4983 | -0.5521 | -18.8139 | 17.6391 | -25.3044 | -8.3355 | -11.8143 | 26.8121 | -27.6624 | 70.3411 | -16.9531 | -20.4771 | -28.6381 | -10.4976 | -49.9423 | -39.374 | -52.6559 | -58.8994 | -64.5087 | -48.6513 | -44.8196 | -42.0637 | -48.994 | -54.6164 | -52.5227 | -49.1887 | -37.5628 | 274 | -34.5718 | -49.1779 | -34.5257 | -39.9808 | -33.4523 | -48.7488 | -33.9267 | -38.8027 | 274 | -38.1556 | -45.0859 | -54.9913 | -61.279 | -45.4216 | -41.0098 | -38.834 | -45.1842 | -55.622 | -60.6989 | -45.3739 | -41.5422 | -35.4659 | -48.7478 | -50.7083 | -49.293 | -45.959 | -33.753 | -36.1443 | -48.8461 | -51.339 | -48.7129 | -45.9113 | -34.2854
275 | -4.0201 | 0 | -3.2593 | 0 | -3.7896 | 0 | -3.2858 | 0 | -54.0034 | -156.7841 | -34.8089 | -82.4414 | -44.9082 | 71.1824 | -61.382 | -175.4427 | -54.358 | -172.6206 | -43.445 | 20.4786 | -57.3381 | 174.1373 | -34.3937 | -154.1606 | -41.1292 | 25.33 | -49.6547 | -11.8541 | -55.3981 | 108.5014 | -44.2696 | -21.9479 | -12.0111 | 82.1207 | -24.3288 | -10.2101 | -19.4906 | -0.4304 | -27.8237 | 9.1796 | -10.8791 | 18.0542 | -26.2562 | 61.9451 | -18.1288 | -32.1468 | -33.6019 | 31.4278 | -49.2649 | -39.1077 | -54.4475 | -56.5305 | -71.1828 | -48.7288 | -45.4976 | -41.1959 | -49.6529 | -52.2359 | -54.4937 | -49.3678 | -38.2926 | 275 | -34.3565 | -50.772 | -34.2433 | -40.9043 | -33.5403 | -48.0803 | -33.8526 | -39.3032 | 275 | -37.1758 | -45.6328 | -52.5104 | -67.9235 | -45.4695 | -41.708 | -37.9366 | -45.8633 | -53.2447 | -67.3932 | -45.443 | -42.2118 | -35.0876 | -50.4274 | -48.2158 | -51.2344 | -46.1085 | -34.503 | -35.8484 | -50.6579 | -48.9501 | -50.7041 | -46.082 | -35.0068
276 | -4.0947 | 0 | -3.2602 | 0 | -3.7788 | 0 | -3.2917 | 0 | -55.1843 | -175.8971 | -34.7819 | -95.864 | -46.363 | 66.0675 | -61.2049 | 151.7101 | -57.4637 | 178.4462 | -44.4342 | 21.0447 | -60.0456 | 173.6976 | -34.556 | -166.651 | -41.7762 | 18.2337 | -47.4182 | -21.3422 | -57.5606 | 96.8262 | -44.577 | -22.6257 | -11.0345 | 67.3839 | -23.0241 | -22.7904 | -20.8779 | -18.6054 | -26.9326 | 32.3938 | -10.2612 | 8.0621 | -25.5106 | 51.4643 | -20.0734 | -42.2172 | -28.7108 | 71.9542 | -48.676 | -38.9563 | -56.8268 | -54.4025 | -69.926 | -48.6555 | -45.8501 | -40.5249 | -50.3877 | -50.0376 | -55.8345 | -49.6968 | -38.3285 | 276 | -34.4533 | -52.5322 | -34.3263 | -42.1523 | -33.7915 | -46.806 | -33.9443 | -39.8698 | 276 | -36.4302 | -46.293 | -50.3078 | -66.6658 | -45.3953 | -42.0713 | -37.2647 | -46.6089 | -51.1108 | -66.1472 | -45.3638 | -42.5584 | -34.8616 | -52.7321 | -45.9429 | -52.5743 | -46.4366 | -34.5497 | -35.6961 | -53.048 | -46.7459 | -52.0557 | -46.4051 | -35.0368
277 | -4.1427 | 0 | -3.2833 | 0 | -3.7599 | 0 | -3.3185 | 0 | -57.3929 | 168.2458 | -35.1349 | -108.9806 | -47.6421 | 65.5277 | -58.6273 | 107.9886 | -61.2688 | -175.2417 | -44.776 | 28.913 | -62.1207 | -171.4768 | -34.9234 | -178.8736 | -42.3478 | 12.6406 | -45.5253 | -31.0571 | -59.5421 | 96.1703 | -44.1905 | -20.736 | -10.4812 | 53.2609 | -22.5708 | -37.5402 | -23.6052 | -37.292 | -24.2199 | 41.9254 | -9.9354 | -2.9553 | -25.5734 | 43.9878 | -23.1786 | -49.8912 | -24.223 | 73.8846 | -48.1131 | -38.9842 | -59.8006 | -52.5701 | -64.7029 | -48.3553 | -45.92 | -40.0607 | -51.3068 | -48.1544 | -56.5724 | -50.2208 | -37.4072 | 277 | -34.8733 | -54.0439 | -34.6696 | -42.9028 | -34.1941 | -45.2659 | -34.1119 | -40.112 | 277 | -35.918 | -47.1641 | -48.4274 | -61.4196 | -45.072 | -42.1601 | -36.7774 | -47.5469 | -49.2516 | -60.943 | -45.0368 | -42.6015 | -34.8415 | -55.6579 | -44.0117 | -53.2891 | -46.9375 | -33.6473 | -35.7009 | -56.0407 | -44.8359 | -52.8125 | -46.9023 | -34.0887
278 | -4.1427 | 0 | -3.2822 | 0 | -3.75 | 0 | -3.3396 | 0 | -61.291 | 155.0755 | -35.8976 | -121.9154 | -48.2029 | 67.8232 | -55.0599 | 68.2637 | -61.7354 | -146.1891 | -43.6225 | 38.6647 | -61.0273 | -147.2988 | -35.5335 | 169.2071 | -42.8432 | 7.3853 | -43.9831 | -43.1191 | -59.4312 | 101.9329 | -43.35 | -20.621 | -10.3502 | 39.4608 | -22.6128 | -53.0987 | -28.6575 | -59.0107 | -21.9577 | 38.7891 | -9.9507 | -13.902 | -25.9185 | 35.5109 | -28.1549 | -45.3667 | -21.6335 | 67.233 | -47.5808 | -39.1969 | -62.5545 | -51.0378 | -60.823 | -47.7243 | -45.6377 | -39.8281 | -52.67 | -46.4736 | -57.2432 | -51.0117 | -36.0182 | 278 | -35.6376 | -53.4367 | -35.1752 | -42.2752 | -34.7831 | -43.7784 | -34.3667 | -40.0288 | 278 | -35.6854 | -48.5273 | -46.8951 | -57.5408 | -44.4421 | -41.8877 | -36.5459 | -48.92 | -47.6982 | -57.073 | -44.3847 | -42.2981 | -35.0542 | -58.4118 | -42.3309 | -53.961 | -47.7295 | -32.2682 | -35.9147 | -58.8045 | -43.134 | -53.4932 | -47.6721 | -32.6786
279 | -4.0885 | 0 | -3.2879 | 0 | -3.7574 | 0 | -3.3786 | 0 | -70.75 | 151.0126 | -37.1039 | -133.8902 | -48.0844 | 68.8846 | -52.233 | 33.572 | -58.1819 | -136.5703 | -41.353 | 38.3847 | -57.6405 | -136.0663 | -36.4123 | 157.6569 | -43.2148 | 2.7936 | -42.7575 | -56.0687 | -57.4707 | 99.5848 | -42.0041 | -23.6834 | -10.5182 | 25.4476 | -23.3992 | -70.1502 | -45.6847 | -131.7227 | -20.461 | 31.0643 | -10.2274 | -25.1231 | -26.9553 | 33.248 | -30.7497 | -0.6999 | -19.9484 | 56.3752 | -47.0591 | -39.5911 | -62.4261 | -49.7505 | -57.5825 | -46.6614 | -45.1004 | -39.8121 | -54.4479 | -45.0066 | -58.6941 | -51.9801 | -34.5569 | 279 | -36.7688 | -51.201 | -35.6222 | -40.4433 | -35.5617 | -42.4788 | -34.6285 | -39.4874 | 279 | -35.7236 | -50.3594 | -45.662 | -54.2946 | -43.3735 | -41.343 | -36.5242 | -50.6905 | -46.3719 | -53.8251 | -43.2828 | -41.7218 | -35.5026 | -58.3376 | -40.9181 | -55.4062 | -48.6922 | -30.7995 | -36.3032 | -58.6687 | -41.628 | -54.9367 | -48.6015 | -31.1783
280 | -4.0102 | 0 | -3.2825 | 0 | -3.7647 | 0 | -3.4264 | 0 | -67.8325 | -64.8831 | -38.8156 | -142.4688 | -47.5669 | 69.6093 | -50.6874 | 0.9616 | -55.291 | -148.847 | -39.355 | 30.0514 | -54.0959 | -136.9601 | -37.6271 | 146.9608 | -43.4934 | -0.6249 | -41.9431 | -69.9077 | -55.3612 | 84.3503 | -40.7213 | -30.0546 | -11.0895 | 12.2396 | -24.8259 | -89.4176 | -29.2522 | 102.9175 | -19.5333 | 19.9525 | -10.88 | -36.0678 | -27.8175 | 33.0089 | -25.8089 | 25.6591 | -19.0297 | 45.1419 | -46.6201 | -40.2468 | -60.0939 | -48.7919 | -54.9911 | -45.2546 | -44.509 | -40.0537 | -56.7251 | -43.8957 | -62.1809 | -52.9756 | -33.2476 | 280 | -38.2673 | -49.3337 | -35.9193 | -38.6493 | -36.5496 | -41.5038 | -34.9306 | -38.783 | 280 | -36.0435 | -52.7149 | -44.7817 | -51.7086 | -41.9721 | -40.7443 | -36.7712 | -52.9604 | -45.3655 | -51.2264 | -41.8282 | -41.0826 | -36.2366 | -56.0837 | -39.8855 | -58.8984 | -49.6931 | -29.4829 | -36.9643 | -56.3292 | -40.4693 | -58.4162 | -49.5492 | -29.8212
281 | -3.9159 | 0 | -3.2831 | 0 | -3.7831 | 0 | -3.4589 | 0 | -58.3448 | -73.479 | -40.9366 | -148.0225 | -46.8575 | 67.416 | -50.8475 | -32.4038 | -54.1263 | -170.5847 | -38.1861 | 16.2681 | -51.0841 | -146.6026 | -39.3463 | 136.8961 | -43.6358 | -5.3142 | -41.6292 | -84.7191 | -53.9782 | 60.9451 | -39.7475 | -38.511 | -12.0968 | -0.4759 | -27.7494 | -109.0686 | -23.2219 | 78.609 | -19.163 | 7.5816 | -11.7536 | -46.6548 | -28.0108 | 33.0861 | -21.8996 | 21.3174 | -18.5511 | 32.736 | -46.3473 | -40.9605 | -57.9449 | -48.3238 | -53.0152 | -43.8277 | -44.037 | -40.5995 | -58.8417 | -43.3222 | -70.9433 | -53.287 | -32.1488 | 281 | -39.885 | -48.678 | -36.1858 | -37.5368 | -37.7643 | -40.9414 | -35.3618 | -38.1451 | 281 | -36.6836 | -54.9258 | -44.4079 | -49.7321 | -40.5446 | -40.2539 | -37.3164 | -55.0586 | -44.8649 | -49.2321 | -40.3688 | -40.5781 | -37.0446 | -54.029 | -39.4063 | -67.6602 | -50.0039 | -28.3657 | -37.6774 | -54.1618 | -39.8633 | -67.1602 | -49.8281 | -28.6899
282 | -3.8011 | 0 | -3.2999 | 0 | -3.7974 | 0 | -3.4642 | 0 | -53.4435 | -87.3455 | -43.3479 | -145.4528 | -45.8689 | 65.0293 | -53.2822 | -67.2896 | -54.4052 | 164.6466 | -37.9679 | 4.1277 | -48.8381 | -159.436 | -41.8192 | 131.2729 | -43.6255 | -8.3794 | -41.7226 | -96.9981 | -53.4313 | 35.1623 | -38.9062 | -46.2873 | -13.7253 | -11.5089 | -32.1051 | -139.9936 | -20.0326 | 58.1503 | -19.5615 | -4.7834 | -13.3489 | -55.196 | -27.986 | 40.4071 | -19.5124 | 10.2855 | -18.8968 | 23.1732 | -46.0828 | -41.4904 | -55.9473 | -48.4109 | -51.7508 | -42.5608 | -43.6319 | -41.4029 | -59.1878 | -43.3507 | -66.9835 | -52.2114 | -31.2801 | 282 | -41.1535 | -48.9115 | -36.765 | -37.2312 | -39.1278 | -40.7128 | -35.8224 | -37.5307 | 282 | -37.6018 | -55.3867 | -44.6098 | -48.4509 | -39.2609 | -39.8345 | -38.103 | -55.3904 | -44.9467 | -47.9534 | -39.0966 | -40.1677 | -37.6893 | -52.1462 | -39.5496 | -63.6836 | -48.9115 | -27.4827 | -38.1905 | -52.1499 | -39.8865 | -63.1861 | -48.7472 | -27.8159
283 | -3.7197 | 0 | -3.3227 | 0 | -3.8484 | 0 | -3.4654 | 0 | -50.1649 | -103.521 | -45.2142 | -132.6926 | -44.6626 | 57.9398 | -60.1118 | -114.541 | -56.3073 | 137.4892 | -38.563 | -4.9078 | -47.3704 | -175.5101 | -44.7931 | 137.1023 | -43.3881 | -12.8215 | -42.0786 | -107.9298 | -53.4653 | 7.8653 | -38.1702 | -54.044 | -16.133 | -19.1102 | -36.439 | 157.7121 | -18.3207 | 40.7053 | -20.3139 | -18.9097 | -15.3017 | -59.757 | -26.8206 | 41.8685 | -17.9376 | -4.4864 | -19.2931 | 13.4585 | -45.8243 | -41.6703 | -54.1823 | -49.0353 | -51.0665 | -41.5766 | -43.3852 | -42.5476 | -57.3525 | -44.0649 | -59.8578 | -50.3093 | -30.8505 | 283 | -41.3132 | -48.8799 | -37.688 | -37.5514 | -40.1179 | -40.7166 | -36.0638 | -36.9307 | 283 | -38.8279 | -53.6328 | -45.3156 | -47.7438 | -38.2539 | -39.5368 | -39.2249 | -53.5041 | -45.5699 | -47.2181 | -38.1112 | -39.9198 | -37.9506 | -50.4626 | -40.3452 | -56.5351 | -46.9866 | -27.0021 | -38.3476 | -50.3339 | -40.5995 | -56.0094 | -46.8439 | -27.3851
284 | -3.6761 | 0 | -3.3362 | 0 | -3.9133 | 0 | -3.4597 | 0 | -47.8996 | -120.7532 | -44.8759 | -114.0938 | -43.6928 | 48.5972 | -61.5353 | 108.0909 | -60.152 | 107.6643 | -39.1346 | -6.8907 | -46.5565 | 168.5311 | -45.8856 | 158.5819 | -43.0079 | -17.9224 | -42.4849 | -117.1134 | -53.7635 | -18.5883 | -37.3659 | -62.5521 | -19.7292 | -16.8306 | -32.3873 | 81.4261 | -17.2386 | 23.5732 | -21.939 | -33.2861 | -17.814 | -56.0645 | -25.7081 | 42.9137 | -17.1365 | -19.6101 | -20.2981 | 8.2621 | -45.58 | -41.4658 | -52.7755 | -50.2714 | -50.7519 | -40.8798 | -43.3284 | -44.179 | -55.2855 | -45.3049 | -56.4963 | -48.5852 | -31.0091 | 284 | -40.3864 | -47.4745 | -38.0885 | -37.8056 | -40.0915 | -40.8233 | -35.7573 | -36.2409 | 284 | -40.5029 | -51.6094 | -46.5953 | -47.4157 | -37.5436 | -39.4151 | -40.8428 | -51.3722 | -46.8117 | -46.8386 | -37.4201 | -39.8687 | -37.7897 | -49.0994 | -41.6288 | -53.1601 | -45.249 | -27.0958 | -38.1296 | -48.8622 | -41.8452 | -52.583 | -45.1255 | -27.5494
285 | -3.6578 | 0 | -3.3414 | 0 | -3.9703 | 0 | -3.4469 | 0 | -46.4554 | -138.4125 | -42.6014 | -104.1758 | -42.9871 | 37.0271 | -53.3602 | 58.9552 | -67.6424 | 54.2587 | -38.8382 | -5.383 | -46.3717 | 153.4318 | -43.6904 | 172.303 | -42.5084 | -25.5009 | -42.9203 | -125.1403 | -53.9708 | -44.8687 | -36.6701 | -71.0311 | -22.6367 | 10.0546 | -27.9182 | 48.5012 | -16.754 | 7.7537 | -25.065 | -51.9406 | -19.1664 | -39.3986 | -24.7786 | 38.485 | -16.9456 | -36.57 | -21.6933 | 7.7585 | -45.4759 | -41.0657 | -51.7571 | -52.1439 | -50.6751 | -40.429 | -43.4391 | -46.0563 | -53.693 | -47.1422 | -54.5524 | -47.1852 | -31.773 | 285 | -38.9339 | -45.622 | -37.2074 | -37.4205 | -39.1387 | -41.0727 | -35.0994 | -35.6003 | 285 | -42.3985 | -50.0352 | -48.4861 | -47.3337 | -37.0876 | -39.4688 | -42.7149 | -49.7227 | -48.697 | -46.7048 | -36.9821 | -39.9922 | -37.4079 | -48.0993 | -43.4844 | -51.211 | -43.8438 | -27.8027 | -37.7243 | -47.7868 | -43.6953 | -50.5821 | -43.7383 | -28.3261
286 | -3.6871 | 0 | -3.3602 | 0 | -4.0574 | 0 | -3.4447 | 0 | -45.7107 | -156.1069 | -40.1486 | -105.8101 | -42.6687 | 23.8425 | -49.7486 | 32.3336 | -64.8583 | -51.6737 | -37.6888 | -6.8001 | -46.7355 | 138.8365 | -41.1897 | 170.45 | -42.2104 | -34.9336 | -43.4363 | -132.5928 | -53.8621 | -70.2657 | -36.0237 | -81.5672 | -19.6217 | 37.0864 | -24.7969 | 26.2954 | -16.576 | -6.853 | -30.8389 | -75.6817 | -18.0035 | -22.9479 | -24.3012 | 32.2754 | -17.0673 | -54.8705 | -22.424 | 13.9208 | -45.5806 | -40.5239 | -51.1418 | -54.9751 | -50.6353 | -40.1138 | -43.7274 | -47.6473 | -52.605 | -49.5242 | -53.2156 | -46.1512 | -33.0671 | 286 | -37.5061 | -44.2283 | -35.5674 | -36.4843 | -38.0312 | -41.5093 | -34.3041 | -35.0301 | 286 | -43.9602 | -48.9179 | -51.288 | -47.2751 | -36.7536 | -39.67 | -44.2871 | -48.5476 | -51.5304 | -46.5779 | -36.6691 | -40.2827 | -36.8368 | -47.4547 | -45.8371 | -49.8554 | -42.791 | -29.0097 | -37.1637 | -47.0844 | -46.0795 | -49.1582 | -42.7065 | -29.6224
287 | -3.7513 | 0 | -3.3779 | 0 | -4.1416 | 0 | -3.4437 | 0 | -45.6037 | -173.4874 | -38.2177 | -113.8193 | -42.7206 | 11.2146 | -47.9641 | 11.9376 | -58.1639 | -88.7032 | -36.4312 | -14.7491 | -47.6312 | 127.0974 | -39.5529 | 161.2202 | -42.0806 | -45.4674 | -44.1988 | -139.6031 | -53.3403 | -96.365 | -35.5897 | -93.9612 | -16.3368 | 41.9794 | -23.5571 | 7.1428 | -16.7724 | -21.0243 | -35.1084 | 174.2457 | -15.6284 | -19.477 | -23.5987 | 22.1927 | -17.6706 | -75.7464 | -22.0907 | 23.2488 | -45.8795 | -39.8463 | -50.9444 | -59.1998 | -50.5123 | -39.8932 | -44.167 | -47.6025 | -51.9857 | -52.5888 | -51.9756 | -45.3095 | -34.7487 | 287 | -36.3506 | -43.4654 | -34.0432 | -35.491 | -37.2117 | -42.2245 | -33.7166 | -34.6515 | 287 | -43.8512 | -48.2344 | -55.4485 | -47.1344 | -36.5153 | -40.0254 | -44.2246 | -47.8441 | -55.7561 | -46.3707 | -36.4495 | -40.7233 | -36.095 | -47.1931 | -48.8375 | -48.5977 | -41.9316 | -30.6071 | -36.4684 | -46.8028 | -49.1451 | -47.834 | -41.8658 | -31.305
288 | -3.8563 | 0 | -3.3711 | 0 | -4.2506 | 0 | -3.4513 | 0 | -46.2739 | 171.5375 | -36.8439 | -125.1844 | -43.3187 | -2.5713 | -47.2953 | -5.0516 | -53.9246 | -110.7228 | -35.5026 | -24.4294 | -49.0166 | 118.9517 | -38.655 | 148.4295 | -42.4091 | -57.073 | -45.4142 | -144.4367 | -52.4085 | -124.4015 | -35.4201 | -107.2977 | -13.7674 | 35.0873 | -22.4421 | -10.6529 | -17.2768 | -35.0043 | -27.185 | 114.8546 | -13.5607 | -24.7005 | -23.6709 | 12.6706 | -18.5304 | -98.2226 | -20.7983 | 28.505 | -46.3532 | -39.0843 | -51.0259 | -61.5954 | -50.154 | -39.7796 | -44.7266 | -46.1568 | -51.7742 | -55.6992 | -50.3828 | -44.6647 | -36.799 | 288 | -35.5754 | -43.3465 | -32.9487 | -34.7848 | -36.8557 | -43.2762 | -33.4475 | -34.5564 | 288 | -42.3005 | -47.9179 | -57.7391 | -46.7829 | -36.4085 | -40.476 | -42.7857 | -47.5236 | -58.1441 | -45.9034 | -36.3283 | -41.2753 | -35.228 | -47.1696 | -51.8429 | -47.0117 | -41.2936 | -32.5484 | -35.7132 | -46.7753 | -52.2479 | -46.1322 | -41.2134 | -33.3477
289 | -3.974 | 0 | -3.3763 | 0 | -4.3724 | 0 | -3.4701 | 0 | -47.7487 | 158.681 | -35.9615 | -138.9037 | -44.5742 | -14.165 | -47.399 | -17.7193 | -50.3974 | -131.9933 | -35.0938 | -36.4407 | -50.4301 | 118.6483 | -38.3724 | 136.0896 | -42.9468 | -67.4357 | -46.9661 | -140.8493 | -51.0195 | -155.9317 | -35.622 | -120.6164 | -12.0823 | 25.3137 | -22.0743 | -28.2994 | -18.1508 | -49.8121 | -22.2521 | 95.1383 | -12.0799 | -34.1079 | -23.8248 | 3.1916 | -19.7579 | -123.9582 | -19.3966 | 26.9366 | -46.8076 | -38.2764 | -51.0146 | -56.9287 | -49.417 | -39.6787 | -45.1888 | -44.2708 | -51.9974 | -54.4193 | -48.306 | -44.3997 | -39.3308 | 289 | -35.1556 | -43.5537 | -32.3575 | -34.5164 | -36.877 | -44.3093 | -33.5694 | -34.7798 | 289 | -40.2968 | -48.0234 | -52.9547 | -46.0407 | -36.3024 | -40.8164 | -40.8945 | -47.625 | -53.4586 | -45.0446 | -36.2086 | -41.7187 | -34.3024 | -47.0406 | -50.4453 | -44.9297 | -41.0234 | -34.9584 | -34.9001 | -46.6422 | -50.9492 | -43.9336 | -40.9296 | -35.8607
290 | -4.0939 | 0 | -3.3967 | 0 | -4.487 | 0 | -3.5033 | 0 | -50.2236 | 155.699 | -35.5688 | -153.2579 | -46.8312 | -20.0039 | -48.3214 | -22.2384 | -47.1808 | -160.3598 | -35.0723 | -47.69 | -50.6765 | 122.5487 | -38.5316 | 124.1622 | -43.6005 | -76.5334 | -46.6949 | -125.4009 | -49.6205 | 161.6989 | -36.202 | -135.7004 | -10.9941 | 14.0798 | -22.1847 | -46.702 | -19.5022 | -65.2033 | -19.5307 | 78.3114 | -11.0524 | -45.1939 | -24.7091 | -4.8588 | -21.2687 | -154.9675 | -17.6142 | 19.0874 | -47.4139 | -37.512 | -50.2049 | -52.6952 | -48.7303 | -39.4144 | -45.1037 | -42.5495 | -52.6798 | -49.9982 | -46.0803 | -44.8307 | -42.164 | 290 | -35.1194 | -43.6295 | -32.1959 | -34.5483 | -37.1572 | -43.8854 | -33.9641 | -35.3116 | 290 | -38.4556 | -48.5859 | -48.6013 | -45.3336 | -36.0177 | -40.6167 | -39.1528 | -48.1928 | -49.1919 | -44.2433 | -35.9111 | -41.6004 | -33.4181 | -46.111 | -45.9043 | -42.6836 | -41.434 | -37.677 | -34.1153 | -45.7179 | -46.4949 | -41.5933 | -41.3274 | -38.6607
291 | -4.18 | 0 | -3.3842 | 0 | -4.5821 | 0 | -3.535 | 0 | -50.4327 | 166.6689 | -35.8542 | -168.7403 | -47.4542 | -8.3007 | -47.1391 | -7.6058 | -46.5058 | 155.3903 | -35.084 | -59.5569 | -50.398 | 117.1604 | -38.9117 | 113.6107 | -43.81 | -86.8783 | -43.2921 | -125.1276 | -51.283 | 101.5347 | -37.8705 | -149.8589 | -10.3909 | 2.7828 | -23.0012 | -67.0931 | -21.661 | -81.2496 | -17.9626 | 62.16 | -10.4839 | -56.927 | -25.8569 | -7.2135 | -22.3806 | 167.7019 | -16.8942 | 9.7796 | -47.8623 | -36.7712 | -49.8066 | -48.1787 | -50.9873 | -39.3337 | -45.0795 | -40.7774 | -55.387 | -47.5599 | -46.6576 | -46.0313 | -43.4933 | 291 | -35.4244 | -42.9471 | -32.2969 | -34.5531 | -37.4668 | -41.9774 | -34.7028 | -36.7301 | 291 | -36.5974 | -51.207 | -43.9987 | -47.6031 | -35.9495 | -40.4974 | -37.3932 | -50.8049 | -44.6437 | -46.4052 | -35.7987 | -41.5445 | -32.5912 | -45.6266 | -43.3799 | -43.2734 | -42.6471 | -38.9112 | -33.387 | -45.2245 | -44.0249 | -42.0755 | -42.4963 | -39.9583
292 | -4.2038 | 0 | -3.3675 | 0 | -4.6125 | 0 | -3.5252 | 0 | -50.2133 | 162.7465 | -36.6376 | 177.5909 | -46.1643 | -11.7813 | -43.2835 | -17.1259 | -50.0839 | 124.8695 | -36.1368 | -73.2675 | -51.7954 | 114.9979 | -39.5346 | 104.5284 | -44.7105 | -100.695 | -41.5714 | -138.8596 | -59.2009 | 56.421 | -40.1063 | -153.0549 | -10.0467 | -8.95 | -24.7763 | -86.8363 | -25.7175 | -97.2084 | -16.8929 | 47.6797 | -10.2746 | -69.6491 | -26.7399 | -4.5299 | -22.5071 | 128.3684 | -16.3772 | 0.1623 | -46.9159 | -36.118 | -51.4124 | -45.1738 | -58.4394 | -40.5516 | -46.3557 | -39.382 | -56.8444 | -46.3206 | -50.8128 | -46.1203 | -44.465 | 292 | -36.0102 | -41.7861 | -32.9479 | -35.569 | -38.1893 | -41.1094 | -35.5512 | -38.775 | 292 | -35.1782 | -52.6406 | -40.97 | -55.0719 | -37.1841 | -41.7432 | -36.0145 | -52.2319 | -41.6486 | -53.8269 | -37.0264 | -42.8305 | -31.9142 | -47.2086 | -42.1168 | -47.4453 | -42.7528 | -39.8525 | -32.7505 | -46.7999 | -42.7954 | -46.2003 | -42.5951 | -40.9398
293 | -4.2119 | 0 | -3.3525 | 0 | -4.5478 | 0 | -3.5166 | 0 | -51.0915 | 163.6249 | -37.6757 | 165.6498 | -45.8965 | -18.5262 | -41.4752 | -38.3139 | -53.8526 | 119.6713 | -37.9642 | -79.5419 | -52.6873 | 123.9103 | -40.0124 | 97.3408 | -46.231 | -111.2366 | -40.6907 | -153.1832 | -70.1099 | 80.4731 | -41.4113 | -149.4029 | -10.0569 | -20.1357 | -27.5994 | -109.6541 | -34.9127 | -105.7483 | -16.4615 | 35.211 | -10.3577 | -81.9062 | -26.5544 | 0.0753 | -22.2508 | 91.3285 | -16.2097 | -11.1636 | -46.0065 | -35.7838 | -52.0768 | -43.7955 | -67.8659 | -42.5104 | -46.9541 | -38.4346 | -54.7275 | -44.6025 | -52.833 | -47.2314 | -44.7635 | 293 | -36.8977 | -40.8042 | -33.9601 | -37.2206 | -38.8968 | -40.4201 | -35.8962 | -40.1696 | 293 | -34.2227 | -50.5156 | -39.5836 | -64.5134 | -39.1579 | -42.4063 | -35.0821 | -50.1797 | -40.2789 | -63.3181 | -38.9938 | -43.4375 | -31.5719 | -47.8649 | -40.3906 | -49.4805 | -43.8789 | -40.2157 | -32.4313 | -47.529 | -41.0859 | -48.2852 | -43.7148 | -41.2469
294 | -4.1811 | 0 | -3.3583 | 0 | -4.3897 | 0 | -3.5084 | 0 | -51.3112 | 171.5181 | -39.0073 | 154.9772 | -45.7727 | -24.2014 | -41.0295 | -59.3873 | -55.4306 | 127.1901 | -39.3546 | -78.4879 | -52.0023 | 136.6481 | -40.1482 | 88.7641 | -48.2161 | -119.2896 | -40.5031 | -168.9048 | -66.1175 | 119.4156 | -41.7597 | -146.326 | -10.219 | -31.1651 | -32.8387 | -143.7709 | -33.2264 | 14.0157 | -16.1147 | 21.4573 | -10.7572 | -94.667 | -26.2182 | 4.2061 | -21.9902 | 61.3384 | -16.341 | -22.7261 | -45.2935 | -35.7194 | -51.7648 | -43.1411 | -67.4966 | -45.4811 | -46.8426 | -37.7491 | -52.6147 | -43.4794 | -52.6044 | -49.8116 | -43.5349 | 294 | -37.9712 | -40.4986 | -34.9404 | -38.3757 | -39.28 | -40.1949 | -35.9792 | -40.8614 | 294 | -33.568 | -48.4336 | -38.96 | -64.1383 | -42.1228 | -42.4529 | -34.3908 | -48.225 | -39.6327 | -63.1069 | -41.9727 | -43.3342 | -31.5383 | -47.5837 | -39.2983 | -49.2461 | -46.4533 | -39.1452 | -32.3611 | -47.3751 | -39.971 | -48.2147 | -46.3032 | -40.0265
295 | -4.1274 | 0 | -3.3595 | 0 | -4.2245 | 0 | -3.5007 | 0 | -50.189 | -179.9631 | -40.4566 | 145.5992 | -45.7565 | -28.4078 | -41.5888 | -78.2857 | -54.7566 | 130.5814 | -39.7774 | -74.2292 | -49.8252 | 143.9759 | -40.1802 | 76.1128 | -50.6089 | -121.7069 | -41.1838 | 176.774 | -63.1842 | 103.7065 | -41.8302 | -144.8286 | -10.792 | -41.636 | -35.472 | 138.8318 | -25.8981 | 5.2476 | -16.5222 | 9.9577 | -11.4811 | -108.187 | -25.3608 | 6.1589 | -21.7359 | 34.9024 | -17.0921 | -35.3075 | -44.7322 | -35.8355 | -51.1329 | -42.8611 | -63.2166 | -50.3824 | -46.3243 | -37.3261 | -50.8539 | -43.0587 | -51.8751 | -53.8456 | -41.6039 | 295 | -38.9907 | -40.847 | -35.7734 | -38.6912 | -39.3916 | -40.6032 | -36.2399 | -41.2619 | 295 | -33.1987 | -46.7265 | -38.7337 | -59.8571 | -47.0229 | -42.0998 | -33.9666 | -46.6294 | -39.3604 | -58.9921 | -46.8817 | -42.8236 | -31.7081 | -47.0055 | -38.9313 | -48.5156 | -50.4861 | -37.3794 | -32.476 | -46.9084 | -39.558 | -47.6506 | -50.3449 | -38.1032
296 | -4.0589 | 0 | -3.3783 | 0 | -4.1016 | 0 | -3.4888 | 0 | -48.2289 | -176.7798 | -42.1389 | 137.1189 | -45.5301 | -32.2344 | -42.8737 | -93.3829 | -53.6355 | 124.7059 | -39.3426 | -71.1389 | -47.3372 | 142.3694 | -40.5597 | 60.6932 | -53.0261 | -114.0654 | -42.0782 | 166.9487 | -62.6724 | 76.5381 | -41.8619 | -143.1071 | -11.6633 | -51.5611 | -30.7804 | 85.2031 | -23.3587 | -10.4535 | -17.4112 | -0.4286 | -12.4543 | -121.4475 | -24.3924 | 3.8658 | -22.2191 | 13.6737 | -18.4144 | -48.0015 | -44.2315 | -35.9586 | -50.4355 | -42.5869 | -60.6729 | -59.3492 | -45.6869 | -37.0937 | -49.3324 | -42.4643 | -51.1674 | -55.0391 | -39.6956 | 296 | -39.8241 | -41.4897 | -36.4007 | -38.278 | -39.533 | -40.9166 | -36.6754 | -41.5085 | 296 | -33.0348 | -45.2735 | -38.528 | -57.2946 | -55.9709 | -41.5853 | -33.7154 | -45.2308 | -39.0981 | -56.5713 | -55.8604 | -42.1981 | -31.8997 | -46.3766 | -38.4054 | -47.7891 | -51.6608 | -35.594 | -32.5803 | -46.3339 | -38.9755 | -47.0658 | -51.5503 | -36.2068
297 | -3.9615 | 0 | -3.3873 | 0 | -3.981 | 0 | -3.481 | 0 | -46.1783 | -179.5638 | -44.3412 | 128.0191 | -45.0639 | -35.5959 | -45.4374 | -103.985 | -52.7878 | 112.7587 | -38.9179 | -71.1115 | -45.2281 | 133.7839 | -41.3497 | 41.7185 | -53.4109 | -97.0069 | -43.4425 | 159.3725 | -63.8043 | 47.4487 | -41.6038 | -140.1114 | -12.8279 | -60.4858 | -27.0611 | 56.7605 | -21.8706 | -27.1675 | -18.9751 | -9.0851 | -13.9277 | -134.051 | -23.3244 | -2.8529 | -22.9225 | -8.4181 | -20.4454 | -58.7193 | -43.7834 | -36.0647 | -49.7951 | -42.5959 | -59.3029 | -52.6936 | -44.9889 | -36.9771 | -48.0006 | -42.0045 | -50.3756 | -50.4654 | -37.8718 | 297 | -40.3587 | -42.3684 | -37.1289 | -37.8326 | -39.6717 | -41.2099 | -37.266 | -41.3019 | 297 | -33.0156 | -44.0391 | -38.6344 | -55.9156 | -49.3063 | -41.0079 | -33.5898 | -44.0196 | -39.1149 | -55.3219 | -49.2126 | -41.5079 | -32.1032 | -45.8336 | -38.043 | -46.9883 | -47.0781 | -33.8908 | -32.6774 | -45.8141 | -38.5235 | -46.3946 | -46.9844 | -34.3908
298 | -3.8712 | 0 | -3.397 | 0 | -3.9138 | 0 | -3.4899 | 0 | -44.4557 | 172.6212 | -47.6265 | 118.7855 | -44.2773 | -41.5113 | -48.4907 | -96.7205 | -52.3318 | 96.5419 | -38.3983 | -71.2863 | -43.649 | 122.5222 | -42.5828 | 19.2575 | -51.4476 | -87.0452 | -44.7665 | 160.427 | -64.7624 | 3.9546 | -40.4296 | -136.0902 | -14.3321 | -65.584 | -23.995 | 36.2612 | -21.2203 | -42.1925 | -20.782 | -12.5346 | -16.0527 | -145.266 | -22.1691 | -10.2357 | -24.3508 | -31.9672 | -23.8575 | -70.6468 | -43.465 | -36.1732 | -49.2829 | -42.7228 | -58.9142 | -46.6029 | -44.3658 | -37.0153 | -46.8165 | -41.8853 | -49.6666 | -46.3981 | -36.0153 | 298 | -40.4352 | -42.5301 | -37.5442 | -37.2632 | -39.7675 | -41.1427 | -37.4685 | -40.0842 | 298 | -33.1441 | -42.9453 | -38.8516 | -55.5172 | -43.2059 | -40.452 | -33.6183 | -42.9027 | -39.2329 | -55.0004 | -43.113 | -40.8759 | -32.302 | -45.4117 | -38.0141 | -46.2696 | -43.0011 | -32.1015 | -32.7762 | -45.3691 | -38.3954 | -45.7528 | -42.9082 | -32.5254
299 | -3.7959 | 0 | -3.4206 | 0 | -3.9127 | 0 | -3.5023 | 0 | -43.1026 | 162.6452 | -54.1565 | 115.1354 | -43.365 | -48.9206 | -47.9188 | -73.9087 | -52.3877 | 78.9067 | -37.4495 | -69.7278 | -42.604 | 108.5067 | -44.1323 | -7.3515 | -49.0067 | -91.2553 | -44.4839 | 166.0321 | -64.3288 | -49.0353 | -38.4826 | -137.3985 | -15.9735 | -68.3555 | -22.6877 | 19.3194 | -21.2472 | -58.266 | -23.9338 | -9.0784 | -18.8294 | -152.7173 | -21.7709 | -21.9608 | -25.831 | -56.4873 | -30.1104 | -70.8204 | -43.2738 | -36.2775 | -48.9927 | -42.805 | -59.5394 | -42.9689 | -43.8581 | -37.2134 | -45.8115 | -41.8112 | -49.2566 | -43.3541 | -34.4632 | 299 | -40.0495 | -41.4955 | -36.992 | -36.3497 | -39.7433 | -40.415 | -36.6545 | -38.1034 | 299 | -33.4175 | -42.0156 | -39.0091 | -56.1188 | -39.5483 | -39.9454 | -33.7928 | -41.8988 | -39.3027 | -55.6267 | -39.4666 | -40.3558 | -32.4816 | -45.1968 | -38.0153 | -45.836 | -39.9335 | -30.5505 | -32.8569 | -45.08 | -38.3089 | -45.3439 | -39.8518 | -30.9609
300 | -3.7424 | 0 | -3.4443 | 0 | -3.9693 | 0 | -3.5288 | 0 | -42.1816 | 150.3671 | -60.4798 | -137.5763 | -42.5559 | -60.7247 | -44.6853 | -70.7469 | -53.1706 | 54.9201 | -35.8655 | -73.0869 | -42.0743 | 94.1185 | -45.647 | -40.3086 | -47.2628 | -102.4456 | -42.8543 | 163.8674 | -61.8353 | -99.3213 | -36.4428 | -146.1072 | -17.5856 | -62.9047 | -21.223 | 5.7296 | -21.564 | -69.535 | -24.5868 | 12.7836 | -23.2586 | -149.2483 | -21.3505 | -34.0156 | -28.0827 | -87.5326 | -37.1385 | -0.2835 | -43.2857 | -36.4553 | -49.1072 | -42.8639 | -61.5123 | -40.385 | -43.4717 | -37.6607 | -45.1096 | -41.6709 | -49.2217 | -40.8834 | -34.0392 | 300 | -39.321 | -40.0292 | -35.3168 | -34.9563 | -39.6637 | -39.4116 | -35.144 | -36.0858 | 300 | -33.9183 | -41.3672 | -39.1215 | -58.068 | -36.9407 | -39.5024 | -34.2164 | -41.1403 | -39.3351 | -57.543 | -36.8562 | -39.9429 | -32.7129 | -45.3648 | -37.9285 | -45.7774 | -37.4391 | -30.0699 | -33.011 | -45.1379 | -38.1421 | -45.2524 | -37.3546 | -30.5104
301 | -3.715 | 0 | -3.4455 | 0 | -4.1134 | 0 | -3.5626 | 0 | -41.6938 | 137.8793 | -48.8323 | -125.822 | -42.0781 | -74.7438 | -42.1842 | -82.1504 | -55.2632 | 26.7537 | -34.1066 | -80.2824 | -42.1227 | 79.5101 | -46.4395 | -76.5688 | -46.151 | -117.6568 | -41.1892 | 152.4104 | -59.2539 | -139.8656 | -34.7449 | -159.2143 | -18.2427 | -54.8192 | -20.8671 | -8.2268 | -21.901 | -84.2879 | -23.0765 | 32.9269 | -25.7928 | -119.5739 | -21.1557 | -45.8407 | -28.6121 | -143.4954 | -26.4191 | 31.4896 | -43.5134 | -36.6931 | -49.8064 | -42.9705 | -66.158 | -38.3376 | -43.2853 | -38.4728 | -44.754 | -41.4494 | -49.797 | -38.7892 | -34.8823 | 301 | -38.4539 | -38.8221 | -33.3534 | -33.4352 | -39.6537 | -38.5832 | -33.624 | -34.4273 | 301 | -34.7578 | -41.039 | -39.2555 | -62.7125 | -34.8921 | -39.1719 | -35.0273 | -40.6406 | -39.4079 | -62.0446 | -34.775 | -39.7227 | -32.9781 | -46.0914 | -37.7344 | -46.3515 | -35.3437 | -30.7689 | -33.2476 | -45.693 | -37.8868 | -45.6836 | -35.2266 | -31.3197
302 | -3.7052 | 0 | -3.4646 | 0 | -4.3609 | 0 | -3.6081 | 0 | -41.6373 | 125.7839 | -43.9951 | -142.205 | -42.1066 | -91.2886 | -40.8387 | -98.8922 | -59.0804 | -14.4898 | -32.5205 | -92.4553 | -42.692 | 66.1085 | -46.2606 | -111.5364 | -45.8679 | -134.0966 | -40.2366 | 134.1039 | -57.6463 | -174.0148 | -33.5492 | -177.1481 | -17.7595 | -48.1868 | -20.7159 | -20.5687 | -22.1069 | -102.3028 | -20.7477 | 39.1129 | -23.0465 | -92.6933 | -21.2543 | -61.9314 | -25.8338 | 166.595 | -21.9961 | 22.8425 | -43.931 | -36.9758 | -51.3981 | -43.224 | -86.1458 | -36.6711 | -43.2458 | -39.8726 | -44.7911 | -41.2341 | -51.2419 | -37.0484 | -36.2859 | 302 | -37.6952 | -38.174 | -31.6622 | -32.0586 | -39.8568 | -38.2327 | -32.5181 | -33.2858 | 302 | -36.1674 | -41.0859 | -39.5188 | -82.6812 | -33.2065 | -38.8849 | -36.408 | -40.4302 | -39.6159 | -81.7849 | -33.063 | -39.6377 | -33.2706 | -47.6929 | -37.5289 | -47.7773 | -33.5838 | -31.925 | -33.5112 | -47.0372 | -37.626 | -46.881 | -33.4403 | -32.6778
303 | -3.7354 | 0 | -3.4543 | 0 | -4.6214 | 0 | -3.6404 | 0 | -42.0301 | 112.2548 | -41.5399 | -162.5887 | -42.9279 | -108.6228 | -40.6733 | -118.4952 | -63.1383 | -88.0956 | -31.4749 | -109.2586 | -43.7627 | 54.3747 | -45.4615 | -138.4052 | -46.1662 | -149.8447 | -40.2647 | 111.1653 | -57.5149 | 157.9477 | -33.0668 | 162.6523 | -16.6676 | -44.7962 | -20.8897 | -30.5484 | -22.9026 | -123.9189 | -18.0444 | 35.228 | -19.6952 | -91.7006 | -21.6147 | -76.1302 | -22.7701 | 129.0043 | -19.1312 | 9.8961 | -44.4832 | -37.2245 | -54.3424 | -43.8504 | -66.9207 | -35.3456 | -43.3997 | -42.1799 | -45.1729 | -41.2473 | -53.7122 | -35.6409 | -37.6984 | 303 | -37.3574 | -38.2744 | -30.6156 | -31.172 | -40.2385 | -38.6042 | -32.1038 | -32.8443 | 303 | -38.4445 | -41.4375 | -40.115 | -63.4664 | -31.8913 | -38.7783 | -38.7256 | -40.5515 | -40.21 | -62.2993 | -31.7052 | -39.7593 | -33.4891 | -50.607 | -37.5119 | -50.2579 | -32.1866 | -33.077 | -33.7702 | -49.721 | -37.6069 | -49.0908 | -32.0005 | -34.058
304 | -3.7686 | 0 | -3.4535 | 0 | -4.8591 | 0 | -3.6655 | 0 | -42.9043 | 100.856 | -40.7508 | 174.6501 | -44.496 | -122.7991 | -41.7181 | -135.6528 | -60.2752 | -162.2082 | -31.1104 | -128.2361 | -45.2753 | 45.5044 | -44.5641 | -159.2331 | -46.7314 | -163.2362 | -41.5338 | 87.5461 | -58.3938 | 136.6852 | -33.3709 | 141.4509 | -15.5151 | -47.3548 | -21.3761 | -40.4504 | -24.3561 | -152.9699 | -16.4786 | 27.5588 | -17.4244 | -99.9058 | -22.2393 | -90.535 | -20.6514 | 100.393 | -17.7209 | -6.3536 | -45.0019 | -37.3919 | -59.0787 | -44.955 | -61.123 | -34.431 | -43.7504 | -45.9216 | -45.7491 | -41.6215 | -56.7425 | -34.7966 | -39.0415 | 304 | -37.6733 | -39.2263 | -30.3346 | -30.9106 | -40.6617 | -39.9407 | -32.4767 | -33.162 | 304 | -42.153 | -41.9805 | -41.1864 | -57.6695 | -30.9775 | -38.8913 | -42.4681 | -40.89 | -41.2895 | -56.2639 | -30.7655 | -40.0849 | -33.6233 | -55.3101 | -37.8529 | -53.289 | -31.3431 | -34.1824 | -33.9384 | -54.2196 | -37.956 | -51.8834 | -31.1311 | -35.376
305 | -3.82 | 0 | -3.4567 | 0 | -4.9801 | 0 | -3.6794 | 0 | -44.3241 | 91.8828 | -41.3062 | 154.9857 | -46.7734 | -133.4702 | -43.6904 | -147.8511 | -57.0223 | 162.0833 | -31.5017 | -148.0292 | -47.2014 | 40.7656 | -43.7773 | -175.6988 | -47.3177 | -175.132 | -44.1873 | 64.347 | -59.5652 | 128.8425 | -34.4987 | 120.0588 | -14.6064 | -53.7488 | -21.9908 | -49.8787 | -25.7161 | 175.0021 | -15.3504 | 18.3145 | -16.1347 | -111.2308 | -23.2544 | -105.5282 | -19.3622 | 73.7468 | -16.3343 | -19.0674 | -45.3957 | -37.5129 | -61.3176 | -46.5012 | -58.3801 | -34.0325 | -44.2731 | -50.6051 | -46.3278 | -42.3317 | -57.8981 | -34.4254 | -40.2677 | 305 | -38.7944 | -40.8786 | -30.8384 | -31.3628 | -40.9964 | -42.3445 | -33.6156 | -34.2647 | 305 | -46.7851 | -42.5078 | -42.6812 | -54.9234 | -30.5758 | -39.293 | -47.1484 | -41.3477 | -42.8218 | -53.4 | -30.3531 | -40.5937 | -33.6929 | -57.4976 | -38.5117 | -54.4414 | -30.9687 | -35.2876 | -34.0562 | -56.3375 | -38.6523 | -52.918 | -30.746 | -36.5883
306 | -3.8716 | 0 | -3.4523 | 0 | -4.924 | 0 | -3.6662 | 0 | -46.3209 | 87.115 | -43.1859 | 135.5023 | -49.3703 | -135.4484 | -45.8485 | -148.3319 | -55.1383 | 139.2964 | -32.6186 | -166.1085 | -49.4114 | 42.608 | -43.1386 | 171.5547 | -47.7587 | 173.5469 | -48.8412 | 47.3473 | -59.2626 | 129.3756 | -36.437 | 100.6562 | -13.9795 | -61.6602 | -22.8332 | -55.212 | -28.1273 | 133.3273 | -14.6413 | 8.2634 | -15.0039 | -124.972 | -24.0931 | -121.1362 | -19.3089 | 51.4535 | -15.874 | -36.2194 | -45.5906 | -37.5622 | -56.8184 | -48.2859 | -56.8445 | -34.07 | -44.9718 | -50.0333 | -46.8052 | -43.3976 | -56.0851 | -34.463 | -41.3871 | 306 | -40.814 | -42.8064 | -32.0675 | -32.5041 | -41.1492 | -45.9016 | -35.3948 | -36.1069 | 306 | -46.1617 | -42.9336 | -44.4143 | -53.3922 | -30.6177 | -40.0478 | -46.581 | -41.8812 | -44.6197 | -51.9205 | -30.4038 | -41.3056 | -33.6906 | -52.9468 | -39.526 | -52.6328 | -31.0107 | -36.4631 | -34.1099 | -51.8944 | -39.7314 | -51.1611 | -30.7968 | -37.7209
307 | -3.9078 | 0 | -3.4352 | 0 | -4.7493 | 0 | -3.6563 | 0 | -48.6436 | 88.9637 | -46.6386 | 123.6847 | -51.456 | -127.9138 | -46.6596 | -143.5992 | -53.789 | 124.0807 | -34.552 | 176.4519 | -51.1409 | 55.1094 | -42.5695 | 159.1794 | -48.0112 | 162.7892 | -55.8032 | 54.8982 | -57.366 | 123.3939 | -39.0844 | 82.5712 | -13.6422 | -70.5608 | -23.8392 | -55.5701 | -29.48 | 82.9144 | -14.2173 | -1.9919 | -14.5841 | -139.2081 | -25.6889 | -135.1961 | -19.7765 | 30.6155 | -15.6759 | -52.6959 | -45.5735 | -37.5868 | -53.3976 | -50.0188 | -55.757 | -34.4501 | -45.7321 | -46.0814 | -47.0406 | -44.6501 | -53.9391 | -34.8978 | -42.3529 | 307 | -43.716 | -44.0423 | -34.0466 | -34.4139 | -41.0326 | -49.1535 | -37.4127 | -38.5044 | 307 | -42.1736 | -43.1328 | -46.111 | -52.3218 | -31.0149 | -40.9828 | -42.6462 | -42.2913 | -46.3625 | -51.0077 | -30.7938 | -42.0758 | -33.679 | -49.4898 | -40.7423 | -50.5039 | -31.4626 | -37.6036 | -34.1516 | -48.6483 | -40.9938 | -49.1898 | -31.2415 | -38.6966
308 | -3.9297 | 0 | -3.4434 | 0 | -4.5445 | 0 | -3.6373 | 0 | -50.2601 | 103.2834 | -51.5256 | 132.0255 | -51.2166 | -116.9505 | -46.249 | -143.1806 | -52.337 | 111.0658 | -37.1958 | 164.1909 | -50.8134 | 73.5884 | -42.1516 | 148.2051 | -48.1163 | 150.8184 | -56.0735 | 101.8283 | -55.4915 | 109.739 | -42.6522 | 69.1094 | -13.577 | -79.8387 | -24.3315 | -59.5036 | -31.3048 | 43.6254 | -14.2787 | -12.0841 | -13.9931 | -152.5394 | -26.8439 | -147.2704 | -21.4402 | 13.0825 | -15.7882 | -69.5246 | -45.4761 | -37.6281 | -51.1968 | -51.355 | -54.7769 | -35.089 | -46.541 | -43.3609 | -47.0508 | -45.9746 | -52.0996 | -35.5992 | -43.0971 | 308 | -46.1955 | -44.092 | -36.5465 | -36.901 | -40.7236 | -48.6692 | -39.2923 | -41.3935 | 308 | -39.4312 | -43.1211 | -47.4253 | -51.3335 | -31.6456 | -41.9965 | -39.9175 | -42.5063 | -47.7177 | -50.2324 | -31.4517 | -42.9037 | -33.6984 | -47.2671 | -42.0449 | -48.6562 | -32.1558 | -38.5526 | -34.1847 | -46.6523 | -42.3373 | -47.5551 | -31.9619 | -39.4598
309 | -3.9484 | 0 | -3.4327 | 0 | -4.3585 | 0 | -3.6085 | 0 | -49.8609 | 121.6387 | -52.2294 | 169.0041 | -50.2089 | -115.4137 | -46.2167 | -150.1313 | -50.6393 | 97.8144 | -40.5585 | 158.81 | -48.8346 | 84.0979 | -41.9754 | 137.3532 | -48.1295 | 137.0032 | -52.446 | 101.0596 | -54.0358 | 88.2604 | -47.4537 | 58.9866 | -13.5864 | -90.3555 | -24.4709 | -63.1194 | -33.4353 | 4.2235 | -14.5828 | -22.0473 | -14.155 | -166.6483 | -28.3968 | -155.5285 | -23.19 | 0.8974 | -16.1314 | -87.2465 | -45.2428 | -37.653 | -49.6764 | -51.9108 | -53.6959 | -35.8913 | -47.3741 | -41.6085 | -46.9406 | -47.1515 | -50.2687 | -36.4484 | -43.4538 | 309 | -45.8769 | -43.6802 | -39.288 | -39.7431 | -40.3661 | -46.4359 | -40.5988 | -44.2823 | 309 | -37.6601 | -42.9922 | -47.9624 | -50.2632 | -32.4586 | -43.0156 | -38.1758 | -42.5821 | -48.3023 | -49.3374 | -32.2828 | -43.7656 | -33.7046 | -45.728 | -43.2031 | -46.836 | -33.0157 | -39.0953 | -34.2203 | -45.3179 | -43.543 | -45.9102 | -32.8399 | -39.8453
310 | -3.9663 | 0 | -3.4601 | 0 | -4.2213 | 0 | -3.5894 | 0 | -48.065 | 134.1164 | -48.7711 | 175.7612 | -49.5236 | -122.0858 | -47.6256 | -158.2434 | -48.6841 | 77.7724 | -44.0261 | 165.3715 | -46.7181 | 88.2008 | -42.0819 | 125.1051 | -47.931 | 119.7382 | -51.5225 | 80.1245 | -53.5268 | 56.7167 | -55.507 | 68.545 | -14.1038 | -100.2485 | -25.252 | -60.5798 | -36.1518 | -29.7434 | -15.0834 | -30.3727 | -14.6609 | 178.8242 | -31.9577 | -165.0755 | -26.0038 | -4.3909 | -17.0377 | -104.8152 | -44.6725 | -37.5157 | -48.2021 | -51.5632 | -52.7975 | -36.6954 | -47.9914 | -40.3658 | -46.6421 | -48.0617 | -48.425 | -37.3541 | -43.5273 | 310 | -43.9747 | -43.3322 | -41.5417 | -41.9199 | -40.03 | -44.8448 | -41.4403 | -46.316 | 310 | -36.3995 | -42.6758 | -47.5969 | -49.3374 | -33.2353 | -43.7701 | -36.9057 | -42.4208 | -47.9738 | -48.5762 | -33.106 | -44.402 | -33.5494 | -44.2358 | -44.0954 | -44.9649 | -33.894 | -39.306 | -34.0556 | -43.9808 | -44.4723 | -44.2037 | -33.7647 | -39.9379
311 | -3.9398 | 0 | -3.4587 | 0 | -4.0973 | 0 | -3.5612 | 0 | -44.7362 | 140.1464 | -47.7202 | 163.5946 | -50.4643 | -124.9322 | -49.3939 | -147.0278 | -48.241 | 45.332 | -45.0674 | -179.0403 | -43.8395 | 88.7587 | -42.9286 | 110.7417 | -48.4364 | 95.0469 | -54.5281 | 52.5676 | -56.5154 | 10.5604 | -56.3764 | 141.532 | -14.6391 | -110.6055 | -25.7145 | -59.5954 | -43.1343 | -31.5323 | -15.9185 | -37.4013 | -15.2948 | 166.0247 | -34.8235 | -156.0798 | -28.9796 | 1.8222 | -18.1584 | -123.3613 | -43.2505 | -37.0408 | -46.1352 | -51.2527 | -54.1572 | -37.2636 | -46.6036 | -39.2217 | -45.2518 | -49.6083 | -47.9337 | -38.0953 | -43.5514 | 311 | -42.2554 | -42.2117 | -42.2521 | -42.5873 | -39.7227 | -43.273 | -42.4582 | -47.2428 | 311 | -35.2819 | -41.312 | -47.3129 | -50.6985 | -33.8049 | -42.5063 | -35.763 | -41.1545 | -47.6915 | -50.0599 | -33.7024 | -43.0424 | -33.101 | -42.1954 | -45.6685 | -44.475 | -34.6366 | -39.4541 | -33.5821 | -42.0379 | -46.0471 | -43.8364 | -34.5341 | -39.9902
312 | -3.9168 | 0 | -3.472 | 0 | -4.0089 | 0 | -3.5321 | 0 | -41.6965 | 129.9867 | -48.8195 | 154.3952 | -49.4375 | -115.2693 | -48.082 | -141.1321 | -50.6947 | 20.6291 | -45.8093 | -169.8265 | -41.047 | 76.9605 | -45.2536 | 99.1697 | -51.1108 | 71.6208 | -62.5102 | 48.8656 | -67.6434 | 5.8518 | -52.5014 | 157.8373 | -15.5971 | -121.3277 | -26.0071 | -56.5549 | -45.0291 | 66.836 | -16.9087 | -42.0117 | -16.1802 | 152.5216 | -34.0476 | -133.5585 | -30.2203 | 19.9349 | -19.3865 | -142.9218 | -42.4499 | -36.6292 | -44.8759 | -52.1751 | -59.739 | -38.225 | -44.9244 | -38.3317 | -43.5284 | -52.5416 | -49.8229 | -39.1563 | -43.6403 | 312 | -40.3541 | -40.3746 | -42.6025 | -43.3582 | -39.3498 | -41.0067 | -44.4356 | -48.6848 | 312 | -34.4149 | -39.6116 | -48.2583 | -56.267 | -34.753 | -40.9155 | -34.8597 | -39.5195 | -48.643 | -55.7301 | -34.6929 | -41.3923 | -32.7124 | -40.9591 | -48.6248 | -46.3509 | -35.6843 | -39.6314 | -33.1572 | -40.867 | -49.0095 | -45.814 | -35.6242 | -40.1082
313 | -3.8654 | 0 | -3.467 | 0 | -3.9553 | 0 | -3.5099 | 0 | -40.2411 | 114.9847 | -51.0104 | 147.6119 | -47.1843 | -120.4513 | -47.8654 | -142.398 | -52.4283 | 11.9159 | -45.7761 | -154.7031 | -39.5949 | 61.3441 | -49.4014 | 97.4648 | -54.8815 | 62.0806 | -69.8569 | 145.008 | -67.1168 | 59.4435 | -49.5795 | 169.0318 | -16.5399 | -131.6913 | -25.8303 | -58.6753 | -37.2076 | 69.2957 | -17.9261 | -45.7174 | -17.3233 | 141.3174 | -32.2173 | -124.9415 | -29.9484 | 32.8039 | -21.1163 | -164.2057 | -42.5776 | -36.4097 | -44.5542 | -52.5425 | -62.7964 | -39.7105 | -44.4006 | -37.8107 | -42.5881 | -54.2521 | -50.6662 | -40.6193 | -43.5922 | 313 | -39.149 | -39.3306 | -42.9482 | -42.8998 | -39.0482 | -39.5831 | -46.4593 | -48.3981 | 313 | -33.9453 | -38.7227 | -48.6771 | -59.3294 | -36.2435 | -40.4453 | -34.3437 | -38.6328 | -49.0326 | -58.8411 | -36.2006 | -40.8907 | -32.5443 | -40.6888 | -50.3867 | -47.1992 | -37.1523 | -39.6369 | -32.9427 | -40.5989 | -50.7422 | -46.7109 | -37.1094 | -40.0823
314 | -3.8372 | 0 | -3.4825 | 0 | -3.9278 | 0 | -3.5218 | 0 | -39.5337 | 102.3978 | -57.1177 | 155.6342 | -45.5726 | -131.6831 | -47.2293 | -137.1124 | -52.5001 | -1.7421 | -43.8314 | -143.2185 | -38.8646 | 46.9134 | -54.8768 | 139.7099 | -58.8908 | 73.6833 | -57.6619 | 170.7177 | -67.6417 | 50.3618 | -46.0987 | 170.7608 | -18.1548 | -142.7108 | -25.9295 | -57.878 | -33.8998 | 50.8801 | -18.9558 | -47.2619 | -18.9578 | 129.5176 | -28.7235 | -126.2314 | -29.1485 | 35.7539 | -23.3338 | 173.6722 | -42.9681 | -36.101 | -44.5025 | -51.8548 | -61.6009 | -41.3783 | -44.252 | -37.3966 | -41.9583 | -53.6817 | -50.0957 | -42.0646 | -43.5645 | 314 | -38.508 | -38.6683 | -42.0583 | -41.2653 | -38.7152 | -38.802 | -45.2987 | -45.8473 | 314 | -33.5594 | -38.1211 | -48.0176 | -58.1184 | -37.8958 | -40.3242 | -33.9141 | -38.0305 | -48.333 | -57.6731 | -37.8565 | -40.7302 | -32.2638 | -40.6653 | -49.8445 | -46.6132 | -38.5821 | -39.6367 | -32.6185 | -40.5747 | -50.1599 | -46.1679 | -38.5428 | -40.0427
315 | -3.815 | 0 | -3.4977 | 0 | -3.9123 | 0 | -3.5385 | 0 | -39.2347 | 90.5281 | -55.2657 | -117.9451 | -44.2162 | -145.1408 | -45.1207 | -135.9675 | -52.9553 | -27.7182 | -41.3811 | -141.6201 | -38.5594 | 32.6108 | -48.0953 | -173.0006 | -58.3346 | 109.4371 | -51.7841 | 153.1256 | -70.9747 | 86.3798 | -43.0682 | 162.1554 | -20.1367 | -152.6361 | -25.5566 | -55.6871 | -32.4597 | 27.9555 | -19.7708 | -46.4577 | -20.9361 | 120.7081 | -26.4268 | -132.8379 | -28.3171 | 36.5938 | -26.2511 | 144.834 | -43.4989 | -35.722 | -44.6951 | -50.6473 | -61.2059 | -43.0189 | -44.0876 | -37.0373 | -41.5259 | -51.7204 | -49.7204 | -42.9748 | -43.3378 | 315 | -37.9555 | -38.0942 | -39.7269 | -39.3666 | -38.0602 | -38.3551 | -41.4585 | -42.9341 | 315 | -33.2223 | -37.7109 | -46.8323 | -57.7082 | -39.5212 | -40.1753 | -33.5396 | -37.6136 | -47.1088 | -57.2936 | -39.4804 | -40.5491 | -31.907 | -40.8801 | -47.9054 | -46.2227 | -39.4771 | -39.4255 | -32.2243 | -40.7828 | -48.1819 | -45.8081 | -39.4363 | -39.7993
316 | -3.7899 | 0 | -3.5142 | 0 | -3.9602 | 0 | -3.5628 | 0 | -39.1755 | 80.1123 | -46.6445 | -117.6592 | -43.244 | -161.8229 | -43.0044 | -146.3412 | -54.5457 | -65.1959 | -38.9353 | -147.8937 | -38.5291 | 19.9145 | -42.0276 | -176.9285 | -53.3249 | 112.3146 | -48.4051 | 127.132 | -63.9495 | 108.292 | -40.5526 | 148.1277 | -22.1134 | -158.7828 | -24.5638 | -56.5597 | -33.7443 | 2.9059 | -20.2434 | -45.514 | -23.4464 | 120.8954 | -24.4509 | -142.322 | -28.6418 | 40.246 | -30.4001 | 116.4014 | -44.0114 | -35.4378 | -45.2558 | -49.2028 | -61.1755 | -43.8323 | -43.7877 | -36.9211 | -41.2547 | -49.2447 | -50.1861 | -42.5187 | -42.4557 | 316 | -37.2138 | -37.5824 | -37.0005 | -37.4794 | -36.8265 | -38.0925 | -37.8203 | -40.3102 | 316 | -33.1312 | -37.4648 | -45.4129 | -57.6613 | -40.3181 | -39.8275 | -33.4069 | -37.2945 | -45.64 | -57.2153 | -40.2695 | -40.2249 | -31.6479 | -41.4659 | -45.4548 | -46.6719 | -39.0045 | -38.4955 | -31.9236 | -41.2956 | -45.6819 | -46.2259 | -38.9559 | -38.8929
317 | -3.767 | 0 | -3.5482 | 0 | -4.0599 | 0 | -3.5678 | 0 | -39.1841 | 71.041 | -42.3198 | -135.8418 | -42.6483 | 179.4722 | -41.8128 | -164.4525 | -56.9649 | -118.0462 | -36.9682 | -161.3344 | -38.6717 | 7.8792 | -38.2692 | 168.3268 | -49.9505 | 98.9439 | -46.9387 | 94.1541 | -60.1452 | 87.9464 | -38.7642 | 128.0752 | -24.7038 | -160.8696 | -23.3392 | -59.5656 | -38.5176 | -47.1339 | -20.391 | -45.0582 | -25.4922 | 118.251 | -23.0663 | -153.4099 | -26.8244 | 45.5012 | -31.1699 | 57.4671 | -44.1742 | -35.4203 | -46.4438 | -47.8617 | -60.7407 | -42.5219 | -43.2592 | -37.267 | -41.2787 | -47.0209 | -51.7123 | -40.4545 | -41.3443 | 317 | -36.3147 | -37.2456 | -34.8747 | -35.8948 | -35.3039 | -38.0415 | -35.1983 | -38.4164 | 317 | -33.5 | -37.5117 | -44.0947 | -57.1925 | -38.9737 | -39.1993 | -33.7188 | -37.2188 | -44.2939 | -56.6808 | -38.9541 | -39.6914 | -31.6533 | -42.6768 | -43.2539 | -48.1641 | -36.9063 | -37.2844 | -31.8721 | -42.3839 | -43.4531 | -47.6524 | -36.8867 | -37.7765
318 | -3.7647 | 0 | -3.5796 | 0 | -4.19 | 0 | -3.5683 | 0 | -39.2289 | 60.4652 | -40.541 | -157.9527 | -42.5279 | 157.069 | -42.0187 | 173.2241 | -57.5244 | 176.8542 | -35.8412 | 178.5157 | -38.9549 | -4.1942 | -36.0614 | 150.2326 | -47.5442 | 80.6304 | -47.2175 | 57.786 | -59.2022 | 64.3211 | -38.0311 | 104.3928 | -29.1477 | -159.9053 | -22.396 | -63.6573 | -49.9436 | 89.9049 | -20.4036 | -40.6502 | -26.7667 | 136.7558 | -21.5182 | -164.6583 | -26.0113 | 44.4747 | -31.6117 | 2.0954 | -43.9321 | -35.9839 | -48.4883 | -46.9243 | -59.8501 | -40.0112 | -42.6187 | -38.3931 | -41.6983 | -45.228 | -53.7788 | -38.1587 | -40.728 | 318 | -35.7907 | -37.3513 | -33.8547 | -34.9732 | -34.0619 | -38.3154 | -33.7264 | -37.5409 | 318 | -34.6284 | -37.9336 | -43.1596 | -56.2705 | -36.4316 | -38.4287 | -34.8135 | -37.5083 | -43.356 | -55.6601 | -36.4429 | -39.0504 | -32.2192 | -44.7236 | -41.4633 | -50.1992 | -34.5791 | -36.538 | -32.4043 | -44.2983 | -41.6597 | -49.5888 | -34.5904 | -37.1597
319 | -3.7488 | 0 | -3.6003 | 0 | -4.2903 | 0 | -3.5488 | 0 | -39.5652 | 49.603 | -40.7061 | -174.2169 | -43.1691 | 134.3754 | -43.7577 | 153.4916 | -55.7263 | 126.8642 | -35.8505 | 156.22 | -39.5205 | -16.2325 | -35.0281 | 133.3656 | -46.3324 | 60.3287 | -48.983 | 17.4249 | -60.8658 | 42.4954 | -38.3162 | 79.7525 | -29.3097 | -132.774 | -21.0077 | -74.9015 | -36.9416 | 118.8367 | -20.1788 | -44.9502 | -25.9797 | 152.2747 | -20.3577 | -175.8358 | -25.8219 | 36.4337 | -29.2781 | -45.0585 | -43.5738 | -37.1857 | -51.2145 | -46.527 | -59.1676 | -37.9865 | -42.2058 | -40.5169 | -42.4832 | -44.3582 | -54.9988 | -36.556 | -40.4999 | 319 | -36.1309 | -38.0883 | -34.122 | -35.0743 | -33.4763 | -39.0263 | -33.2405 | -37.6587 | 319 | -36.7681 | -38.7344 | -42.7782 | -55.5673 | -34.3862 | -37.9155 | -36.9166 | -38.1929 | -42.9782 | -54.8773 | -34.4377 | -38.657 | -33.4369 | -47.4657 | -40.6094 | -51.3985 | -32.9557 | -36.2096 | -33.5854 | -46.9242 | -40.8094 | -50.7085 | -33.0072 | -36.9511
320 | -3.7414 | 0 | -3.6061 | 0 | -4.2989 | 0 | -3.5232 | 0 | -40.3828 | 38.6788 | -41.9308 | -179.1221 | -44.4522 | 110.7865 | -47.3614 | 137.7292 | -54.1912 | 93.8923 | -36.9929 | 134.716 | -40.596 | -28.5164 | -34.7078 | 119.2532 | -45.756 | 41.7228 | -51.5796 | -30.0255 | -65.0323 | 40.3777 | -39.5811 | 55.104 | -28.7536 | -117.7374 | -20.1922 | -86.6229 | -33.5624 | 104.8853 | -20.0285 | -47.7065 | -24.3037 | 152.4341 | -19.4324 | 171.1595 | -25.934 | 28.9223 | -27.273 | -76.7053 | -43.3334 | -38.8153 | -52.9023 | -46.5443 | -58.8217 | -36.8544 | -42.1295 | -43.5958 | -43.5344 | -44.2467 | -54.7467 | -35.7521 | -40.4848 | 320 | -37.1773 | -39.4412 | -35.4926 | -36.2063 | -33.4488 | -40.2484 | -33.4169 | -38.6325 | 320 | -39.8544 | -39.793 | -42.8029 | -55.2156 | -33.2483 | -37.8306 | -39.9897 | -39.2355 | -43.0211 | -54.5228 | -33.3312 | -38.6063 | -35.0739 | -49.1609 | -40.5053 | -51.1406 | -32.146 | -36.1859 | -35.2092 | -48.6034 | -40.7235 | -50.4478 | -32.2289 | -36.9616
321 | -3.7426 | 0 | -3.6059 | 0 | -4.2621 | 0 | -3.5199 | 0 | -41.7686 | 29.6606 | -41.9194 | -171.4954 | -46.5588 | 88.7425 | -53.1446 | 140.0724 | -53.1852 | 70.1482 | -39.1563 | 115.1884 | -42.3343 | -38.5803 | -34.5872 | 109.1462 | -45.9025 | 25.4001 | -53.1134 | -84.3491 | -66.2829 | 72.7163 | -41.6812 | 31.8438 | -26.3397 | -118.7659 | -19.5026 | -100.7441 | -30.5151 | 90.7021 | -20.1035 | -50.4845 | -22.7054 | 152.2005 | -18.5929 | 161.3642 | -26.2772 | 28.6355 | -25.4981 | -104.4011 | -43.2745 | -40.3799 | -51.9385 | -46.755 | -58.587 | -36.4385 | -42.3051 | -46.8051 | -44.559 | -44.5981 | -54.2621 | -35.5512 | -40.5766 | 321 | -38.1556 | -41.1805 | -37.1995 | -38.2877 | -33.6465 | -41.9696 | -33.7619 | -40.2768 | 321 | -43.0625 | -40.8164 | -43.0124 | -54.9811 | -32.8326 | -38.043 | -43.1992 | -40.2969 | -43.2351 | -54.3249 | -32.9186 | -38.7852 | -36.6373 | -48.1959 | -40.8555 | -50.6562 | -31.9453 | -36.3145 | -36.774 | -47.6764 | -41.0782 | -50 | -32.0313 | -37.0567
322 | -3.7638 | 0 | -3.6149 | 0 | -4.2169 | 0 | -3.5103 | 0 | -43.652 | 25.0073 | -39.9061 | -168.444 | -49.1812 | 67.563 | -56.2603 | -172.1208 | -52.6461 | 51.1256 | -42.2851 | 98.724 | -44.6826 | -42.0424 | -34.3206 | 100.6066 | -46.2433 | 14.1079 | -52.3956 | -129.2264 | -62.3943 | 87.1787 | -44.4299 | 9.7732 | -23.6789 | -126.15 | -18.8688 | -116.0644 | -29.6706 | 88.1651 | -19.812 | -58.4763 | -21.4438 | 148.0678 | -17.9567 | 151.3892 | -26.8253 | 34.4701 | -23.3768 | -128.2559 | -43.3068 | -41.4752 | -50.1471 | -47.0607 | -58.1935 | -36.3932 | -42.5719 | -48.2989 | -45.295 | -45.1227 | -54.025 | -35.6466 | -40.6951 | 322 | -38.0302 | -42.9298 | -37.8612 | -41.1578 | -33.6902 | -43.9408 | -33.8553 | -42.1907 | 322 | -44.5351 | -41.5312 | -43.2969 | -54.5786 | -32.7783 | -38.355 | -44.684 | -41.0781 | -43.5504 | -53.9766 | -32.8829 | -39.0616 | -37.7114 | -46.3833 | -41.3589 | -50.4101 | -32.0317 | -36.4782 | -37.8603 | -45.9302 | -41.6124 | -49.8081 | -32.1363 | -37.1848
323 | -3.7833 | 0 | -3.6255 | 0 | -4.1751 | 0 | -3.5278 | 0 | -45.7599 | 28.4936 | -37.7388 | -173.9869 | -52.8782 | 45.3464 | -51.7871 | -148.4226 | -52.4025 | 36.8016 | -46.5583 | 87.2402 | -47.2829 | -35.4001 | -33.9343 | 92.4688 | -46.676 | 4.2237 | -51.0761 | -160.1673 | -59.0763 | 81.3313 | -47.9838 | -15.7513 | -22.9848 | -139.8587 | -18.4177 | -132.0503 | -28.0724 | 81.6377 | -19.7639 | -64.0205 | -20.5965 | 138.413 | -17.4756 | 140.5792 | -26.0354 | 40.1839 | -22.1062 | -148.7552 | -43.3877 | -42.1833 | -48.6158 | -47.2822 | -57.6533 | -36.5388 | -42.8872 | -47.8001 | -45.7052 | -45.6763 | -54.0708 | -35.9212 | -40.9265 | 323 | -36.9894 | -44.0978 | -37.0547 | -44.8156 | -33.5226 | -45.5695 | -33.6867 | -44.1293 | 323 | -44.0168 | -41.9219 | -43.4989 | -54.0278 | -32.9133 | -38.7121 | -44.1746 | -41.5301 | -43.7544 | -53.4782 | -33.011 | -39.3594 | -38.4 | -44.8325 | -41.893 | -50.4453 | -32.2957 | -36.7514 | -38.5578 | -44.4407 | -42.1485 | -49.8957 | -32.3934 | -37.3987
324 | -3.7961 | 0 | -3.6496 | 0 | -4.1556 | 0 | -3.5315 | 0 | -47.0451 | 41.1259 | -36.1234 | 173.2877 | -58.8307 | 20.1196 | -48.6825 | -149.9797 | -52.3499 | 22.0712 | -53.0786 | 80.6731 | -48.1848 | -16.3061 | -33.5256 | 82.9279 | -46.8121 | -1.9175 | -49.9211 | -179.8656 | -56.8242 | 69.8507 | -52.2301 | -50.9276 | -22.6925 | -156.9816 | -18.6793 | -152.4372 | -25.8911 | 70.0314 | -20.1558 | -66.7917 | -20.2018 | 133.2925 | -17.1544 | 130.1641 | -25.3407 | 39.4276 | -21.4287 | -171.0049 | -43.4702 | -42.5543 | -47.4292 | -47.435 | -57.0053 | -36.7692 | -43.1965 | -46.9486 | -45.8352 | -46.1691 | -54.2004 | -36.2572 | -41.3208 | 324 | -35.7641 | -44.0769 | -35.8068 | -49.1894 | -33.1868 | -45.6146 | -33.3703 | -45.3915 | 324 | -43.1525 | -42.0391 | -43.6389 | -53.3557 | -33.1196 | -39.0409 | -43.299 | -41.6796 | -43.9035 | -52.8497 | -33.2377 | -39.665 | -38.7582 | -43.6331 | -42.373 | -50.5508 | -32.6076 | -37.1652 | -38.9047 | -43.2736 | -42.6376 | -50.0448 | -32.7257 | -37.7893
325 | -3.8118 | 0 | -3.6594 | 0 | -4.1204 | 0 | -3.554 | 0 | -46.1927 | 55.4646 | -35.1592 | 160.5863 | -69.9486 | -71.8449 | -46.8665 | -155.2851 | -52.3756 | 11.4873 | -65.1389 | 141.9978 | -46.2187 | -1.7622 | -33.2462 | 71.7428 | -46.7376 | -7.4097 | -48.9471 | 166.3552 | -55.3001 | 54.943 | -54.7626 | -104.361 | -22.0382 | -169.7312 | -18.5728 | -168.7162 | -25.5945 | 59.0906 | -19.6815 | -76.1634 | -19.9173 | 122.6782 | -16.9604 | 119.8846 | -25.067 | 33.3798 | -20.5661 | 174.7604 | -43.6205 | -42.6283 | -46.4565 | -47.5151 | -56.4526 | -37.019 | -43.4524 | -46.3704 | -45.7922 | -46.6633 | -54.3391 | -36.6243 | -41.9649 | 325 | -34.8284 | -42.9765 | -34.8715 | -52.0801 | -32.8513 | -44.0252 | -33.1012 | -45.6088 | 325 | -42.5586 | -41.9804 | -43.7033 | -52.7932 | -33.3596 | -39.332 | -42.711 | -41.6718 | -43.9611 | -52.3322 | -33.465 | -39.8984 | -38.8165 | -42.6447 | -42.8515 | -50.6797 | -32.9649 | -37.8445 | -38.9689 | -42.3361 | -43.1093 | -50.2187 | -33.0703 | -38.4109
326 | -3.8352 | 0 | -3.6658 | 0 | -4.0947 | 0 | -3.5568 | 0 | -44.1754 | 61.1092 | -34.7514 | 146.2072 | -59.6726 | -166.1176 | -45.6915 | -161.5039 | -52.5051 | -0.4038 | -55.3508 | -157.3065 | -43.6515 | 0.2993 | -33.2227 | 60.158 | -46.3725 | -11.3629 | -47.9919 | 156.1759 | -54.4027 | 40.6344 | -52.6608 | -154.5439 | -22.1915 | 175.1034 | -18.928 | 172.5547 | -24.8956 | 46.5291 | -19.886 | -82.5627 | -19.9531 | 113.5705 | -17.1496 | 111.8657 | -24.5357 | 26.9078 | -20.1509 | 158.5018 | -43.7947 | -42.6025 | -45.6673 | -47.5213 | -55.9861 | -37.2744 | -43.7166 | -45.7236 | -45.6048 | -47.1502 | -54.2752 | -36.997 | -43.0443 | 326 | -34.2693 | -41.4985 | -34.3801 | -50.1719 | -32.6574 | -42.0312 | -33.0327 | -44.9347 | 326 | -41.8884 | -41.7696 | -43.6861 | -52.3203 | -33.6086 | -39.6219 | -42.0578 | -41.5101 | -43.9645 | -51.8914 | -33.7176 | -40.1598 | -38.7673 | -41.8321 | -43.315 | -50.6094 | -33.3312 | -38.9496 | -38.9367 | -41.5726 | -43.5934 | -50.1805 | -33.4402 | -39.4875
327 | -3.8655 | 0 | -3.671 | 0 | -4.0558 | 0 | -3.579 | 0 | -42.1928 | 58.1564 | -34.9071 | 131.1596 | -54.2772 | 170.7748 | -44.8006 | -166.7561 | -52.6472 | -10.303 | -50.9991 | -157.6484 | -41.5268 | -5.5971 | -33.5722 | 47.3727 | -45.7283 | -17.7243 | -46.9424 | 147.9955 | -53.9671 | 24.7682 | -49.8269 | 175.8428 | -22.6297 | 157.0879 | -19.5668 | 152.5942 | -25.6631 | 32.5885 | -19.5271 | -92.3868 | -20.7778 | 110.037 | -17.742 | 104.7915 | -25.5428 | 14.911 | -20.1732 | 149.3381 | -43.9287 | -42.2315 | -44.9357 | -47.5498 | -55.7685 | -37.4698 | -43.9444 | -44.6964 | -45.4202 | -47.8624 | -53.9757 | -37.298 | -44.677 | 327 | -34.1211 | -40.048 | -34.3876 | -47.666 | -32.705 | -40.2416 | -33.2795 | -43.8554 | 327 | -40.8309 | -41.5547 | -43.6843 | -52.0975 | -33.7988 | -39.8886 | -41.0254 | -41.3644 | -43.9708 | -51.7127 | -33.8908 | -40.3654 | -38.366 | -41.0702 | -43.9969 | -50.3047 | -33.627 | -40.6212 | -38.5605 | -40.8799 | -44.2834 | -49.9199 | -33.719 | -41.098
328 | -3.9154 | 0 | -3.6741 | 0 | -4.0098 | 0 | -3.5993 | 0 | -40.5181 | 51.9608 | -35.9471 | 117.142 | -50.9396 | 149.1369 | -43.8545 | -171.7803 | -52.6834 | -20.9573 | -48.8023 | -160.8385 | -39.8581 | -14.3653 | -34.541 | 33.3478 | -45.0972 | -24.726 | -45.6918 | 137.9524 | -54.0135 | 9.4821 | -47.7471 | 154.5882 | -23.1533 | 142.9161 | -20.4373 | 131.4303 | -26.3951 | 22.6131 | -19.9979 | -103.2179 | -21.0217 | 102.0186 | -17.7657 | 94.9249 | -26.6547 | 6.1271 | -19.8573 | 131.9966 | -44.0019 | -41.1267 | -44.2315 | -47.7754 | -55.8535 | -37.5642 | -44.0647 | -42.8965 | -45.2943 | -48.8733 | -53.5178 | -37.5605 | -46.8885 | 328 | -34.546 | -38.6866 | -35.1059 | -45.7478 | -33.1361 | -38.7207 | -34.0313 | -42.8659 | 328 | -38.9811 | -41.3789 | -43.86 | -52.1794 | -33.8901 | -40.0549 | -39.2224 | -41.2845 | -44.1761 | -51.8437 | -33.9649 | -40.4654 | -37.2113 | -40.3161 | -44.9579 | -49.8437 | -33.8864 | -42.8787 | -37.4526 | -40.2217 | -45.274 | -49.508 | -33.9612 | -43.2892
329 | -3.9512 | 0 | -3.6816 | 0 | -3.9785 | 0 | -3.6113 | 0 | -39.1771 | 41.6388 | -38.1002 | 106.6492 | -49.2503 | 130.2375 | -42.8713 | -178.1649 | -52.9319 | -34.988 | -47.4096 | -165.6152 | -38.5556 | -25.5363 | -36.7042 | 19.5722 | -44.7835 | -34.5238 | -44.3765 | 127.1433 | -54.6199 | -5.3792 | -46.6473 | 137.3288 | -24.1161 | 128.9875 | -21.8561 | 109.3926 | -28.4177 | 10.9219 | -19.8533 | -115.1885 | -21.0399 | 93.57 | -18.3704 | 88.5248 | -29.0625 | -0.5797 | -19.7554 | 118.9014 | -44.0562 | -39.9429 | -43.5484 | -48.2632 | -56.3414 | -37.6265 | -43.9316 | -40.8418 | -45.0488 | -50.3183 | -53.1035 | -37.7402 | -49.4897 | 329 | -35.4118 | -37.5061 | -36.4848 | -44.543 | -34.1309 | -37.4615 | -35.6585 | -42.341 | 329 | -36.8906 | -41.0976 | -44.312 | -52.6598 | -33.9449 | -39.9531 | -37.1602 | -41.0703 | -44.6519 | -52.3629 | -34.0152 | -40.3203 | -35.9917 | -39.5972 | -46.3671 | -49.4219 | -34.0586 | -45.5112 | -36.2613 | -39.5699 | -46.707 | -49.125 | -34.1289 | -45.8784
330 | -3.9475 | 0 | -3.676 | 0 | -3.9338 | 0 | -3.6093 | 0 | -38.3449 | 29.3603 | -40.7378 | 106.6924 | -47.8624 | 115.7824 | -42.109 | 173.1389 | -53.6706 | -49.3538 | -46.6756 | -167.6498 | -37.606 | -37.7102 | -40.3772 | 15.6621 | -44.9066 | -41.4023 | -43.348 | 113.1571 | -55.5893 | -17.6595 | -45.9401 | 125.0412 | -24.9815 | 109.7032 | -24.4078 | 86.0726 | -32.139 | 2.3906 | -20.4766 | -129.4531 | -22.2195 | 89.2468 | -19.249 | 85.3702 | -34.195 | 1.4277 | -20.0203 | 109.3385 | -44.3551 | -39.4996 | -43.2517 | -48.8942 | -57.1246 | -37.7691 | -43.6799 | -39.5861 | -44.5413 | -51.84 | -52.8049 | -37.8713 | -52.0423 | 330 | -36.0708 | -36.7322 | -37.7622 | -43.7516 | -35.2647 | -36.5255 | -37.8673 | -42.1797 | 330 | -35.6386 | -40.5938 | -44.9467 | -53.4486 | -34.0931 | -39.7461 | -35.9101 | -40.6075 | -45.2849 | -53.1908 | -34.1598 | -40.0706 | -35.5521 | -39.3042 | -47.8925 | -49.1289 | -34.1953 | -48.1085 | -35.8236 | -39.3179 | -48.2307 | -48.8711 | -34.262 | -48.433
331 | -3.9356 | 0 | -3.6824 | 0 | -3.9041 | 0 | -3.5927 | 0 | -37.9883 | 17.3071 | -43.0785 | 120.3639 | -46.5864 | 101.6011 | -41.582 | 163.8309 | -55.1135 | -63.2885 | -45.7188 | -167.3881 | -37.0463 | -51.2503 | -44.6794 | 36.3836 | -44.9256 | -46.6718 | -42.7821 | 98.5647 | -56.7709 | -28.0279 | -45.3097 | 114.4674 | -27.5816 | 96.9964 | -27.6335 | 55.6013 | -39.6973 | -0.3532 | -20.5997 | -142.0185 | -24.0304 | 87.9705 | -20.3057 | 86.0429 | -38.4378 | 59.1944 | -20.4329 | 101.097 | -44.7833 | -39.4464 | -43.2044 | -49.7364 | -58.3301 | -37.9737 | -43.5574 | -39.0409 | -44.1504 | -52.7762 | -52.7058 | -38.076 | -52.7545 | 331 | -36.3811 | -36.3551 | -38.3717 | -42.8545 | -35.7901 | -35.9824 | -39.3483 | -41.9573 | 331 | -35.1053 | -40.2148 | -45.8008 | -54.6477 | -34.2913 | -39.6533 | -35.3585 | -40.2463 | -46.1437 | -54.426 | -34.381 | -39.9647 | -35.5108 | -39.2688 | -48.8406 | -49.0234 | -34.3936 | -48.8504 | -35.764 | -39.3003 | -49.1835 | -48.8017 | -34.4833 | -49.1618
332 | -3.9274 | 0 | -3.6918 | 0 | -3.903 | 0 | -3.5763 | 0 | -37.9379 | 5.0628 | -42.5798 | 144.2728 | -45.0599 | 87.6933 | -41.2583 | 153.4854 | -57.1129 | -76.6032 | -44.3908 | -169.5645 | -36.7606 | -65.2817 | -42.9648 | 75.6048 | -44.7683 | -49.4584 | -42.746 | 83.1881 | -57.8346 | -35.9319 | -44.5915 | 103.1855 | -29.9638 | 86.4788 | -31.7044 | 13.4902 | -34.8734 | 75.7743 | -21.6913 | -159.7512 | -24.8277 | 90.1362 | -20.3127 | 89.7743 | -30.068 | 89.0227 | -20.9183 | 94.3142 | -44.9683 | -39.5623 | -43.325 | -50.898 | -60.1167 | -38.3045 | -43.4496 | -38.9109 | -43.9899 | -52.4301 | -52.6567 | -38.3327 | -51.0227 | 332 | -36.07 | -36.2422 | -37.7874 | -41.579 | -35.306 | -35.7574 | -38.5885 | -41.5649 | 332 | -34.9835 | -40.0625 | -46.9706 | -56.4249 | -34.6127 | -39.5466 | -35.2191 | -40.0869 | -47.3217 | -56.2137 | -34.7282 | -39.8733 | -35.6349 | -39.3976 | -48.5027 | -48.9649 | -34.6409 | -47.1197 | -35.8705 | -39.422 | -48.8538 | -48.7537 | -34.7564 | -47.4464
333 | -3.9265 | 0 | -3.6843 | 0 | -3.9187 | 0 | -3.5749 | 0 | -38.1078 | -7.6252 | -39.6445 | 153.7332 | -43.7475 | 71.1781 | -41.2586 | 143.2056 | -60.3834 | -87.6839 | -43.0882 | -175.5467 | -36.7923 | -79.5967 | -38.6092 | 82.6751 | -44.3753 | -52.1504 | -43.1787 | 69.6675 | -58.9536 | -43.9849 | -44.2002 | 91.1915 | -33.1914 | 89.4921 | -33.5096 | -70.1751 | -30.3638 | 81.8336 | -22.9101 | -179.0626 | -26.6459 | 104.0695 | -20.5252 | 97.023 | -27.1144 | 90.2023 | -22.1056 | 89.7708 | -44.7263 | -39.8356 | -43.488 | -52.2771 | -62.2849 | -38.6481 | -43.4304 | -39.1726 | -44.0359 | -51.2117 | -52.4812 | -38.4773 | -48.874 | 333 | -35.1523 | -36.3759 | -36.3361 | -40.3517 | -34.1616 | -35.8725 | -36.5002 | -41.203 | 333 | -35.2461 | -40.1094 | -48.3506 | -58.6006 | -34.9638 | -39.5117 | -35.4883 | -40.1172 | -48.7022 | -58.3662 | -35.0732 | -39.8555 | -35.9091 | -39.5615 | -47.2852 | -48.7969 | -34.793 | -44.9553 | -36.1513 | -39.5693 | -47.6368 | -48.5625 | -34.9024 | -45.2991
334 | -3.9559 | 0 | -3.7045 | 0 | -3.9606 | 0 | -3.5817 | 0 | -38.454 | -18.9282 | -36.9739 | 151.4146 | -42.5825 | 55.4794 | -41.5671 | 133.1257 | -64.6354 | -83.5687 | -42.288 | 176.4856 | -37.1455 | -93.5453 | -35.7105 | 75.3047 | -43.5554 | -53.3853 | -43.9657 | 58.6154 | -60.3504 | -52.6893 | -44.1555 | 78.6564 | -33.2219 | 108.0391 | -27.2242 | -128.6521 | -26.5208 | 73.7459 | -24.144 | 162.5421 | -25.4249 | 115.1939 | -19.4271 | 101.5629 | -24.5233 | 81.5558 | -22.1783 | 86.8453 | -44.219 | -40.229 | -43.3141 | -53.3205 | -64.4299 | -38.9008 | -43.5326 | -39.7301 | -44.1004 | -49.9975 | -52.2084 | -38.4371 | -47.2242 | 334 | -33.9939 | -36.7201 | -34.8216 | -39.4094 | -32.9623 | -36.3078 | -34.5962 | -40.7865 | 334 | -35.7742 | -40.1445 | -49.3646 | -60.7254 | -35.1963 | -39.572 | -36.0256 | -40.1398 | -49.7388 | -60.4693 | -35.3191 | -39.9509 | -36.2731 | -39.3582 | -46.0416 | -48.5039 | -34.7326 | -43.2636 | -36.5245 | -39.3535 | -46.4158 | -48.2478 | -34.8554 | -43.6425
335 | -3.9797 | 0 | -3.7216 | 0 | -3.9741 | 0 | -3.595 | 0 | -39.1709 | -30.8774 | -35.0617 | 144.3141 | -41.54 | 38.595 | -42.2342 | 125.6163 | -66.0308 | -62.1117 | -41.6111 | 168.3043 | -37.9645 | -108.1717 | -33.96 | 65.4798 | -42.1873 | -58.7994 | -44.9935 | 50.2304 | -62.2828 | -63.0275 | -44.2965 | 66.0305 | -32.3519 | 132.5031 | -22.5394 | -153.5402 | -26.4019 | 59.4217 | -26.4522 | 156.2491 | -23.9883 | 126.5856 | -17.8547 | 100.4626 | -24.1821 | 72.5523 | -23.0749 | 86.6629 | -43.6848 | -40.24 | -42.4998 | -53.318 | -65.8338 | -38.9356 | -43.6024 | -40.1681 | -43.7067 | -49.2333 | -51.9552 | -38.233 | -46.0201 | 335 | -32.9848 | -37.4216 | -33.56 | -38.5573 | -32.062 | -37.1658 | -33.2731 | -40.0786 | 335 | -36.1884 | -39.727 | -49.3383 | -62.1122 | -35.214 | -39.6283 | -36.4465 | -39.7326 | -49.723 | -61.8597 | -35.3406 | -40.0074 | -36.2603 | -38.5201 | -45.2536 | -48.2336 | -34.5114 | -42.046 | -36.5184 | -38.5257 | -45.6383 | -47.9811 | -34.638 | -42.4251
336 | -4.0008 | 0 | -3.7509 | 0 | -3.9942 | 0 | -3.6144 | 0 | -40.2336 | -42.8412 | -33.6757 | 135.1915 | -40.8062 | 19.4843 | -43.0363 | 118.8923 | -65.0404 | -49.2138 | -41.3879 | 157.7293 | -39.2096 | -121.3147 | -32.7668 | 55.1555 | -40.9249 | -67.4825 | -46.1278 | 44.3194 | -65.6814 | -76.8712 | -44.7898 | 52.2896 | -28.9138 | 126.0211 | -19.8144 | -176.9705 | -25.4856 | 47.1281 | -29.3112 | 144.1342 | -22.1292 | 128.5262 | -16.5778 | 96.7856 | -23.6768 | 63.459 | -24.3094 | 88.7893 | -43.2496 | -40.0464 | -41.4863 | -52.5838 | -65.8802 | -38.8597 | -43.5257 | -40.3887 | -43.0068 | -48.7309 | -51.8329 | -38.0603 | -45.0759 | 336 | -32.1696 | -38.393 | -32.586 | -38.0683 | -31.3691 | -38.3977 | -32.3179 | -39.4203 | 336 | -36.3879 | -39.006 | -48.583 | -62.1293 | -35.1088 | -39.5315 | -36.6378 | -39.0126 | -48.9694 | -61.886 | -35.2453 | -39.9113 | -36.0456 | -37.4855 | -44.7301 | -48.082 | -34.3094 | -41.0817 | -36.2955 | -37.4921 | -45.1165 | -47.8387 | -34.4459 | -41.4615
337 | -4.027 | 0 | -3.8043 | 0 | -4.0035 | 0 | -3.6246 | 0 | -41.7438 | -53.5788 | -32.6084 | 125.7083 | -40.397 | -0.4878 | -43.926 | 114.3006 | -63.8755 | -55.0439 | -41.5351 | 146.3161 | -40.9821 | -132.9097 | -31.8825 | 45.2019 | -39.9549 | -79.8838 | -47.302 | 40.9538 | -73.867 | -93.0516 | -45.5552 | 37.5202 | -26.4203 | 114.1739 | -17.6866 | 163.4108 | -26.0203 | 31.053 | -32.9399 | 131.5439 | -20.4828 | 125.8746 | -15.3307 | 90.8957 | -23.0069 | 57.1032 | -23.7896 | 94.2189 | -42.9512 | -39.8457 | -40.623 | -51.4512 | -64.6113 | -38.7637 | -43.277 | -40.5387 | -42.3004 | -48.3473 | -51.8395 | -37.9879 | -44.2077 | 337 | -31.5078 | -39.6724 | -31.8098 | -37.9076 | -30.8141 | -40.0694 | -31.582 | -38.897 | 337 | -36.5117 | -38.2734 | -47.4242 | -60.807 | -34.9594 | -39.2735 | -36.7344 | -38.2969 | -47.8266 | -60.6078 | -35.1391 | -39.6524 | -35.8187 | -36.596 | -44.3203 | -48.0352 | -34.1836 | -40.2042 | -36.0414 | -36.6195 | -44.7227 | -47.836 | -34.3633 | -40.5831
338 | -4.0396 | 0 | -3.8439 | 0 | -3.9914 | 0 | -3.6478 | 0 | -43.8181 | -60.9317 | -31.7022 | 117.2566 | -40.6632 | -20.7591 | -44.7313 | 113.2088 | -63.9674 | -68.8731 | -42.6549 | 136.4079 | -43.4043 | -140.2966 | -31.1613 | 35.8189 | -39.5936 | -91.9931 | -48.364 | 41.3945 | -72.5689 | 78.2175 | -47.4334 | 21.6887 | -25.2879 | 98.1892 | -16.2959 | 145.2712 | -28.2766 | 9.2064 | -36.9687 | -173.028 | -19.7633 | 124.3913 | -14.5953 | 83.004 | -24.9427 | 51.8723 | -24.0366 | 102.4811 | -42.8969 | -39.8686 | -40.1043 | -50.2211 | -62.6977 | -38.7866 | -42.883 | -40.8899 | -41.8599 | -48.0353 | -51.8478 | -38.0618 | -43.3399 | 338 | -30.9523 | -41.2173 | -31.1711 | -38.5231 | -30.3582 | -42.1973 | -30.98 | -38.9305 | 338 | -36.8503 | -37.8203 | -46.1815 | -58.8538 | -34.9427 | -38.8916 | -37.046 | -37.8685 | -46.5733 | -58.7063 | -35.1388 | -39.2352 | -35.829 | -36.0647 | -43.9957 | -48.0039 | -34.2179 | -39.3485 | -36.0247 | -36.1129 | -44.3875 | -47.8564 | -34.414 | -39.6921
339 | -4.0515 | 0 | -3.8981 | 0 | -3.9973 | 0 | -3.6731 | 0 | -46.3566 | -63.7086 | -30.9408 | 106.1077 | -41.2851 | -40.2588 | -45.3676 | 113.0154 | -65.4619 | -96.8936 | -44.3846 | 130.3796 | -46.4539 | -140.3615 | -30.6094 | 24.8571 | -39.5094 | -105.0721 | -49.0339 | 45.1693 | -62.881 | 55.0271 | -50.2743 | 7.905 | -24.1887 | 79.7774 | -15.2223 | 126.8399 | -31.7294 | 4.7927 | -30.742 | -148.8351 | -18.6111 | 115.9048 | -13.8642 | 73.9942 | -24.9422 | 56.7189 | -23.0323 | 108.7326 | -42.9978 | -39.9916 | -39.8231 | -49.0173 | -61.2126 | -38.9447 | -42.441 | -41.5793 | -41.7078 | -47.7887 | -51.5817 | -38.2668 | -42.5253 | 339 | -30.4443 | -42.8001 | -30.6012 | -39.5426 | -29.9841 | -44.4815 | -30.5014 | -39.1413 | 339 | -37.5278 | -37.6563 | -44.9658 | -57.3145 | -35.0466 | -38.4437 | -37.6812 | -37.7105 | -45.3442 | -57.2153 | -35.2716 | -38.7679 | -35.9401 | -35.7716 | -43.7372 | -47.6836 | -34.3687 | -38.528 | -36.0935 | -35.8258 | -44.1156 | -47.5844 | -34.5937 | -38.8522
340 | -4.0659 | 0 | -3.9397 | 0 | -3.9883 | 0 | -3.7153 | 0 | -48.9322 | -57.6611 | -30.4143 | 94.719 | -42.4811 | -57.716 | -45.5872 | 116.0033 | -68.1864 | -159.9902 | -46.8369 | 131.7628 | -49.1895 | -123.216 | -30.285 | 13.8862 | -39.7046 | -115.5514 | -48.9187 | 51.4752 | -58.284 | 35.8754 | -54.6579 | -8.751 | -25.4021 | 57.5159 | -14.8746 | 111.0178 | -43.5189 | -19.0426 | -25.6622 | -151.566 | -18.0563 | 110.6966 | -13.5394 | 64.412 | -26.1892 | 65.2657 | -21.0965 | 110.6663 | -43.4846 | -40.1583 | -39.603 | -47.8362 | -61.051 | -39.1231 | -42.0139 | -42.2774 | -41.8003 | -47.6076 | -50.9397 | -38.4454 | -41.7388 | 340 | -30.0954 | -43.9187 | -30.1893 | -41.1155 | -29.7651 | -45.79 | -30.2103 | -39.51 | 340 | -38.2115 | -37.7344 | -43.7703 | -57.1113 | -35.1834 | -38.0256 | -38.3377 | -37.812 | -44.1209 | -57.0627 | -35.4078 | -38.2986 | -36.0924 | -35.5371 | -43.5417 | -47 | -34.5057 | -37.7505 | -36.2186 | -35.6147 | -43.8923 | -46.9514 | -34.7301 | -38.0235
341 | -4.0729 | 0 | -3.9675 | 0 | -3.9909 | 0 | -3.7565 | 0 | -50.7692 | -41.5437 | -30.2108 | 82.7323 | -44.168 | -74.7421 | -45.4098 | 117.4963 | -63.2689 | 119.2972 | -48.8911 | 148.4803 | -48.1516 | -98.0104 | -30.2872 | 2.4546 | -40.0834 | -127.5342 | -47.8901 | 55.5099 | -55.2243 | 15.6538 | -64.3168 | -45.5746 | -26.548 | 32.0403 | -14.7885 | 94.4734 | -37.3168 | 173.3855 | -22.3069 | -164.3953 | -17.6864 | 106.0074 | -13.5096 | 54.6197 | -25.0914 | 77.3819 | -19.3352 | 108.5912 | -44.2076 | -40.149 | -39.5865 | -46.9693 | -63.2662 | -39.1842 | -41.655 | -42.6784 | -42.1472 | -47.5808 | -50.1081 | -38.5612 | -41.0654 | 341 | -30.0031 | -44.2454 | -30.0248 | -42.8668 | -29.7905 | -44.6138 | -30.2107 | -39.9366 | 341 | -38.6055 | -38.0743 | -42.8964 | -59.2987 | -35.2167 | -37.6641 | -38.7109 | -38.1563 | -43.2128 | -59.2753 | -35.4277 | -37.8985 | -36.0761 | -35.5136 | -43.5079 | -46.1406 | -34.5937 | -37.0745 | -36.1815 | -35.5956 | -43.8243 | -46.1172 | -34.8047 | -37.3089
342 | -4.0799 | 0 | -3.9714 | 0 | -4.005 | 0 | -3.7875 | 0 | -49.8896 | -18.1122 | -30.3685 | 70.547 | -46.6482 | -89.2435 | -44.8168 | 119.2128 | -57.4741 | 73.1774 | -47.6838 | 172.8507 | -44.9839 | -92.1769 | -30.6306 | -9.295 | -41.0459 | -138.0054 | -46.5534 | 54.1441 | -53.5206 | -7.7025 | -58.4656 | 169.0487 | -27.9192 | 9.3378 | -14.5051 | 78.598 | -28.0833 | 128.9944 | -19.97 | 177.8172 | -17.71 | 102.7142 | -13.6279 | 45.4467 | -23.1895 | 83.4165 | -18.1979 | 104.305 | -44.8442 | -39.9755 | -39.8277 | -46.5044 | -69.0903 | -39.2216 | -41.4597 | -42.7746 | -42.5799 | -47.4441 | -49.5378 | -38.5519 | -40.5169 | 342 | -30.2203 | -43.4648 | -30.1382 | -43.9286 | -30.1091 | -42.3433 | -30.514 | -40.7331 | 342 | -38.6947 | -38.5 | -42.4245 | -65.1189 | -35.2502 | -37.4547 | -38.8032 | -38.5749 | -42.7169 | -65.0853 | -35.4341 | -37.6722 | -35.8956 | -35.7478 | -43.3642 | -45.5664 | -34.5805 | -36.5119 | -36.0041 | -35.8227 | -43.6566 | -45.5328 | -34.7644 | -36.7294
343 | -4.0532 | 0 | -3.937 | 0 | -4.0465 | 0 | -3.8302 | 0 | -46.7803 | -10.6192 | -30.8906 | 58.4662 | -50.101 | -100.3594 | -43.8019 | 118.5003 | -54.4596 | 39.8251 | -44.6833 | 178.4183 | -42.6065 | -99.3067 | -31.2845 | -20.7429 | -42.3881 | -145.4329 | -45.4237 | 48.8598 | -53.0544 | -33.3787 | -51.0676 | 139.7464 | -30.3209 | -37.4871 | -15.163 | 62.7769 | -24.7271 | 115.2365 | -18.156 | 162.8102 | -16.6428 | 97.4306 | -14.1998 | 36.2999 | -20.8554 | 82.9351 | -16.4921 | 96.6927 | -45.009 | -39.7474 | -40.1877 | -46.3527 | -66.4933 | -39.2278 | -41.5542 | -42.652 | -42.6001 | -47.1284 | -49.5972 | -38.441 | -40.0387 | 343 | -30.7296 | -41.7889 | -30.5048 | -43.2453 | -30.6726 | -40.5303 | -31.0765 | -41.5198 | 343 | -38.5988 | -38.5469 | -42.2995 | -62.5563 | -35.2908 | -37.5077 | -38.715 | -38.5536 | -42.5225 | -62.4468 | -35.3976 | -37.724 | -35.6942 | -36.1345 | -43.0752 | -45.6602 | -34.504 | -35.9922 | -35.8104 | -36.1412 | -43.2982 | -45.5507 | -34.6108 | -36.2085
344 | -4.0624 | 0 | -3.8921 | 0 | -4.0655 | 0 | -3.8626 | 0 | -44.1586 | -16.8978 | -31.8114 | 48.6997 | -57.0008 | -110.2639 | -42.6258 | 114.7642 | -52.9353 | 13.0066 | -42.3635 | 176.3263 | -41.1385 | -109.8416 | -32.26 | -28.5407 | -44.0363 | -146.3339 | -44.4693 | 44.2241 | -53.7156 | -54.0853 | -47.2565 | 120.5775 | -28.4126 | -95.5487 | -16.1954 | 47.917 | -22.9655 | 99.4475 | -16.9697 | 148.617 | -17.1921 | 96.6465 | -15.2078 | 27.4765 | -19.8442 | 78.1788 | -15.571 | 87.9556 | -44.8936 | -39.5905 | -40.4897 | -46.2725 | -61.3936 | -39.2468 | -41.8491 | -42.3741 | -42.2655 | -46.646 | -50.0679 | -38.3312 | -39.6357 | 344 | -31.5531 | -40.0834 | -31.126 | -41.8634 | -31.4831 | -39.321 | -31.8787 | -42.0385 | 344 | -38.3117 | -38.2031 | -42.2101 | -57.5015 | -35.3547 | -37.7836 | -38.482 | -38.2 | -42.4099 | -57.3281 | -35.3842 | -37.9865 | -35.5281 | -36.4273 | -42.5836 | -46.1758 | -34.4391 | -35.5702 | -35.6984 | -36.4242 | -42.7834 | -46.0024 | -34.4686 | -35.7731
345 | -4.0606 | 0 | -3.8379 | 0 | -4.0723 | 0 | -3.8965 | 0 | -42.444 | -28.1662 | -33.1826 | 38.732 | -62.5373 | 19.7426 | -41.5632 | 106.4652 | -52.3424 | -11.1914 | -40.5112 | 169.1662 | -40.2459 | -121.7671 | -33.5634 | -35.8045 | -45.0261 | -141.04 | -43.5354 | 37.6213 | -55.0632 | -72.4485 | -44.8759 | 103.4452 | -26.7486 | -144.8708 | -17.5874 | 36.8736 | -20.711 | 81.9071 | -15.6598 | 130.2438 | -16.9404 | 94.5449 | -16.6355 | 20.659 | -19.0887 | 71.2822 | -14.9617 | 78.4943 | -44.7222 | -39.5621 | -40.6402 | -46.1792 | -58.8785 | -39.23 | -42.2403 | -42.0411 | -41.7598 | -46.0879 | -50.7442 | -38.2911 | -39.2557 | 345 | -32.6916 | -38.7756 | -31.9435 | -40.2098 | -32.4708 | -38.4796 | -32.8646 | -41.7335 | 345 | -37.9805 | -37.6992 | -42.1186 | -55.0406 | -35.3921 | -38.168 | -38.2032 | -37.6875 | -42.2827 | -54.8062 | -35.3335 | -38.3438 | -35.5015 | -36.5796 | -42.0273 | -46.9063 | -34.4532 | -35.1834 | -35.7242 | -36.5679 | -42.1914 | -46.6719 | -34.3946 | -35.3592
346 | -4.063 | 0 | -3.7831 | 0 | -4.0927 | 0 | -3.9351 | 0 | -41.4071 | -41.2368 | -35.1214 | 33.1442 | -50.3548 | 20.2201 | -40.781 | 97.2514 | -52.4147 | -31.0986 | -39.0989 | 160.6467 | -39.7141 | -134.2202 | -35.1551 | -38.269 | -44.8149 | -130.6241 | -42.7275 | 29.2641 | -57.1837 | -88.336 | -43.2524 | 86.6202 | -23.4367 | -168.4303 | -20.3653 | 20.8113 | -20.9747 | 63.5332 | -15.2769 | 116.0488 | -17.1917 | 93.1398 | -18.559 | 15.5174 | -18.6747 | 63.4959 | -15.0311 | 67.3187 | -44.5149 | -39.6995 | -40.6074 | -46.1009 | -57.4485 | -39.18 | -42.7284 | -41.7684 | -41.2544 | -45.5487 | -51.5565 | -38.2997 | -38.9556 | 346 | -34.0999 | -37.9156 | -32.8894 | -38.6009 | -33.517 | -37.9027 | -33.917 | -40.8512 | 346 | -37.7054 | -37.1914 | -42.0379 | -53.6654 | -35.3969 | -38.6357 | -37.9853 | -37.1617 | -42.1658 | -53.3558 | -35.2449 | -38.7933 | -35.6365 | -36.5444 | -41.4857 | -47.7734 | -34.5166 | -34.8629 | -35.9164 | -36.5147 | -41.6136 | -47.4638 | -34.3646 | -35.0205
347 | -4.0884 | 0 | -3.7521 | 0 | -4.0999 | 0 | -3.962 | 0 | -40.8652 | -55.6699 | -37.5582 | 36.1191 | -45.1837 | 3.1383 | -40.3192 | 85.6717 | -53.03 | -49.6473 | -38.1851 | 149.7913 | -39.4956 | -147.1111 | -36.8449 | -35.8309 | -43.284 | -126.5085 | -42.1203 | 18.8521 | -60.2857 | -99.309 | -42.3427 | 67.6895 | -21.2546 | 163.6789 | -24.3202 | 21.025 | -20.9837 | 46.5896 | -15.0156 | 101.2983 | -16.3116 | 89.7108 | -20.485 | 23.7633 | -17.9246 | 57.5684 | -14.5186 | 58.4141 | -44.2026 | -39.9527 | -40.4335 | -46.0347 | -56.4644 | -39.1168 | -43.2716 | -41.7405 | -40.7642 | -45.0138 | -52.5373 | -38.3303 | -38.7284 | 347 | -35.4104 | -37.4514 | -33.7649 | -37.2777 | -34.3647 | -37.579 | -34.8617 | -39.7391 | 347 | -37.6521 | -36.6758 | -41.9463 | -52.7123 | -35.3647 | -39.1717 | -37.9884 | -36.6643 | -42.0727 | -52.3645 | -35.1548 | -39.3096 | -35.8643 | -36.3451 | -40.9254 | -48.7852 | -34.5782 | -34.6285 | -36.2006 | -36.3336 | -41.0518 | -48.4374 | -34.3683 | -34.7664
348 | -4.1157 | 0 | -3.736 | 0 | -4.0987 | 0 | -3.9616 | 0 | -40.7776 | -70.5084 | -39.3808 | 51.9645 | -42.1343 | -12.6917 | -40.2043 | 73.69 | -54.294 | -67.156 | -37.7834 | 138.4982 | -39.5788 | -160.2097 | -37.7538 | -25.0769 | -41.5928 | -128.088 | -41.7919 | 7.6952 | -65.1925 | -100.8042 | -42.0735 | 50.4729 | -19.9713 | 143.9895 | -28.9467 | 53.1678 | -22.1475 | 27.2338 | -15.1249 | 86.7489 | -15.7866 | 86.6394 | -21.4915 | 38.7872 | -18.0903 | 52.4211 | -14.8088 | 47.971 | -43.8076 | -40.3968 | -40.1091 | -45.9951 | -55.6982 | -39.0687 | -43.8571 | -41.9268 | -40.2485 | -44.5837 | -53.8141 | -38.3526 | -38.5631 | 348 | -35.8485 | -37.3819 | -34.2329 | -36.3547 | -34.594 | -37.5281 | -35.2876 | -38.8062 | 348 | -37.8111 | -36.1328 | -41.8794 | -51.9622 | -35.3327 | -39.7584 | -38.1908 | -36.1498 | -42.0335 | -51.5995 | -35.1071 | -39.8955 | -36.2811 | -35.9934 | -40.468 | -50.0781 | -34.6166 | -34.4644 | -36.6608 | -36.0104 | -40.6221 | -49.7154 | -34.391 | -34.6015
349 | -4.1422 | 0 | -3.7438 | 0 | -4.0836 | 0 | -3.9547 | 0 | -41.0644 | -84.9548 | -38.2026 | 73.288 | -39.7794 | -29.2443 | -40.4454 | 61.0396 | -56.3333 | -83.4796 | -37.6834 | 128.3699 | -39.9962 | -173.0332 | -36.9378 | -12.58 | -39.9922 | -134.1485 | -41.7643 | -4.1374 | -69.9807 | -56.3768 | -42.2099 | 33.3807 | -19.4828 | 124.4409 | -26.6483 | 92.2827 | -24.311 | 3.5679 | -15.7841 | 72.6439 | -15.5983 | 83.2351 | -20.7447 | 52.0772 | -18.447 | 49.5004 | -15.4356 | 37.5811 | -43.3934 | -40.9598 | -39.6669 | -45.9559 | -55.0692 | -39.0887 | -44.3922 | -42.4508 | -39.7477 | -44.2047 | -55.4821 | -38.3961 | -38.4542 | 349 | -34.7529 | -37.674 | -33.8511 | -35.5594 | -33.9505 | -37.778 | -34.8262 | -37.948 | 349 | -38.3086 | -35.6055 | -41.8137 | -51.3254 | -35.3449 | -40.3086 | -38.707 | -35.6641 | -42.0012 | -50.9856 | -35.134 | -40.4375 | -36.8176 | -35.5247 | -40.0625 | -51.7383 | -34.6523 | -34.3706 | -37.216 | -35.5833 | -40.25 | -51.3985 | -34.4414 | -34.4995
350 | -4.1643 | 0 | -3.7817 | 0 | -4.0885 | 0 | -3.9269 | 0 | -41.7546 | -99.7253 | -35.2841 | 80.4808 | -38.0568 | -47.2442 | -41.1287 | 47.698 | -60.0614 | -95.0807 | -38.0408 | 117.6946 | -40.7461 | 173.8299 | -34.9585 | -7.9061 | -38.5947 | -142.7058 | -42.0713 | -15.5809 | -64.7113 | -22.3285 | -42.8025 | 15.4376 | -19.1279 | 103.6859 | -21.5329 | 96.7402 | -28.7796 | -22.7581 | -16.7018 | 60.1744 | -15.3501 | 80.7671 | -18.5487 | 59.5592 | -18.6067 | 50.4859 | -16.4923 | 30.5814 | -43.0325 | -41.4444 | -39.1449 | -45.9937 | -54.5085 | -39.1521 | -44.7599 | -43.4985 | -39.2886 | -43.9788 | -57.3998 | -38.5181 | -38.4005 | 350 | -32.845 | -38.3904 | -32.7546 | -35.0249 | -32.6625 | -38.338 | -33.6273 | -37.1898 | 350 | -39.3342 | -35.1243 | -41.8294 | -50.7268 | -35.3704 | -40.6714 | -39.7168 | -35.2001 | -42.0668 | -50.42 | -35.2252 | -40.833 | -37.2801 | -34.9806 | -39.8145 | -53.6181 | -34.7364 | -34.312 | -37.6627 | -35.0564 | -40.0519 | -53.3113 | -34.5912 | -34.4736
351 | -4.1716 | 0 | -3.8386 | 0 | -4.119 | 0 | -3.8959 | 0 | -42.8762 | -114.0401 | -32.6933 | 76.9506 | -36.8063 | -65.2751 | -42.3278 | 35.3007 | -65.6416 | -91.4816 | -38.7539 | 109.5014 | -41.8262 | 161.7085 | -32.9643 | -10.1115 | -37.5346 | -153.6874 | -42.7805 | -27.9992 | -60.3216 | -24.9216 | -44.1345 | -3.0727 | -19.6303 | 84.3655 | -18.244 | 88.9495 | -35.5309 | -98.5972 | -18.2976 | 49.2887 | -15.2187 | 78.4368 | -16.845 | 57.2043 | -18.2132 | 53.4816 | -18.1048 | 24.4543 | -42.7633 | -41.7274 | -38.6543 | -46.0622 | -54.0518 | -39.3113 | -44.9362 | -45.2209 | -38.8938 | -43.9011 | -59.0703 | -38.7126 | -38.3606 | 351 | -30.9797 | -39.5723 | -31.3691 | -34.6581 | -31.2644 | -39.233 | -32.2429 | -36.6566 | 351 | -41.0493 | -34.7222 | -41.8906 | -50.2132 | -35.4727 | -40.8172 | -41.3823 | -34.7748 | -42.1663 | -49.9328 | -35.4154 | -41.0403 | -37.5558 | -34.4827 | -39.7295 | -55.2317 | -34.874 | -34.2416 | -37.8888 | -34.5353 | -40.0052 | -54.9513 | -34.8167 | -34.4647
352 | -4.182 | 0 | -3.8973 | 0 | -4.1621 | 0 | -3.8608 | 0 | -44.4485 | -127.618 | -30.7011 | 68.3965 | -35.9232 | -83.6551 | -44.1612 | 23.5959 | -68.856 | -39.5765 | -39.8706 | 103.3923 | -43.3127 | 150.8142 | -31.3134 | -17.28 | -36.6673 | -166.0609 | -43.9547 | -39.0838 | -57.7425 | -35.6581 | -46.2228 | -23.6978 | -21.3113 | 63.0532 | -16.5521 | 77.0321 | -28.1507 | 179.6024 | -20.9066 | 41.1613 | -15.3121 | 76.8111 | -15.5186 | 51.0919 | -17.5368 | 55.0626 | -20.3442 | 24.0236 | -42.6521 | -41.6474 | -38.2337 | -46.2303 | -53.6717 | -39.5654 | -44.866 | -48.0683 | -38.5765 | -43.9363 | -59.409 | -38.9785 | -38.2749 | 352 | -29.4214 | -41.2846 | -30.0335 | -34.4512 | -29.9953 | -40.5283 | -30.9522 | -36.1806 | 352 | -43.8863 | -34.3945 | -42.0483 | -49.7744 | -35.6681 | -40.7039 | -44.171 | -34.4144 | -42.3695 | -49.5096 | -35.7046 | -41.0052 | -37.4654 | -34.0517 | -39.7543 | -55.5117 | -35.0812 | -34.1128 | -37.7501 | -34.0716 | -40.0755 | -55.2469 | -35.1177 | -34.4141
353 | -4.1889 | 0 | -3.9428 | 0 | -4.2357 | 0 | -3.849 | 0 | -46.6093 | -140.6727 | -29.2844 | 57.4413 | -35.4684 | -102.1119 | -46.8862 | 18.1228 | -63.6322 | -17.5009 | -41.0491 | 101.4455 | -45.1269 | 142.8671 | -30.0759 | -26.4481 | -36.1568 | -178.1484 | -45.7083 | -47.9679 | -56.3324 | -49.0944 | -50.0693 | -46.2649 | -24.8968 | 31.2582 | -15.3222 | 64.3096 | -23.1738 | 154.1729 | -25.1573 | 39.2113 | -15.7226 | 76.0411 | -14.7723 | 41.5849 | -16.9065 | 52.4449 | -22.8621 | 23.6287 | -42.6976 | -41.1468 | -37.9359 | -46.4515 | -53.3656 | -39.889 | -44.5912 | -52.9662 | -38.3725 | -44.0521 | -58.1732 | -39.3256 | -38.0517 | 353 | -28.2832 | -43.691 | -28.9342 | -34.4025 | -29.0112 | -42.2255 | -29.9166 | -35.944 | 353 | -48.7773 | -34.1836 | -42.2626 | -49.4228 | -35.9462 | -40.3555 | -49.0234 | -34.1368 | -42.6025 | -49.1299 | -36.04 | -40.7422 | -36.9579 | -33.747 | -39.8632 | -54.2304 | -35.3828 | -33.816 | -37.204 | -33.7002 | -40.2031 | -53.9375 | -35.4766 | -34.2027
354 | -4.1969 | 0 | -3.9631 | 0 | -4.2993 | 0 | -3.8371 | 0 | -49.5657 | -150.7231 | -28.3431 | 44.5873 | -35.2813 | -121.1083 | -50.5049 | 22.3333 | -60.6768 | -24.0099 | -41.9841 | 104.2339 | -47.2463 | 139.4154 | -29.2152 | -38.0457 | -35.818 | 168.3126 | -48.2704 | -52.8289 | -55.8334 | -62.9382 | -56.7771 | -85.1661 | -31.2809 | -3.0113 | -14.6474 | 51.3623 | -19.7638 | 131.279 | -28.4208 | 76.3704 | -15.0414 | 77.6832 | -14.3223 | 32.1362 | -15.9004 | 48.3377 | -24.1854 | 45.2967 | -42.8585 | -40.3978 | -37.8032 | -46.6007 | -53.1007 | -40.2689 | -44.2482 | -57.5922 | -38.3102 | -44.1779 | -56.3224 | -39.6704 | -37.6348 | 354 | -27.5155 | -46.8173 | -28.134 | -34.43 | -28.3007 | -44.3944 | -29.154 | -35.7406 | 354 | -53.3953 | -34.1133 | -42.4038 | -49.1376 | -36.3058 | -39.9489 | -53.6291 | -34.0109 | -42.7636 | -48.8014 | -36.4318 | -40.4111 | -36.2009 | -33.6063 | -39.981 | -52.3593 | -35.7073 | -33.3355 | -36.4347 | -33.5039 | -40.3408 | -52.0231 | -35.8333 | -33.7977
355 | -4.2414 | 0 | -3.9706 | 0 | -4.3776 | 0 | -3.8567 | 0 | -53.5922 | -155.0322 | -27.7953 | 31.2225 | -35.5152 | -140.6156 | -52.4445 | 49.5481 | -59.8441 | -35.0136 | -42.2941 | 109.7297 | -49.3683 | 139.5467 | -28.6882 | -49.2082 | -35.8191 | 154.316 | -51.6757 | -46.0538 | -56.3918 | -74.2888 | -57.4146 | 166.6688 | -29.0283 | -114.3047 | -14.4884 | 38.8221 | -17.4474 | 112.4397 | -24.4712 | 109.6458 | -14.5044 | 78.2866 | -14.1993 | 23.5123 | -15.1479 | 41.6236 | -22.4856 | 63.4337 | -43.116 | -39.5815 | -37.8829 | -46.5261 | -52.698 | -40.6167 | -43.9159 | -50.9791 | -38.4719 | -44.3026 | -54.5565 | -39.901 | -37.0451 | 355 | -27.1072 | -49.5447 | -27.6295 | -34.6743 | -27.8886 | -46.8488 | -28.6606 | -35.7515 | 355 | -46.7377 | -34.2305 | -42.2847 | -48.7274 | -36.6461 | -39.5383 | -47.0085 | -34.0943 | -42.6694 | -48.3204 | -36.76 | -40.0592 | -35.3401 | -33.6415 | -40.0612 | -50.5859 | -35.9304 | -32.6675 | -35.6109 | -33.5053 | -40.4459 | -50.1789 | -36.0443 | -33.1884
356 | -4.2892 | 0 | -3.947 | 0 | -4.4304 | 0 | -3.904 | 0 | -58.8484 | -141.0751 | -27.6123 | 18.5569 | -36.2219 | -160.4748 | -49.686 | 70.3018 | -61.3603 | -39.9159 | -41.803 | 114.7511 | -50.8022 | 147.6598 | -28.4826 | -61.2952 | -36.1792 | 139.6458 | -53.454 | -17.75 | -57.7855 | -75.9668 | -50.1495 | 123.4794 | -21.9489 | -156.9618 | -14.8882 | 25.7825 | -16.3969 | 96.412 | -20.5972 | 111.7594 | -13.477 | 77.7796 | -14.4784 | 14.3714 | -14.4581 | 35.3785 | -19.9064 | 66.6519 | -43.4557 | -38.861 | -38.0947 | -46.2682 | -52.2408 | -40.8961 | -43.654 | -46.2117 | -38.7775 | -44.3845 | -52.6853 | -39.9773 | -36.4027 | 356 | -27.049 | -48.9332 | -27.424 | -35.1509 | -27.7792 | -48.3884 | -28.4394 | -35.9798 | 356 | -41.9225 | -34.4883 | -41.979 | -48.2938 | -36.9491 | -39.2236 | -42.2647 | -34.3471 | -42.3642 | -47.8104 | -36.9921 | -39.75 | -34.5718 | -33.8055 | -40.0953 | -48.7383 | -36.0303 | -31.9723 | -34.914 | -33.6643 | -40.4805 | -48.2549 | -36.0733 | -32.4987
357 | -4.3881 | 0 | -3.931 | 0 | -4.4466 | 0 | -3.9662 | 0 | -59.8642 | -94.0371 | -27.7583 | 6.2552 | -37.3552 | -179.3542 | -46.6451 | 69.3793 | -62.1499 | -5.7434 | -40.9256 | 117.3571 | -50.8334 | 155.668 | -28.5667 | -72.9453 | -36.9311 | 125.4129 | -50.6631 | 3.2547 | -57.561 | -60.2135 | -45.8871 | 100.1307 | -17.7329 | -177.3293 | -15.7398 | 12.372 | -15.9694 | 80.5 | -18.1596 | 104.2049 | -12.3667 | 75.5696 | -15.2205 | 6.5031 | -14.3224 | 26.4578 | -17.5876 | 64.6947 | -43.7678 | -38.2287 | -38.4865 | -46.049 | -51.9397 | -40.9475 | -43.474 | -43.2631 | -39.2904 | -44.5443 | -50.5521 | -39.7591 | -35.9033 | 357 | -27.3037 | -46.3278 | -27.5005 | -35.7631 | -27.9534 | -47.3069 | -28.4607 | -36.378 | 357 | -38.875 | -34.9023 | -41.6609 | -48.0087 | -37.0165 | -39.0274 | -39.3321 | -34.8438 | -42.0828 | -47.4931 | -36.9813 | -39.5078 | -33.8406 | -34.0984 | -40.1562 | -46.6211 | -35.8281 | -31.4567 | -34.2977 | -34.0399 | -40.5781 | -46.1055 | -35.7929 | -31.9371
358 | -4.4805 | 0 | -3.894 | 0 | -4.4519 | 0 | -4.0348 | 0 | -55.5172 | -76.1017 | -28.1969 | -5.8215 | -38.9403 | 160.9933 | -45.0042 | 60.0099 | -55.084 | 2.7584 | -39.7038 | 117.5686 | -49.9725 | 158.092 | -28.9452 | -83.9739 | -38.0331 | 112.5682 | -47.7907 | 6.0877 | -53.6325 | -58.1084 | -43.1516 | 81.5741 | -15.0873 | 163.1572 | -17.3335 | 2.9914 | -15.7261 | 66.0165 | -15.9421 | 94.0924 | -11.568 | 70.7244 | -16.2229 | -1.308 | -14.4492 | 18.6086 | -16.3137 | 54.9666 | -44.0354 | -37.7652 | -38.9461 | -46.1994 | -52.5979 | -40.5738 | -43.4721 | -41.3621 | -39.8633 | -45.0971 | -48.5658 | -39.2801 | -36.4829 | 358 | -27.8381 | -44.2596 | -27.8165 | -36.238 | -28.4096 | -45.0825 | -28.7291 | -36.7774 | 358 | -36.8816 | -35.3828 | -41.7189 | -48.7039 | -36.6798 | -39.0202 | -37.4681 | -35.4114 | -42.1646 | -48.146 | -36.539 | -39.4373 | -33.2847 | -34.4656 | -40.6166 | -44.6718 | -35.3861 | -32.031 | -33.8712 | -34.4942 | -41.0623 | -44.1139 | -35.2453 | -32.4481
359 | -4.6004 | 0 | -3.8684 | 0 | -4.4121 | 0 | -4.0856 | 0 | -52.3099 | -80.3374 | -28.9013 | -16.4114 | -41.0621 | 139.2809 | -44.24 | 52.5887 | -50.7732 | -22.9464 | -38.2475 | 113.0495 | -49.23 | 152.5213 | -29.5967 | -94.5944 | -39.708 | 100.6604 | -45.4938 | 2.9287 | -50.8346 | -77.1114 | -41.2756 | 62.7083 | -13.0806 | 146.399 | -19.4655 | -6.3635 | -16.3813 | 50.8732 | -15.1111 | 82.6124 | -10.7675 | 64.1759 | -17.8541 | -4.5574 | -14.918 | 9.9067 | -15.4386 | 43.9383 | -44.1895 | -37.5262 | -39.4645 | -46.1856 | -55.1817 | -40.0535 | -43.6223 | -40.0879 | -40.3582 | -45.8216 | -47.6106 | -38.7598 | -40.0173 | 359 | -28.6263 | -42.8471 | -28.3114 | -36.2638 | -29.1499 | -43.1501 | -29.2079 | -37.2181 | 359 | -35.4875 | -35.7578 | -41.5852 | -51.3133 | -36.1851 | -39.2102 | -36.2195 | -35.9461 | -42.1 | -50.7696 | -35.9679 | -39.5367 | -32.9258 | -34.8641 | -41.2212 | -43.7422 | -34.8914 | -35.6052 | -33.6578 | -35.0524 | -41.736 | -43.1985 | -34.6742 | -35.9317
360 | -4.6967 | 0 | -3.8461 | 0 | -4.3591 | 0 | -4.1125 | 0 | -50.4631 | -90.6056 | -29.895 | -25.8669 | -44.1842 | 113.6926 | -43.2376 | 45.8291 | -49.4007 | -52.5617 | -37.2456 | 104.2057 | -48.9762 | 144.4208 | -30.5557 | -104.0844 | -42.1767 | 91.0599 | -43.4944 | -4.5315 | -50.0879 | -98.5682 | -40.1602 | 44.7569 | -11.8964 | 130.7529 | -22.0699 | -12.6377 | -17.7101 | 34.8819 | -14.5405 | 70.3989 | -10.0196 | 57.4609 | -19.7665 | -3.4707 | -15.8515 | 7.1215 | -14.9847 | 34.2092 | -44.3664 | -37.4848 | -39.8342 | -45.6476 | -59.839 | -39.6918 | -43.85 | -39.32 | -40.6928 | -45.8812 | -47.8226 | -38.4723 | -46.269 | 360 | -29.6996 | -41.6801 | -28.9946 | -36.2307 | -30.2085 | -41.7273 | -29.9098 | -37.7791 | 360 | -34.6233 | -35.9961 | -40.9509 | -55.9929 | -35.8457 | -39.4909 | -35.4739 | -36.3337 | -41.5351 | -55.4799 | -35.5793 | -39.7375 | -32.7881 | -35.1375 | -41.1845 | -43.9765 | -34.6262 | -41.9099 | -33.6387 | -35.4751 | -41.7687 | -43.4635 | -34.3598 | -42.1565
361 | -4.7983 | 0 | -3.8373 | 0 | -4.3295 | 0 | -4.1186 | 0 | -49.5327 | -103.6537 | -31.2318 | -34.1127 | -48.4095 | 74.7942 | -42.0448 | 34.594 | -49.6639 | -81.3554 | -36.9061 | 93.4288 | -49.1492 | 133.7002 | -31.7923 | -111.3084 | -45.6392 | 90.1611 | -41.9715 | -15.2615 | -50.3271 | -117.0247 | -39.5679 | 27.279 | -10.8179 | 114.5406 | -27.0435 | 15.8526 | -19.664 | 28.0014 | -14.0446 | 60.1029 | -9.5806 | 49.4366 | -20.9992 | 0.5721 | -16.852 | -0.3829 | -14.9098 | 20.3209 | -44.592 | -37.6427 | -39.8888 | -45.0763 | -66.006 | -39.6623 | -44.0873 | -38.9819 | -40.7592 | -45.2631 | -48.6498 | -38.4194 | -50.5989 | 361 | -31.0868 | -40.7371 | -29.9166 | -36.3995 | -31.5408 | -40.7084 | -30.7788 | -38.3259 | 361 | -34.1836 | -35.9609 | -40.278 | -62.1687 | -35.825 | -39.7578 | -35.1446 | -36.4297 | -40.9577 | -61.6765 | -35.5437 | -39.9687 | -32.8444 | -35.0905 | -40.4648 | -44.8125 | -34.5821 | -46.2694 | -33.8054 | -35.5593 | -41.1445 | -44.3203 | -34.3008 | -46.4803
362 | -4.8717 | 0 | -3.8302 | 0 | -4.3018 | 0 | -4.1023 | 0 | -49.1785 | -116.7962 | -32.9194 | -38.8087 | -50.1823 | 6.2409 | -41.3169 | 19.2179 | -51.0049 | -107.6304 | -36.9828 | 84.5193 | -49.8235 | 121.3106 | -33.3337 | -116.3973 | -49.1581 | 109.4642 | -40.9446 | -28.2641 | -51.322 | -132.4453 | -39.5278 | 9.9247 | -10.3224 | 99.8091 | -26.4236 | 46.1887 | -23.5254 | 21.3253 | -14.2941 | 49.5157 | -9.528 | 40.5599 | -21.5455 | 12.6041 | -18.1236 | -1.0776 | -15.3071 | 6.9979 | -44.7723 | -37.9783 | -39.6615 | -44.6903 | -66.4208 | -39.8494 | -44.2677 | -38.9659 | -40.5241 | -44.9044 | -49.8419 | -38.4854 | -46.0557 | 362 | -32.7389 | -40.2752 | -31.0528 | -36.6186 | -33.1276 | -40.077 | -31.8306 | -38.8273 | 362 | -34.0942 | -35.6524 | -39.8186 | -62.5906 | -36.0192 | -39.9659 | -35.1357 | -36.2223 | -40.588 | -62.119 | -35.7471 | -40.1654 | -33.1066 | -34.7898 | -40.0327 | -46.0117 | -34.6552 | -41.7539 | -34.1481 | -35.3597 | -40.8021 | -45.5401 | -34.3831 | -41.9534
363 | -4.8794 | 0 | -3.8533 | 0 | -4.3106 | 0 | -4.0692 | 0 | -49.1869 | -130.6912 | -34.8862 | -37.9717 | -45.984 | -48.4576 | -41.1953 | 2.7469 | -53.6166 | -135.3636 | -37.3203 | 76.8223 | -51.0826 | 107.2359 | -35.0721 | -116.4397 | -48.0465 | 144.1425 | -40.4904 | -42.432 | -52.8017 | -142.7176 | -40.019 | -7.0639 | -10.4875 | 85.5948 | -23.0623 | 55.2671 | -30.1115 | 37.5195 | -15.0863 | 36.6617 | -9.5856 | 32.39 | -20.5219 | 21.6837 | -19.1837 | 6.919 | -16.2207 | -6.1943 | -44.9947 | -38.4207 | -39.1653 | -44.6666 | -62.3619 | -40.0926 | -44.4549 | -39.3419 | -40.0591 | -44.8455 | -51.2401 | -38.6817 | -42.5723 | 363 | -34.4142 | -40.3458 | -32.3217 | -36.6776 | -34.7561 | -39.8986 | -33.0111 | -39.1905 | 363 | -34.4625 | -35.1797 | -39.7872 | -58.5086 | -36.2393 | -40.1443 | -35.4886 | -35.7485 | -40.5974 | -58.0513 | -36.0234 | -40.3857 | -33.5413 | -34.2859 | -39.9661 | -47.3868 | -34.8284 | -38.2617 | -34.5674 | -34.8547 | -40.7763 | -46.9295 | -34.6125 | -38.5031
364 | -4.8327 | 0 | -3.8992 | 0 | -4.3262 | 0 | -4.0264 | 0 | -49.6437 | -146.1637 | -36.4389 | -28.0734 | -42.0617 | -80.1171 | -41.6644 | -15.559 | -57.6609 | -169.1138 | -37.9819 | 69.8643 | -53.0068 | 91.0519 | -36.5761 | -109.4083 | -43.8204 | 154.4243 | -40.5308 | -55.6922 | -54.3431 | -146.899 | -41.054 | -23.7566 | -10.8078 | 71.9642 | -20.2503 | 53.7106 | -28.7647 | 101.9738 | -16.1332 | 28.9601 | -9.9335 | 24.143 | -19.0999 | 28.3142 | -18.8681 | 15.6727 | -18.1166 | -18.0185 | -45.228 | -39.0027 | -38.474 | -45.1499 | -59.7866 | -40.5183 | -44.5242 | -40.0371 | -39.5006 | -45.0906 | -52.5672 | -39.002 | -40.4239 | 364 | -35.2273 | -40.9295 | -33.426 | -36.5156 | -35.7434 | -40.1243 | -34.1237 | -39.0791 | 364 | -35.2044 | -34.6679 | -40.3172 | -55.8874 | -36.6191 | -40.198 | -36.1379 | -35.1744 | -41.1235 | -55.4604 | -36.4919 | -40.4978 | -34.17 | -33.6413 | -40.2579 | -48.668 | -35.1028 | -36.0977 | -35.1035 | -34.1478 | -41.0642 | -48.241 | -34.9756 | -36.3975
365 | -4.7398 | 0 | -3.9312 | 0 | -4.3882 | 0 | -3.9898 | 0 | -50.6601 | -164.0721 | -36.1493 | -12.5629 | -39.3532 | -104.1848 | -42.7374 | -32.724 | -62.3082 | 134.8457 | -38.8901 | 65.638 | -55.9655 | 71.1349 | -36.8764 | -97.4167 | -40.3482 | 149.2974 | -40.9183 | -68.5597 | -55.3935 | -145.8117 | -42.9351 | -41.5474 | -11.6004 | 59.5875 | -18.6156 | 43.562 | -21.8058 | 110.1847 | -17.6562 | 21.3375 | -10.5755 | 16.9543 | -17.9258 | 26.5048 | -17.5211 | 24.5696 | -21.0232 | -31.0429 | -45.3928 | -39.6975 | -37.8069 | -46.3108 | -58.3733 | -41.1819 | -44.4507 | -41.2984 | -38.8999 | -45.5796 | -53.564 | -39.5366 | -39.029 | 365 | -34.3492 | -42.0467 | -33.7155 | -36.0948 | -35.2271 | -40.6368 | -34.7224 | -38.3548 | 365 | -36.5586 | -34.1601 | -41.571 | -54.4421 | -37.2507 | -40.0625 | -37.3672 | -34.5117 | -42.321 | -53.9851 | -37.1921 | -40.4609 | -34.9577 | -33.0671 | -40.8398 | -49.6328 | -35.6054 | -34.6408 | -35.7663 | -33.4187 | -41.5898 | -49.1758 | -35.5468 | -35.0392
366 | -4.6366 | 0 | -3.9504 | 0 | -4.4554 | 0 | -3.9865 | 0 | -52.4974 | 175.2329 | -34.1814 | -4.673 | -37.4692 | -126.0234 | -44.4139 | -51.062 | -60.4336 | 64.6875 | -39.6645 | 66.4744 | -60.7001 | 39.3241 | -35.5447 | -86.9485 | -37.9018 | 137.1767 | -41.578 | -80.8324 | -55.5058 | -141.2545 | -46.2484 | -56.3731 | -13.2178 | 47.2964 | -17.7342 | 32.247 | -18.526 | 101.7522 | -19.5241 | 21.1537 | -11.5578 | 10.9861 | -17.179 | 20.4694 | -15.8962 | 21.4591 | -24.9381 | -43.0992 | -45.3652 | -40.4951 | -37.1959 | -48.3261 | -57.4863 | -42.1436 | -44.2239 | -43.4124 | -38.4218 | -46.2004 | -54.0286 | -40.2366 | -38.0142 | 366 | -32.4677 | -43.6933 | -32.7898 | -35.4056 | -33.5466 | -41.3549 | -34.2921 | -37.2434 | 366 | -38.7758 | -33.7852 | -43.6895 | -53.5359 | -38.1932 | -39.7685 | -39.462 | -33.9664 | -44.3396 | -53.0309 | -38.1571 | -40.2374 | -35.8585 | -32.5593 | -41.5638 | -50.0782 | -36.2862 | -33.5588 | -36.5447 | -32.7405 | -42.2139 | -49.5732 | -36.2501 | -34.0277
367 | -4.5191 | 0 | -3.9542 | 0 | -4.5423 | 0 | -3.9917 | 0 | -55.577 | 149.5189 | -32.0051 | -6.8872 | -36.1464 | -146.5942 | -46.7204 | -68.0331 | -55.9658 | 29.5254 | -39.8382 | 68.203 | -65.1736 | -32.7893 | -33.4513 | -85.1073 | -36.1671 | 122.9326 | -42.5499 | -94.2401 | -54.6652 | -138.4552 | -52.5165 | -63.4972 | -15.7208 | 39.7076 | -17.6171 | 22.3726 | -16.0218 | 90.1544 | -21.0875 | 29.2299 | -12.8319 | 8.8694 | -16.9202 | 13.7423 | -14.6218 | 15.1212 | -36.0986 | -44.249 | -45.201 | -41.2188 | -36.7854 | -51.2947 | -56.9275 | -43.3477 | -43.8995 | -46.8392 | -38.0777 | -46.6261 | -53.7511 | -40.9486 | -37.2223 | 367 | -30.5757 | -45.7544 | -31.2189 | -34.5694 | -31.5881 | -42.2686 | -32.8996 | -36.008 | 367 | -42.3201 | -33.5586 | -46.7756 | -52.9733 | -39.3935 | -39.3572 | -42.885 | -33.5354 | -47.303 | -52.3852 | -39.356 | -39.9078 | -36.6997 | -32.2663 | -42.107 | -49.7969 | -36.9944 | -32.68 | -37.2646 | -32.2431 | -42.6344 | -49.2088 | -36.9569 | -33.2306
368 | -4.4518 | 0 | -3.936 | 0 | -4.6304 | 0 | -4.0217 | 0 | -60.6759 | 111.4332 | -30.3132 | -14.8982 | -35.3222 | -166.1466 | -49.6494 | -86.1272 | -52.7195 | 7.0946 | -39.4692 | 69.2664 | -60.9376 | -99.6534 | -31.5419 | -91.3131 | -34.8983 | 107.5109 | -44.1138 | -108.4884 | -53.4053 | -141.5672 | -61.6416 | 5.4963 | -19.6055 | 43.2771 | -18.1252 | 11.0725 | -14.7474 | 77.6884 | -21.2615 | 40.5371 | -14.1354 | 13.0847 | -17.2256 | 7.8083 | -13.8596 | 6.3531 | -31.0812 | 98.4053 | -44.9601 | -41.4709 | -36.5892 | -53.5812 | -56.5773 | -44.553 | -43.6548 | -50.0679 | -37.9986 | -46.854 | -52.9438 | -41.3062 | -36.6855 | 368 | -29.119 | -47.6846 | -29.7705 | -33.8514 | -29.8899 | -43.5505 | -31.3041 | -34.8284 | 368 | -45.6161 | -33.5468 | -49.1294 | -52.6413 | -40.617 | -39.0244 | -46.1319 | -33.3682 | -49.5595 | -51.9469 | -40.5313 | -39.6331 | -37.0191 | -32.1374 | -42.4022 | -49.0078 | -37.3702 | -32.0551 | -37.5349 | -31.9588 | -42.8323 | -48.3134 | -37.2845 | -32.6638
369 | -4.447 | 0 | -3.9196 | 0 | -4.6696 | 0 | -4.072 | 0 | -65.0222 | 33.7917 | -29.2249 | -26.171 | -34.9668 | 173.6948 | -53.0968 | -108.3279 | -50.332 | -11.3711 | -38.8459 | 67.3014 | -57.652 | -130.7676 | -30.1892 | -100.1074 | -34.0285 | 91.5959 | -46.8548 | -125.9215 | -52.2175 | -147.9155 | -51.9064 | 50.3287 | -22.5917 | 75.106 | -19.1481 | -1.2767 | -14.2358 | 63.628 | -20.0271 | 47.9398 | -14.4097 | 20.509 | -17.5399 | 0.501 | -13.4637 | -4.7635 | -24.765 | 80.3703 | -44.8383 | -40.9945 | -36.6078 | -51.4593 | -56.4672 | -45.4125 | -43.5446 | -46.9196 | -38.1813 | -46.8844 | -51.8923 | -41.1696 | -36.4669 | 369 | -28.1977 | -48.3923 | -28.7591 | -33.3879 | -28.6819 | -45.4746 | -30.0681 | -33.8939 | 369 | -42.4726 | -33.7343 | -47.0123 | -52.5476 | -41.4929 | -38.875 | -43 | -33.5117 | -47.3873 | -51.7976 | -41.3405 | -39.4726 | -36.5475 | -32.1608 | -42.4374 | -47.9727 | -37.25 | -31.7973 | -37.0749 | -31.9382 | -42.8124 | -47.2227 | -37.0976 | -32.3949
370 | -4.5194 | 0 | -3.9198 | 0 | -4.7048 | 0 | -4.0943 | 0 | -61.4475 | -29.9843 | -28.6942 | -38.2671 | -35.0137 | 155.718 | -56.5799 | -145.9086 | -48.5422 | -29.2857 | -38.3468 | 61.8047 | -56.3806 | -152.0589 | -29.3806 | -111.7609 | -33.5655 | 74.2856 | -52.2176 | -148.2793 | -51.1914 | -156.4882 | -46.9828 | 45.9976 | -17.8225 | 105.3411 | -21.6543 | -8.4785 | -13.8928 | 53.203 | -18.6179 | 47.1642 | -13.5697 | 28.1781 | -18.7044 | -1.5454 | -13.6606 | -15.8236 | -20.8785 | 73.4408 | -44.8736 | -40.1001 | -36.8325 | -48.0845 | -56.5728 | -45.7094 | -43.6151 | -42.947 | -38.6444 | -46.744 | -51.0135 | -40.7595 | -36.7952 | 370 | -27.7814 | -47.7203 | -28.2411 | -33.2281 | -27.9708 | -47.9852 | -29.2837 | -33.301 | 370 | -38.4276 | -34.125 | -43.5651 | -52.653 | -41.7896 | -38.9103 | -39.0272 | -33.9396 | -43.9902 | -51.868 | -41.6151 | -39.5208 | -35.5807 | -32.3131 | -42.2246 | -47.0937 | -36.8397 | -32.0904 | -36.1803 | -32.1277 | -42.6497 | -46.3087 | -36.6652 | -32.7009
371 | -4.6972 | 0 | -3.9369 | 0 | -4.7013 | 0 | -4.1463 | 0 | -59.0308 | -56.6143 | -28.6134 | -49.9147 | -35.3029 | 137.6622 | -56.5852 | 157.4202 | -47.2515 | -46.9683 | -38.2366 | 54.7958 | -56.7746 | -169.1959 | -29.0474 | -123.9957 | -33.4601 | 57.192 | -64.1313 | 114.8552 | -50.2821 | -168.3024 | -44.1467 | 37.3299 | -14.1361 | 104.9121 | -25.2987 | -9.4958 | -14.2997 | 41.663 | -17.5101 | 44.0849 | -12.0009 | 31.3072 | -20.13 | 2.0552 | -14.0306 | -27.2094 | -18.9212 | 59.8133 | -44.9961 | -39.1551 | -37.2447 | -45.4454 | -56.6602 | -45.3504 | -43.7845 | -40.3419 | -39.4237 | -46.3158 | -50.4994 | -40.2482 | -37.7215 | 371 | -27.7668 | -46.5218 | -28.1576 | -33.3363 | -27.7002 | -49.2596 | -28.9139 | -33.0219 | 371 | -35.6447 | -34.7265 | -40.7482 | -52.7233 | -41.4135 | -39.0832 | -36.405 | -34.7224 | -41.2991 | -51.9589 | -41.2041 | -39.6382 | -34.4579 | -32.5475 | -41.6186 | -46.5625 | -36.3113 | -33.0202 | -35.2182 | -32.5434 | -42.1695 | -45.7981 | -36.1019 | -33.5752
372 | -4.9135 | 0 | -3.9503 | 0 | -4.7184 | 0 | -4.1696 | 0 | -58.2424 | -71.5575 | -28.9161 | -61.1755 | -35.8257 | 121.2488 | -53.0152 | 115.3625 | -46.4836 | -64.744 | -38.6198 | 47.7803 | -59.43 | 177.8015 | -29.1112 | -134.7523 | -33.6221 | 40.8294 | -51.2382 | 26.893 | -49.604 | 177.9324 | -42.2041 | 29.1567 | -11.5064 | 97.5133 | -29.9305 | 17.4132 | -15.1841 | 31.4071 | -16.8951 | 36.6604 | -10.5494 | 26.8176 | -20.1444 | 2.1827 | -14.9934 | -38.1067 | -17.9425 | 46.699 | -45.2088 | -38.4144 | -37.7892 | -43.4236 | -56.1463 | -44.5082 | -43.9893 | -38.6286 | -40.5034 | -45.5753 | -50.4776 | -39.6403 | -39.3208 | 372 | -28.1066 | -45.3812 | -28.4591 | -33.7535 | -27.7923 | -47.0743 | -28.8779 | -32.9632 | 372 | -33.7151 | -35.5899 | -38.5101 | -52.196 | -40.5579 | -39.2709 | -34.6783 | -35.785 | -39.254 | -51.4279 | -40.3386 | -39.8197 | -33.5009 | -32.8757 | -40.6618 | -46.5273 | -35.69 | -34.6024 | -34.4641 | -33.0708 | -41.4057 | -45.7592 | -35.4707 | -35.1512
373 | -5.1425 | 0 | -3.9667 | 0 | -4.7206 | 0 | -4.1776 | 0 | -58.2999 | -77.7032 | -29.5042 | -70.1006 | -36.5886 | 104.6985 | -49.7283 | 87.8323 | -46.411 | -83.3348 | -39.4244 | 43.191 | -67.0987 | -173.8633 | -29.4644 | -144.8186 | -34.0051 | 24.1283 | -45.5143 | 3.612 | -49.4124 | 160.689 | -40.5646 | 22.4584 | -9.9984 | 86.1897 | -27.4446 | 59.7451 | -16.5301 | 23.9626 | -16.7694 | 27.8286 | -9.3813 | 19.9562 | -20.5986 | 14.9091 | -16.3257 | -47.2786 | -17.4727 | 33.143 | -45.4986 | -37.8892 | -38.3932 | -41.8775 | -54.9049 | -43.276 | -44.2636 | -37.4315 | -41.7597 | -44.7558 | -51.1073 | -38.8534 | -41.534 | 373 | -28.7232 | -44.5624 | -29.0457 | -34.4809 | -28.1557 | -44.0083 | -29.0408 | -33.0373 | 373 | -32.289 | -36.6172 | -36.735 | -50.9382 | -39.3093 | -39.543 | -33.4648 | -37.0391 | -37.6999 | -50.1843 | -39.0984 | -40.086 | -32.7467 | -33.2507 | -39.6133 | -47.1406 | -34.8867 | -36.8134 | -33.9225 | -33.6726 | -40.5782 | -46.3867 | -34.6758 | -37.3564
374 | -5.3542 | 0 | -4.002 | 0 | -4.743 | 0 | -4.1659 | 0 | -58.3397 | -75.9184 | -30.2993 | -78.2848 | -37.5986 | 88.2226 | -47.3926 | 64.7119 | -47.1627 | -101.4074 | -40.5365 | 43.3364 | -63.2896 | -76.9425 | -29.9804 | -152.4931 | -34.6472 | 7.1493 | -42.4237 | -15.7575 | -49.9299 | 141.8344 | -38.9365 | 14.1748 | -8.8089 | 75.3348 | -22.5398 | 71.988 | -18.2783 | 23.6492 | -17.0137 | 17.2437 | -8.5902 | 10.9931 | -19.674 | 21.1535 | -18.2161 | -54.8341 | -18.0349 | 23.1899 | -45.862 | -37.4156 | -39.019 | -40.7604 | -53.3268 | -41.7788 | -44.5918 | -36.5008 | -42.9832 | -44.0645 | -52.6816 | -37.8172 | -44.0408 | 374 | -29.5518 | -44.0991 | -29.8296 | -35.5062 | -28.7032 | -41.6837 | -29.2464 | -33.1795 | 374 | -31.1466 | -37.629 | -35.4062 | -49.3248 | -37.7768 | -39.8488 | -32.4988 | -38.2402 | -36.5945 | -48.5838 | -37.6129 | -40.4259 | -32.0614 | -33.6648 | -38.7103 | -48.6796 | -33.8152 | -39.2978 | -33.4136 | -34.276 | -39.8986 | -47.9386 | -33.6513 | -39.8749
375 | -5.4923 | 0 | -4.0344 | 0 | -4.7727 | 0 | -4.1455 | 0 | -57.7303 | -72.6609 | -31.1446 | -83.2372 | -38.779 | 72.4218 | -45.806 | 44.6075 | -48.8651 | -115.8469 | -41.1046 | 50.6025 | -55.0697 | -77.1351 | -30.5098 | -158.2503 | -35.5625 | -9.7712 | -40.5877 | -32.4914 | -51.5087 | 122.0498 | -37.3943 | 4.1406 | -8.1201 | 64.6565 | -19.7101 | 63.7585 | -19.76 | 30.4768 | -17.9025 | 9.3153 | -8.1609 | 1.5586 | -18.3288 | 23.0093 | -20.1618 | -55.2463 | -18.2297 | 8.0197 | -46.4218 | -36.9531 | -39.5086 | -39.9335 | -51.8085 | -40.1757 | -44.9875 | -35.7063 | -43.8126 | -43.5305 | -55.5031 | -36.5891 | -45.516 | 375 | -30.4457 | -43.8786 | -30.5942 | -36.5171 | -29.3175 | -40.109 | -29.3599 | -33.306 | 375 | -30.214 | -38.3203 | -34.4412 | -47.7741 | -36.1413 | -40.2148 | -31.6719 | -39.0399 | -35.788 | -47.0358 | -36.0302 | -40.842 | -31.4608 | -34.0163 | -38.0382 | -51.4687 | -32.5547 | -40.7433 | -32.9187 | -34.7359 | -39.385 | -50.7304 | -32.4436 | -41.3705
376 | -5.5686 | 0 | -4.0799 | 0 | -4.8295 | 0 | -4.13 | 0 | -56.9268 | -69.9023 | -31.8582 | -86.5918 | -40.2833 | 53.0211 | -44.9455 | 23.5918 | -51.4744 | -120.3132 | -40.0265 | 59.1694 | -50.6313 | -88.5058 | -30.8885 | -163.9252 | -36.7436 | -27.2766 | -39.6129 | -48.8461 | -54.8291 | 102.7956 | -36.0503 | -9.0523 | -7.8365 | 53.4255 | -17.9067 | 54.1466 | -19.9348 | 43.1928 | -19.4053 | 2.2356 | -7.9265 | -8.8884 | -17.4297 | 21.7848 | -23.0794 | -53.9634 | -20.3375 | 0.0862 | -47.0572 | -36.3068 | -39.667 | -39.4283 | -50.5259 | -38.6076 | -45.5877 | -34.9662 | -43.9592 | -43.3768 | -58.5799 | -35.353 | -44.7721 | 376 | -31.2632 | -43.8539 | -31.0607 | -36.9854 | -29.8494 | -39.1629 | -29.3085 | -33.3419 | 376 | -29.3976 | -38.3906 | -33.8597 | -46.446 | -34.5277 | -40.7582 | -30.8863 | -39.1297 | -35.2983 | -45.6964 | -34.4776 | -41.4577 | -30.7382 | -34.0984 | -37.8082 | -54.5 | -31.2731 | -39.9426 | -32.2269 | -34.8375 | -39.2468 | -53.7504 | -31.223 | -40.6421
377 | -5.5646 | 0 | -4.0959 | 0 | -4.8615 | 0 | -4.0959 | 0 | -56.5971 | -67.139 | -32.2423 | -88.7668 | -42.4521 | 30.2207 | -44.8016 | 2.2925 | -52.7132 | -106.052 | -38.1458 | 57.857 | -47.8648 | -100.6283 | -31.0382 | -169.0423 | -38.1861 | -45.5995 | -39.2411 | -62.8866 | -62.5958 | 102.6345 | -35.049 | -23.6028 | -7.8747 | 42.2459 | -16.8162 | 39.9384 | -18.9846 | 44.8679 | -21.2935 | -3.0809 | -7.9376 | -19.739 | -16.202 | 12.0207 | -25.0391 | -36.0946 | -23.2312 | -5.6309 | -47.5536 | -35.4911 | -39.3348 | -39.2645 | -49.6825 | -37.2176 | -46.3341 | -34.2091 | -43.3341 | -43.6896 | -55.4435 | -34.2677 | -42.7573 | 377 | -31.8325 | -43.91 | -31.062 | -36.6662 | -30.1974 | -38.6648 | -29.1394 | -33.3248 | 377 | -28.6445 | -37.7695 | -33.6999 | -45.5866 | -33.1217 | -41.4726 | -30.1132 | -38.4726 | -35.1686 | -44.821 | -33.1217 | -42.2382 | -29.9265 | -33.7702 | -38.125 | -51.3476 | -30.1718 | -37.8958 | -31.3952 | -34.4733 | -39.5937 | -50.582 | -30.1718 | -38.6614
378 | -5.4813 | 0 | -4.1139 | 0 | -4.8673 | 0 | -4.1008 | 0 | -56.0419 | -52.7376 | -32.4253 | -92.8249 | -45.7868 | -2.9999 | -45.543 | -19.3464 | -49.8195 | -102.5912 | -36.7224 | 47.3405 | -45.9117 | -110.7543 | -31.1767 | -176.6176 | -40.1297 | -68.2902 | -39.1984 | -73.65 | -59.1029 | 176.6623 | -34.5792 | -42.5894 | -8.1673 | 33.0963 | -16.5996 | 31.8216 | -17.7299 | 48.0702 | -24.6324 | 8.7463 | -8.1467 | -29.7227 | -16.1179 | 4.8112 | -24.5301 | -21.1133 | -26.0231 | -2.9067 | -47.1029 | -34.6258 | -38.3922 | -39.5091 | -49.5013 | -36.036 | -46.9498 | -33.6056 | -41.9462 | -44.7271 | -50.7936 | -33.5548 | -41.2242 | 378 | -32.2115 | -43.8915 | -30.9007 | -36.0292 | -30.5288 | -38.3228 | -29.0963 | -33.5 | 378 | -28.1243 | -36.4649 | -34.0278 | -45.3874 | -31.9221 | -42.0825 | -29.4917 | -37.0789 | -35.4083 | -44.634 | -31.9352 | -42.849 | -29.1445 | -32.9109 | -39.2458 | -46.6797 | -29.4409 | -36.3569 | -30.5119 | -33.5249 | -40.6263 | -45.9263 | -29.454 | -37.1234
379 | -5.3371 | 0 | -4.1267 | 0 | -4.8089 | 0 | -4.1079 | 0 | -51.9331 | -41.1795 | -32.7925 | -98.5642 | -49.9316 | -66.9202 | -46.8587 | -38.9724 | -48.0029 | -126.4108 | -36.3707 | 33.6883 | -43.7718 | -117.9217 | -31.6651 | 174.0347 | -43.1294 | -100.6 | -38.9488 | -83.5272 | -52.6845 | 148.2054 | -35.0896 | -61.8202 | -8.7413 | 23.0918 | -16.8221 | 19.3936 | -16.8349 | 43.3605 | -25.592 | 33.9271 | -9.2934 | -40.9377 | -16.3337 | -1.0661 | -23.2106 | -11.2777 | -30.0928 | 34.8798 | -45.5063 | -33.9463 | -37.0839 | -39.9203 | -50.9242 | -35.3916 | -46.3298 | -33.2503 | -40.0598 | -46.1774 | -48.7985 | -33.4378 | -43.2127 | 379 | -32.6578 | -43.6796 | -31.096 | -35.9068 | -31.123 | -37.5762 | -29.5129 | -34.3913 | 379 | -27.9132 | -34.7227 | -34.5832 | -46.7975 | -31.2649 | -41.5209 | -29.1236 | -35.2509 | -35.8124 | -46.1153 | -31.2837 | -42.2219 | -28.6092 | -31.7468 | -40.8403 | -44.6718 | -29.3111 | -38.4038 | -29.8196 | -32.275 | -42.0695 | -43.9896 | -29.3299 | -39.1048
380 | -5.1471 | 0 | -4.1079 | 0 | -4.7293 | 0 | -4.1249 | 0 | -48.2013 | -51.5686 | -33.5246 | -102.1842 | -47.5636 | -145.5669 | -48.0847 | -64.2764 | -49.9828 | -154.9963 | -37.2271 | 23.2674 | -41.4332 | -130.6663 | -32.7987 | 166.052 | -47.4601 | -153.8425 | -38.99 | -97.5042 | -52.5987 | 107.4321 | -36.8555 | -79.3939 | -9.5903 | 13.5868 | -17.474 | 7.2734 | -16.2522 | 36.2973 | -23.5648 | 40.8302 | -10.1242 | -49.797 | -16.3059 | -9.0745 | -19.8948 | -17.2407 | -26.6824 | 56.3092 | -44.3586 | -33.6401 | -36.14 | -40.4289 | -54.175 | -35.5581 | -45.1821 | -33.2175 | -38.5885 | -46.1704 | -50.1665 | -33.9597 | -52.645 | 380 | -33.2165 | -43.9026 | -31.8771 | -36.6369 | -32.1126 | -36.9128 | -30.668 | -36.388 | 380 | -28.0704 | -33.4414 | -35.2818 | -50.0671 | -31.4502 | -40.4528 | -29.1096 | -33.8592 | -36.304 | -49.4457 | -31.4332 | -41.0572 | -28.493 | -30.9929 | -41.0233 | -46.0586 | -29.8518 | -47.9157 | -29.5322 | -31.4107 | -42.0455 | -45.4372 | -29.8348 | -48.5201
381 | -4.9555 | 0 | -4.0727 | 0 | -4.6508 | 0 | -4.1313 | 0 | -46.1334 | -64.8186 | -34.424 | -104.9866 | -43.4599 | 172.8805 | -49.9753 | -106.6158 | -55.3282 | -174.5189 | -38.5247 | 17.9466 | -39.8694 | -146.2127 | -34.5001 | 161.2258 | -47.1894 | 128.2799 | -39.9452 | -110.8453 | -56.1726 | 71.375 | -39.6208 | -91.2469 | -11.0337 | 7.9039 | -19.3557 | 1.0024 | -16.0641 | 33.5053 | -21.3773 | 48.2759 | -12.0317 | -60.0859 | -17.7622 | -12.845 | -19.7278 | -23.8437 | -23.2345 | 61.6567 | -43.5109 | -33.6672 | -35.6789 | -41.7961 | -56.5266 | -36.2922 | -44.7797 | -33.4555 | -37.8305 | -45.9086 | -52.2719 | -34.6313 | -57.5159 | 381 | -33.6601 | -44.2773 | -32.9108 | -37.2476 | -33.2152 | -36.8458 | -32.478 | -38.8393 | 381 | -28.5 | -32.875 | -36.8406 | -52.4539 | -32.2195 | -40.1289 | -29.3828 | -33.1797 | -37.6648 | -51.8758 | -32.1609 | -40.6484 | -28.7117 | -30.7234 | -40.9531 | -48.1992 | -30.5586 | -52.8651 | -29.5945 | -31.0281 | -41.7773 | -47.6211 | -30.5 | -53.3846
382 | -4.7688 | 0 | -4.0592 | 0 | -4.5642 | 0 | -4.1416 | 0 | -44.5184 | -77.6245 | -35.0605 | -102.698 | -40.728 | 145.7401 | -50.7368 | -162.674 | -68.5848 | -149.3458 | -39.5093 | 19.5676 | -38.8603 | -162.634 | -36.3691 | 164.9905 | -43.0072 | 80.6517 | -41.3647 | -121.0413 | -64.0204 | 16.7141 | -43.5335 | -92.473 | -12.9654 | 7.5688 | -22.1362 | 1.0383 | -16.0517 | 29.4523 | -19.5883 | 44.1735 | -14.2918 | -63.3963 | -18.8035 | -13.0407 | -18.6226 | -35.2494 | -20.8211 | 59.7501 | -42.6263 | -34.0219 | -35.4609 | -44.3099 | -56.4193 | -37.4555 | -44.4381 | -34.0446 | -37.4719 | -46.3209 | -52.5982 | -35.5017 | -48.7926 | 382 | -33.6477 | -43.5744 | -33.6426 | -37.0627 | -33.8641 | -36.9157 | -34.5832 | -40.2339 | 382 | -29.2758 | -32.7031 | -39.5411 | -52.3601 | -33.3963 | -39.8739 | -29.9854 | -32.9077 | -40.1683 | -51.8551 | -33.3139 | -40.2965 | -29.2531 | -30.6921 | -41.5521 | -48.539 | -31.4425 | -44.2284 | -29.9627 | -30.8967 | -42.1793 | -48.034 | -31.3601 | -44.651
383 | -4.6552 | 0 | -4.0583 | 0 | -4.4781 | 0 | -4.1819 | 0 | -43.2578 | -90.9019 | -35.0214 | -98.7448 | -39.1173 | 124.1222 | -48.5635 | 148.5379 | -57.6156 | -53.8532 | -39.6988 | 24.4068 | -38.3776 | -178.5165 | -36.7552 | 177.1306 | -39.946 | 50.1547 | -43.6868 | -129.7756 | -61.832 | -117.0141 | -46.8049 | -66.3517 | -14.0971 | 11.5714 | -23.5631 | 6.5106 | -15.9419 | 21.5362 | -18.1028 | 29.5452 | -17.4126 | -57.367 | -19.4411 | -9.6246 | -18.9494 | -51.9686 | -19.3759 | 53.0174 | -41.8989 | -34.6156 | -35.4997 | -48.1762 | -54.6801 | -39.1312 | -44.2028 | -35.0758 | -37.499 | -46.3317 | -51.1052 | -36.6266 | -45.6481 | 383 | -33.1476 | -42.0147 | -33.6074 | -36.3554 | -33.3948 | -37.2415 | -35.6106 | -39.1089 | 383 | -30.4206 | -32.8438 | -43.521 | -50.6218 | -35.0729 | -39.7247 | -31.0175 | -33.0209 | -43.9943 | -50.202 | -34.9493 | -40.0209 | -29.9604 | -30.8445 | -41.6765 | -47.0469 | -32.5683 | -41.17 | -30.5573 | -31.0216 | -42.1498 | -46.6271 | -32.4447 | -41.4662
384 | -4.6297 | 0 | -4.0993 | 0 | -4.4643 | 0 | -4.2174 | 0 | -42.5018 | -106.0331 | -34.3426 | -99.0479 | -38.0982 | 104.7446 | -45.8645 | 115.1427 | -50.8438 | -66.0917 | -39.1767 | 25.5343 | -38.4101 | 165.3715 | -35.3612 | -176.5524 | -38.005 | 24.57 | -48.1183 | -127.6727 | -54.7241 | -161.8041 | -44.7829 | -37.4697 | -14.5091 | 24.0952 | -24.8074 | 43.4332 | -16.2031 | 17.7421 | -17.922 | 21.6325 | -18.3984 | -32.4279 | -19.8705 | -0.2042 | -19.0982 | -67.7431 | -18.448 | 42.2882 | -41.4907 | -35.4377 | -35.6734 | -50.4047 | -52.4633 | -41.6447 | -43.9977 | -36.4487 | -37.6843 | -45.2907 | -49.2399 | -37.812 | -44.0133 | 384 | -32.3727 | -40.4402 | -32.8845 | -35.466 | -32.2657 | -37.8781 | -34.6896 | -37.1014 | 384 | -31.819 | -33.0546 | -45.775 | -48.364 | -37.5454 | -39.5334 | -32.3494 | -33.22 | -46.1873 | -47.999 | -37.4273 | -39.7803 | -30.808 | -31.0437 | -40.661 | -45.1406 | -33.7127 | -39.549 | -31.3384 | -31.2091 | -41.0733 | -44.7756 | -33.5946 | -39.7959
385 | -4.6941 | 0 | -4.1433 | 0 | -4.4714 | 0 | -4.237 | 0 | -42.3694 | -121.4041 | -33.6689 | -102.536 | -37.438 | 86.9583 | -43.7824 | 92.0565 | -47.1987 | -84.7232 | -38.8761 | 23.0371 | -38.9173 | 150.6556 | -33.8683 | -179.7667 | -36.8048 | 2.038 | -51.2419 | -79.1945 | -51.1545 | 167.3374 | -41.5621 | -30.2981 | -13.3176 | 31.4944 | -21.6037 | 55.1016 | -16.4537 | 13.0727 | -18.1382 | 9.7659 | -16.5354 | -15.48 | -19.5685 | 9.5518 | -20.2068 | -87.5549 | -18.2259 | 31.8881 | -41.3823 | -36.1636 | -35.937 | -46.6167 | -50.3198 | -44.7456 | -43.6745 | -37.9597 | -37.9714 | -43.5808 | -47.9792 | -38.8074 | -42.997 | 385 | -31.7524 | -39.2494 | -32.211 | -34.8283 | -31.2646 | -38.4317 | -33.1188 | -35.434 | 385 | -33.2656 | -33.2773 | -41.9226 | -46.1765 | -40.6023 | -39.2031 | -33.8164 | -33.5 | -42.3797 | -45.8484 | -40.5086 | -39.4375 | -31.4695 | -31.2429 | -38.8867 | -43.8359 | -34.6641 | -38.5256 | -32.0203 | -31.4656 | -39.3438 | -43.5078 | -34.5704 | -38.76
386 | -4.8209 | 0 | -4.1902 | 0 | -4.5391 | 0 | -4.2704 | 0 | -42.8318 | -134.8087 | -33.3879 | -109.3966 | -37.057 | 69.534 | -42.0848 | 74.7148 | -45.1278 | -106.4019 | -39.1348 | 20.8477 | -39.9544 | 137.5565 | -32.8983 | 172.3487 | -36.1215 | -18.2792 | -44.7456 | -52.2317 | -49.2806 | 137.0333 | -38.8944 | -31.3055 | -11.7761 | 33.4449 | -18.6034 | 59.624 | -17.1721 | 14.6126 | -19.5059 | 0.2903 | -13.9182 | -15.6229 | -18.0167 | 12.7237 | -22.5074 | -109.2684 | -18.6923 | 23.8649 | -41.5113 | -36.5594 | -36.2787 | -42.7847 | -48.5308 | -44.9305 | -43.3113 | -39.4063 | -38.1451 | -41.6902 | -47.4519 | -38.957 | -42.3578 | 386 | -31.5034 | -38.3959 | -31.9227 | -34.5633 | -30.6632 | -38.345 | -31.7032 | -34.1448 | 386 | -34.5854 | -33.3242 | -37.9638 | -44.3406 | -40.7403 | -38.7722 | -35.2161 | -33.606 | -38.5143 | -43.9917 | -40.6601 | -39.0409 | -31.7385 | -31.4578 | -36.8693 | -43.2617 | -34.7668 | -37.8187 | -32.3692 | -31.7396 | -37.4198 | -42.9128 | -34.6866 | -38.0874
387 | -4.9588 | 0 | -4.2374 | 0 | -4.6716 | 0 | -4.2916 | 0 | -43.8092 | -145.4849 | -33.5436 | -115.687 | -36.9546 | 53.7078 | -40.5515 | 60.6185 | -44.2772 | -128.3015 | -39.4573 | 23.8633 | -41.572 | 127.3171 | -32.44 | 163.0049 | -35.7331 | -38.1233 | -40.0277 | -59.6784 | -48.6713 | 106.5796 | -36.3743 | -35.4754 | -10.4729 | 28.4343 | -16.4881 | 51.2964 | -17.1763 | 13.026 | -21.293 | -10.6314 | -11.9771 | -23.6235 | -16.2681 | 9.7666 | -24.685 | -130.9748 | -19.2747 | 16.0763 | -41.9023 | -36.524 | -36.612 | -40.0312 | -47.1796 | -41.1216 | -42.9484 | -40.2732 | -38.1151 | -39.8194 | -47.6632 | -37.7107 | -41.9592 | 387 | -31.6403 | -37.7723 | -31.9138 | -34.5311 | -30.4244 | -37.3856 | -30.4577 | -32.9146 | 387 | -35.3144 | -33.1563 | -35.0724 | -42.9422 | -36.8842 | -38.2768 | -36.0358 | -33.4435 | -35.7396 | -42.508 | -36.83 | -38.6568 | -31.5652 | -31.6532 | -34.8606 | -43.4258 | -33.4733 | -37.2876 | -32.2866 | -31.9404 | -35.5278 | -42.9916 | -33.4191 | -37.6676
388 | -5.0766 | 0 | -4.2561 | 0 | -4.83 | 0 | -4.3237 | 0 | -45.1151 | -152.0558 | -33.944 | -120.3607 | -36.9812 | 38.6273 | -39.2046 | 46.1284 | -44.4697 | -149.398 | -38.8036 | 31.7724 | -43.8406 | 121.9505 | -32.3304 | 153.4286 | -35.5881 | -57.5734 | -37.1445 | -74.789 | -49.0359 | 75.4326 | -33.9527 | -45.3927 | -9.6239 | 22.3822 | -15.0153 | 42.5271 | -16.9481 | 12.4191 | -24.9407 | -17.2116 | -10.5629 | -33.9641 | -15.2239 | 4.7866 | -27.1432 | -160.4557 | -20.6593 | 13.7382 | -42.4367 | -36.073 | -36.8704 | -38.0734 | -46.2921 | -37.5651 | -42.721 | -39.9745 | -37.893 | -38.1819 | -48.5647 | -35.7753 | -41.7543 | 388 | -31.9759 | -37.2903 | -31.837 | -34.3434 | -30.4469 | -36.0769 | -29.2804 | -31.6044 | 388 | -34.8979 | -32.8164 | -32.9968 | -42.036 | -33.309 | -37.891 | -35.7184 | -33.063 | -33.7497 | -41.4621 | -33.2414 | -38.3973 | -30.9964 | -31.7938 | -33.1053 | -44.3086 | -31.5192 | -36.9243 | -31.8169 | -32.0404 | -33.8582 | -43.7347 | -31.4516 | -37.4306
389 | -5.1787 | 0 | -4.2725 | 0 | -4.9911 | 0 | -4.3252 | 0 | -46.5096 | -152.5172 | -34.2217 | -122.4256 | -37.1044 | 23.8577 | -38.115 | 31.8964 | -45.5916 | -167.2379 | -36.5778 | 36.1271 | -46.3428 | 127.9271 | -32.4467 | 144.5377 | -35.749 | -76.4784 | -35.4354 | -91.6722 | -50.1327 | 43.7295 | -32.056 | -59.8854 | -8.8751 | 13.648 | -14.0511 | 31.8064 | -16.3801 | 8.8498 | -29.7783 | -9.3754 | -9.8961 | -46.673 | -14.3217 | -3.0945 | -27.2449 | 159.8869 | -22.2619 | 18.8515 | -43.0822 | -35.4082 | -36.9608 | -36.6586 | -45.7454 | -35.0108 | -42.7431 | -38.7555 | -37.5493 | -36.8991 | -50.0548 | -34.0259 | -41.5326 | 389 | -32.2518 | -36.8977 | -31.2347 | -33.543 | -30.6619 | -34.9625 | -28.3026 | -30.4638 | 389 | -33.5768 | -32.3706 | -31.4799 | -41.4729 | -30.7383 | -37.752 | -34.483 | -32.5582 | -32.3334 | -40.7543 | -30.6856 | -38.4179 | -30.2295 | -31.7821 | -31.7204 | -45.7823 | -29.7534 | -36.5415 | -31.1357 | -31.9697 | -32.5739 | -45.0637 | -29.7007 | -37.2074
390 | -5.2261 | 0 | -4.2623 | 0 | -5.1208 | 0 | -4.3514 | 0 | -47.5453 | -146.4635 | -34.164 | -124.0208 | -37.4432 | 9.2322 | -37.3498 | 17.2949 | -47.6087 | 179.3772 | -34.3485 | 30.0844 | -47.4696 | 146.4391 | -32.6772 | 135.4534 | -36.0687 | -95.3956 | -34.551 | -108.8837 | -51.8646 | 7.9585 | -30.71 | -76.3786 | -8.6899 | 6.1 | -13.6615 | 22.3188 | -16.2135 | 4.4972 | -31.9885 | 79.1213 | -9.5293 | -59.5437 | -13.8912 | -11.1993 | -27.8124 | 130.005 | -22.7212 | 30.2064 | -43.682 | -34.6313 | -36.9203 | -35.6456 | -45.4897 | -33.1502 | -42.9436 | -37.3032 | -37.1435 | -35.9395 | -51.9908 | -32.7439 | -41.1504 | 390 | -32.3573 | -36.595 | -30.2926 | -32.4801 | -30.942 | -34.2587 | -27.5952 | -29.5745 | 390 | -32.0771 | -31.9174 | -30.4195 | -41.2274 | -28.8879 | -37.8228 | -33.0409 | -32.0227 | -31.2942 | -40.3689 | -28.7988 | -38.5922 | -29.4052 | -31.6942 | -30.7134 | -47.7285 | -28.4816 | -36.0296 | -30.369 | -31.7995 | -31.5881 | -46.87 | -28.3925 | -36.799
391 | -5.2299 | 0 | -4.2352 | 0 | -5.2216 | 0 | -4.3806 | 0 | -47.525 | -136.4315 | -33.7817 | -127.0066 | -37.9191 | -5.0141 | -36.9239 | 3.4619 | -50.2598 | 176.4347 | -32.5676 | 19.7357 | -45.6804 | 164.6555 | -33.014 | 125.9972 | -36.6648 | -113.685 | -34.3227 | -124.5824 | -53.8426 | -32.235 | -29.9637 | -94.8675 | -8.4841 | -3.0241 | -13.3953 | 10.9524 | -15.4762 | -5.2372 | -25.1429 | 79.4163 | -9.4708 | -72.6233 | -13.7385 | -20.3488 | -25.9748 | 106.6676 | -21.1715 | 38.7454 | -44.0877 | -33.867 | -36.7542 | -34.9862 | -45.4862 | -31.8436 | -43.3915 | -35.995 | -36.7533 | -35.2548 | -54.3173 | -31.9247 | -40.7948 | 391 | -32.2346 | -36.3798 | -29.2984 | -31.3993 | -31.2951 | -33.9711 | -27.264 | -29.1078 | 391 | -30.7651 | -31.5234 | -29.7563 | -41.251 | -27.6084 | -38.1699 | -31.7598 | -31.5317 | -30.6056 | -40.2646 | -27.463 | -39.0109 | -28.6371 | -31.5243 | -30.0249 | -50.0821 | -27.6895 | -35.5732 | -29.6318 | -31.5326 | -30.8742 | -49.0957 | -27.5441 | -36.4142
392 | -5.1647 | 0 | -4.2011 | 0 | -5.244 | 0 | -4.3771 | 0 | -46.23 | -128.805 | -33.318 | -133.0617 | -38.6856 | -19.244 | -36.8834 | -11.6518 | -51.8706 | -173.8059 | -31.5384 | 3.5647 | -42.903 | 168.3318 | -33.5423 | 115.091 | -37.4158 | -132.7739 | -34.67 | -139.0388 | -54.8139 | -78.5266 | -29.7505 | -113.3954 | -8.8256 | -11.4166 | -13.9918 | 1.8822 | -16.2335 | -14.2524 | -20.4458 | 83.4237 | -9.7891 | -85.2925 | -13.9874 | -29.5682 | -24.7737 | 83.108 | -19.1519 | 39.8284 | -44.0536 | -33.159 | -36.5485 | -34.5888 | -45.6161 | -30.9598 | -44.1113 | -34.9471 | -36.4186 | -34.8925 | -56.5878 | -31.5604 | -40.8055 | 392 | -32.0414 | -36.2842 | -28.625 | -30.7388 | -31.7075 | -34.0259 | -27.3455 | -29.0527 | 392 | -29.7824 | -31.2539 | -29.4241 | -41.415 | -26.7587 | -38.8673 | -30.746 | -31.1746 | -30.2117 | -40.3721 | -26.5827 | -39.7342 | -27.9943 | -31.3838 | -29.7278 | -52.3867 | -27.3593 | -35.5615 | -28.9579 | -31.3045 | -30.5154 | -51.3438 | -27.1833 | -36.4284
393 | -5.0736 | 0 | -4.1674 | 0 | -5.2259 | 0 | -4.4017 | 0 | -44.2257 | -126.5568 | -33.08 | -142.0878 | -39.5795 | -32.6765 | -37.1735 | -25.2361 | -50.8618 | -163.8452 | -31.2034 | -10.4541 | -40.5034 | 163.1296 | -34.4148 | 103.9125 | -38.5232 | -152.5289 | -35.3799 | -150.5813 | -54.4328 | -121.6573 | -30.0207 | -131.212 | -9.2602 | -19.256 | -14.642 | -6.8322 | -17.1551 | -24.8345 | -17.7328 | 70.3688 | -10.606 | -100.8883 | -14.7367 | -38.411 | -23.2081 | 70.7914 | -17.5836 | 36.6437 | -43.5238 | -32.5316 | -36.3519 | -34.4457 | -45.8519 | -30.3793 | -45.1244 | -34.1869 | -36.1869 | -34.7767 | -58.2689 | -31.472 | -41.479 | 393 | -31.9382 | -36.2396 | -28.4111 | -30.5732 | -32.2812 | -34.1748 | -27.8335 | -29.4334 | 393 | -29.1133 | -31.1133 | -29.3721 | -41.6845 | -26.2119 | -39.8985 | -30.0195 | -30.961 | -30.044 | -40.626 | -25.9776 | -40.7227 | -27.458 | -31.2783 | -29.7031 | -54.1015 | -27.3046 | -36.2531 | -28.3642 | -31.126 | -30.375 | -53.043 | -27.0703 | -37.0773
394 | -4.9498 | 0 | -4.1411 | 0 | -5.1639 | 0 | -4.4175 | 0 | -42.2261 | -130.0268 | -33.133 | -151.3654 | -40.6442 | -45.356 | -37.7657 | -37.4663 | -49.0968 | -164.5962 | -31.3619 | -24.0683 | -38.6727 | 154.3351 | -35.7948 | 90.6699 | -40.0798 | -171.1657 | -36.2215 | -159.1492 | -53.5469 | -155.713 | -30.8617 | -149.627 | -9.7749 | -25.7416 | -15.6581 | -12.7029 | -17.7677 | -33.8891 | -15.915 | 59.3705 | -11.7474 | -116.4849 | -16.1546 | -48.0439 | -23.062 | 57.7187 | -16.6546 | 29.5134 | -42.6616 | -32.0438 | -36.1813 | -34.5015 | -46.2007 | -30.032 | -46.6021 | -33.656 | -36.0514 | -34.8325 | -58.6997 | -31.5389 | -43.1826 | 394 | -31.9916 | -36.2073 | -28.5881 | -30.8126 | -33.0341 | -34.2152 | -28.7875 | -30.3497 | 394 | -28.7062 | -31.1016 | -29.5517 | -42.0596 | -25.8909 | -41.4382 | -29.5149 | -30.8875 | -30.084 | -41.0368 | -25.6145 | -42.1846 | -27.094 | -31.2315 | -29.8827 | -54.5586 | -27.3978 | -38.0187 | -27.9027 | -31.0174 | -30.415 | -53.5358 | -27.1214 | -38.7651
395 | -4.8161 | 0 | -4.12 | 0 | -5.07 | 0 | -4.4407 | 0 | -40.627 | -138.6857 | -33.506 | -162.725 | -42.1469 | -58.2728 | -38.7777 | -48.342 | -47.8132 | -173.0424 | -31.9523 | -37.3916 | -37.338 | 143.4296 | -37.8062 | 78.6428 | -42.1116 | 171.2342 | -36.9062 | -164.3214 | -52.677 | -178.1626 | -32.2931 | -165.7931 | -10.7374 | -31.8808 | -17.0524 | -14.6335 | -20.8396 | -43.4901 | -14.6872 | 48.6063 | -13.3772 | -130.5387 | -17.4819 | -50.0825 | -22.7178 | 54.2363 | -15.4157 | 18.3519 | -41.7616 | -31.7546 | -36.0124 | -34.7772 | -46.7108 | -29.8601 | -48.6395 | -33.3122 | -36.0348 | -35.0575 | -57.2918 | -31.6442 | -46.0614 | 395 | -32.2649 | -36.2781 | -29.1489 | -31.4541 | -33.8531 | -34.0465 | -30.1801 | -31.8265 | 395 | -28.4961 | -31.2187 | -29.9611 | -42.5908 | -25.7401 | -43.5695 | -29.1922 | -30.9648 | -30.3365 | -41.6408 | -25.4194 | -44.1988 | -26.9385 | -31.1963 | -30.2414 | -53.1718 | -27.5242 | -40.9914 | -27.6346 | -30.9424 | -30.6168 | -52.2218 | -27.2035 | -41.6207
396 | -4.7102 | 0 | -4.1126 | 0 | -4.9797 | 0 | -4.441 | 0 | -39.5509 | -148.8375 | -34.292 | -175.2706 | -44.0449 | -67.9957 | -40.2898 | -56.6792 | -47.2049 | 176.0992 | -32.9708 | -48.6022 | -36.4721 | 131.1852 | -40.709 | 65.404 | -44.6075 | 154.5716 | -37.2219 | -168.9818 | -51.4134 | 164.6723 | -34.3598 | -179.5889 | -11.7485 | -36.5334 | -18.3796 | -10.269 | -25.2016 | -48.1332 | -14.0419 | 36.8554 | -15.8099 | -144.4577 | -20.1379 | -52.2941 | -23.3684 | 43.0569 | -15.2633 | 5.8212 | -40.9652 | -31.5823 | -35.8363 | -35.3207 | -47.5394 | -29.8518 | -51.1126 | -33.175 | -36.1087 | -35.4368 | -54.9446 | -31.7648 | -49.4868 | 396 | -32.819 | -36.5078 | -30.1308 | -32.4949 | -34.6235 | -33.7456 | -31.9316 | -33.8903 | 396 | -28.4648 | -31.3985 | -30.6105 | -43.4268 | -25.7392 | -46.1329 | -29.0624 | -31.129 | -30.8797 | -42.5597 | -25.4108 | -46.6716 | -26.8721 | -31.1261 | -30.7266 | -50.832 | -27.6522 | -44.5071 | -27.4697 | -30.8566 | -30.9958 | -49.9649 | -27.3238 | -45.0458
397 | -4.6012 | 0 | -4.1324 | 0 | -4.8824 | 0 | -4.402 | 0 | -38.9547 | -158.1596 | -35.6204 | 171.6276 | -45.8405 | -73.7297 | -42.3851 | -58.8291 | -46.8093 | 166.815 | -34.2675 | -56.2085 | -36.0893 | 118.4863 | -45.274 | 53.2685 | -47.9973 | 139.8911 | -37.3216 | -175.6597 | -49.6595 | 148.134 | -37.0569 | 170.4722 | -12.6596 | -37.237 | -19.4398 | -0.522 | -30.3869 | -29.6998 | -13.8279 | 24.9882 | -19.5728 | -155.6901 | -21.8625 | -38.9696 | -24.2089 | 46.1009 | -14.9257 | -7.0308 | -40.3366 | -31.5202 | -35.6452 | -36.1062 | -48.6882 | -30.0359 | -53.0855 | -33.2418 | -36.1754 | -35.9527 | -52.6949 | -31.9488 | -48.2372 | 397 | -33.6916 | -36.8655 | -31.5107 | -33.7548 | -35.3518 | -33.544 | -33.852 | -36.5052 | 397 | -28.6406 | -31.5742 | -31.505 | -44.5558 | -25.9035 | -48.2031 | -29.1094 | -31.293 | -31.7042 | -43.8058 | -25.6339 | -48.6835 | -26.919 | -31.044 | -31.3515 | -48.5625 | -27.8164 | -43.3548 | -27.3878 | -30.7628 | -31.5507 | -47.8125 | -27.5468 | -43.8352
398 | -4.5283 | 0 | -4.1726 | 0 | -4.7683 | 0 | -4.3761 | 0 | -38.6786 | -165.5424 | -37.7447 | 156.0709 | -47.7892 | -79.6146 | -44.4034 | -47.8149 | -46.1833 | 156.219 | -35.4719 | -60.0987 | -36.137 | 107.3384 | -54.6543 | 42.6147 | -52.45 | 134.8827 | -37.6043 | 175.6868 | -47.7602 | 127.1963 | -40.6154 | 167.1756 | -13.6082 | -37.3165 | -18.5665 | 8.5934 | -29.1159 | 21.2538 | -13.9858 | 13.5533 | -25.3809 | -162.679 | -22.6771 | -24.7193 | -24.6893 | 51.0698 | -15.2486 | -20.757 | -39.8027 | -31.5585 | -35.3497 | -37.1112 | -50.2323 | -30.371 | -53.0906 | -33.5301 | -36.1494 | -36.7234 | -51.0203 | -32.2449 | -43.0685 | 398 | -34.9446 | -37.0792 | -33.1155 | -34.8894 | -35.9774 | -33.6277 | -35.7869 | -39.6168 | 398 | -29.0018 | -31.6211 | -32.5829 | -46.0597 | -26.1984 | -48.3223 | -29.3575 | -31.3811 | -32.7351 | -45.464 | -25.9949 | -48.7145 | -27.0302 | -30.8214 | -32.1951 | -46.8477 | -28.0723 | -38.3002 | -27.3859 | -30.5814 | -32.3473 | -46.252 | -27.8688 | -38.6924
399 | -4.4836 | 0 | -4.2305 | 0 | -4.6719 | 0 | -4.3297 | 0 | -38.0954 | -170.5766 | -41.509 | 135.1228 | -51.4698 | -82.1831 | -43.1724 | -30.2285 | -45.8746 | 137.1199 | -36.8441 | -65.2147 | -36.4083 | 98.6857 | -58.366 | -158.1975 | -56.9837 | 136.8365 | -38.6715 | 166.134 | -46.764 | 96.9764 | -44.3554 | -177.007 | -14.1813 | -35.1774 | -17.3149 | 12.7333 | -24.7987 | 37.3379 | -14.6487 | 3.058 | -33.0946 | -103.276 | -19.7575 | -11.5946 | -23.373 | 55.0114 | -16.0022 | -33.4946 | -38.8957 | -31.6028 | -34.8246 | -38.0871 | -53.1262 | -30.7785 | -50.5 | -34.0782 | -35.7609 | -37.7891 | -50.2656 | -32.7032 | -39.7729 | 399 | -36.3297 | -36.4003 | -34.8727 | -36.2015 | -36.3431 | -34.1397 | -37.5964 | -42.2365 | 399 | -29.5946 | -31.2773 | -33.6035 | -48.8957 | -26.548 | -45.8281 | -29.8477 | -31.089 | -33.7574 | -48.4543 | -26.4488 | -46.1703 | -27.1192 | -30.341 | -33.3055 | -46.0351 | -28.4727 | -35.101 | -27.3723 | -30.1527 | -33.4594 | -45.5937 | -28.3735 | -35.4432
400 | -4.475 | 0 | -4.2816 | 0 | -4.6133 | 0 | -4.287 | 0 | -36.8482 | -179.2873 | -50.4511 | 100.8891 | -53.5527 | -45.6845 | -41.1176 | -32.0325 | -48.1139 | 117.6843 | -38.9504 | -61.316 | -36.3153 | 90.7404 | -49.7156 | -156.4183 | -68.6056 | -127.8785 | -40.8646 | 162.2764 | -47.766 | 66.6934 | -44.1947 | -152.2173 | -14.5359 | -34.1446 | -15.7073 | 11.9116 | -21.2688 | 26.3983 | -15.7707 | -5.6583 | -24.6975 | -64.9612 | -17.7784 | -11.4461 | -21.8221 | 50.54 | -17.3579 | -47.9573 | -38.232 | -31.9309 | -34.1793 | -39.3844 | -57.6656 | -31.4856 | -47.0824 | -34.5742 | -35.0726 | -38.3597 | -51.3402 | -33.0313 | -39.5737 | 400 | -36.5748 | -35.2379 | -36.7027 | -38.3212 | -36.1188 | -34.785 | -38.8376 | -42.6019 | 400 | -30.0992 | -30.5976 | -34.9094 | -53.384 | -27.204 | -42.4691 | -30.2926 | -30.4593 | -35.0974 | -53.0523 | -27.1986 | -42.7954 | -27.4559 | -29.7043 | -33.8847 | -47.0586 | -28.7497 | -34.9604 | -27.6493 | -29.566 | -34.0727 | -46.7269 | -28.7443 | -35.2867
401 | -4.4608 | 0 | -4.2967 | 0 | -4.5662 | 0 | -4.2381 | 0 | -36.4104 | 166.3396 | -51.0892 | -40.703 | -49.8792 | -36.8009 | -40.1084 | -33.6514 | -50.8486 | 120.7303 | -39.2226 | -45.5105 | -36.3136 | 79.7468 | -45.0026 | -156.7489 | -52.2784 | -115.0932 | -41.9893 | 173.4778 | -49.3191 | 44.3342 | -43.018 | -137.907 | -14.413 | -32.6653 | -14.5019 | 6.4967 | -19.8178 | 14.9478 | -17.0633 | -10.8715 | -20.7942 | -75.7324 | -16.0092 | -17.6098 | -21.2017 | 46.4683 | -19.3129 | -61.015 | -38.6573 | -32.5909 | -34.0362 | -40.7511 | -54.4737 | -32.6144 | -45.3123 | -35.0311 | -34.7069 | -37.8201 | -52.953 | -33.2069 | -41.0189 | 401 | -36.08 | -34.7587 | -36.4797 | -38.5978 | -35.6669 | -35.1055 | -38.3933 | -41.7052 | 401 | -30.5703 | -30.2461 | -36.2903 | -50.177 | -28.3177 | -40.7461 | -30.7344 | -30.1407 | -36.513 | -49.9075 | -28.3763 | -41.0742 | -28.1301 | -29.5754 | -33.3593 | -48.6563 | -28.9102 | -36.4527 | -28.2942 | -29.47 | -33.582 | -48.3868 | -28.9688 | -36.7808
402 | -4.4828 | 0 | -4.3151 | 0 | -4.5788 | 0 | -4.2098 | 0 | -36.5917 | 156.0186 | -42.8312 | -69.5801 | -48.2965 | -39.358 | -38.5831 | -35.5355 | -50.9403 | 127.2255 | -37.298 | -36.6443 | -36.7536 | 69.3639 | -41.8061 | -162.5211 | -47.3802 | -137.5901 | -40.6712 | -177.8255 | -50.6201 | 23.5782 | -40.3481 | -126.0042 | -13.4998 | -32.2035 | -13.0486 | -1.0989 | -17.9693 | -1.8313 | -17.6793 | -10.4141 | -17.5483 | -80.8918 | -14.4067 | -24.7285 | -20.1904 | 34.3713 | -22.2035 | -71.9606 | -39.4882 | -33.2129 | -34.1286 | -40.6757 | -52.1171 | -33.5527 | -44.5534 | -35.7272 | -34.4906 | -37.0651 | -53.3737 | -33.3835 | -43.008 | 402 | -35.4348 | -34.3673 | -34.2369 | -36.7954 | -35.2954 | -35.1496 | -36.1269 | -39.2355 | 402 | -31.2444 | -30.0078 | -36.1929 | -47.802 | -29.2376 | -39.9746 | -31.4121 | -29.9118 | -36.4659 | -47.5383 | -29.3429 | -40.3436 | -28.7301 | -29.6458 | -32.5823 | -49.0586 | -29.0684 | -38.4292 | -28.8978 | -29.5498 | -32.8553 | -48.7949 | -29.1737 | -38.7982
403 | -4.4991 | 0 | -4.3266 | 0 | -4.6217 | 0 | -4.217 | 0 | -37.0962 | 145.0677 | -38.9908 | -85.6258 | -46.7742 | -41.833 | -37.2187 | -43.1932 | -50.1554 | 126.4292 | -35.3994 | -39.1075 | -37.6003 | 58.5098 | -39.8139 | -171.1205 | -45.0262 | -159.2281 | -38.9451 | 177.2527 | -52.2246 | -2.4525 | -36.9337 | -129.4565 | -13.2234 | -33.61 | -12.7211 | -9.1016 | -17.6544 | -15.1862 | -18.9345 | -4.3729 | -16.4277 | -98.9097 | -14.0433 | -36.8566 | -20.6566 | 30.9028 | -27.3425 | -81.6433 | -40.2498 | -33.6817 | -34.2504 | -39.6755 | -51.1755 | -33.9981 | -44.0609 | -36.485 | -34.2608 | -36.5219 | -53.432 | -33.4772 | -45.0978 | 403 | -34.6555 | -34.0392 | -32.1873 | -34.9606 | -35.0923 | -35.125 | -33.6204 | -36.1975 | 403 | -31.9859 | -29.7617 | -35.1764 | -46.8489 | -29.6715 | -39.4392 | -32.1584 | -29.6391 | -35.4585 | -46.5538 | -29.7811 | -39.8439 | -29.1826 | -29.7513 | -32.0228 | -49.1054 | -29.1506 | -40.4761 | -29.3551 | -29.6287 | -32.3049 | -48.8103 | -29.2602 | -40.8808
404 | -4.5128 | 0 | -4.3444 | 0 | -4.6968 | 0 | -4.2269 | 0 | -37.8731 | 135.5693 | -36.6167 | -98.877 | -44.8087 | -48.7197 | -36.1202 | -52.3181 | -49.6063 | 118.6524 | -33.9334 | -45.2387 | -38.9615 | 50.1671 | -38.4579 | -177.6889 | -43.8912 | -178.9421 | -37.8508 | 166.6596 | -54.4934 | -34.043 | -34.4209 | -141.448 | -13.1115 | -38.0554 | -12.7079 | -18.0944 | -19.5415 | -31.9449 | -19.9522 | 5.8638 | -15.593 | -114.0593 | -13.5627 | -48.5241 | -20.974 | 29.4939 | -36.7657 | -50.2622 | -40.963 | -34.1552 | -34.3579 | -38.6348 | -50.9708 | -33.8153 | -43.6178 | -37.2788 | -34.0518 | -35.8366 | -53.8835 | -33.5405 | -46.8877 | 404 | -33.8282 | -33.7834 | -30.6222 | -33.4847 | -35.0799 | -35.3077 | -31.7523 | -33.9179 | 404 | -32.766 | -29.539 | -34.122 | -46.6264 | -29.4709 | -38.921 | -32.9344 | -29.355 | -34.4079 | -46.274 | -29.5884 | -39.3909 | -29.6424 | -29.8451 | -31.3238 | -49.5391 | -29.1961 | -42.1909 | -29.8108 | -29.6611 | -31.6097 | -49.1867 | -29.3136 | -42.6608
405 | -4.5313 | 0 | -4.3321 | 0 | -4.8009 | 0 | -4.2501 | 0 | -38.9387 | 127.8578 | -34.9639 | -112.3059 | -43.3004 | -60.9037 | -35.3294 | -62.6662 | -49.5353 | 110.8822 | -32.5447 | -55.4694 | -40.8857 | 45.1605 | -37.4476 | 176.2511 | -43.3181 | 164.772 | -37.7344 | 152.3033 | -56.8476 | -73.016 | -32.9132 | -157.7397 | -13.115 | -43.9938 | -12.8807 | -27.3586 | -21.4487 | -51.4665 | -18.7204 | 13.5118 | -15.5713 | -132.077 | -13.4279 | -58.8099 | -20.8147 | 30.5135 | -30.0817 | 26.1532 | -41.5523 | -34.5523 | -34.4937 | -37.896 | -51.2632 | -33.2124 | -43.3829 | -37.9844 | -33.9298 | -34.9415 | -53.5548 | -33.7149 | -48.1559 | 405 | -33.0687 | -33.6458 | -29.3234 | -32.1149 | -35.1128 | -35.9842 | -30.6561 | -32.5185 | 405 | -33.4531 | -29.3985 | -33.3647 | -46.9311 | -28.8803 | -38.582 | -33.6523 | -29.1289 | -33.6459 | -46.4623 | -28.9623 | -39.1328 | -30.021 | -29.9624 | -30.4102 | -49.2227 | -29.3828 | -43.355 | -30.2202 | -29.6928 | -30.6914 | -48.7539 | -29.4648 | -43.9058
406 | -4.5381 | 0 | -4.3065 | 0 | -4.906 | 0 | -4.2904 | 0 | -40.3065 | 123.9497 | -34.0128 | -126.5626 | -42.368 | -75.4964 | -34.944 | -73.4773 | -49.5913 | 103.0935 | -31.5565 | -67.9283 | -43.2736 | 47.8733 | -36.6043 | 170.9387 | -42.7366 | 150.3078 | -38.5247 | 139.0019 | -57.6208 | -119.0446 | -32.0325 | -172.8717 | -12.8207 | -48.5306 | -12.8292 | -33.6564 | -24.3541 | -76.539 | -17.3803 | 14.9018 | -16.0612 | -148.6804 | -13.7296 | -68.657 | -19.6194 | 27.1804 | -22.7024 | 21.2337 | -42.0189 | -34.8254 | -34.6685 | -37.2923 | -51.6009 | -32.6027 | -43.4159 | -38.6872 | -33.8311 | -34.2557 | -53.1659 | -34.031 | -49.4486 | 406 | -32.6115 | -33.7212 | -28.4892 | -31.1478 | -34.9639 | -37.2299 | -30.0645 | -31.667 | 406 | -34.1491 | -29.293 | -32.7542 | -47.2944 | -28.2962 | -38.5099 | -34.3807 | -28.9251 | -33.0019 | -46.6949 | -28.3123 | -39.1255 | -30.2873 | -30.1304 | -29.7176 | -48.8594 | -29.7245 | -44.5426 | -30.5189 | -29.7625 | -29.9653 | -48.2599 | -29.7406 | -45.1582
407 | -4.5321 | 0 | -4.2775 | 0 | -5.0042 | 0 | -4.324 | 0 | -41.8615 | 125.1927 | -33.6554 | -140.3555 | -41.666 | -90.1804 | -34.8376 | -81.8531 | -49.7076 | 95.5753 | -31.0804 | -81.2659 | -44.9101 | 63.8277 | -35.8334 | 164.9649 | -42.2476 | 134.8202 | -40.1445 | 127.3182 | -56.5231 | -164.2103 | -31.502 | 170.1338 | -13.0203 | -55.6096 | -13.369 | -41.8246 | -28.8867 | -101.5302 | -15.7127 | 11.7203 | -16.7144 | -168.2516 | -14.5124 | -81.4171 | -19.0778 | 26.6211 | -21.0588 | 8.4533 | -42.3884 | -34.912 | -34.9086 | -36.783 | -51.7947 | -31.9589 | -43.7189 | -39.4222 | -33.8134 | -33.7463 | -53.3947 | -34.3285 | -51.2188 | 407 | -32.4852 | -33.935 | -28.1276 | -30.6621 | -34.5235 | -38.8194 | -29.725 | -31.1382 | 407 | -34.8901 | -29.2813 | -32.2509 | -47.5172 | -27.6814 | -38.7147 | -35.1447 | -28.8092 | -32.459 | -46.7905 | -27.6349 | -39.3949 | -30.3799 | -30.3765 | -29.2142 | -49.1172 | -30.051 | -46.2146 | -30.6345 | -29.9044 | -29.4223 | -48.3905 | -30.0045 | -46.8948
408 | -4.4993 | 0 | -4.2381 | 0 | -5.131 | 0 | -4.3354 | 0 | -42.8137 | 133.8748 | -33.8525 | -153.8775 | -41.4449 | -108.6941 | -34.8687 | -91.279 | -49.8397 | 88.9761 | -30.9559 | -95.2862 | -43.6296 | 83.0224 | -35.1235 | 159.5101 | -42.2346 | 117.6331 | -42.6401 | 122.9789 | -55.3569 | 159.1982 | -31.3801 | 151.862 | -13.2763 | -61.9981 | -14.0916 | -48.2564 | -30.265 | 168.7352 | -15.0645 | 6.6391 | -17.6512 | 173.4145 | -15.6644 | -92.7622 | -18.087 | 22.9523 | -18.8968 | -6.9626 | -42.5365 | -34.8395 | -35.286 | -36.3412 | -51.7905 | -31.3708 | -44.3592 | -40.1739 | -33.9212 | -33.367 | -54.7069 | -34.4786 | -52.8025 | 408 | -32.7094 | -34.1047 | -28.1241 | -30.533 | -33.8669 | -39.969 | -29.6274 | -31.0212 | 408 | -35.6746 | -29.4219 | -31.8419 | -47.5524 | -27.1327 | -39.2282 | -35.9358 | -28.7902 | -32.0058 | -46.6595 | -27.0354 | -40.0238 | -30.3402 | -30.7867 | -28.8677 | -50.4688 | -30.2405 | -47.6715 | -30.6014 | -30.155 | -29.0316 | -49.5759 | -30.1432 | -48.4671
409 | -4.5081 | 0 | -4.2152 | 0 | -5.2464 | 0 | -4.3636 | 0 | -42.1674 | 146.0657 | -34.6082 | -166.8152 | -42.1213 | -128.3828 | -34.9425 | -100.4828 | -49.8138 | 82.3158 | -31.1496 | -109.8372 | -40.9335 | 87.8356 | -34.5887 | 152.683 | -42.7079 | 103.8003 | -45.3268 | 132.2645 | -55.1317 | 130.2425 | -31.7831 | 132.5775 | -13.6069 | -68.9405 | -14.7213 | -53.2758 | -25.1862 | 119.656 | -14.4163 | 0.2587 | -18.8697 | 154.0305 | -17.4353 | -104.0099 | -17.0452 | 14.5063 | -17.5252 | -22.7856 | -42.5136 | -34.709 | -35.7324 | -35.9785 | -51.6269 | -30.8379 | -45.3363 | -40.887 | -34.223 | -33.0589 | -57.8597 | -34.3363 | -51.5899 | 409 | -33.2961 | -34.0717 | -28.4346 | -30.7612 | -33.1704 | -39.467 | -29.8287 | -31.427 | 409 | -36.3789 | -29.7149 | -31.4704 | -47.4117 | -26.6227 | -40.0899 | -36.6718 | -28.9766 | -31.6149 | -46.3805 | -26.4743 | -40.9727 | -30.2009 | -31.2243 | -28.5508 | -53.6445 | -30.1211 | -46.3435 | -30.4938 | -30.486 | -28.6953 | -52.6133 | -29.9727 | -47.2263
410 | -4.5047 | 0 | -4.1744 | 0 | -5.3271 | 0 | -4.3602 | 0 | -40.3587 | 151.6284 | -36.0063 | -177.8363 | -43.7619 | -143.0136 | -35.0329 | -108.5949 | -49.6089 | 74.3572 | -31.7353 | -123.4762 | -38.6314 | 83.6317 | -34.3231 | 145.6243 | -43.2531 | 93.8364 | -45.1379 | 155.0048 | -56.3217 | 108.0445 | -32.7515 | 114.0431 | -14.2031 | -74.5828 | -15.2867 | -53.8854 | -21.884 | 83.7949 | -13.6233 | -5.8661 | -20.5453 | 135.3053 | -19.7874 | -116.7701 | -16.5069 | 5.3742 | -16.8977 | -40.9277 | -42.3557 | -34.4928 | -36.0689 | -35.7503 | -51.5393 | -30.3327 | -46.4595 | -41.3115 | -34.5946 | -32.8189 | -64.4127 | -33.7607 | -48.5573 | 410 | -34.1459 | -33.8001 | -29.0824 | -31.405 | -32.5658 | -37.6952 | -30.311 | -32.3634 | 410 | -36.8068 | -30.0899 | -31.2456 | -47.3649 | -26.1583 | -41.1324 | -37.1371 | -29.2675 | -31.3901 | -46.2122 | -25.9725 | -42.0993 | -29.9881 | -31.5642 | -28.3142 | -60.2383 | -29.5863 | -43.2302 | -30.3184 | -30.7418 | -28.4587 | -59.0856 | -29.4005 | -44.1971
411 | -4.4904 | 0 | -4.1558 | 0 | -5.3881 | 0 | -4.3465 | 0 | -38.4733 | 148.9758 | -38.3494 | 171.9892 | -45.7632 | -150.4667 | -35.2138 | -117.1895 | -49.403 | 64.1705 | -32.8342 | -138.7224 | -36.9825 | 74.4456 | -34.3792 | 138.8816 | -43.7877 | 84.7969 | -42.1621 | 162.2511 | -58.8163 | 101.7052 | -34.233 | 95.5042 | -15.1815 | -81.6443 | -16.4267 | -59.1478 | -19.5474 | 69.1268 | -13.7979 | -13.8901 | -22.3613 | 119.1502 | -23.1845 | -122.8964 | -16.5601 | -5.4688 | -16.4477 | -55.4682 | -42.177 | -34.2218 | -36.1132 | -35.677 | -51.6653 | -29.9406 | -47.7105 | -41.3373 | -34.9123 | -32.7535 | -65.8433 | -32.9623 | -46.4191 | 411 | -35.0184 | -33.4234 | -30.1414 | -32.5283 | -32.1684 | -35.8099 | -30.9533 | -33.7631 | 411 | -36.8469 | -30.4219 | -31.1866 | -47.5095 | -25.7848 | -42.3224 | -37.1815 | -29.5242 | -31.3305 | -46.2772 | -25.5941 | -43.364 | -29.7314 | -31.6228 | -28.2631 | -61.6875 | -28.8065 | -41.031 | -30.066 | -30.7251 | -28.407 | -60.4552 | -28.6158 | -42.0726
412 | -4.4911 | 0 | -4.1492 | 0 | -5.3786 | 0 | -4.3019 | 0 | -36.9155 | 142.4939 | -42.2365 | 168.0465 | -47.1347 | -150.8454 | -35.5263 | -126.3795 | -49.6201 | 51.6925 | -34.4336 | -151.4077 | -35.832 | 63.8595 | -34.7985 | 134.0246 | -44.2488 | 79.1911 | -39.6522 | 154.3252 | -59.7588 | 118.7019 | -36.4922 | 74.8525 | -16.3005 | -89.4358 | -17.0411 | -58.9624 | -18.1488 | 50.4334 | -13.668 | -19.8484 | -25.817 | 98.2635 | -27.793 | -113.8079 | -17.1257 | -15.5057 | -16.4514 | -75.7647 | -42.0884 | -34.0132 | -35.9382 | -35.858 | -52.108 | -29.6382 | -48.9265 | -40.6911 | -35.1239 | -32.864 | -59.0164 | -32.1052 | -45.3277 | 412 | -35.4892 | -33.0584 | -31.548 | -34.0834 | -32.007 | -34.3122 | -31.7792 | -35.8017 | 412 | -36.2 | -30.6328 | -31.3669 | -47.9588 | -25.489 | -43.5479 | -36.5419 | -29.7453 | -31.5561 | -46.7294 | -25.3363 | -44.6246 | -29.5221 | -31.4471 | -28.3729 | -54.8672 | -27.956 | -39.9491 | -29.864 | -30.5596 | -28.5621 | -53.6378 | -27.8033 | -41.0258
413 | -4.4849 | 0 | -4.149 | 0 | -5.2935 | 0 | -4.2896 | 0 | -35.7309 | 133.2784 | -48.87 | -172.3651 | -47.6444 | -149.6567 | -36.1659 | -136.154 | -50.4513 | 40.3453 | -36.584 | -162.2597 | -35.0681 | 53.2427 | -35.5591 | 131.3961 | -44.1442 | 76.5106 | -38.2859 | 138.3817 | -56.4808 | 127.8667 | -40.2951 | 53.3307 | -17.5743 | -92.6812 | -17.4863 | -57.0842 | -17.3381 | 34.4767 | -13.7709 | -25.7112 | -30.6984 | 77.3148 | -29.1961 | -103.2079 | -18.5147 | -27.3881 | -16.2201 | -101.0617 | -42.0649 | -33.9047 | -35.5649 | -36.3149 | -52.7289 | -29.4125 | -50.0826 | -39.6178 | -35.2115 | -33.317 | -55.6099 | -31.3639 | -44.9965 | 413 | -35.2663 | -32.8564 | -33.2392 | -36.0942 | -32.0215 | -33.3541 | -32.8412 | -38.7228 | 413 | -35.1329 | -30.7266 | -31.83 | -48.5799 | -25.2635 | -44.7891 | -35.4688 | -29.918 | -32.0253 | -47.4354 | -25.1229 | -45.793 | -29.4198 | -31.08 | -28.8321 | -51.4609 | -27.2149 | -39.703 | -29.7557 | -30.2714 | -29.0274 | -50.3164 | -27.0743 | -40.7069
414 | -4.4752 | 0 | -4.1732 | 0 | -5.1422 | 0 | -4.2689 | 0 | -34.9276 | 123.0771 | -47.4371 | -97.5251 | -47.2112 | -149.0662 | -37.3495 | -144.3575 | -51.6465 | 32.5844 | -39.3683 | -169.0329 | -34.6128 | 41.6268 | -36.2809 | 136.1949 | -43.1479 | 73.2108 | -38.0783 | 122.2667 | -53.4661 | 118.0205 | -47.6591 | 34.6741 | -19.2392 | -95.3634 | -17.4603 | -57.0823 | -17.4315 | 21.694 | -13.8475 | -30.331 | -38.2901 | 52.0251 | -26.8792 | -60.2671 | -18.2004 | -29.3225 | -17.0083 | -117.1824 | -42.1594 | -33.9409 | -35.1802 | -37.0695 | -53.2727 | -29.3433 | -50.6614 | -38.5953 | -35.1901 | -34.0677 | -53.7864 | -30.8453 | -45.0796 | 414 | -34.454 | -32.9032 | -34.9785 | -38.4922 | -32.0093 | -32.9596 | -33.8907 | -41.5437 | 414 | -34.1201 | -30.7149 | -32.5943 | -49.0995 | -25.1701 | -45.5192 | -34.4221 | -30.0479 | -32.8006 | -48.1305 | -25.0744 | -46.3925 | -29.4657 | -30.705 | -29.5925 | -49.6132 | -26.6721 | -39.9374 | -29.7677 | -30.038 | -29.7988 | -48.6442 | -26.5764 | -40.8107
415 | -4.4657 | 0 | -4.1787 | 0 | -4.9554 | 0 | -4.2445 | 0 | -34.4818 | 111.8991 | -40.3205 | -83.5085 | -45.9529 | -154.6675 | -39.118 | -149.2737 | -52.6148 | 29.6984 | -42.6751 | -165.1489 | -34.4046 | 30.9227 | -35.9003 | 147.1277 | -42.2532 | 63.2354 | -38.9167 | 106.3154 | -51.9337 | 101.5746 | -64.5791 | 138.836 | -20.7831 | -92.4759 | -17.3934 | -56.4656 | -17.8088 | 10.7247 | -14.0016 | -34.657 | -42.9587 | -134.0744 | -22.9525 | -46.4516 | -18.7489 | -35.6597 | -17.1531 | -139.9239 | -42.3641 | -34.1409 | -34.9246 | -37.8524 | -53.4071 | -29.5315 | -50.1943 | -37.9554 | -35.1454 | -34.999 | -52.8037 | -30.6273 | -45.5062 | 415 | -33.2369 | -33.1489 | -35.6958 | -40.7119 | -31.6798 | -33.0327 | -34.1375 | -41.7863 | 415 | -33.4897 | -30.6797 | -33.3867 | -49.2284 | -25.3528 | -45.2389 | -33.7767 | -30.19 | -33.6079 | -48.4517 | -25.287 | -45.9498 | -29.6752 | -30.4589 | -30.5333 | -48.625 | -26.4486 | -40.5508 | -29.9622 | -29.9692 | -30.7545 | -47.8483 | -26.3828 | -41.2617
416 | -4.4667 | 0 | -4.2036 | 0 | -4.7793 | 0 | -4.225 | 0 | -34.3165 | 101.1054 | -35.7154 | -88.5427 | -45.1137 | -168.1893 | -41.0267 | -146.0504 | -52.8426 | 29.3486 | -44.3883 | -149.4048 | -34.4271 | 20.1293 | -34.0324 | 154.2253 | -41.7842 | 52.9104 | -40.4228 | 95.0361 | -51.4946 | 86.2053 | -49.7488 | 169.4622 | -21.8439 | -84.9189 | -16.8069 | -53.7506 | -17.7508 | 0.7231 | -13.8125 | -37.1542 | -35.7398 | -140.1181 | -21.2349 | -67.818 | -19.1834 | -45.68 | -17.5321 | -160.4756 | -42.5883 | -34.4687 | -34.7147 | -38.3696 | -53.1508 | -29.9062 | -49.1254 | -37.6933 | -35.0643 | -35.9301 | -52.2661 | -30.6738 | -46.3535 | 416 | -31.7449 | -33.4269 | -34.1618 | -41.4021 | -30.8498 | -33.3854 | -33.0411 | -40.7575 | 416 | -33.2266 | -30.5976 | -33.9029 | -48.9472 | -25.7026 | -44.3461 | -33.4897 | -30.285 | -34.1446 | -48.3715 | -25.6812 | -44.9004 | -30.002 | -30.248 | -31.4634 | -48.0625 | -26.4702 | -41.5742 | -30.2651 | -29.9354 | -31.7051 | -47.4868 | -26.4488 | -42.1285
417 | -4.4696 | 0 | -4.2235 | 0 | -4.6727 | 0 | -4.2001 | 0 | -34.4453 | 90.377 | -32.4383 | -98.9379 | -45.1517 | 177.4464 | -41.7809 | -135.1263 | -52.3418 | 27.0498 | -44.5142 | -138.719 | -34.685 | 9.0131 | -31.731 | 153.4292 | -41.2873 | 44.2094 | -42.0556 | 88.4091 | -51.5742 | 75.1405 | -45.2209 | 164.5468 | -22.2155 | -81.5106 | -16.7433 | -59.8989 | -19.4724 | -8.9686 | -14.0209 | -43.8192 | -30.8234 | -168.1365 | -19.8919 | -79.2574 | -19.9066 | -55.2429 | -18.1641 | 179.1206 | -42.7762 | -34.8114 | -34.6356 | -38.5067 | -52.9091 | -30.3427 | -48.0516 | -37.6571 | -34.9501 | -36.5165 | -51.7821 | -30.8837 | -47.622 | 417 | -30.1762 | -33.6502 | -31.7256 | -41.4427 | -29.6431 | -33.8799 | -31.1712 | -39.5326 | 417 | -33.1875 | -30.4805 | -34.0371 | -48.6856 | -26.1192 | -43.3789 | -33.4336 | -30.2774 | -34.3066 | -48.2364 | -26.1426 | -43.8515 | -30.3418 | -30.166 | -32.0469 | -47.5586 | -26.6602 | -42.9493 | -30.5879 | -29.9629 | -32.3164 | -47.1094 | -26.6836 | -43.4219
418 | -4.4782 | 0 | -4.2622 | 0 | -4.6412 | 0 | -4.1995 | 0 | -34.8303 | 81.2637 | -30.0362 | -111.6232 | -45.335 | 165.9014 | -40.8982 | -125.5963 | -51.2206 | 21.4735 | -44.3391 | -128.746 | -35.1816 | -1.4375 | -29.7668 | 146.0423 | -40.5864 | 32.856 | -43.565 | 84.006 | -51.8668 | 64.42 | -42.2068 | 155.4465 | -21.4318 | -67.0013 | -16.2777 | -63.5725 | -19.6171 | -14.5714 | -13.7163 | -46.29 | -27.0174 | 173.1487 | -19.0569 | -93.6389 | -21.7436 | -73.2514 | -18.884 | 159.8816 | -42.8033 | -35.2253 | -34.5505 | -38.4166 | -52.8307 | -30.7682 | -47.1997 | -37.7584 | -34.8298 | -36.6958 | -51.1372 | -31.1842 | -48.321 | 418 | -28.6973 | -33.7914 | -29.5474 | -41.3285 | -28.3989 | -34.5126 | -29.3579 | -38.1237 | 418 | -33.2802 | -30.3516 | -33.9384 | -48.5685 | -26.506 | -42.5585 | -33.4962 | -30.1886 | -34.2171 | -48.1895 | -26.5687 | -43.0002 | -30.7471 | -30.0723 | -32.2176 | -46.875 | -26.922 | -43.6798 | -30.9631 | -29.9093 | -32.4963 | -46.496 | -26.9847 | -44.1215
419 | -4.5033 | 0 | -4.2933 | 0 | -4.602 | 0 | -4.1846 | 0 | -35.4393 | 72.0167 | -28.2874 | -124.3278 | -45.5953 | 152.2637 | -39.3557 | -122.6708 | -49.9854 | 8.3419 | -43.0808 | -121.4168 | -35.9189 | -11.0637 | -28.2137 | 137.2239 | -40.2083 | 19.864 | -45.2554 | 78.6937 | -52.4612 | 54.8203 | -40.3597 | 142.0394 | -20.506 | -62.4639 | -15.6133 | -63.0282 | -20.1869 | -17.3106 | -13.5401 | -50.1229 | -28.003 | 152.2092 | -18.3179 | -111.5357 | -23.842 | -78.2352 | -20.3636 | 131.9338 | -42.4906 | -35.5845 | -34.517 | -38.2367 | -53.3813 | -31.1158 | -46.4417 | -37.9301 | -34.6322 | -36.6448 | -50.4378 | -31.4731 | -46.1647 | 419 | -27.455 | -33.8528 | -27.8289 | -40.6148 | -27.3048 | -35.3549 | -27.8764 | -37.1435 | 419 | -33.4268 | -30.1289 | -33.7334 | -49.088 | -26.8225 | -41.8397 | -33.6368 | -30.0302 | -34.0521 | -48.7793 | -26.9312 | -42.2571 | -31.0812 | -30.0137 | -32.1415 | -46.1445 | -27.1798 | -41.5627 | -31.2912 | -29.915 | -32.4602 | -45.8358 | -27.2885 | -41.9801
420 | -4.5279 | 0 | -4.3375 | 0 | -4.6287 | 0 | -4.1752 | 0 | -35.9967 | 64.4318 | -27.0442 | -139.0303 | -46.7112 | 138.5584 | -37.9773 | -126.9417 | -49.7557 | -11.6606 | -41.6518 | -122.5302 | -36.7511 | -17.7986 | -27.0716 | 127.3813 | -40.3824 | 6.3072 | -47.6923 | 75.4523 | -53.4402 | 52.7702 | -39.4729 | 128.4146 | -20.2055 | -72.6903 | -15.165 | -70.5143 | -22.0781 | -19.7171 | -13.7645 | -57.7279 | -27.6072 | 138.5031 | -18.2396 | -126.2304 | -27.0748 | -88.1999 | -21.6806 | 118.067 | -41.6286 | -35.8495 | -34.3738 | -38.1716 | -55.2419 | -31.3691 | -45.2594 | -38.2029 | -34.2623 | -36.4117 | -50.1266 | -31.7693 | -42.629 | 420 | -26.4825 | -33.7543 | -26.5704 | -39.9885 | -26.4484 | -36.3295 | -26.7932 | -36.7984 | 420 | -33.675 | -29.7344 | -33.6437 | -50.9044 | -27.0316 | -40.6307 | -33.8654 | -29.6336 | -33.9964 | -50.6132 | -27.1939 | -41.0842 | -31.3216 | -29.8459 | -31.8838 | -45.7891 | -27.4318 | -38.0003 | -31.512 | -29.7451 | -32.2365 | -45.4979 | -27.5941 | -38.4538
421 | -4.5324 | 0 | -4.3566 | 0 | -4.6495 | 0 | -4.1652 | 0 | -36.7306 | 54.9217 | -26.2454 | -153.7037 | -47.745 | 133.8086 | -37.0775 | -133.7513 | -51.2753 | -30.7533 | -40.779 | -125.6551 | -37.7008 | -25.9644 | -26.191 | 115.5006 | -40.8953 | -5.125 | -51.2675 | 75.7489 | -53.1749 | 53.6654 | -38.9984 | 115.0759 | -20.0818 | -73.1792 | -14.7607 | -79.2663 | -23.1401 | -13.799 | -14.0297 | -62.7517 | -29.4538 | 117.1537 | -18.5181 | -143.9199 | -30.3679 | -55.9943 | -23.5604 | 95.0294 | -40.9759 | -35.9993 | -34.1634 | -38.472 | -58.5657 | -31.4954 | -43.7863 | -38.4347 | -33.8214 | -36.0441 | -50.8761 | -31.966 | -40.1655 | 421 | -25.8453 | -33.8117 | -25.7619 | -39.6721 | -25.7594 | -37.3975 | -25.9564 | -36.7341 | 421 | -33.9023 | -29.289 | -33.9396 | -54.2091 | -27.1388 | -39.1368 | -34.0781 | -29.1719 | -34.3068 | -53.9162 | -27.3302 | -39.6211 | -31.4669 | -29.631 | -31.5117 | -46.5195 | -27.6094 | -35.516 | -31.6427 | -29.5139 | -31.8789 | -46.2266 | -27.8008 | -36.0003
422 | -4.5536 | 0 | -4.3982 | 0 | -4.6992 | 0 | -4.1852 | 0 | -38.4047 | 45.934 | -25.8801 | -168.355 | -47.1464 | 126.6842 | -36.6265 | -141.4025 | -52.5357 | -38.8398 | -39.7331 | -130.2437 | -39.279 | -31.2996 | -25.6114 | 103.7436 | -41.2806 | -14.79 | -58.9912 | 107.9374 | -52.2719 | 47.9228 | -38.805 | 99.8814 | -20.3219 | -75.9589 | -14.4883 | -85.5796 | -23.8688 | -5.8739 | -14.4823 | -69.657 | -30.584 | 121.1116 | -18.1588 | -164.0808 | -31.6457 | -51.3722 | -26.8263 | 75.1073 | -41.1582 | -36.1583 | -34.1846 | -38.7559 | -61.0996 | -31.6076 | -43.0037 | -38.9335 | -33.62 | -35.5584 | -51.7654 | -32.2304 | -39.348 | 422 | -25.6132 | -34.3485 | -25.3671 | -38.8204 | -25.3172 | -39.0223 | -25.4062 | -36.7353 | 422 | -34.3799 | -29.0664 | -34.2023 | -56.7014 | -27.2094 | -38.3045 | -34.5353 | -28.9208 | -34.5707 | -56.4004 | -27.4224 | -38.8185 | -31.6047 | -29.631 | -31.0048 | -47.3672 | -27.8322 | -34.6488 | -31.7601 | -29.4854 | -31.3732 | -47.0662 | -28.0452 | -35.1628
423 | -4.5537 | 0 | -4.4169 | 0 | -4.7684 | 0 | -4.1973 | 0 | -40.9803 | 44.3861 | -25.9209 | 178.8701 | -46.5957 | 107.8195 | -36.4248 | -148.2103 | -53.1192 | -50.7929 | -38.826 | -139.7231 | -41.1441 | -28.7918 | -25.3619 | 91.6484 | -41.8864 | -24.362 | -51.8724 | -178.4669 | -51.8367 | 39.9238 | -39.113 | 83.7735 | -20.8261 | -79.1968 | -14.4102 | -92.3404 | -22.3256 | 2.2804 | -15.0195 | -70.6866 | -34.7343 | 121.8699 | -18.2288 | 176.5148 | -27.3164 | -34.3919 | -33.7324 | 47.2951 | -41.6222 | -36.1925 | -34.3371 | -38.7472 | -63.7043 | -31.712 | -42.6943 | -39.9051 | -33.6435 | -34.9638 | -52.4638 | -32.5458 | -39.8861 | 423 | -25.7516 | -35.0522 | -25.3508 | -38.0185 | -25.1555 | -40.4629 | -25.1733 | -37.1225 | 423 | -35.3514 | -29.0898 | -34.1935 | -59.2874 | -27.2951 | -37.9259 | -35.4882 | -28.8751 | -34.5499 | -58.9359 | -27.5147 | -38.497 | -31.6388 | -29.7834 | -30.4101 | -48.0469 | -28.1289 | -35.1177 | -31.7756 | -29.5687 | -30.7665 | -47.6954 | -28.3485 | -35.6888
424 | -4.5773 | 0 | -4.4542 | 0 | -4.8666 | 0 | -4.2283 | 0 | -43.5762 | 56.1945 | -26.3795 | 164.7533 | -47.3194 | 82.9509 | -36.3608 | -154.6952 | -54.5686 | -69.2779 | -38.686 | -152.4265 | -42.0703 | -17.9123 | -25.4253 | 79.7481 | -42.8619 | -33.5714 | -45.0421 | 177.6013 | -51.7907 | 29.4479 | -40.215 | 66.3544 | -21.346 | -88.0558 | -14.2593 | -105.6609 | -22.7843 | 3.3571 | -15.6715 | -76.1602 | -35.2069 | 159.8378 | -18.5789 | 157.583 | -26.4007 | -55.3322 | -38.6793 | -86.304 | -42.351 | -36.1852 | -34.5873 | -38.6088 | -65.7299 | -31.7516 | -42.673 | -41.4994 | -33.7491 | -34.4152 | -53.4425 | -32.808 | -41.5507 | 424 | -26.2633 | -35.551 | -25.7378 | -38.031 | -25.2562 | -39.9991 | -25.2378 | -38.1381 | 424 | -36.9221 | -29.1718 | -34.0315 | -61.2757 | -27.2974 | -37.8064 | -37.0452 | -28.8825 | -34.3805 | -60.8633 | -27.5233 | -38.4447 | -31.6079 | -30.01 | -29.8379 | -48.9883 | -28.3538 | -36.6841 | -31.731 | -29.7207 | -30.1869 | -48.5759 | -28.5797 | -37.3224
425 | -4.5912 | 0 | -4.4623 | 0 | -4.9545 | 0 | -4.2475 | 0 | -43.391 | 79.2734 | -27.2805 | 153.1191 | -49.4817 | 57.2488 | -36.327 | -159.2274 | -57.8109 | -87.7512 | -39.3386 | -165.6628 | -41.0747 | -7.5677 | -25.8397 | 67.9055 | -43.8565 | -39.7474 | -41.1287 | 164.2308 | -52.1189 | 18.6748 | -41.9614 | 49.5505 | -22.0774 | -82.0517 | -14.5263 | -114.5663 | -20.6514 | 1.2971 | -16.1131 | -72.8979 | -31.1268 | -173.6456 | -18.8242 | 137.6765 | -25.3671 | -77.7801 | -27.9614 | -130.6088 | -43.1638 | -36.2263 | -34.8239 | -38.3864 | -62.7536 | -31.7341 | -42.7045 | -43.8334 | -33.9623 | -33.892 | -54.9428 | -32.849 | -44.4356 | 425 | -27.15 | -35.5218 | -26.5367 | -38.8816 | -25.6454 | -37.9228 | -25.6112 | -39.5489 | 425 | -39.2422 | -29.3711 | -33.7952 | -58.2913 | -27.2718 | -37.75 | -39.3711 | -29.0078 | -34.1389 | -57.7991 | -27.4866 | -38.457 | -31.6351 | -30.2327 | -29.3008 | -50.4805 | -28.3867 | -39.4811 | -31.764 | -29.8694 | -29.6445 | -49.9883 | -28.6015 | -40.1881
426 | -4.5809 | 0 | -4.4734 | 0 | -5.0411 | 0 | -4.2696 | 0 | -40.7649 | 90.2931 | -28.6238 | 142.7891 | -52.8329 | 29.3719 | -36.2224 | -164.3855 | -64.2005 | -98.7399 | -40.6148 | -178.2153 | -39.2317 | -5.2822 | -26.6388 | 58.1935 | -45.0214 | -45.8406 | -38.6185 | 148.3916 | -53.0586 | 8.1969 | -44.6624 | 30.7351 | -22.4039 | -83.4006 | -14.885 | -125.2136 | -19.8357 | -5.5254 | -16.0375 | -71.0308 | -27.8894 | -177.2573 | -19.0768 | 118.7291 | -24.6284 | -94.1715 | -23.0304 | -150.9448 | -43.9639 | -36.3832 | -35.048 | -38.1866 | -59.2491 | -31.6566 | -42.7351 | -47.3731 | -34.202 | -33.4695 | -56.7195 | -32.6778 | -49.1433 | 426 | -28.3508 | -34.9096 | -27.6999 | -40.3438 | -26.3468 | -35.8212 | -26.308 | -41.5125 | 426 | -42.7922 | -29.6211 | -33.6057 | -54.7757 | -27.1832 | -37.694 | -42.8997 | -29.1609 | -33.917 | -54.208 | -27.387 | -38.4655 | -31.8023 | -30.4671 | -28.8886 | -52.2461 | -28.2044 | -44.1022 | -31.9098 | -30.0069 | -29.1999 | -51.6784 | -28.4082 | -44.8737
427 | -4.5984 | 0 | -4.4647 | 0 | -5.0849 | 0 | -4.3203 | 0 | -38.3057 | 88.4838 | -30.5078 | 136.8188 | -56.791 | -20.6542 | -36.0901 | -170.3379 | -73.6504 | -29.6061 | -43.2199 | 168.5321 | -37.5195 | -10.4254 | -27.859 | 49.9319 | -46.9931 | -45.9717 | -37.0363 | 131.425 | -54.6991 | 0.1729 | -49.95 | 3.7432 | -22.1768 | -83.5349 | -15.0945 | -137.3914 | -20.2794 | -15.8571 | -15.3715 | -71.3951 | -25.1362 | 177.5028 | -19.4138 | 97.4978 | -24.0647 | -118.6104 | -19.9473 | -167.3843 | -44.6584 | -36.638 | -35.1593 | -37.9552 | -56.9005 | -31.4544 | -42.8436 | -52.9443 | -34.3953 | -33.2615 | -57.91 | -32.2881 | -55.281 | 427 | -29.8319 | -34.0473 | -29.269 | -43.0294 | -27.3655 | -34.2218 | -27.3396 | -44.7509 | 427 | -48.3459 | -29.7969 | -33.3568 | -52.4358 | -26.9897 | -37.7587 | -48.4796 | -29.3104 | -33.6349 | -51.8156 | -27.1341 | -38.5233 | -32.0396 | -30.5609 | -28.6631 | -53.4453 | -27.8234 | -50.1961 | -32.1733 | -30.0744 | -28.9412 | -52.8251 | -27.9678 | -50.9607
428 | -4.5959 | 0 | -4.4111 | 0 | -5.0522 | 0 | -4.3373 | 0 | -36.4587 | 81.2115 | -32.7922 | 137.7475 | -55.4686 | -107.8998 | -35.9282 | -175.1469 | -63.5829 | 7.7227 | -48.4615 | 173.1628 | -36.1457 | -18.8085 | -29.4439 | 45.7945 | -47.9143 | -33.5462 | -36.2057 | 114.8936 | -56.5228 | -2.0722 | -59.823 | -94.4788 | -21.6563 | -87.0114 | -15.9033 | -147.8248 | -20.0993 | -20.7812 | -14.446 | -73.8794 | -23.9593 | 168.0076 | -19.6542 | 77.8547 | -22.9628 | -141.0933 | -17.9382 | 177.1123 | -45.0888 | -37.0127 | -35.2272 | -37.7259 | -55.3416 | -31.281 | -43.0183 | -57.6137 | -34.549 | -33.284 | -58.1083 | -31.8289 | -52.9667 | 428 | -31.2228 | -33.1711 | -30.9943 | -47.5626 | -28.5522 | -33.1453 | -28.61 | -47.1145 | 428 | -53.0178 | -29.9531 | -33.13 | -50.9305 | -26.8699 | -37.9661 | -53.2026 | -29.4968 | -33.3886 | -50.2894 | -26.9437 | -38.681 | -32.4168 | -30.6313 | -28.6881 | -53.6972 | -27.4178 | -47.9145 | -32.6016 | -30.175 | -28.9467 | -53.0561 | -27.4916 | -48.6294
429 | -4.6092 | 0 | -4.3807 | 0 | -4.9842 | 0 | -4.3865 | 0 | -35.1078 | 71.6932 | -34.7825 | 150.2369 | -50.5552 | -156.4756 | -35.7739 | 178.8275 | -59.1587 | -1.0337 | -50.9536 | -146.0724 | -35.128 | -29.287 | -31.1452 | 48.1535 | -47.3891 | -19.9477 | -35.9282 | 99.0392 | -58.3842 | 1.8077 | -51.5225 | 172.1262 | -21.259 | -84.0126 | -17.6564 | -156.1497 | -20.2767 | -23.5243 | -13.4458 | -77.4666 | -22.4732 | 160.5412 | -20.8224 | 66.0507 | -23.4261 | -157.9663 | -16.1662 | 163.9271 | -45.2932 | -37.5011 | -35.2112 | -37.5764 | -54.3025 | -31.1662 | -43.2652 | -54.1618 | -34.6736 | -33.5637 | -57.8491 | -31.4859 | -49.1525 | 429 | -31.8726 | -32.4086 | -32.1817 | -47.4371 | -29.6118 | -32.4882 | -29.869 | -45.729 | 429 | -49.5526 | -30.0644 | -32.9672 | -49.9218 | -26.7855 | -38.281 | -49.7811 | -29.6894 | -33.1899 | -49.3183 | -26.7797 | -38.8787 | -32.8919 | -30.602 | -28.9545 | -53.4684 | -27.1052 | -44.1683 | -33.1204 | -30.227 | -29.1772 | -52.8649 | -27.0994 | -44.766
430 | -4.6227 | 0 | -4.3426 | 0 | -4.9045 | 0 | -4.4422 | 0 | -34.1576 | 62.2641 | -34.682 | 172.1177 | -46.6139 | 171.4889 | -35.7577 | 172.2734 | -56.8657 | -12.8325 | -46.5285 | -120.1844 | -34.3923 | -41.4791 | -32.0365 | 58.95 | -45.0564 | -15.1996 | -36.0031 | 84.9355 | -59.4127 | 9.9312 | -46.3411 | 144.145 | -21.0428 | -78.4428 | -19.9969 | -164.5904 | -18.7408 | -18.4081 | -12.7178 | -80.7174 | -22.4265 | 149.3194 | -22.0101 | 48.0022 | -22.4861 | -172.4724 | -14.9657 | 150.4054 | -45.1731 | -37.9187 | -35.172 | -37.4778 | -53.5911 | -31.1452 | -43.5457 | -51.3889 | -34.7517 | -33.9637 | -57.6473 | -31.3069 | -46.9136 | 430 | -31.2727 | -31.8603 | -32.0198 | -43.3624 | -29.9114 | -32.1051 | -30.458 | -42.5507 | 430 | -46.7662 | -30.129 | -32.8551 | -49.2485 | -26.8026 | -38.6412 | -47.0463 | -29.8472 | -33.0356 | -48.6866 | -26.703 | -39.1035 | -33.296 | -30.5493 | -29.341 | -53.3047 | -26.9643 | -42.0091 | -33.5761 | -30.2675 | -29.5215 | -52.7428 | -26.8647 | -42.4714
431 | -4.6493 | 0 | -4.3259 | 0 | -4.8392 | 0 | -4.5023 | 0 | -33.5981 | 49.1594 | -31.9175 | -176.735 | -44.1119 | 149.2598 | -36.0052 | 164.4744 | -55.5201 | -25.601 | -43.8827 | -122.6149 | -33.9933 | -53.6183 | -30.9541 | 69.7657 | -42.7528 | -16.4009 | -36.4095 | 71.2761 | -59.349 | 22.37 | -43.7895 | 127.9597 | -21.0021 | -96.4391 | -21.3229 | -168.0566 | -18.9554 | -28.0769 | -12.045 | -94.4736 | -22.5346 | 142.5146 | -23.6383 | 32.6121 | -22.1275 | 171.5004 | -14.1162 | 137.7629 | -44.7226 | -37.8173 | -35.1165 | -37.467 | -53.1251 | -31.232 | -43.9075 | -49.992 | -34.7548 | -34.4531 | -57.5544 | -31.2591 | -45.6002 | 431 | -29.5134 | -31.609 | -30.2926 | -40.8352 | -29.0151 | -32.0172 | -29.6934 | -40.1771 | 431 | -45.3427 | -30.1055 | -32.8177 | -48.7992 | -26.9061 | -39.0683 | -45.6661 | -29.9156 | -32.9647 | -48.2859 | -26.7297 | -39.4052 | -33.168 | -30.4672 | -29.8038 | -53.2285 | -26.9332 | -40.761 | -33.4914 | -30.2773 | -29.9508 | -52.7152 | -26.7568 | -41.0979
432 | -4.6781 | 0 | -4.2978 | 0 | -4.8074 | 0 | -4.5582 | 0 | -33.3118 | 37.1035 | -29.1303 | -175.5873 | -42.2363 | 125.25 | -36.4445 | 156.9192 | -54.6039 | -38.1519 | -42.1568 | -129.5695 | -33.8509 | -67.0113 | -29.1402 | 74.1348 | -41.0325 | -23.8142 | -37.0527 | 57.8616 | -58.524 | 31.7148 | -42.8362 | 110.862 | -21.2618 | -105.0024 | -22.6484 | -165.6838 | -18.2607 | -35.9005 | -11.6005 | -105.8837 | -22.9486 | 140.4166 | -26.495 | 18.8165 | -20.9244 | 160.8728 | -13.4933 | 126.7127 | -44.1111 | -37.2899 | -35.0399 | -37.4877 | -52.8034 | -31.3816 | -44.3772 | -48.8566 | -34.7309 | -34.931 | -57.5964 | -31.2917 | -44.7723 | 432 | -27.5747 | -31.5697 | -28.2122 | -39.0631 | -27.6706 | -32.1429 | -28.3324 | -38.7847 | 432 | -44.1785 | -30.0528 | -32.8096 | -48.5056 | -27.0838 | -39.5698 | -44.5588 | -29.9235 | -32.9295 | -47.996 | -26.8234 | -39.819 | -32.6118 | -30.3618 | -30.2529 | -53.2986 | -26.9939 | -39.9649 | -32.9921 | -30.2325 | -30.3728 | -52.789 | -26.7335 | -40.2141
433 | -4.7091 | 0 | -4.2873 | 0 | -4.7912 | 0 | -4.6154 | 0 | -33.2943 | 24.0615 | -26.7925 | 177.7214 | -40.8148 | 104.7488 | -37.0891 | 150.1641 | -53.996 | -51.0333 | -41.2556 | -136.6802 | -33.9746 | -80.4133 | -27.2641 | 72.2482 | -39.3766 | -32.8985 | -38.0004 | 45.2332 | -56.9326 | 37.0281 | -42.1442 | 96.7839 | -21.7788 | -114.5591 | -23.101 | -158.1034 | -17.7983 | -48.5755 | -11.1321 | -119.4597 | -23.3601 | 135.8454 | -30.4019 | 11.1722 | -20.6727 | 143.2731 | -12.8563 | 113.9126 | -43.4577 | -36.4265 | -34.9772 | -37.6022 | -52.6061 | -31.5593 | -44.9943 | -47.6974 | -34.674 | -35.3888 | -57.7794 | -31.3927 | -44.3318 | 433 | -25.7771 | -31.7535 | -26.2649 | -37.911 | -26.2098 | -32.5108 | -26.7839 | -37.4837 | 433 | -42.9883 | -29.9649 | -32.8931 | -48.3188 | -27.272 | -40.2031 | -43.4101 | -29.8828 | -32.9868 | -47.8149 | -26.9439 | -40.3789 | -31.7174 | -30.2681 | -30.6797 | -53.4921 | -27.1054 | -39.5406 | -32.1392 | -30.186 | -30.7734 | -52.9882 | -26.7773 | -39.7164
434 | -4.7556 | 0 | -4.2953 | 0 | -4.8095 | 0 | -4.6536 | 0 | -33.6611 | 10.8269 | -24.9913 | 167.6648 | -39.7077 | 84.9356 | -37.9841 | 145.778 | -53.7351 | -62.5892 | -40.7913 | -142.7013 | -34.491 | -95.0256 | -25.6671 | 65.2518 | -38.2734 | -42.1419 | -39.4996 | 33.2427 | -55.2052 | 35.9035 | -42.598 | 82.7367 | -23.8688 | -112.6632 | -23.2214 | -148.1346 | -17.3695 | -60.2195 | -11.3882 | -130.5671 | -23.7029 | 137.3388 | -39.511 | 25.994 | -19.9651 | 134.4979 | -12.6142 | 102.7598 | -42.8446 | -35.3666 | -34.8948 | -37.7275 | -52.6142 | -31.7416 | -45.9086 | -46.3993 | -34.5798 | -35.8304 | -57.8343 | -31.493 | -44.2447 | 434 | -24.3109 | -32.2642 | -24.6711 | -37.11 | -24.9263 | -33.2718 | -25.4073 | -36.8442 | 434 | -41.6437 | -29.8242 | -32.9719 | -48.3189 | -27.4463 | -41.0991 | -42.104 | -29.7703 | -33.0739 | -47.8047 | -27.088 | -41.255 | -30.611 | -30.1392 | -31.0748 | -53.539 | -27.1977 | -39.4352 | -31.0713 | -30.0853 | -31.1768 | -53.0248 | -26.8394 | -39.5911
435 | -4.7884 | 0 | -4.322 | 0 | -4.8156 | 0 | -4.6667 | 0 | -34.4394 | -2.2892 | -23.6879 | 156.1094 | -39.0461 | 66.2144 | -39.0341 | 144.536 | -53.6532 | -74.1397 | -40.7614 | -146.6203 | -35.3876 | -108.8428 | -24.3977 | 56.0758 | -37.2066 | -52.323 | -41.7613 | 23.0495 | -53.522 | 31.9317 | -43.4413 | 72.3165 | -26.2077 | -101.2405 | -22.0163 | -146.6577 | -17.5966 | -73.7476 | -11.878 | -143.6179 | -23.088 | 142.1206 | -32.5294 | 117.2158 | -19.519 | 121.1339 | -12.7195 | 92.8808 | -42.5042 | -34.3689 | -34.8495 | -37.8949 | -52.7464 | -31.9236 | -46.8885 | -45.1476 | -34.4602 | -36.1424 | -57.826 | -31.6398 | -44.3799 | 435 | -23.2221 | -33.1067 | -23.4809 | -36.7204 | -23.8593 | -34.433 | -24.2659 | -36.1983 | 435 | -40.3592 | -29.6718 | -33.1065 | -48.4244 | -27.6016 | -42.0729 | -40.8256 | -29.6446 | -33.2282 | -47.9308 | -27.2569 | -42.2218 | -29.5805 | -30.0611 | -31.354 | -53.504 | -27.3178 | -39.5643 | -30.0469 | -30.0339 | -31.4757 | -53.0104 | -26.9731 | -39.7132
436 | -4.8477 | 0 | -4.3472 | 0 | -4.815 | 0 | -4.6704 | 0 | -35.7523 | -14.4791 | -22.7821 | 142.6535 | -38.5008 | 47.7779 | -40.1099 | 145.4346 | -53.8033 | -87.3343 | -40.4241 | -147.3399 | -36.7055 | -121.9973 | -23.4742 | 45.753 | -36.1218 | -64.0783 | -45.1888 | 15.6509 | -52.1156 | 23.3952 | -44.3135 | 63.4592 | -25.9593 | -69.8367 | -20.0049 | -151.4171 | -18.1702 | -89.0539 | -12.6873 | -157.3697 | -22.0153 | 146.795 | -26.8468 | 109.9411 | -19.3253 | 114.399 | -12.818 | 82.4128 | -42.588 | -33.4855 | -34.7916 | -37.9669 | -52.8575 | -32.1496 | -47.9956 | -43.8423 | -34.3907 | -36.3667 | -57.7105 | -31.7681 | -44.4145 | 436 | -22.4589 | -34.3463 | -22.6297 | -36.2692 | -23.0529 | -36.0215 | -23.4096 | -35.4148 | 436 | -38.9946 | -29.543 | -33.1192 | -48.5103 | -27.8024 | -43.1806 | -39.4951 | -29.5757 | -33.2965 | -48.0425 | -27.4792 | -43.3252 | -28.6378 | -29.9439 | -31.519 | -53.3633 | -27.4209 | -39.5995 | -29.1383 | -29.9766 | -31.6963 | -52.8955 | -27.0977 | -39.7441
437 | -4.897 | 0 | -4.4048 | 0 | -4.8266 | 0 | -4.6391 | 0 | -37.6115 | -23.3828 | -22.2561 | 129.2257 | -38.0474 | 29.7034 | -40.674 | 151.9569 | -54.352 | -101.6433 | -39.8857 | -151.159 | -38.5851 | -133.7767 | -22.8487 | 34.0568 | -35.3891 | -78.8375 | -50.9099 | 26.0097 | -51.2114 | 12.3844 | -46.0638 | 51.8311 | -22.7569 | -57.3033 | -18.8019 | -160.6202 | -19.3942 | -103.6879 | -14.08 | -171.7994 | -19.9015 | 154.0202 | -22.362 | 99.476 | -19.1262 | 102.6338 | -13.1273 | 73.1536 | -43.1143 | -32.7667 | -34.6183 | -37.8136 | -52.7003 | -32.3018 | -48.8032 | -42.8071 | -34.4868 | -36.3657 | -57.8384 | -31.9946 | -44.3326 | 437 | -22.0215 | -35.8068 | -22.1208 | -35.7987 | -22.5048 | -38.1195 | -22.8213 | -34.9289 | 437 | -37.9101 | -29.5898 | -32.9166 | -48.2955 | -27.897 | -43.9766 | -38.4023 | -29.6602 | -33.1745 | -47.8737 | -27.6627 | -44.1641 | -27.8697 | -29.7213 | -31.4687 | -53.4336 | -27.5898 | -39.506 | -28.3619 | -29.7917 | -31.7266 | -53.0118 | -27.3555 | -39.6935
438 | -4.9442 | 0 | -4.4443 | 0 | -4.8081 | 0 | -4.5844 | 0 | -39.8871 | -29.6706 | -22.1321 | 115.1215 | -37.9925 | 9.5709 | -40.2078 | 159.6053 | -55.4526 | -113.5297 | -39.6649 | -155.2684 | -40.9334 | -141.6139 | -22.511 | 22.114 | -35.157 | -93.4565 | -51.8522 | 85.8908 | -50.9068 | 0.8841 | -49.9512 | 48.1323 | -19.7818 | -74.0998 | -17.2377 | -171.3012 | -20.4241 | -125.2092 | -15.4519 | 174.4475 | -18.0913 | 150.5946 | -19.6534 | 89.636 | -18.6364 | 90.5488 | -13.5601 | 64.664 | -43.9312 | -32.3029 | -34.2749 | -37.607 | -52.3414 | -32.3888 | -48.3974 | -41.98 | -34.7215 | -36.1708 | -58.2997 | -32.2925 | -43.8923 | 438 | -21.9505 | -36.9721 | -21.9902 | -35.6923 | -22.2222 | -40.2089 | -22.4981 | -34.9049 | 438 | -37.0358 | -29.7773 | -32.6628 | -47.8971 | -27.9445 | -43.5893 | -37.5357 | -29.9134 | -33.0226 | -47.5333 | -27.8044 | -43.813 | -27.3587 | -29.3307 | -31.2266 | -53.8554 | -27.8482 | -39.0842 | -27.8586 | -29.4668 | -31.5864 | -53.4916 | -27.7081 | -39.3079
439 | -5.0283 | 0 | -4.4716 | 0 | -4.7931 | 0 | -4.5404 | 0 | -42.4363 | -28.5324 | -22.3796 | 101.9342 | -38.3455 | -7.6585 | -38.8671 | 163.3622 | -56.9685 | -122.762 | -39.3542 | -156.5484 | -43.6756 | -142.6035 | -22.5686 | 9.3512 | -35.2354 | -106.7939 | -45.9297 | 103.8354 | -50.9169 | -10.9029 | -53.9881 | 80.7069 | -17.8973 | -76.0339 | -16.9558 | 174.3761 | -23.6392 | -141.6505 | -18.1674 | 160.0022 | -16.2484 | 144.4824 | -17.9614 | 78.8726 | -19.0541 | 88.5305 | -14.8399 | 57.7359 | -44.8531 | -31.9949 | -33.984 | -37.3414 | -51.982 | -32.4558 | -47.1201 | -40.9064 | -34.9697 | -35.9013 | -59.1044 | -32.5235 | -43.0649 | 439 | -22.2294 | -37.2382 | -22.1988 | -35.7772 | -22.3079 | -41.162 | -22.5455 | -35.0636 | 439 | -35.8781 | -29.9414 | -32.3131 | -47.5104 | -27.9842 | -42.327 | -36.4348 | -30.1766 | -32.801 | -47.1889 | -27.9154 | -42.5797 | -26.9666 | -28.9557 | -30.873 | -54.6328 | -28.0519 | -38.2718 | -27.5233 | -29.1909 | -31.3609 | -54.3113 | -27.9831 | -38.5245
440 | -5.1222 | 0 | -4.4905 | 0 | -4.7709 | 0 | -4.4753 | 0 | -44.6625 | -18.6509 | -23.0815 | 88.5525 | -38.7853 | -24.0625 | -37.2688 | 161.6765 | -58.5137 | -127.7072 | -38.6233 | -160.6379 | -46.2899 | -134.8556 | -23.0329 | -3.8294 | -35.4767 | -119.452 | -41.9756 | 98.6563 | -51.1749 | -21.9433 | -50.5871 | 113.9615 | -16.1476 | -88.3064 | -16.2024 | 161.8931 | -28.062 | -163.8277 | -21.9981 | 150.7669 | -14.8203 | 137.5103 | -16.7037 | 66.9117 | -19.2911 | 83.3096 | -16.0599 | 53.7213 | -45.9423 | -31.7227 | -33.7264 | -37.0751 | -51.6962 | -32.4453 | -45.6468 | -39.8021 | -35.1457 | -35.4515 | -60.3343 | -32.7709 | -42.1482 | 440 | -22.937 | -36.5143 | -22.8037 | -35.6706 | -22.7729 | -40.2421 | -22.9703 | -35.2328 | 440 | -34.6799 | -30.0235 | -31.9529 | -47.2057 | -27.9548 | -40.8759 | -35.3116 | -30.3748 | -32.5998 | -46.9253 | -27.97 | -41.1715 | -26.6005 | -28.6042 | -30.3293 | -55.8438 | -28.2804 | -37.3773 | -27.2322 | -28.9555 | -30.9762 | -55.5634 | -28.2956 | -37.6729
441 | -5.2137 | 0 | -4.4871 | 0 | -4.7332 | 0 | -4.4285 | 0 | -45.3199 | -1.5673 | -24.2824 | 77.3989 | -38.8602 | -39.8218 | -35.8083 | 155.4291 | -59.927 | -130.5718 | -38.1157 | -167.5471 | -47.1428 | -117.9964 | -23.9667 | -15.3684 | -35.9811 | -132.6934 | -39.3827 | 88.9853 | -51.9354 | -32.4016 | -46.7142 | 120.0149 | -14.7176 | -104.2094 | -15.8103 | 151.2965 | -32.4395 | -179.5518 | -28.7817 | 162.4067 | -13.741 | 126.3829 | -15.6574 | 56.1249 | -19.2756 | 81.6026 | -17.3575 | 54.3497 | -47.4194 | -31.6382 | -33.4077 | -36.8139 | -51.5014 | -32.4546 | -44.5262 | -38.9988 | -35.0496 | -34.991 | -62.6473 | -32.9207 | -41.4427 | 441 | -24.1007 | -35.3325 | -23.8224 | -35.4462 | -23.6822 | -38.5083 | -23.8213 | -35.5284 | 441 | -33.7851 | -29.8359 | -31.6002 | -47.0143 | -27.9675 | -39.793 | -34.5117 | -30.3164 | -32.3854 | -46.7682 | -28.0261 | -40.0977 | -26.4245 | -28.194 | -29.7773 | -58.1602 | -28.4336 | -36.7095 | -27.1511 | -28.6745 | -30.5625 | -57.9141 | -28.4922 | -37.0142
442 | -5.2717 | 0 | -4.4852 | 0 | -4.7269 | 0 | -4.4113 | 0 | -43.9771 | 12.0131 | -25.9878 | 69.6684 | -39.0379 | -60.261 | -34.6649 | 147.4659 | -61.241 | -130.1788 | -38.1638 | -172.5582 | -46.1368 | -106.8748 | -25.3634 | -24.6788 | -36.8633 | -145.5667 | -37.5952 | 77.3605 | -53.086 | -41.3099 | -43.5772 | 114.821 | -14.3429 | -113.5621 | -16.0638 | 133.2107 | -40.4689 | 12.1037 | -29.9838 | -123.7568 | -13.0393 | 117.457 | -14.8379 | 45.0402 | -19.38 | 78.8789 | -18.3971 | 61.0303 | -48.9956 | -31.9053 | -33.1923 | -36.5542 | -51.3823 | -32.4483 | -43.9578 | -38.8519 | -34.5998 | -34.5867 | -66.5516 | -32.9964 | -41.1318 | 442 | -25.7125 | -34.1752 | -25.2098 | -35.5568 | -25.0325 | -36.9202 | -25.0497 | -35.9397 | 442 | -33.5802 | -29.3281 | -31.2825 | -46.8971 | -27.9631 | -39.2309 | -34.3667 | -29.8729 | -32.1429 | -46.6554 | -28.037 | -39.5465 | -26.6336 | -27.9206 | -29.315 | -62.0664 | -28.5112 | -36.4049 | -27.4201 | -28.4654 | -30.1754 | -61.8247 | -28.5851 | -36.7205
443 | -5.281 | 0 | -4.4779 | 0 | -4.7245 | 0 | -4.4111 | 0 | -41.9118 | 16.2066 | -27.9421 | 66.1944 | -39.9719 | -84.6238 | -33.8269 | 137.2229 | -62.2219 | -126.6763 | -38.1839 | -174.4714 | -44.7257 | -103.2118 | -27.1886 | -31.1111 | -38.1105 | -157.8085 | -36.3 | 65.0041 | -54.7264 | -49.7922 | -41.3775 | 103.2681 | -13.7785 | -126.9992 | -16.2797 | 117.7301 | -28.6231 | -22.9109 | -23.2209 | -111.8246 | -12.6713 | 109.5744 | -15.2325 | 31.0372 | -19.8089 | 85.2311 | -18.8433 | 71.3617 | -50.4219 | -32.6646 | -33.1548 | -36.3008 | -51.3516 | -32.5396 | -43.8685 | -39.3651 | -34.281 | -34.2982 | -70.0013 | -33.1034 | -41.1647 | 443 | -27.5173 | -33.1941 | -26.6306 | -35.9659 | -26.7806 | -35.6627 | -26.5409 | -36.3696 | 443 | -34.0841 | -29 | -31.0198 | -46.8737 | -28.0617 | -39.144 | -34.8872 | -29.5565 | -31.8897 | -46.6271 | -28.1285 | -39.4574 | -27.3836 | -27.8738 | -29.0172 | -65.5234 | -28.6255 | -36.4402 | -28.1867 | -28.4303 | -29.8871 | -65.2768 | -28.6923 | -36.7536
444 | -5.2555 | 0 | -4.4487 | 0 | -4.7488 | 0 | -4.4537 | 0 | -40.0096 | 12.2201 | -29.8171 | 71.167 | -41.7845 | -112.3044 | -33.282 | 125.4478 | -62.1382 | -120.0325 | -37.9131 | -177.0347 | -43.1232 | -104.3017 | -29.2845 | -30.7488 | -39.8478 | -169.1245 | -35.3057 | 50.9422 | -57.4751 | -55.615 | -40.1748 | 90.4135 | -13.4935 | -140.9663 | -16.6944 | 103.5147 | -24.3168 | -41.9499 | -18.9268 | -124.3265 | -12.7927 | 104.2608 | -15.764 | 16.6421 | -19.7437 | 89.9648 | -17.7985 | 79.49 | -51.4514 | -33.8179 | -33.3168 | -36.049 | -51.4162 | -32.7397 | -44.062 | -40.4832 | -34.1813 | -34.1753 | -67.6792 | -33.198 | -41.4821 | 444 | -29.1754 | -32.4407 | -27.7614 | -36.4091 | -28.757 | -34.6188 | -28.0413 | -36.9592 | 444 | -35.2277 | -28.9258 | -30.7935 | -46.9675 | -28.291 | -39.3132 | -36.0345 | -29.4325 | -31.5953 | -46.6674 | -28.286 | -39.6083 | -28.5624 | -28.0613 | -28.9198 | -63.2305 | -28.7493 | -36.7333 | -29.3692 | -28.568 | -29.7216 | -62.9304 | -28.7443 | -37.0284
445 | -5.2296 | 0 | -4.4171 | 0 | -4.7921 | 0 | -4.5109 | 0 | -38.5627 | 3.2306 | -30.8641 | 82.8561 | -44.1323 | -145.6554 | -33.0051 | 113.5232 | -61.1379 | -117.9667 | -37.5983 | -179.9725 | -41.4763 | -109.6828 | -30.8522 | -19.324 | -42.5657 | -175.9354 | -34.6079 | 37.9589 | -61.5929 | -42.946 | -39.4266 | 80.7031 | -13.7371 | -154.9302 | -17.5166 | 91.3337 | -21.8842 | -67.4002 | -16.7227 | -138.2008 | -12.4823 | 94.4975 | -15.9742 | 6.6536 | -18.7339 | 90.9368 | -15.9752 | 81.3139 | -51.6073 | -35.0721 | -33.5487 | -35.8729 | -51.5292 | -32.9823 | -44.3507 | -42.2453 | -34.3585 | -34.0968 | -63.8585 | -33.3234 | -42.0998 | 445 | -30.0112 | -31.9341 | -28.2564 | -36.7114 | -30.2301 | -33.7884 | -28.921 | -37.6905 | 445 | -37.0157 | -29.1289 | -30.6433 | -47.1121 | -28.5652 | -39.5586 | -37.8282 | -29.5664 | -31.362 | -46.7371 | -28.4714 | -39.8398 | -29.8425 | -28.3191 | -28.8672 | -59.4414 | -28.9063 | -37.3077 | -30.655 | -28.7566 | -29.5859 | -59.0664 | -28.8125 | -37.5889
446 | -5.1649 | 0 | -4.387 | 0 | -4.8467 | 0 | -4.6265 | 0 | -37.5374 | -7.786 | -30.063 | 96.7087 | -45.8598 | 167.6514 | -32.9825 | 101.0602 | -59.2633 | -125.4981 | -37.1917 | 177.4951 | -39.9843 | -118.6933 | -30.352 | -4.2685 | -46.1869 | -169.8677 | -34.1726 | 22.9192 | -60.9169 | -1.5112 | -38.7433 | 70.6571 | -14.9868 | -172.0313 | -18.1646 | 78.6638 | -20.5702 | -87.0787 | -15.406 | -155.2091 | -12.6716 | 88.0499 | -16.6036 | -3.714 | -17.7362 | 90.0273 | -14.5824 | 77.4477 | -50.4483 | -35.9353 | -33.7418 | -35.7022 | -51.7217 | -33.2947 | -44.8245 | -44.6709 | -34.6571 | -34.1604 | -60.3948 | -33.3741 | -43.0334 | 446 | -29.2524 | -31.6704 | -27.7476 | -36.6147 | -29.8023 | -33.1536 | -28.4215 | -38.0017 | 446 | -39.506 | -29.4922 | -30.5373 | -47.3347 | -28.9077 | -39.9778 | -40.2839 | -29.8104 | -31.0757 | -46.875 | -28.6682 | -40.198 | -30.7704 | -28.5769 | -28.9955 | -56.0078 | -28.9871 | -38.1867 | -31.5483 | -28.8951 | -29.5339 | -55.5481 | -28.7476 | -38.4069
447 | -5.1291 | 0 | -4.38 | 0 | -4.9327 | 0 | -4.7462 | 0 | -36.9045 | -22.5125 | -28.0162 | 101.0677 | -44.7594 | 114.1938 | -33.2264 | 88.0271 | -58.0057 | -146.5521 | -36.5776 | 173.8626 | -38.8331 | -131.8279 | -28.2756 | 1.8365 | -48.0591 | -143.3295 | -34.0849 | 7.0646 | -56.0125 | 8.9954 | -38.3159 | 60.0626 | -15.6527 | 173.8271 | -19.835 | 70.9904 | -19.1139 | -112.1797 | -14.2646 | -171.4315 | -12.9951 | 83.3087 | -17.7943 | -14.8438 | -16.3569 | 84.9817 | -13.3453 | 70.8539 | -48.1132 | -35.7049 | -33.8349 | -35.6366 | -52.3124 | -33.5213 | -45.7707 | -46.6749 | -35.0549 | -34.3058 | -57.0949 | -33.3898 | -44.2836 | 447 | -27.4079 | -31.6668 | -26.4309 | -35.9361 | -27.8677 | -32.8089 | -26.9353 | -37.8118 | 447 | -41.5458 | -29.9258 | -30.5075 | -47.9324 | -29.1413 | -40.838 | -42.2949 | -30.1222 | -30.8904 | -47.3797 | -28.7751 | -41.0245 | -30.5758 | -28.7058 | -29.1767 | -52.7149 | -29.0098 | -39.3509 | -31.3249 | -28.9022 | -29.5596 | -52.1622 | -28.6436 | -39.5374
448 | -5.0999 | 0 | -4.3489 | 0 | -4.995 | 0 | -4.8396 | 0 | -36.8714 | -39.6768 | -26.0233 | 97.1523 | -41.6955 | 73.314 | -33.9079 | 73.0853 | -58.2985 | -179.2948 | -35.9373 | 167.9153 | -38.1606 | -149.0795 | -26.2357 | -2.04 | -45.9623 | -116.883 | -34.497 | -9.3123 | -52.4666 | -2.3482 | -38.0848 | 48.9666 | -17.5159 | 159.0174 | -20.9248 | 64.975 | -18.7263 | -133.2484 | -13.857 | 171.2407 | -13.2993 | 79.142 | -19.508 | -20.3414 | -15.7665 | 80.9622 | -12.4436 | 62.5594 | -45.1876 | -34.4977 | -33.5831 | -35.8634 | -53.9298 | -33.5836 | -47.6692 | -45.6903 | -35.2327 | -34.6966 | -54.3919 | -33.1434 | -44.9437 | 448 | -25.5726 | -32.1208 | -25.0032 | -34.8946 | -25.9222 | -32.8949 | -25.3915 | -37.2949 | 448 | -40.5904 | -30.1328 | -30.7635 | -49.5809 | -29.2347 | -42.6742 | -41.3414 | -30.2377 | -31.0238 | -48.9348 | -28.744 | -42.8296 | -29.3978 | -28.4832 | -29.5967 | -50.043 | -28.7945 | -39.9487 | -30.1488 | -28.5881 | -29.857 | -49.3969 | -28.3038 | -40.1041
449 | -5.0893 | 0 | -4.3237 | 0 | -5.019 | 0 | -4.9214 | 0 | -37.7463 | -58.0834 | -24.5777 | 90.3964 | -38.6855 | 43.1296 | -35.2723 | 58.9431 | -62.0125 | 133.3683 | -35.3105 | 160.3587 | -38.3506 | -168.3861 | -24.8133 | -8.8146 | -41.694 | -108.1112 | -35.5669 | -25.338 | -50.7114 | -19.1794 | -37.8292 | 39.6912 | -20.3134 | 149.4436 | -23.0088 | 66.6212 | -17.6773 | -155.0794 | -13.4099 | 156.0834 | -13.7063 | 78.5282 | -21.9662 | -22.1197 | -14.7976 | 73.6975 | -11.8548 | 53.6034 | -43.01 | -33.3342 | -33.092 | -36.6038 | -57.0647 | -33.5022 | -51.4995 | -43.8901 | -34.7417 | -35.519 | -53.0034 | -32.6831 | -44.8975 | 449 | -24.2152 | -33.3193 | -23.897 | -33.6614 | -24.5406 | -33.643 | -24.2671 | -36.1792 | 449 | -38.8008 | -29.6524 | -31.5145 | -52.741 | -29.1785 | -46.4805 | -39.5664 | -29.7227 | -31.6824 | -52.0457 | -28.5808 | -46.5781 | -28.2449 | -28.0027 | -30.4297 | -48.6797 | -28.3594 | -39.8785 | -29.0105 | -28.073 | -30.5976 | -47.9844 | -27.7617 | -39.9761
450 | -5.0629 | 0 | -4.2961 | 0 | -4.9847 | 0 | -4.9415 | 0 | -39.4818 | -75.8361 | -23.5408 | 80.7606 | -36.234 | 16.0444 | -37.2657 | 46.2485 | -67.5926 | 38.5878 | -34.9285 | 149.2457 | -39.3571 | 171.3487 | -23.7722 | -17.8964 | -37.9468 | -117.7442 | -37.0088 | -39.0263 | -50.2755 | -36.5728 | -37.8018 | 24.5922 | -25.9164 | 145.4648 | -22.5256 | 68.8819 | -18.1163 | -177.6866 | -13.4684 | 138.6256 | -13.9353 | 79.1533 | -24.9577 | -13.9114 | -13.8619 | 66.2515 | -11.4051 | 44.7636 | -41.9412 | -32.579 | -32.5087 | -37.4958 | -58.4138 | -33.3524 | -58.0344 | -42.4105 | -33.7972 | -36.4563 | -52.8821 | -32.2972 | -45.2965 | 450 | -23.2096 | -35.2211 | -23.0678 | -32.5207 | -23.4951 | -34.8884 | -23.4099 | -34.7403 | 450 | -37.3476 | -28.7343 | -32.4329 | -54.1177 | -29.0563 | -53.0497 | -38.1144 | -28.8125 | -32.5543 | -53.4291 | -28.4109 | -53.0929 | -27.5161 | -27.4458 | -31.3934 | -48.586 | -28.0011 | -40.3118 | -28.2829 | -27.524 | -31.5148 | -47.8974 | -27.3557 | -40.355
451 | -5.1083 | 0 | -4.3192 | 0 | -4.9733 | 0 | -4.9239 | 0 | -41.858 | -88.8843 | -22.8178 | 70.5538 | -34.465 | -8.2467 | -39.785 | 37.5119 | -62.0876 | -46.9417 | -35.1958 | 137.339 | -41.0232 | 155.6505 | -23.0501 | -28.5884 | -35.7234 | -133.2103 | -38.7986 | -51.6549 | -50.6867 | -49.8912 | -38.6224 | 9.314 | -32.3711 | -146.7472 | -22.6342 | 74.8302 | -18.0876 | 160.6663 | -13.774 | 121.8782 | -13.9832 | 81.2057 | -26.5318 | -4.2135 | -13.8956 | 58.9888 | -11.694 | 32.6259 | -41.731 | -32.2171 | -32.2193 | -38.2467 | -56.0396 | -33.4281 | -63.6278 | -40.5788 | -33.0497 | -37.4091 | -53.7411 | -32.2702 | -46.8317 | 451 | -22.4799 | -37.6729 | -22.4919 | -31.8007 | -22.7563 | -36.5873 | -22.8203 | -33.8345 | 451 | -35.4705 | -27.9414 | -33.1384 | -51.7204 | -29.1089 | -58.6545 | -36.2596 | -28.0764 | -33.3228 | -51.0663 | -28.5042 | -58.7039 | -27.1088 | -27.111 | -32.3008 | -49.4219 | -27.951 | -41.8584 | -27.8979 | -27.246 | -32.4852 | -48.7678 | -27.3463 | -41.9078
452 | -5.1824 | 0 | -4.3429 | 0 | -4.9502 | 0 | -4.8665 | 0 | -45.0402 | -102.6103 | -22.3895 | 61.0615 | -33.3135 | -31.7243 | -42.9962 | 32.288 | -57.7321 | -86.3757 | -36.2993 | 125.2962 | -42.986 | 142.4539 | -22.5364 | -38.132 | -34.4041 | -149.1642 | -40.9758 | -62.9626 | -51.4503 | -59.9771 | -40.3225 | -3.4601 | -23.1854 | -116.7347 | -21.2671 | 76.6822 | -18.1738 | 139.5276 | -14.219 | 104.01 | -13.0617 | 82.8565 | -24.1175 | 26.4446 | -13.256 | 51.8196 | -11.7099 | 26.3735 | -41.8211 | -32.0143 | -31.9926 | -38.6961 | -53.5711 | -33.5573 | -57.3039 | -38.7354 | -32.5027 | -38.1242 | -55.214 | -32.376 | -49.4806 | 452 | -22.0301 | -40.7998 | -22.1803 | -31.534 | -22.2261 | -38.6227 | -22.4039 | -33.3466 | 452 | -33.553 | -27.3203 | -33.5137 | -49.2282 | -29.2144 | -52.3537 | -34.3925 | -27.5525 | -33.8296 | -48.6209 | -28.6908 | -52.4374 | -26.8319 | -26.8102 | -32.9418 | -50.8711 | -28.0331 | -44.5304 | -27.6714 | -27.0424 | -33.2577 | -50.2638 | -27.5095 | -44.6141
453 | -5.3144 | 0 | -4.3496 | 0 | -4.9238 | 0 | -4.7832 | 0 | -49.5452 | -116.0186 | -22.2295 | 49.5576 | -32.6769 | -53.2793 | -47.2698 | 38.6577 | -55.3545 | -117.1803 | -38.3261 | 117.0036 | -45.12 | 130.6794 | -22.2934 | -48.5798 | -33.6089 | -164.0283 | -44.0422 | -75.1555 | -52.2701 | -66.4753 | -42.9976 | -13.7855 | -17.2761 | -127.2992 | -20.8652 | 76.5913 | -18.6626 | 120.7914 | -15.3543 | 88.8912 | -12.0692 | 83.5392 | -20.6923 | 36.7323 | -13.4398 | 44.2685 | -12.4886 | 15.687 | -42.0621 | -31.8941 | -31.9293 | -38.8316 | -51.7574 | -33.648 | -53.4746 | -37.2011 | -32.1972 | -38.5332 | -57.041 | -32.6425 | -53.5676 | 453 | -21.847 | -44.8453 | -22.1108 | -31.6125 | -21.9629 | -41.1852 | -22.2279 | -33.083 | 453 | -31.8867 | -26.8828 | -33.5172 | -47.4078 | -29.2984 | -48.5508 | -32.8515 | -27.2734 | -34.0484 | -46.8336 | -28.8648 | -48.6914 | -26.5797 | -26.6149 | -33.2188 | -52.6914 | -28.2929 | -48.6438 | -27.5445 | -27.0055 | -33.75 | -52.1172 | -27.8593 | -48.7844
454 | -5.4789 | 0 | -4.3772 | 0 | -4.9079 | 0 | -4.6994 | 0 | -57.9947 | -130.14 | -22.3146 | 38.7047 | -32.3502 | -73.4154 | -50.6911 | 72.9053 | -53.8805 | -144.2585 | -40.9552 | 117.9143 | -47.4724 | 120.9046 | -22.3337 | -61.3549 | -33.0913 | 179.9019 | -49.2935 | -86.3208 | -53.0949 | -72.0176 | -46.91 | -17.0712 | -14.5288 | -140.3487 | -19.7964 | 70.3971 | -19.5985 | 100.3703 | -16.5047 | 71.6287 | -11.1048 | 81.5927 | -19.896 | 27.1186 | -13.911 | 37.4737 | -13.5703 | 5.9003 | -42.3983 | -31.89 | -32.0039 | -38.7537 | -50.4764 | -33.7493 | -51.0803 | -36.0681 | -32.0804 | -38.6897 | -59.4084 | -33.0017 | -55.7159 | 454 | -21.9028 | -48.4747 | -22.2494 | -31.7625 | -21.9712 | -44.6135 | -22.3099 | -32.8732 | 454 | -30.5892 | -26.6015 | -33.2748 | -46.0992 | -29.3721 | -46.1724 | -31.6909 | -27.1725 | -34.0543 | -45.5685 | -29.0499 | -46.3809 | -26.4111 | -26.525 | -33.2108 | -55.0312 | -28.6245 | -50.808 | -27.5128 | -27.096 | -33.9903 | -54.5005 | -28.3023 | -51.0165
455 | -5.6565 | 0 | -4.3812 | 0 | -4.9055 | 0 | -4.6248 | 0 | -64.2538 | 50.6812 | -22.6327 | 28.9196 | -32.2514 | -92.045 | -47.48 | 106.6676 | -52.9613 | -170.3019 | -43.3936 | 133.0267 | -50.0102 | 112.5614 | -22.6963 | -72.901 | -32.9239 | 164.1438 | -66.1622 | -81.4275 | -54.019 | -76.6821 | -53.0077 | 7.5939 | -12.4562 | -154.8121 | -18.9752 | 62.5373 | -21.2087 | 80.9277 | -19.2748 | 57.0895 | -10.0527 | 77.4399 | -17.9005 | 24.9027 | -14.5887 | 31.8811 | -15.0442 | 0.3207 | -42.8007 | -32.0398 | -32.1698 | -38.5077 | -49.6014 | -33.7469 | -49.3812 | -35.2922 | -32.1058 | -38.5179 | -62.4007 | -33.3196 | -51.2332 | 455 | -22.1824 | -46.327 | -22.5823 | -31.8956 | -22.2952 | -48.4826 | -22.6921 | -32.8482 | 455 | -29.6357 | -26.4493 | -32.8512 | -45.2202 | -29.3657 | -44.4757 | -30.911 | -27.2003 | -33.8829 | -44.6959 | -29.1221 | -44.7564 | -26.3833 | -26.5133 | -32.8614 | -58.0195 | -28.9384 | -46.3277 | -27.6586 | -27.2643 | -33.8931 | -57.4952 | -28.6948 | -46.6084
456 | -5.8056 | 0 | -4.3997 | 0 | -4.8962 | 0 | -4.5614 | 0 | -53.0531 | 33.6722 | -23.173 | 18.3024 | -32.4459 | -112.1438 | -43.6433 | 110.2077 | -52.516 | 162.744 | -42.8349 | 160.0928 | -52.6557 | 104.4961 | -23.3597 | -83.0148 | -33.1533 | 148.3804 | -51.898 | 59.2257 | -54.6661 | -76.2765 | -49.388 | 65.7044 | -11.0845 | -170.0198 | -18.771 | 52.7608 | -24.2513 | 62.6263 | -21.7987 | 44.2402 | -9.437 | 71.2111 | -17.4131 | 12.2998 | -15.2952 | 28.5632 | -17.0411 | -3.9919 | -43.2762 | -32.3821 | -32.436 | -38.1863 | -49.0066 | -33.7141 | -48.1418 | -34.8688 | -32.3017 | -38.0754 | -66.3919 | -33.6501 | -47.4505 | 456 | -22.6837 | -42.6944 | -23.0879 | -32.027 | -22.922 | -48.1531 | -23.3428 | -33.0213 | 456 | -29.0632 | -26.4961 | -32.3807 | -44.6069 | -29.3144 | -43.2456 | -30.4691 | -27.4055 | -33.6249 | -44.1104 | -29.1527 | -43.5804 | -26.5765 | -26.6304 | -32.2698 | -61.9922 | -29.2504 | -42.5543 | -27.9824 | -27.5398 | -33.514 | -61.4957 | -29.0887 | -42.8891
457 | -5.924 | 0 | -4.4201 | 0 | -4.924 | 0 | -4.5255 | 0 | -48.9329 | 22.1787 | -23.9376 | 10.0829 | -33.0488 | -131.3189 | -40.9898 | 105.0231 | -52.372 | 138.5326 | -39.4449 | 171.5077 | -55.3762 | 96.9852 | -24.3522 | -93.2579 | -33.6585 | 133.944 | -45.2618 | 47.0055 | -54.6749 | -76.1588 | -43.8895 | 67.4575 | -10.2109 | 175.0563 | -18.4753 | 43.1018 | -26.5135 | 43.205 | -28.3345 | 35.0886 | -8.3846 | 63.5304 | -16.4961 | 8.955 | -15.8983 | 28.0902 | -19.2821 | 2.2768 | -43.8512 | -32.8786 | -32.7887 | -37.8669 | -48.6286 | -33.6715 | -47.2443 | -34.756 | -32.631 | -37.4747 | -68.7052 | -33.8771 | -45.0566 | 457 | -23.4227 | -40.079 | -23.7346 | -32.1112 | -23.8674 | -44.4272 | -24.2695 | -33.2338 | 457 | -28.832 | -26.707 | -31.9429 | -44.2085 | -29.2514 | -42.3203 | -30.3359 | -27.707 | -33.3414 | -43.7046 | -29.146 | -42.7188 | -26.9546 | -26.8647 | -31.5507 | -64.2851 | -29.457 | -40.1326 | -28.4585 | -27.8647 | -32.9492 | -63.7812 | -29.3516 | -40.5311
458 | -6.0037 | 0 | -4.431 | 0 | -4.9435 | 0 | -4.5147 | 0 | -46.651 | 11.0433 | -24.9846 | 2.0779 | -34.0263 | -149.3902 | -39.2047 | 95.4824 | -52.5554 | 114.4899 | -36.5023 | 167.8244 | -58.0416 | 85.0908 | -25.7209 | -100.7598 | -34.3419 | 120.3936 | -41.7488 | 34.1731 | -54.4574 | -81.836 | -40.8801 | 58.0749 | -9.6316 | 160.0561 | -18.2162 | 34.6334 | -33.4855 | 30.3785 | -33.8337 | 74.1244 | -7.9681 | 55.9627 | -16.5762 | -1.5201 | -17.0706 | 28.8438 | -21.043 | 13.0552 | -44.5691 | -33.523 | -33.2122 | -37.573 | -48.4871 | -33.6441 | -46.5755 | -34.9161 | -33.0388 | -36.7903 | -65.0716 | -33.9786 | -43.5371 | 458 | -24.448 | -38.3188 | -24.5378 | -32.0411 | -25.1596 | -41.4263 | -25.4866 | -33.437 | 458 | -28.9124 | -27.0351 | -31.5693 | -44.0561 | -29.2131 | -41.632 | -30.4851 | -28.0953 | -33.0583 | -43.5436 | -29.1294 | -42.0608 | -27.5193 | -27.2085 | -30.7866 | -60.6406 | -29.5476 | -38.5936 | -29.092 | -28.2687 | -32.2756 | -60.1281 | -29.4639 | -39.0224
459 | -6.0232 | 0 | -4.4151 | 0 | -5.001 | 0 | -4.5398 | 0 | -45.3147 | 0.8189 | -26.3013 | -3.1929 | -35.3024 | -166.9215 | -38.0238 | 84.4093 | -52.9832 | 92.6771 | -34.4195 | 160.0046 | -60.3476 | 62.6948 | -27.4357 | -107.0518 | -35.2996 | 105.3928 | -39.4661 | 19.7927 | -54.7684 | -91.0116 | -38.9132 | 46.5107 | -9.3624 | 144.959 | -18.0229 | 27.3534 | -42.8615 | 133.219 | -28.3048 | 116.897 | -7.8571 | 46.5074 | -16.7886 | -13.7143 | -17.2849 | 31.3193 | -20.5915 | 30.7098 | -45.3501 | -34.272 | -33.6301 | -37.3188 | -48.5415 | -33.604 | -46.1221 | -35.3252 | -33.5193 | -36.1533 | -61.0244 | -33.9854 | -42.6261 | 459 | -25.7383 | -37.1655 | -25.4324 | -31.7951 | -26.776 | -39.3056 | -26.8903 | -33.6966 | 459 | -29.302 | -27.4961 | -31.2956 | -44.1264 | -29.1889 | -41.1211 | -30.9101 | -28.5183 | -32.779 | -43.5405 | -29.0642 | -41.5823 | -28.2488 | -27.6069 | -30.1301 | -56.6093 | -29.5703 | -37.6251 | -29.8569 | -28.6291 | -31.6135 | -56.0234 | -29.4456 | -38.0863
460 | -5.9868 | 0 | -4.4235 | 0 | -5.0349 | 0 | -4.5638 | 0 | -44.5318 | -8.5529 | -27.8048 | -4.3753 | -36.9979 | 174.4953 | -37.3047 | 72.0915 | -53.7104 | 72.0813 | -32.8444 | 150.5091 | -61.1255 | 26.785 | -29.3875 | -105.6557 | -36.7213 | 92.8003 | -37.9397 | 5.0814 | -55.8581 | -98.468 | -37.4283 | 35.3945 | -9.3385 | 131.361 | -19.0544 | 16.6091 | -29.5854 | 159.8286 | -23.8196 | 121.4381 | -7.7467 | 38.9365 | -17.3387 | -22.7348 | -16.473 | 35.7879 | -18.9814 | 38.8996 | -46.1945 | -35.0558 | -33.9804 | -37.1398 | -48.7374 | -33.5675 | -45.9313 | -36.027 | -33.9633 | -35.5837 | -57.9626 | -33.902 | -42.2225 | 460 | -27.2294 | -36.4688 | -26.2649 | -31.4065 | -28.6487 | -37.8496 | -28.2595 | -34.0216 | 460 | -30.0402 | -27.9765 | -31.153 | -44.3139 | -29.144 | -40.8964 | -31.6035 | -28.9284 | -32.576 | -43.7025 | -29.0037 | -41.3675 | -29.069 | -27.9936 | -29.5969 | -53.5391 | -29.4785 | -37.1876 | -30.6323 | -28.9455 | -31.0199 | -52.9277 | -29.3382 | -37.6587
461 | -5.9007 | 0 | -4.4085 | 0 | -5.057 | 0 | -4.5843 | 0 | -44.16 | -18.0813 | -29.122 | 0.1852 | -39.5222 | 154.7244 | -36.9236 | 59.8218 | -54.7359 | 54.9338 | -31.6617 | 138.3236 | -59.2855 | -10.1682 | -30.8897 | -96.3712 | -38.5781 | 81.1284 | -36.9107 | -9.1504 | -57.8695 | -104.5088 | -36.4945 | 22.7395 | -9.6026 | 117.8277 | -19.6285 | 10.433 | -24.7656 | 144.7226 | -20.7493 | 108.0392 | -7.8578 | 30.6187 | -18.2602 | -27.3326 | -15.2058 | 36.714 | -17.2962 | 38.3444 | -47.1091 | -35.8083 | -34.2029 | -37.0896 | -49.074 | -33.4958 | -45.9281 | -36.9788 | -34.3616 | -35.1351 | -55.596 | -33.7952 | -42.2838 | 461 | -28.62 | -36.1119 | -26.7588 | -30.9851 | -30.2014 | -36.8511 | -29.0567 | -34.3827 | 461 | -31.0781 | -28.4609 | -31.1889 | -44.6655 | -29.0873 | -40.8711 | -32.5703 | -29.3046 | -32.5053 | -44.017 | -28.9115 | -41.3438 | -29.9076 | -28.3022 | -29.2344 | -51.1875 | -29.3867 | -37.2268 | -31.3998 | -29.1459 | -30.5508 | -50.539 | -29.2109 | -37.6995
462 | -5.762 | 0 | -4.3946 | 0 | -5.1036 | 0 | -4.6218 | 0 | -44.1559 | -26.9157 | -29.4625 | 9.0547 | -43.3469 | 135.5396 | -36.7851 | 48.083 | -55.8022 | 41.7817 | -30.9333 | 125.3183 | -56.5901 | -37.104 | -30.7811 | -82.5198 | -40.844 | 72.1868 | -36.2661 | -23.2052 | -61.6762 | -101.7897 | -36.0585 | 10.9487 | -10.2466 | 104.9258 | -20.3038 | 5.9615 | -22.0542 | 130.5357 | -18.9445 | 94.6602 | -8.3338 | 23.2086 | -19.5704 | -31.5648 | -14.6121 | 32.5568 | -16.166 | 34.3526 | -47.9389 | -36.4214 | -34.2282 | -37.1342 | -49.4506 | -33.4136 | -46.1602 | -38.2013 | -34.5979 | -34.8047 | -53.5469 | -33.713 | -42.9048 | 462 | -29.1491 | -36.0087 | -26.6796 | -30.6777 | -30.3625 | -36.2136 | -28.796 | -34.8037 | 462 | -32.4393 | -28.8359 | -31.3722 | -45.056 | -29.019 | -41.0566 | -33.8067 | -29.4943 | -32.5124 | -44.347 | -28.7918 | -41.5384 | -30.6594 | -28.4662 | -29.0427 | -49.1523 | -29.3184 | -37.8012 | -32.0268 | -29.1246 | -30.1829 | -48.4433 | -29.0912 | -38.283
463 | -5.607 | 0 | -4.373 | 0 | -5.1303 | 0 | -4.6356 | 0 | -44.5542 | -34.9385 | -28.5423 | 15.9406 | -49.7962 | 108.1395 | -36.8689 | 35.1846 | -56.8206 | 34.5872 | -30.6595 | 111.2481 | -54.4727 | -57.4725 | -29.203 | -75.5866 | -43.9864 | 64.6502 | -35.953 | -39.1534 | -64.812 | -58.3938 | -35.8523 | -1.35 | -11.3034 | 93.1076 | -21.4948 | -2.0765 | -20.5363 | 118.9245 | -18.5185 | 82.4224 | -9.1573 | 14.9028 | -21.0626 | -37.4906 | -14.073 | 26.5008 | -15.6102 | 26.0612 | -48.4837 | -36.8347 | -34.1318 | -37.3118 | -49.7571 | -33.3465 | -46.6698 | -39.474 | -34.6891 | -34.6737 | -51.7519 | -33.5873 | -44.0956 | 463 | -28.4032 | -36.1482 | -26.0843 | -30.5965 | -29.0485 | -35.8868 | -27.6568 | -35.2267 | 463 | -33.867 | -29.0821 | -31.7048 | -45.3841 | -28.9735 | -41.5395 | -35.101 | -29.5588 | -32.6762 | -44.6268 | -28.7109 | -42.0342 | -31.2277 | -28.5248 | -29.0667 | -47.3789 | -29.2143 | -38.9653 | -32.4617 | -29.0015 | -30.0381 | -46.6216 | -28.9517 | -39.46
464 | -5.4709 | 0 | -4.3715 | 0 | -5.1386 | 0 | -4.6245 | 0 | -45.4608 | -43.4489 | -26.9962 | 16.8147 | -57.0023 | 2.9962 | -37.1396 | 20.9851 | -56.6678 | 36.1322 | -30.7202 | 98.1977 | -53.3212 | -73.2727 | -27.3577 | -76.2595 | -48.9948 | 70.7226 | -35.9736 | -54.2669 | -58.5174 | -27.8522 | -35.6879 | -12.0499 | -13.3125 | 83.7509 | -22.5049 | -7.9934 | -19.6103 | 104.823 | -18.2888 | 68.335 | -10.1044 | 11.409 | -22.901 | -35.3731 | -13.56 | 20.6458 | -15.3966 | 19.3303 | -48.3064 | -36.9251 | -33.9215 | -37.6423 | -49.7907 | -33.3196 | -47.4769 | -40.5058 | -34.6701 | -34.7543 | -50.1019 | -33.4785 | -46.069 | 464 | -26.9305 | -36.5012 | -25.175 | -30.699 | -27.3171 | -35.8707 | -26.2706 | -35.4681 | 464 | -35.0349 | -29.1992 | -32.1714 | -45.4192 | -28.9481 | -42.3383 | -36.1343 | -29.5315 | -33.0178 | -44.6521 | -28.6951 | -42.8524 | -31.4542 | -28.4506 | -29.2834 | -45.7304 | -29.107 | -40.9304 | -32.5536 | -28.7829 | -30.1298 | -44.9633 | -28.854 | -41.4445
465 | -5.3501 | 0 | -4.3736 | 0 | -5.1157 | 0 | -4.6079 | 0 | -47.4848 | -48.9069 | -25.5369 | 13.0675 | -47.1795 | -59.8269 | -37.6085 | 7.0339 | -54.1634 | 34.1293 | -31.1686 | 85.1024 | -53.4454 | -84.2583 | -25.8102 | -82.8422 | -51.9287 | 113.5818 | -36.4012 | -71.9078 | -53.3081 | -35.6928 | -35.7781 | -24.2726 | -15.5791 | 78.5877 | -23.2389 | -8.9173 | -19.0897 | 90.8049 | -18.4253 | 54.7473 | -11.4525 | 6.6516 | -24.9095 | -26.9183 | -13.8594 | 10.0164 | -15.6987 | 10.1421 | -46.9686 | -36.5858 | -33.6835 | -38.1366 | -49.4178 | -33.4374 | -48.7759 | -40.7329 | -34.5845 | -35.0181 | -48.4126 | -33.3618 | -46.5033 | 465 | -25.4798 | -37.097 | -24.2805 | -31.0399 | -25.7921 | -36.2303 | -25.062 | -35.5997 | 465 | -35.3828 | -29.2344 | -32.7865 | -45.0442 | -29.0638 | -43.6602 | -36.3593 | -29.4688 | -33.5287 | -44.3021 | -28.8295 | -44.168 | -31.2357 | -28.3334 | -29.668 | -44.039 | -28.9882 | -41.3876 | -32.2122 | -28.5678 | -30.4102 | -43.2969 | -28.7539 | -41.8954
466 | -5.3048 | 0 | -4.3811 | 0 | -5.108 | 0 | -4.5957 | 0 | -51.0793 | -38.659 | -24.4141 | 3.6617 | -42.0644 | -82.1929 | -38.3329 | -10.101 | -51.0279 | 13.3451 | -32.1003 | 73.3437 | -54.6354 | -80.5319 | -24.7116 | -92.3105 | -47.779 | 145.3493 | -37.3634 | -90.0576 | -49.8468 | -53.9801 | -36.1873 | -36.7323 | -18.3005 | 86.1427 | -23.733 | -7.7885 | -18.6118 | 76.4676 | -19.1936 | 43.1768 | -12.4997 | 12.6233 | -25.5161 | -23.5186 | -14.2376 | 2.0273 | -16.396 | 2.8034 | -44.73 | -35.8007 | -33.3568 | -38.8745 | -48.9644 | -33.6757 | -51.2522 | -40.0064 | -34.3634 | -35.4592 | -46.8186 | -33.2252 | -41.8159 | 466 | -24.3309 | -37.8918 | -23.5829 | -31.6329 | -24.6858 | -37.0485 | -24.1982 | -35.7248 | 466 | -34.7016 | -29.0586 | -33.5697 | -44.5833 | -29.2946 | -46.1442 | -35.6253 | -29.2554 | -34.2788 | -43.8564 | -29.08 | -46.6565 | -30.4959 | -28.052 | -30.1544 | -42.4375 | -28.8441 | -36.7079 | -31.4196 | -28.2488 | -30.8635 | -41.7106 | -28.6295 | -37.2202
467 | -5.3397 | 0 | -4.4125 | 0 | -5.0764 | 0 | -4.6 | 0 | -49.0053 | -3.9218 | -23.8006 | -7.0298 | -38.5602 | -99.6416 | -39.6729 | -30.1162 | -49.7582 | -24.1629 | -33.262 | 64.2286 | -51.721 | -65.108 | -24.1064 | -103.1522 | -42.4502 | 150.1161 | -38.9904 | -110.0403 | -48.3524 | -81.2755 | -36.7822 | -52.0376 | -18.2082 | 106.3386 | -24.2143 | -10.9068 | -18.9249 | 65.1323 | -20.6585 | 34.6481 | -12.9215 | 17.4695 | -25.7112 | -14.3813 | -15.2111 | -7.943 | -17.5637 | -2.1731 | -42.7906 | -34.8345 | -32.7862 | -40.0422 | -49.5383 | -33.9132 | -54.2366 | -39.0775 | -33.6222 | -36.0876 | -45.9868 | -33.1526 | -38.4824 | 467 | -23.6452 | -38.8283 | -23.2351 | -32.064 | -24.0359 | -38.3117 | -23.7462 | -35.5085 | 467 | -33.7378 | -28.2825 | -34.7025 | -45.1258 | -29.5007 | -49.1602 | -34.665 | -28.5458 | -35.4422 | -44.4619 | -29.3132 | -49.6366 | -29.4948 | -27.4465 | -30.7479 | -41.5743 | -28.7401 | -33.406 | -30.422 | -27.7098 | -31.4876 | -40.9104 | -28.5526 | -33.8824
468 | -5.4201 | 0 | -4.4376 | 0 | -5.0469 | 0 | -4.581 | 0 | -44.5712 | 3.1727 | -23.573 | -18.6053 | -35.9297 | -120.8607 | -41.7528 | -53.7382 | -50.3169 | -69.8628 | -34.7766 | 55.1667 | -48.0448 | -67.9539 | -23.8019 | -114.5863 | -38.7785 | 138.5134 | -41.1449 | -131.2113 | -48.8098 | -110.0102 | -38.2738 | -68.7209 | -16.136 | 120.9223 | -24.9831 | -20.9219 | -19.8213 | 55.5813 | -22.8285 | 29.2633 | -12.2005 | 24.1799 | -25.4818 | -0.677 | -16.3788 | -13.5855 | -19.0233 | -2.8316 | -41.8969 | -34.0711 | -32.2649 | -41.3087 | -51.7742 | -34.042 | -52.7945 | -38.3109 | -32.8308 | -36.8882 | -46.2805 | -33.3202 | -37.839 | 468 | -23.2952 | -39.5471 | -23.1947 | -32.2366 | -23.6502 | -39.7607 | -23.5729 | -35.3101 | 468 | -32.8908 | -27.4107 | -35.8886 | -47.3366 | -29.6044 | -47.7476 | -33.8733 | -27.7839 | -36.7277 | -46.7273 | -29.461 | -48.2135 | -28.651 | -26.8448 | -31.4681 | -41.8429 | -28.8826 | -32.7921 | -29.6335 | -27.218 | -32.3072 | -41.2336 | -28.7392 | -33.258
469 | -5.5496 | 0 | -4.4558 | 0 | -5.0223 | 0 | -4.5613 | 0 | -41.7722 | -10.6955 | -23.6394 | -28.7831 | -34.4151 | -143.0745 | -44.6183 | -80.2514 | -52.6451 | -123.0388 | -36.8908 | 49.2849 | -45.8306 | -84.4978 | -23.7732 | -126.759 | -36.2439 | 121.6968 | -43.8823 | -157.6684 | -51.2619 | -134.8754 | -40.7265 | -85.8048 | -13.5455 | 122.6465 | -26.0775 | -29.4551 | -20.4411 | 49.2906 | -25.1255 | 33.2261 | -10.785 | 28.055 | -24.4524 | 15.7438 | -17.8833 | -13.3919 | -20.7521 | 3.5214 | -41.9688 | -33.6211 | -32.0625 | -42.3594 | -56.5078 | -34.25 | -49.0457 | -37.6863 | -32.3035 | -37.6043 | -47.6004 | -33.784 | -38.4846 | 469 | -23.2294 | -39.7281 | -23.4057 | -32.4271 | -23.5085 | -41.2784 | -23.6452 | -34.8209 | 469 | -32.1367 | -26.7539 | -36.8098 | -52.052 | -29.7942 | -44.0234 | -33.2305 | -27.2812 | -37.7981 | -51.4855 | -29.6887 | -44.4844 | -28.0715 | -26.5129 | -32.0547 | -43.1446 | -29.3282 | -33.4623 | -29.1653 | -27.0402 | -33.043 | -42.5781 | -29.2227 | -33.9233
470 | -5.7205 | 0 | -4.4572 | 0 | -5.0477 | 0 | -4.5348 | 0 | -40.8936 | -27.4203 | -23.9967 | -39.6265 | -33.7786 | -164.369 | -47.4147 | -117.2596 | -54.6392 | 173.402 | -39.9131 | 50.5098 | -45.3025 | -98.852 | -24.1851 | -139.3546 | -35.0618 | 101.3736 | -46.675 | 157.9014 | -55.6956 | -149.3204 | -45.7204 | -104.246 | -11.4564 | 116.125 | -28.567 | -34.1778 | -21.7238 | 47.4515 | -27.9374 | 51.3678 | -9.5222 | 24.0221 | -23.5687 | 16.3711 | -19.8054 | -12.8113 | -21.7046 | 14.8252 | -42.7592 | -33.377 | -32.3388 | -42.9232 | -63.7865 | -34.7325 | -46.9885 | -37.1727 | -32.3103 | -37.7814 | -49.1799 | -34.4227 | -37.7954 | 470 | -23.4829 | -39.8727 | -23.8677 | -32.8035 | -23.813 | -42.7009 | -24.1305 | -34.6694 | 470 | -31.4522 | -26.5898 | -37.2027 | -59.3293 | -30.2753 | -41.9408 | -32.7155 | -27.2626 | -38.3884 | -58.7388 | -30.1977 | -42.4537 | -27.6565 | -26.6183 | -32.0609 | -44.7227 | -29.9655 | -32.7477 | -28.9198 | -27.2911 | -33.2466 | -44.1322 | -29.8879 | -33.2606
471 | -5.9015 | 0 | -4.4584 | 0 | -5.0747 | 0 | -4.5368 | 0 | -40.9988 | -41.0121 | -24.6196 | -49.1397 | -33.8195 | 176.444 | -47.9235 | -165.524 | -53.5801 | 119.0066 | -42.4294 | 68.6149 | -45.5085 | -107.9405 | -24.9541 | -150.5123 | -34.4997 | 83.961 | -46.4605 | 102.9166 | -64.175 | -144.6995 | -58.5595 | -130.0506 | -9.6751 | 105.4891 | -33.2997 | -18.1478 | -21.0238 | 50.7988 | -24.2781 | 72.1865 | -8.5911 | 15.1855 | -22.5738 | 17.4776 | -21.3099 | -10.5781 | -21.1284 | 27.4018 | -43.7603 | -33.2868 | -32.8246 | -43.1861 | -63.2135 | -35.2165 | -45.8373 | -36.8911 | -32.5499 | -37.6537 | -50.7201 | -35.1059 | -35.7287 | 471 | -24.0382 | -40.0013 | -24.5284 | -33.219 | -24.4626 | -42.9155 | -24.9216 | -34.478 | 471 | -30.9896 | -26.6484 | -37.2846 | -58.7551 | -30.7581 | -40.7626 | -32.4327 | -27.4752 | -38.6493 | -58.1388 | -30.6797 | -41.3005 | -27.3853 | -26.9231 | -31.7522 | -46.2617 | -30.6475 | -30.654 | -28.8284 | -27.7499 | -33.1169 | -45.6454 | -30.5691 | -31.1919
472 | -6.07 | 0 | -4.466 | 0 | -5.1465 | 0 | -4.5614 | 0 | -41.7516 | -51.9494 | -25.5451 | -59.3296 | -34.2737 | 158.0773 | -45.6333 | 150.1151 | -51.4865 | 83.5513 | -41.652 | 94.2035 | -46.173 | -111.2321 | -26.0948 | -160.6077 | -34.2216 | 68.5239 | -43.4483 | 64.4787 | -62.1425 | -48.0997 | -50.8995 | 56.6474 | -9.0942 | 95.6072 | -40.6422 | -60.7182 | -22.3416 | 50.2267 | -23.5345 | 77.8167 | -7.756 | 11.3012 | -21.2466 | 23.683 | -21.0323 | 13.1072 | -19.6199 | 34.7688 | -44.768 | -33.3469 | -33.3837 | -42.9672 | -59.1039 | -35.6203 | -45.091 | -36.9864 | -32.9763 | -37.1106 | -52.2551 | -35.9668 | -33.6718 | 472 | -24.9082 | -39.9463 | -25.3986 | -33.4751 | -25.4362 | -41.552 | -26.0016 | -34.1224 | 472 | -30.9164 | -26.9063 | -36.8972 | -54.6379 | -31.1543 | -39.9445 | -32.5204 | -27.8298 | -38.4058 | -53.9574 | -31.0589 | -40.5296 | -27.2769 | -27.3137 | -31.0406 | -47.7891 | -31.5008 | -28.5253 | -28.8809 | -28.2372 | -32.5492 | -47.1086 | -31.4054 | -29.1104
473 | -6.2061 | 0 | -4.4678 | 0 | -5.2334 | 0 | -4.5732 | 0 | -42.9027 | -58.716 | -26.7131 | -66.4865 | -34.974 | 142.8356 | -43.2131 | 118.0911 | -49.3914 | 61.9904 | -38.5001 | 106.1629 | -46.3342 | -107.2006 | -27.6355 | -168.6914 | -34.1895 | 51.4886 | -40.5138 | 37.2202 | -54.5524 | -49.6743 | -43.547 | 37.6026 | -8.1722 | 84.9709 | -38.7739 | 103.7534 | -20.8101 | 50.8166 | -20.1134 | 71.9455 | -7.4558 | -0.2723 | -20.1862 | 17.6573 | -20.4135 | 12.0944 | -18.3307 | 30.4816 | -45.7814 | -33.4572 | -34.0119 | -42.1369 | -56.9767 | -36.1173 | -44.5537 | -37.2529 | -33.5381 | -36.1709 | -52.4209 | -36.6553 | -32.1026 | 473 | -26.019 | -39.5673 | -26.3442 | -33.2709 | -26.7202 | -39.3702 | -27.3126 | -33.6774 | 473 | -31.0468 | -27.332 | -35.9308 | -52.5089 | -31.6495 | -39.3203 | -32.7851 | -28.3047 | -37.5637 | -51.7433 | -31.5441 | -39.9805 | -27.2511 | -27.8058 | -29.9648 | -47.9531 | -32.1875 | -26.8692 | -28.9894 | -28.7785 | -31.5977 | -47.1875 | -32.0821 | -27.5294
474 | -6.2854 | 0 | -4.4818 | 0 | -5.3409 | 0 | -4.6161 | 0 | -44.3529 | -59.7203 | -28.1044 | -72.2503 | -35.8844 | 128.9123 | -41.5527 | 92.8315 | -47.4186 | 44.8773 | -35.574 | 102.9909 | -45.2306 | -100.2945 | -29.5803 | -173.3252 | -34.437 | 35.931 | -38.2578 | 19.0869 | -50.7842 | -62.0786 | -39.9868 | 22.3834 | -7.8136 | 74.5324 | -31.214 | 106.9559 | -20.7161 | 45.4845 | -19.004 | 63.2399 | -7.3233 | -7.8323 | -19.0463 | 16.6169 | -18.8857 | 17.0903 | -17.2753 | 28.7145 | -46.7836 | -33.5178 | -34.56 | -40.9399 | -55.6157 | -36.3186 | -44.1927 | -37.5597 | -34.1409 | -35.2435 | -50.9661 | -36.8565 | -31.0579 | 474 | -27.3473 | -39.0391 | -27.2256 | -32.5715 | -28.2639 | -37.2656 | -28.6931 | -33.2915 | 474 | -31.2743 | -27.8555 | -34.6545 | -51.1339 | -31.8368 | -38.8518 | -33.0779 | -28.8 | -36.3238 | -50.2748 | -31.7025 | -39.5766 | -27.2324 | -28.2746 | -28.9581 | -46.4843 | -32.3747 | -25.717 | -29.036 | -29.2191 | -30.6274 | -45.6252 | -32.2404 | -26.4418
475 | -6.2919 | 0 | -4.4964 | 0 | -5.4602 | 0 | -4.6568 | 0 | -45.642 | -55.3105 | -29.6825 | -75.2836 | -37.1304 | 115.6804 | -40.6399 | 71.7386 | -45.5171 | 28.4446 | -33.5336 | 92.539 | -43.3688 | -99.3047 | -31.7552 | -172.3524 | -34.8864 | 21.5359 | -36.6021 | 1.0688 | -48.3042 | -76.5392 | -38.0183 | 8.9418 | -7.6247 | 64.6929 | -28.7313 | 103.6712 | -20.4405 | 40.3516 | -18.2286 | 53.3319 | -7.3825 | -19.1532 | -18.1177 | 15.4926 | -18.1753 | 11.5876 | -16.7006 | 24.4338 | -47.6889 | -33.6019 | -35 | -39.7436 | -54.56 | -36.0863 | -44.0745 | -37.9016 | -34.6903 | -34.5862 | -49.0511 | -36.5305 | -30.4703 | 475 | -28.8714 | -38.4878 | -27.9442 | -31.7722 | -29.8372 | -35.5364 | -29.8128 | -33.0346 | 475 | -31.6097 | -28.3984 | -33.4517 | -50.0636 | -31.5899 | -38.6143 | -33.4052 | -29.2301 | -35.0868 | -49.0998 | -31.4295 | -39.4177 | -27.31 | -28.7081 | -28.2943 | -44.5547 | -32.0341 | -25.0101 | -29.1055 | -29.5398 | -29.9294 | -43.5909 | -31.8737 | -25.8135
476 | -6.2122 | 0 | -4.5307 | 0 | -5.57 | 0 | -4.7002 | 0 | -46.0099 | -43.4536 | -31.2787 | -72.7301 | -38.7285 | 105.4234 | -40.3287 | 52.8548 | -43.7102 | 10.895 | -32.3913 | 79.9751 | -41.4606 | -103.0944 | -33.4712 | -162.5983 | -35.3483 | 6.1899 | -35.4156 | -15.6774 | -46.4646 | -91.3935 | -36.7546 | -2.9863 | -7.8685 | 54.013 | -24.6623 | 90.644 | -20.965 | 34.4694 | -18.2432 | 42.3627 | -7.6682 | -29.2843 | -17.3648 | 4.8792 | -17.9069 | 2.4838 | -16.5062 | 17.4478 | -48.4185 | -33.7703 | -35.2172 | -38.6958 | -53.6724 | -35.4656 | -44.0033 | -38.1754 | -35.1068 | -34.1518 | -47.3471 | -35.7926 | -30.2403 | 476 | -30.4382 | -37.9498 | -28.4947 | -31.2311 | -30.8993 | -34.1864 | -30.2312 | -32.7938 | 476 | -31.9632 | -28.8946 | -32.4836 | -49.1417 | -30.9349 | -38.4333 | -33.6447 | -29.5368 | -33.9956 | -48.1024 | -30.7654 | -39.3031 | -27.5581 | -29.005 | -27.9396 | -42.8164 | -31.2619 | -24.6703 | -29.2396 | -29.6472 | -29.4516 | -41.7771 | -31.0924 | -25.5401
477 | -6.0774 | 0 | -4.5383 | 0 | -5.6438 | 0 | -4.7375 | 0 | -44.7499 | -31.5546 | -32.3476 | -65.6139 | -40.3913 | 99.0567 | -40.506 | 36.425 | -42.3123 | -8.0352 | -31.9529 | 67.8257 | -39.7597 | -109.7747 | -33.6628 | -149.958 | -35.9037 | -9.4307 | -34.6278 | -31.6797 | -45.1415 | -109.5837 | -35.6735 | -12.9928 | -8.1473 | 45.5417 | -22.171 | 81.3277 | -21.055 | 32.8803 | -18.6263 | 33.6154 | -8.3912 | -38.0215 | -16.7981 | -3.1907 | -18.1045 | -7.381 | -16.6359 | 11.9727 | -48.8362 | -33.9768 | -35.2347 | -37.8558 | -52.8479 | -34.6917 | -43.9055 | -38.3703 | -35.4328 | -33.9602 | -46.0032 | -34.9133 | -30.2908 | 477 | -31.5039 | -37.418 | -28.8297 | -31.0351 | -31.0086 | -33.1802 | -29.8065 | -32.5319 | 477 | -32.2929 | -29.3554 | -31.7784 | -48.3096 | -30.1534 | -38.2617 | -33.832 | -29.789 | -33.1183 | -47.2041 | -29.9542 | -39.168 | -27.8994 | -29.1573 | -27.8828 | -41.4649 | -30.375 | -24.647 | -29.4385 | -29.5909 | -29.2227 | -40.3594 | -30.1758 | -25.5533
478 | -5.9044 | 0 | -4.5493 | 0 | -5.6539 | 0 | -4.7687 | 0 | -42.6009 | -27.7702 | -32.2556 | -57.9658 | -42.0422 | 94.0902 | -40.9738 | 21.5978 | -41.4598 | -28.9315 | -31.9093 | 56.7753 | -38.3268 | -118.6005 | -32.4541 | -141.4441 | -36.7993 | -25.5474 | -34.2148 | -45.5818 | -44.3116 | -128.5412 | -34.7689 | -23.9402 | -8.8933 | 36.631 | -21.6239 | 72.6162 | -21.8252 | 30.5563 | -20.2612 | 23.2456 | -9.4128 | -48.0062 | -16.7933 | -6.1948 | -19.0006 | -14.3732 | -17.1155 | 9.5469 | -49.0151 | -34.1627 | -35.0577 | -37.2339 | -52.1753 | -33.9361 | -43.9047 | -38.4859 | -35.6348 | -33.9829 | -45.0258 | -34.0562 | -30.5354 | 478 | -31.4732 | -36.8548 | -28.7973 | -31.089 | -30.342 | -32.4953 | -28.9254 | -32.3693 | 478 | -32.5815 | -29.7304 | -31.3295 | -47.626 | -29.3868 | -38.2508 | -33.9366 | -29.9809 | -32.4652 | -46.5214 | -29.1674 | -39.136 | -28.2583 | -29.1533 | -28.0785 | -40.4765 | -29.5069 | -24.8815 | -29.6134 | -29.4038 | -29.2142 | -39.3719 | -29.2875 | -25.7667
479 | -5.6931 | 0 | -4.5807 | 0 | -5.6561 | 0 | -4.7917 | 0 | -40.4638 | -30.1095 | -31.3361 | -53.1331 | -43.8475 | 94.9037 | -41.7064 | 7.7477 | -41.2105 | -49.1912 | -32.0801 | 47.3151 | -37.1525 | -128.0318 | -30.9351 | -141.3244 | -38.0945 | -42.2192 | -34.1578 | -61.864 | -44.1008 | -148.0755 | -34.2091 | -35.491 | -9.742 | 31.0339 | -20.2739 | 65.8455 | -22.0396 | 31.9973 | -21.7828 | 22.2004 | -10.7925 | -56.9723 | -16.6641 | -16.9898 | -20.4478 | -23.8061 | -17.6577 | 6.39 | -49.0114 | -34.2821 | -34.7527 | -36.8278 | -51.691 | -33.2235 | -43.8776 | -38.5819 | -35.7048 | -34.2369 | -44.5533 | -33.3514 | -30.9753 | 479 | -30.6234 | -36.3254 | -28.4707 | -31.3292 | -29.3779 | -32.1081 | -28.0422 | -32.4157 | 479 | -32.8888 | -30.0117 | -31.1347 | -47.1103 | -28.6428 | -38.2215 | -34.0012 | -30.0487 | -32.0361 | -46.0349 | -28.4318 | -39.0859 | -28.589 | -29.0596 | -28.5438 | -39.9726 | -28.7707 | -25.3192 | -29.7014 | -29.0966 | -29.4452 | -38.8972 | -28.5597 | -26.1836
480 | -5.513 | 0 | -4.588 | 0 | -5.6313 | 0 | -4.8088 | 0 | -38.6489 | -37.8052 | -30.2796 | -55.4462 | -44.9396 | 102.9341 | -42.5184 | -6.1545 | -41.5837 | -70.6595 | -32.4523 | 38.7579 | -36.2082 | -138.6888 | -29.6609 | -145.7121 | -39.7557 | -57.8559 | -34.4589 | -76.2102 | -44.5058 | -169.4048 | -33.9289 | -46.6832 | -10.9616 | 26.9049 | -20.2819 | 58.2696 | -23.5023 | 27.279 | -24.552 | 24.5136 | -12.9196 | -60.9064 | -17.2927 | -21.3576 | -23.1227 | -22.6045 | -18.2983 | 6.9673 | -49.0187 | -34.2338 | -34.3616 | -36.6476 | -51.5343 | -32.5033 | -43.8029 | -38.5571 | -35.6771 | -34.6896 | -44.5021 | -32.7836 | -31.5952 | 480 | -29.5616 | -35.8181 | -28.0626 | -31.7389 | -28.4575 | -31.9856 | -27.3422 | -32.6289 | 480 | -33.0441 | -30.1641 | -31.1346 | -46.9463 | -27.9153 | -38.1716 | -33.9691 | -30.0458 | -31.8388 | -45.903 | -27.6945 | -38.9941 | -28.7208 | -28.8486 | -29.1766 | -39.9141 | -28.1956 | -25.9639 | -29.6458 | -28.7303 | -29.8808 | -38.8708 | -27.9748 | -26.7864
481 | -5.3745 | 0 | -4.5971 | 0 | -5.5854 | 0 | -4.808 | 0 | -37.2772 | -48.7665 | -29.5498 | -61.8478 | -44.5169 | 108.3069 | -43.3628 | -23.7082 | -42.7656 | -90.9899 | -32.7869 | 31.2142 | -35.5003 | -149.3362 | -28.7828 | -153.5153 | -42.0056 | -75.1918 | -35.1309 | -89.8226 | -45.7777 | 170.0282 | -33.7509 | -57.7798 | -12.1853 | 27.4986 | -20.2339 | 53.6624 | -23.6251 | 35.4271 | -26.1362 | 44.1619 | -15.3669 | -56.589 | -17.9526 | -26.8251 | -26.3113 | -19.9936 | -18.731 | 10.6635 | -49.1801 | -34.0238 | -33.9379 | -36.7621 | -51.8832 | -31.8481 | -43.7885 | -38.4643 | -35.5229 | -35.3705 | -44.9174 | -32.2768 | -32.3931 | 481 | -28.7557 | -35.4335 | -27.7425 | -32.1138 | -27.7772 | -32.1106 | -26.8784 | -32.9153 | 481 | -33.0898 | -30.1484 | -31.3876 | -47.2861 | -27.251 | -38.2031 | -33.8672 | -29.9375 | -31.9541 | -46.2978 | -27.0401 | -38.9805 | -28.6493 | -28.5634 | -29.996 | -40.3203 | -27.6797 | -26.8077 | -29.4267 | -28.3525 | -30.5625 | -39.332 | -27.4688 | -27.5851
482 | -5.3023 | 0 | -4.5907 | 0 | -5.5359 | 0 | -4.7868 | 0 | -36.4158 | -60.2337 | -29.2276 | -69.5996 | -43.5942 | 110.0976 | -44.4159 | -46.0302 | -45.0524 | -109.5294 | -33.0495 | 22.7426 | -35.0172 | -160.5115 | -28.3064 | -162.2693 | -45.9065 | -94.7209 | -36.2816 | -103.8607 | -47.9808 | 149.4381 | -33.8386 | -70.3327 | -12.8778 | 32.9729 | -20.4119 | 52.4868 | -23.9079 | 42.2161 | -24.3731 | 66.1114 | -16.713 | -40.6337 | -19.0879 | -28.0344 | -28.4417 | 12.6356 | -18.6922 | 14.7521 | -49.6072 | -33.7478 | -33.6196 | -37.1189 | -53.0174 | -31.3376 | -43.8758 | -38.4734 | -35.275 | -36.2703 | -45.7 | -31.9344 | -33.461 | 482 | -28.3368 | -35.2919 | -27.6288 | -32.4377 | -27.4051 | -32.4694 | -26.7253 | -33.4221 | 482 | -33.1711 | -29.9727 | -31.8166 | -48.4267 | -26.7469 | -38.3399 | -33.8827 | -29.7391 | -32.3321 | -47.4815 | -26.5508 | -39.089 | -28.4455 | -28.3173 | -30.968 | -41.1093 | -27.3437 | -27.9251 | -29.1571 | -28.0837 | -31.4835 | -40.1641 | -27.1476 | -28.6742
483 | -5.3167 | 0 | -4.6245 | 0 | -5.4655 | 0 | -4.7616 | 0 | -36.0417 | -72.0709 | -29.4254 | -78.7117 | -42.6802 | 106.7652 | -45.7029 | -80.197 | -48.7241 | -118.8921 | -33.3939 | 14.0998 | -34.8126 | -171.8912 | -28.2042 | -172.9436 | -54.0812 | -99.9642 | -38.2113 | -117.102 | -51.5279 | 128.8279 | -34.6211 | -83.5023 | -12.454 | 41.3113 | -21.0075 | 52.2489 | -22.8219 | 51.762 | -21.3969 | 73.9781 | -15.5158 | -24.7067 | -20.6175 | -21.0311 | -24.8374 | 44.7481 | -18.1085 | 18.1908 | -50.1137 | -33.525 | -33.3996 | -37.5317 | -55.0864 | -30.9507 | -44.0035 | -38.7428 | -35.0276 | -37.398 | -46.7066 | -31.7936 | -34.6719 | 483 | -28.4037 | -35.3895 | -27.8886 | -32.7976 | -27.3373 | -33.1143 | -26.9721 | -34.4855 | 483 | -33.4261 | -29.7109 | -32.215 | -50.4619 | -26.3262 | -38.538 | -34.1183 | -29.5621 | -32.7701 | -49.6209 | -26.1891 | -39.2419 | -28.2083 | -28.0829 | -32.0813 | -42.0821 | -27.1691 | -29.2064 | -28.9005 | -27.9341 | -32.6364 | -41.2411 | -27.032 | -29.9103
484 | -5.4105 | 0 | -4.6484 | 0 | -5.4325 | 0 | -4.7373 | 0 | -36.0614 | -83.1469 | -30.1754 | -86.8588 | -41.7634 | 101.0176 | -46.0471 | -127.6656 | -52.3544 | -108.3742 | -34.1932 | 2.3829 | -34.9148 | 177.1969 | -28.4566 | 177.5031 | -56.7604 | -7.6672 | -41.5058 | -129.348 | -58.0878 | 104.8073 | -36.1723 | -93.8951 | -11.6022 | 43.5284 | -20.5418 | 59.1876 | -21.1227 | 55.7286 | -19.4335 | 71.7165 | -13.4413 | -20.4137 | -21.1148 | -11.2642 | -21.3991 | 49.4266 | -17.2916 | 19.4151 | -50.0789 | -33.4334 | -33.3293 | -37.8016 | -57.1297 | -30.7654 | -44.1367 | -39.4286 | -34.805 | -38.4687 | -47.7538 | -31.9833 | -35.979 | 484 | -28.9459 | -35.5545 | -28.6453 | -33.4368 | -27.5663 | -34.0368 | -27.5974 | -36.1069 | 484 | -34.0181 | -29.3945 | -32.3911 | -52.4813 | -26.117 | -38.7042 | -34.7802 | -29.3725 | -33.0643 | -51.6972 | -26.0281 | -39.3994 | -28.0229 | -27.9188 | -33.0582 | -43.1054 | -27.3349 | -30.5465 | -28.785 | -27.8968 | -33.7314 | -42.3213 | -27.246 | -31.2417
485 | -5.5387 | 0 | -4.7028 | 0 | -5.4215 | 0 | -4.7379 | 0 | -36.3276 | -92.2826 | -31.2905 | -92.17 | -41.2548 | 91.2813 | -44.4083 | -172.8534 | -53.1608 | -92.5116 | -35.7664 | -8.924 | -35.3987 | 166.2759 | -29.0703 | 166.7425 | -49.3609 | -2.4537 | -47.9995 | -131.6833 | -68.6493 | -29.8564 | -38.143 | -99.4581 | -10.3299 | 43.2753 | -20.3159 | 63.4987 | -19.3902 | 53.611 | -17.7775 | 65.3126 | -11.7476 | -26.0032 | -20.2762 | -1.4163 | -19.2101 | 46.228 | -16.566 | 19.1636 | -49.1919 | -33.5982 | -33.3169 | -37.7857 | -55.4224 | -30.8482 | -44.3551 | -40.4723 | -34.6637 | -39.027 | -48.3395 | -32.4528 | -36.7572 | 485 | -29.7849 | -35.6224 | -29.812 | -34.6243 | -28.1282 | -35.1645 | -28.5142 | -37.8231 | 485 | -34.9336 | -29.125 | -32.247 | -50.7196 | -26.1454 | -38.9336 | -35.7695 | -29.2422 | -33.0478 | -50.0009 | -26.1103 | -39.6172 | -28.0595 | -27.7782 | -33.4883 | -43.6367 | -27.75 | -31.3357 | -28.8954 | -27.8954 | -34.2891 | -42.918 | -27.7149 | -32.0193
486 | -5.7 | 0 | -4.7521 | 0 | -5.4436 | 0 | -4.7146 | 0 | -36.7236 | -100.8272 | -32.4056 | -94.004 | -41.2007 | 83.9119 | -41.8611 | 154.3844 | -53.612 | -82.5631 | -38.6055 | -20.3176 | -36.2377 | 157.1122 | -30.091 | 155.7526 | -45.9574 | -11.9955 | -53.5933 | -32.7816 | -55.2913 | -87.7585 | -40.2168 | -98.8522 | -9.5229 | 37.3214 | -19.5642 | 67.0227 | -18.5379 | 44.4578 | -16.9302 | 56.6096 | -10.4121 | -36.0242 | -18.2985 | 0.4375 | -18.8745 | 26.8545 | -15.9657 | 13.5028 | -47.7022 | -33.9522 | -33.3726 | -37.6709 | -51.417 | -31.2569 | -44.7209 | -41.9084 | -34.5789 | -38.6779 | -47.5881 | -33.135 | -35.6505 | 486 | -30.639 | -35.4954 | -31.0918 | -36.6142 | -29.0572 | -36.1059 | -29.6707 | -39.0849 | 486 | -36.2084 | -28.8789 | -31.9709 | -46.6649 | -26.5048 | -39.2773 | -37.1563 | -29.1353 | -32.9563 | -45.9734 | -26.5423 | -40.0063 | -28.2522 | -27.6726 | -32.9779 | -42.836 | -28.3829 | -30.2069 | -29.2001 | -27.929 | -33.9633 | -42.1445 | -28.4204 | -30.9359
487 | -5.8292 | 0 | -4.8494 | 0 | -5.4816 | 0 | -4.7326 | 0 | -37.1238 | -108.2663 | -33.2171 | -93.5169 | -40.9263 | 78.2434 | -39.5698 | 128.9965 | -54.3048 | -59.9083 | -44.3203 | -21.7774 | -37.3743 | 151.8015 | -31.7337 | 146.2082 | -43.6618 | -24.8149 | -42.4468 | -14.9582 | -50.4161 | -108.9464 | -42.0036 | -90.4125 | -8.6567 | 33.0646 | -17.5077 | 70.756 | -17.6336 | 37.1509 | -16.3632 | 47.974 | -9.9222 | -46.0881 | -16.6668 | 2.1955 | -18.1421 | 25.1482 | -15.774 | 8.3199 | -46.3501 | -34.4356 | -33.4081 | -37.8033 | -48.0923 | -32.0371 | -45.3259 | -43.5559 | -34.4386 | -37.5759 | -45.7595 | -33.7941 | -32.4426 | 487 | -31.2409 | -35.1139 | -32.0472 | -39.1548 | -30.4724 | -36.0369 | -31.0192 | -39.3868 | 487 | -37.7267 | -28.6094 | -31.9741 | -43.2429 | -27.1877 | -39.8443 | -38.7065 | -28.957 | -33.0707 | -42.6107 | -27.3045 | -40.5933 | -28.6064 | -27.5789 | -31.7467 | -40.9101 | -28.9447 | -26.961 | -29.5862 | -27.9265 | -32.8433 | -40.2779 | -29.0615 | -27.71
488 | -5.9272 | 0 | -4.9336 | 0 | -5.5667 | 0 | -4.724 | 0 | -37.7492 | -115.7548 | -33.755 | -93.0424 | -40.5026 | 68.3972 | -37.7252 | 107.1755 | -49.6549 | -35.2464 | -47.6199 | 43.1115 | -38.3833 | 149.6083 | -34.341 | 138.4125 | -41.9728 | -39.6396 | -37.1898 | -28.6899 | -47.4862 | -123.7198 | -42.9722 | -76.3934 | -8.2232 | 25.3572 | -15.9596 | 68.4558 | -17.6978 | 26.7897 | -16.5941 | 38.6103 | -9.3865 | -59.0928 | -15.0962 | -2.9188 | -18.4876 | 14.4461 | -15.8978 | 3.0551 | -45.8484 | -34.8604 | -33.3772 | -38.0749 | -46.0242 | -33.2393 | -45.539 | -45.051 | -34.2553 | -36.2265 | -44.1367 | -34.2581 | -30.0941 | 488 | -31.6865 | -34.5894 | -32.1656 | -39.3108 | -32.391 | -34.5108 | -32.1504 | -38.8018 | 488 | -39.1238 | -28.3281 | -32.1477 | -41.0906 | -28.3057 | -39.9723 | -40.1174 | -28.6886 | -33.3509 | -40.4575 | -28.5153 | -40.815 | -28.9332 | -27.45 | -30.2993 | -39.2031 | -29.3245 | -24.5274 | -29.9268 | -27.8105 | -31.5025 | -38.57 | -29.5341 | -25.3701
489 | -5.9725 | 0 | -5.0233 | 0 | -5.6795 | 0 | -4.7381 | 0 | -39.0647 | -122.4208 | -34.3251 | -92.2612 | -40.7611 | 57.5719 | -36.4738 | 88.2926 | -44.7002 | -42.0358 | -41.0581 | 60.7217 | -39.2222 | 149.1471 | -37.996 | 140.2566 | -40.7855 | -54.8959 | -34.3225 | -44.9477 | -44.7636 | -138.4618 | -42.4877 | -55.8933 | -7.9389 | 18.2229 | -14.2958 | 64.272 | -18.476 | 16.6095 | -17.2327 | 31.57 | -9.428 | -71.3795 | -14.0565 | -7.9466 | -19.1991 | 6.0354 | -16.3282 | -0.5601 | -46.0748 | -34.9185 | -33.4928 | -37.5982 | -44.5826 | -34.4693 | -45.0233 | -46.8241 | -34.1952 | -35.3124 | -42.8709 | -34.6522 | -29.5275 | 489 | -32.3856 | -34.1664 | -31.7199 | -37.0733 | -34.4165 | -32.8181 | -32.3311 | -37.6135 | 489 | -40.8516 | -28.2227 | -31.6257 | -39.5593 | -29.446 | -39.3438 | -41.8008 | -28.5157 | -32.8601 | -38.9031 | -29.7312 | -40.2852 | -28.946 | -27.5203 | -29.3399 | -37.8476 | -29.6289 | -23.848 | -29.8952 | -27.8133 | -30.5743 | -37.1914 | -29.9141 | -24.7894
490 | -5.9686 | 0 | -5.1186 | 0 | -5.8114 | 0 | -4.767 | 0 | -40.8595 | -122.181 | -34.9017 | -90.495 | -41.533 | 49.5839 | -35.7896 | 70.4051 | -41.6156 | -58.756 | -37.8257 | 54.5622 | -40.025 | 152.6817 | -41.2695 | 162.6837 | -39.8959 | -70.1748 | -32.7081 | -61.9026 | -42.4812 | -156.6601 | -39.3174 | -39.9996 | -7.9283 | 8.9293 | -13.2193 | 57.6194 | -19.9192 | 6.3741 | -18.735 | 25.5996 | -9.8667 | -83.9906 | -13.0574 | -17.7853 | -20.5692 | 6.331 | -16.9075 | -1.8495 | -46.3341 | -34.7887 | -33.6646 | -36.4591 | -43.2052 | -35.1168 | -44.2983 | -49.6239 | -34.2029 | -34.8217 | -41.6733 | -34.6903 | -29.6126 | 490 | -33.226 | -33.8233 | -31.2372 | -35.1688 | -35.583 | -31.5993 | -31.3804 | -35.5921 | 490 | -43.6553 | -28.2343 | -30.4905 | -38.0866 | -29.9982 | -38.4869 | -44.5053 | -28.3915 | -31.6921 | -37.3938 | -30.3498 | -39.5313 | -28.8201 | -27.696 | -28.8531 | -36.5547 | -29.5717 | -23.8012 | -29.6701 | -27.8532 | -30.0547 | -35.8619 | -29.9233 | -24.8456
491 | -5.9071 | 0 | -5.1922 | 0 | -5.9631 | 0 | -4.8023 | 0 | -42.3338 | -114.0787 | -35.2029 | -87.6244 | -42.0229 | 45.3125 | -35.3733 | 56.0357 | -39.5699 | -77.4123 | -36.0664 | 45.4627 | -40.3301 | 160.7679 | -40.3829 | -169.0085 | -39.1308 | -86.8697 | -31.8032 | -76.6147 | -40.8588 | -178.8455 | -35.6328 | -42.3238 | -8.0141 | 2.877 | -12.2202 | 51.3974 | -21.452 | 9.7755 | -20.6736 | 25.4392 | -10.7085 | -97.4622 | -12.5297 | -27.0744 | -22.1851 | 11.2112 | -17.4424 | -0.4287 | -46.232 | -34.6239 | -33.7906 | -35.3687 | -41.857 | -34.8114 | -43.5477 | -54.3029 | -34.1884 | -34.5165 | -40.6649 | -34.0568 | -29.7762 | 491 | -33.7367 | -33.3817 | -30.7606 | -33.7618 | -35.1371 | -30.7834 | -29.8923 | -33.2097 | 491 | -48.3958 | -28.2813 | -29.4616 | -36.6648 | -29.6192 | -37.5846 | -49.1107 | -28.2253 | -30.5664 | -35.8939 | -30.0091 | -38.7454 | -28.7168 | -27.8835 | -28.6094 | -35.4727 | -28.8646 | -23.8131 | -29.4317 | -27.8275 | -29.7142 | -34.7018 | -29.2545 | -24.9739
492 | -5.8289 | 0 | -5.2429 | 0 | -6.1284 | 0 | -4.8615 | 0 | -41.9639 | -97.4294 | -35.0954 | -84.9879 | -42.0234 | 43.9406 | -34.9095 | 44.9337 | -38.339 | -97.3664 | -34.8921 | 37.3134 | -39.3904 | 169.364 | -37.8397 | -159.373 | -38.6763 | -105.326 | -31.2768 | -89.7561 | -40.0327 | 155.9049 | -32.7897 | -53.0489 | -8.3212 | -4.7074 | -11.6578 | 42.3866 | -23.0655 | 10.9223 | -22.2189 | 38.915 | -11.5263 | -110.0591 | -11.8968 | -38.1011 | -22.806 | 19.3855 | -17.6309 | 2.4118 | -45.9193 | -34.4103 | -33.8413 | -34.5248 | -40.6849 | -33.7736 | -42.8327 | -61.1558 | -34.1219 | -34.239 | -39.9655 | -32.937 | -29.8675 | 492 | -33.6078 | -32.7319 | -30.1935 | -32.7284 | -33.8179 | -30.1791 | -28.4291 | -31.1865 | 492 | -55.3269 | -28.293 | -28.6959 | -35.442 | -28.5307 | -36.7043 | -55.9129 | -27.9935 | -29.6633 | -34.5565 | -28.9121 | -37.9712 | -28.5814 | -28.0124 | -28.4101 | -34.7226 | -27.6941 | -23.7391 | -29.1674 | -27.7129 | -29.3775 | -33.8371 | -28.0755 | -25.006
493 | -5.7149 | 0 | -5.2696 | 0 | -6.2813 | 0 | -4.9258 | 0 | -39.8194 | -88.4103 | -34.794 | -84.914 | -41.801 | 41.145 | -34.389 | 33.2883 | -37.9446 | -117.8581 | -34.0725 | 29.5993 | -37.4975 | 173.1209 | -36.0895 | -160.6069 | -38.7981 | -126.3324 | -30.993 | -101.3622 | -40.018 | 131.1688 | -30.9476 | -67.029 | -8.8291 | -9.0684 | -11.0962 | 35.7545 | -24.0633 | 17.473 | -22.5524 | 58.2712 | -13.3075 | -124.1285 | -11.9695 | -48.4459 | -21.4638 | 41.0279 | -17.4303 | 6.5602 | -45.7702 | -34.1061 | -33.8092 | -33.86 | -39.817 | -32.5163 | -42.1211 | -57.3594 | -34.0508 | -33.8907 | -39.6836 | -31.6993 | -29.9501 | 493 | -32.9939 | -32.0151 | -29.6373 | -32.0895 | -32.5502 | -29.6935 | -27.3385 | -29.8488 | 493 | -51.6445 | -28.3359 | -28.1451 | -34.5474 | -27.2467 | -35.8398 | -52.0898 | -27.7695 | -28.9342 | -33.5357 | -27.5905 | -37.1953 | -28.3912 | -28.0943 | -28.1758 | -34.414 | -26.4297 | -23.6688 | -28.8365 | -27.5279 | -28.9649 | -33.4023 | -26.7735 | -25.0243
494 | -5.6074 | 0 | -5.2714 | 0 | -6.4075 | 0 | -4.9797 | 0 | -37.4066 | -89.0975 | -34.6234 | -88.0303 | -41.0338 | 38.1429 | -34.0154 | 20.1699 | -38.2561 | -136.702 | -33.3688 | 23.029 | -35.4357 | 169.5415 | -35.1841 | -165.1122 | -39.3816 | -143.1281 | -30.8007 | -112.8189 | -40.7483 | 107.6903 | -29.8006 | -82.6988 | -9.4621 | -15.657 | -10.8584 | 27.7361 | -24.4314 | 26.9673 | -20.2929 | 72.7413 | -15.7739 | -137.2988 | -12.0122 | -58.4474 | -19.6633 | 40.2476 | -16.7753 | 9.994 | -46.0064 | -33.6073 | -33.7135 | -33.2954 | -39.2212 | -31.3377 | -41.4394 | -52.2434 | -33.9785 | -33.455 | -39.791 | -30.5833 | -30.0179 | 494 | -32.1797 | -31.3798 | -29.2011 | -31.6202 | -31.5215 | -29.2015 | -26.612 | -29.0432 | 494 | -46.636 | -28.3711 | -27.688 | -33.9498 | -26.0663 | -35.0319 | -46.972 | -27.571 | -28.3157 | -32.8137 | -26.358 | -36.4597 | -27.9999 | -28.1061 | -27.8476 | -34.5196 | -25.3119 | -23.6104 | -28.3359 | -27.306 | -28.4753 | -33.3835 | -25.6036 | -25.0382
495 | -5.5025 | 0 | -5.241 | 0 | -6.4847 | 0 | -5.0418 | 0 | -35.3361 | -95.7582 | -34.9449 | -93.7208 | -39.8228 | 30.6446 | -33.9221 | 6.6564 | -38.9837 | -152.3049 | -32.5719 | 15.3571 | -33.704 | 162.5572 | -35.0192 | -169.4358 | -40.154 | -158.8442 | -30.7585 | -123.4896 | -42.2556 | 83.791 | -29.0585 | -96.7942 | -10.3411 | -18.5649 | -10.6808 | 22.9788 | -23.7217 | 39.6956 | -17.5212 | 76.0215 | -19.4607 | -150.4074 | -12.5352 | -68.9809 | -17.5235 | 41.973 | -15.8283 | 10.639 | -46.8119 | -32.993 | -33.5967 | -32.8783 | -38.9447 | -30.2743 | -40.8934 | -49.18 | -33.8853 | -33.1785 | -40.1629 | -29.637 | -30.1187 | 495 | -31.4442 | -30.8388 | -28.9324 | -31.0588 | -30.77 | -28.7764 | -26.2039 | -28.5447 | 495 | -43.6775 | -28.3828 | -27.3758 | -33.7037 | -25.0333 | -34.4087 | -43.939 | -27.4006 | -27.8365 | -32.46 | -25.2325 | -35.8516 | -27.4905 | -28.0942 | -27.676 | -34.9219 | -24.396 | -23.634 | -27.752 | -27.112 | -28.1367 | -33.6782 | -24.5952 | -25.0769
496 | -5.4228 | 0 | -5.2144 | 0 | -6.5427 | 0 | -5.1001 | 0 | -33.7047 | -105.6977 | -36.0988 | -98.7155 | -38.8718 | 18.2729 | -34.1393 | -8.8002 | -40.0425 | -166.8268 | -31.776 | 5.4309 | -32.3969 | 152.0323 | -35.3035 | -169.8625 | -41.1708 | -174.5405 | -30.8273 | -134.9625 | -44.2813 | 64.2276 | -28.6561 | -112.9653 | -11.0937 | -21.3822 | -10.7664 | 16.218 | -22.8514 | 46.8433 | -15.7348 | 73.0904 | -25.86 | -150.2857 | -13.6323 | -79.6618 | -16.0013 | 34.7294 | -14.8193 | 8.4873 | -48.3008 | -32.4025 | -33.4233 | -32.6055 | -38.9532 | -29.3791 | -40.4878 | -47.2966 | -33.7705 | -33.0699 | -40.6753 | -28.9646 | -30.2471 | 496 | -30.9619 | -30.4063 | -28.8758 | -30.4913 | -30.236 | -28.4172 | -26.0483 | -28.3081 | 496 | -41.8738 | -28.3477 | -27.1827 | -33.7388 | -24.1647 | -33.9451 | -42.0822 | -27.2278 | -27.5054 | -32.4105 | -24.279 | -35.3877 | -26.9797 | -28.0005 | -27.6471 | -35.4609 | -23.7502 | -23.7044 | -27.1881 | -26.8806 | -27.9698 | -34.1326 | -23.8645 | -25.147
497 | -5.3635 | 0 | -5.1643 | 0 | -6.5393 | 0 | -5.1408 | 0 | -32.5248 | -117.5791 | -38.5082 | -98.2681 | -38.4011 | 4.1232 | -34.8585 | -24.9823 | -41.4556 | -179.2177 | -31.2718 | -6.0591 | -31.43 | 142.1156 | -35.5192 | -164.9356 | -42.9441 | 173.8374 | -31.0298 | -144.3138 | -46.4688 | 49.5451 | -28.6692 | -126.7202 | -11.7725 | -22.5763 | -11.0976 | 9.8654 | -21.5964 | 52.2937 | -14.3076 | 67.2564 | -39.4662 | -103.0453 | -15.2891 | -90.2774 | -14.6858 | 32.9134 | -13.8456 | 5.4805 | -50.4382 | -31.9304 | -33.2233 | -32.4616 | -39.2194 | -28.7311 | -40.2971 | -46.1057 | -33.6526 | -33.1135 | -41.2854 | -28.4455 | -30.3376 | 497 | -30.7333 | -30.1892 | -29.1584 | -30.1675 | -29.7847 | -28.1505 | -26.1474 | -28.4409 | 497 | -40.7422 | -28.2891 | -27.0981 | -34.0551 | -23.5668 | -33.7578 | -40.9414 | -27.1133 | -27.3208 | -32.6801 | -23.5903 | -35.1563 | -26.5669 | -27.8598 | -27.75 | -36.1211 | -23.2812 | -23.7983 | -26.7661 | -26.684 | -27.9727 | -34.7461 | -23.3047 | -25.1968
498 | -5.3237 | 0 | -5.1252 | 0 | -6.5205 | 0 | -5.1708 | 0 | -31.7452 | -130.4575 | -41.8836 | -76.828 | -38.0516 | -8.4602 | -36.3451 | -40.1884 | -43.183 | 174.0977 | -31.1419 | -18.4487 | -30.7679 | 129.8232 | -35.1024 | -158.7129 | -45.2749 | 169.3123 | -31.4175 | -155.4498 | -48.5744 | 33.2961 | -29.0079 | -141.1875 | -12.4266 | -17.7039 | -11.5106 | 6.9995 | -19.2897 | 54.952 | -12.8545 | 61.617 | -26.4215 | -41.19 | -17.2525 | -96.0239 | -13.9385 | 23.0389 | -13.0831 | -2.1021 | -52.9733 | -31.642 | -33.0312 | -32.4811 | -39.7428 | -28.3021 | -40.3635 | -45.5713 | -33.4956 | -33.3674 | -42.0432 | -28.1298 | -30.4713 | 498 | -30.5036 | -30.2267 | -29.724 | -30.1168 | -29.2942 | -28.0318 | -26.4073 | -28.8599 | 498 | -40.2476 | -28.1719 | -27.1574 | -34.6176 | -23.1769 | -33.843 | -40.4461 | -26.9751 | -27.3103 | -33.2223 | -23.1313 | -35.1927 | -26.3183 | -27.7075 | -28.0437 | -36.918 | -23.0046 | -23.9508 | -26.5168 | -26.5107 | -28.1966 | -35.5227 | -22.959 | -25.3005
499 | -5.2953 | 0 | -5.0952 | 0 | -6.4628 | 0 | -5.1842 | 0 | -31.3338 | -143.2518 | -39.3146 | -35.099 | -37.8568 | -25.0634 | -39.0368 | -56.0045 | -44.6941 | 172.7234 | -31.2964 | -32.0678 | -30.3843 | 117.4501 | -33.8759 | -152.7185 | -46.2112 | 177.2994 | -32.0847 | -166.2423 | -50.3709 | 17.4966 | -29.445 | -154.7029 | -12.4355 | -16.5234 | -11.9434 | 3.3312 | -17.7415 | 49.5994 | -12.2351 | 54.2263 | -21.0038 | -52.0026 | -20.1903 | -95.1849 | -13.4702 | 13.5323 | -12.528 | -9.4192 | -53.2597 | -31.5491 | -32.9089 | -32.58 | -40.4667 | -28.1233 | -40.5913 | -45.4315 | -33.2914 | -33.6929 | -42.9195 | -27.9315 | -30.6051 | 499 | -29.9291 | -30.4851 | -30.0707 | -30.2703 | -28.7002 | -28.1156 | -26.6459 | -29.3203 | 499 | -40.1362 | -27.9961 | -27.2847 | -35.3715 | -23.0281 | -34.1285 | -40.3363 | -26.8286 | -27.3958 | -34.0039 | -22.9391 | -35.4071 | -26.2538 | -27.6136 | -28.3976 | -37.8243 | -22.8363 | -24.1423 | -26.4539 | -26.4461 | -28.5087 | -36.4567 | -22.7473 | -25.4209
500 | -5.2776 | 0 | -5.1072 | 0 | -6.3876 | 0 | -5.1627 | 0 | -31.2082 | -155.8215 | -34.3492 | -29.6154 | -38.1635 | -42.4495 | -43.5204 | -67.6806 | -45.6583 | 172.4219 | -31.9094 | -47.7826 | -30.2887 | 104.7543 | -32.2877 | -151.4216 | -45.5612 | -177.2205 | -33.1026 | -176.9529 | -51.218 | -7.6751 | -30.0139 | -168.7429 | -12.2638 | -16.6237 | -12.2713 | 2.7158 | -16.4277 | 41.9881 | -11.6913 | 46.4173 | -18.5489 | -65.4869 | -23.3886 | -77.6932 | -13.3118 | 3.6682 | -12.2778 | -18.2217 | -50.6974 | -31.7552 | -32.8912 | -32.6739 | -41.4552 | -28.1419 | -41.0525 | -45.4501 | -33.0627 | -34.0915 | -44.0603 | -27.8681 | -30.8583 | 500 | -28.9376 | -30.8156 | -29.7631 | -30.8404 | -28.0855 | -28.4384 | -26.826 | -29.8626 | 500 | -40.1725 | -27.7851 | -27.3963 | -36.348 | -23.0347 | -34.6649 | -40.3429 | -26.6751 | -27.5112 | -35.0676 | -22.9792 | -35.8898 | -26.4776 | -27.6136 | -28.8139 | -38.9531 | -22.7609 | -24.4707 | -26.648 | -26.5036 | -28.9288 | -37.6727 | -22.7054 | -25.6956
501 | -5.2817 | 0 | -5.1527 | 0 | -6.2934 | 0 | -5.1176 | 0 | -31.3821 | -169.5018 | -31.3041 | -38.7678 | -38.9615 | -59.2397 | -55.6387 | -65.3743 | -46.5505 | 171.8627 | -33.3108 | -64.4793 | -30.5149 | 91.082 | -30.7263 | -153.9408 | -44.1083 | -175.7624 | -34.6063 | 172.608 | -50.7348 | -49.4588 | -31.0397 | 176.0718 | -11.9632 | -18.2908 | -12.3512 | 6.0113 | -15.8941 | 32.0186 | -11.4358 | 39.4423 | -17.3914 | -80.9887 | -22.5757 | -47.5102 | -13.5847 | -4.3421 | -12.3003 | -27.259 | -48.2038 | -32.2351 | -32.7898 | -32.8601 | -43.0632 | -28.1882 | -41.934 | -45.0941 | -32.7699 | -34.6293 | -45.5434 | -27.891 | -31.1626 | 501 | -27.9723 | -31.2362 | -29.1725 | -32.1062 | -27.5128 | -29.0557 | -27.0348 | -30.7864 | 501 | -39.8124 | -27.4882 | -27.5784 | -37.9105 | -23.0355 | -35.6406 | -39.9414 | -26.4765 | -27.7425 | -36.7698 | -23.0706 | -36.8164 | -26.9534 | -27.5081 | -29.3476 | -40.3907 | -22.7383 | -24.8692 | -27.0824 | -26.4964 | -29.5117 | -39.25 | -22.7734 | -26.045
502 | -5.2989 | 0 | -5.2313 | 0 | -6.1679 | 0 | -5.0505 | 0 | -31.9465 | 177.7398 | -29.3093 | -48.7061 | -39.8875 | -74.8257 | -47.0682 | 64.547 | -47.1737 | 176.3011 | -35.9507 | -81.3477 | -31.1696 | 77.9705 | -29.4103 | -158.8455 | -41.7861 | 179.4586 | -36.9083 | 164.3825 | -48.6561 | -98.8057 | -32.6749 | 160.387 | -11.8118 | -18.3855 | -11.9337 | 7.4853 | -15.6716 | 21.6182 | -11.4592 | 31.7804 | -16.9433 | -97.1337 | -19.3493 | -37.3312 | -14.0075 | -13.5807 | -12.6318 | -36.6323 | -46.3761 | -32.9103 | -32.6156 | -33.1847 | -45.7199 | -28.3478 | -43.1298 | -44.7694 | -32.506 | -34.9345 | -47.2431 | -28.0468 | -31.4474 | 502 | -27.1811 | -31.6903 | -28.3981 | -34.2498 | -27.043 | -30.0819 | -27.2368 | -32.0757 | 502 | -39.4705 | -27.2071 | -27.8858 | -40.4886 | -23.1165 | -36.9619 | -39.5381 | -26.3381 | -28.1342 | -39.552 | -23.2973 | -38.0793 | -27.6114 | -27.3167 | -29.6356 | -42.0118 | -22.8155 | -25.2795 | -27.679 | -26.4477 | -29.884 | -41.0752 | -22.9963 | -26.3969
503 | -5.2828 | 0 | -5.3275 | 0 | -6.0328 | 0 | -4.9951 | 0 | -32.9936 | 165.1898 | -27.9842 | -60.6524 | -40.8516 | -91.5035 | -39.3001 | 51.5573 | -46.5395 | -178.409 | -40.7157 | -97.4093 | -32.3288 | 65.9295 | -28.3736 | -165.9683 | -39.6821 | 165.2238 | -40.7369 | 163.1924 | -45.9172 | -144.9505 | -34.7751 | 147.3497 | -11.6031 | -22.3954 | -11.2359 | 7.1805 | -16.005 | 10.4916 | -11.7136 | 25.8015 | -17.0504 | -113.3521 | -16.6619 | -40.772 | -14.983 | -19.1713 | -13.2569 | -44.9506 | -45.3238 | -33.8729 | -32.3651 | -33.7418 | -50.5895 | -28.7205 | -44.7767 | -44.3805 | -32.2437 | -34.8666 | -48.4916 | -28.3766 | -31.7773 | 503 | -26.6258 | -31.9274 | -27.4643 | -37.2311 | -26.6821 | -31.5805 | -27.2777 | -33.314 | 503 | -39.0977 | -26.9609 | -28.459 | -45.262 | -23.393 | -38.7439 | -39.053 | -26.2109 | -28.7467 | -44.5567 | -23.7254 | -39.7816 | -28.5901 | -27.0823 | -29.5838 | -43.1641 | -23.0491 | -25.7445 | -28.5454 | -26.3323 | -29.8715 | -42.4588 | -23.3815 | -26.7822
504 | -5.2953 | 0 | -5.4501 | 0 | -5.9509 | 0 | -4.9218 | 0 | -34.6523 | 155.012 | -27.0612 | -71.4598 | -42.4278 | -112.7738 | -35.4076 | 33.2322 | -45.1163 | -179.2753 | -53.4216 | -104.8661 | -34.0626 | 56.3708 | -27.629 | -173.1085 | -38.5111 | 147.1685 | -44.7069 | -166.2785 | -43.8959 | 175.2497 | -37.6845 | 129.8028 | -11.5676 | -27.7488 | -10.4225 | 4.1068 | -16.8218 | 0.5297 | -12.1295 | 20.0165 | -17.6827 | -130.8684 | -14.6681 | -49.1494 | -16.2458 | -23.0335 | -14.2572 | -52.6597 | -44.88 | -35.0019 | -32.1197 | -34.1456 | -63.6691 | -29.3691 | -46.2392 | -44.322 | -31.9984 | -34.1064 | -48.5673 | -28.7634 | -32.2346 | 504 | -26.2578 | -31.7962 | -26.4593 | -40.338 | -26.4598 | -33.3067 | -27.1433 | -34.5333 | 504 | -39.0267 | -26.7031 | -28.8503 | -58.219 | -23.919 | -40.2883 | -38.8719 | -26.0475 | -29.2238 | -57.7182 | -24.4473 | -41.3174 | -29.7066 | -26.8244 | -28.8111 | -43.1172 | -23.3133 | -26.2837 | -29.5518 | -26.1688 | -29.1846 | -42.6164 | -23.8416 | -27.3128
505 | -5.2935 | 0 | -5.5513 | 0 | -5.9263 | 0 | -4.8795 | 0 | -36.7534 | 150.2539 | -26.6248 | -84.2033 | -45.1112 | -133.0694 | -33.2937 | 16.3382 | -43.7979 | 174.1161 | -45.4763 | 44.5517 | -36.3621 | 51.2576 | -27.179 | 179.147 | -37.9706 | 129.437 | -41.058 | -132.3828 | -42.7752 | 140.8413 | -43.7281 | 102.9203 | -11.922 | -29.9561 | -9.7056 | 1.681 | -18.6161 | -3.8733 | -12.501 | 18.6831 | -18.9934 | -145.2981 | -13.531 | -59.5355 | -17.7075 | -21.5294 | -15.5401 | -57.8191 | -44.946 | -36.1296 | -31.989 | -34.1296 | -57.2702 | -30.1296 | -46.5904 | -44.4029 | -31.8053 | -33.1373 | -47.8248 | -29.1021 | -32.8938 | 505 | -26.1667 | -31.4188 | -25.7315 | -39.9624 | -26.3726 | -34.4099 | -26.9134 | -35.9392 | 505 | -39.1094 | -26.5118 | -28.8361 | -51.7189 | -24.5783 | -40.6641 | -38.8516 | -25.879 | -29.2501 | -51.3439 | -25.2501 | -41.7109 | -30.8361 | -26.6955 | -27.8438 | -42.2735 | -23.5508 | -26.9675 | -30.5783 | -26.0627 | -28.2578 | -41.8985 | -24.2226 | -28.0143
506 | -5.2824 | 0 | -5.6478 | 0 | -5.9828 | 0 | -4.8408 | 0 | -38.9921 | 153.3374 | -26.7835 | -95.5918 | -47.8024 | -154.6151 | -32.1666 | 0.1152 | -42.8148 | 163.1269 | -37.9502 | 26.8377 | -38.796 | 57.1555 | -27.0505 | 171.0608 | -37.5414 | 109.412 | -37.0194 | -133.7017 | -42.585 | 108.1668 | -48.6447 | 3.7859 | -12.3875 | -33.881 | -9.1614 | -2.6376 | -21.241 | -6.2888 | -13.1141 | 17.1442 | -20.8608 | -164.2785 | -12.4109 | -70.71 | -18.1553 | -15.0774 | -17.2223 | -60.1492 | -45.3338 | -37.0854 | -31.9192 | -33.7524 | -50.6048 | -30.8116 | -45.7614 | -44.3068 | -31.6709 | -32.2008 | -47.122 | -29.2816 | -33.4174 | 506 | -26.4976 | -31.0478 | -25.4291 | -36.3977 | -26.4201 | -34.1372 | -26.6065 | -36.1093 | 506 | -39.0244 | -26.3885 | -28.47 | -44.957 | -25.1638 | -39.7786 | -38.659 | -25.6881 | -28.9116 | -44.622 | -25.9708 | -40.9206 | -31.803 | -26.6368 | -26.9184 | -41.4742 | -23.6338 | -27.4346 | -31.4376 | -25.9364 | -27.36 | -41.1392 | -24.4408 | -28.5766
507 | -5.2599 | 0 | -5.7227 | 0 | -6.0903 | 0 | -4.8243 | 0 | -40.5896 | 164.5182 | -27.4133 | -106.5733 | -52.5156 | 163.3165 | -31.4897 | -14.2467 | -42.3584 | 149.6133 | -34.4727 | 11.5685 | -40.0979 | 72.7653 | -27.0936 | 164.4958 | -37.9874 | 88.8981 | -34.5727 | -142.7569 | -43.1899 | 77.3735 | -41.7403 | -89.2587 | -12.8884 | -37.3776 | -8.6473 | -9.3925 | -24.1364 | 4.8245 | -13.6531 | 16.9353 | -23.5625 | 176.9053 | -11.8817 | -82.7184 | -17.737 | -8.3562 | -18.7664 | -55.9123 | -45.8892 | -37.82 | -31.8791 | -33.3398 | -47.4016 | -31.3189 | -44.4735 | -43.9371 | -31.6017 | -31.3662 | -46.791 | -29.2819 | -33.2915 | 507 | -27.1964 | -30.6802 | -25.4048 | -33.7597 | -26.5572 | -33.0569 | -26.255 | -35.624 | 507 | -38.6772 | -26.3418 | -28.0799 | -41.6789 | -25.5962 | -38.3832 | -38.2144 | -25.5114 | -28.5155 | -41.3113 | -26.4946 | -39.6492 | -32.5601 | -26.6192 | -26.1063 | -41.0683 | -23.5592 | -27.2012 | -32.0973 | -25.7888 | -26.5419 | -40.7007 | -24.4576 | -28.4672
508 | -5.252 | 0 | -5.7753 | 0 | -6.2491 | 0 | -4.8244 | 0 | -40.6836 | 179.8582 | -28.5676 | -115.6001 | -58.1456 | 108.9759 | -31.0621 | -28.2151 | -42.2296 | 135.5178 | -32.1125 | -5.8618 | -39.1949 | 90.1864 | -27.225 | 160.9749 | -38.6283 | 68.2998 | -33.0846 | -154.7239 | -44.4443 | 48.0726 | -36.7039 | -112.7315 | -13.3663 | -40.9699 | -8.2432 | -16.6861 | -24.8179 | 34.2214 | -13.9292 | 18.8365 | -27.096 | 152.4082 | -11.471 | -95.4439 | -16.4958 | -6.2336 | -19.7403 | -46.0935 | -46.5839 | -38.1983 | -31.877 | -32.9667 | -45.3573 | -31.5069 | -43.1112 | -43.1593 | -31.6348 | -30.6464 | -46.8378 | -29.0929 | -32.471 | 508 | -28.3042 | -30.323 | -25.5461 | -31.6992 | -26.6715 | -31.8854 | -25.8509 | -34.1264 | 508 | -37.9073 | -26.3828 | -27.7147 | -39.582 | -25.7316 | -36.8621 | -37.384 | -25.3857 | -28.1423 | -39.1082 | -26.6825 | -38.2868 | -32.9463 | -26.625 | -25.3944 | -41.0625 | -23.3176 | -26.2219 | -32.423 | -25.6279 | -25.822 | -40.5887 | -24.2685 | -27.6466
509 | -5.2117 | 0 | -5.7976 | 0 | -6.4461 | 0 | -4.868 | 0 | -38.9578 | -168.7477 | -30.165 | -118.1417 | -52.5287 | 27.1851 | -30.7191 | -39.3586 | -42.8562 | 120.5361 | -30.8106 | -21.0394 | -36.875 | 95.2888 | -27.4953 | 157.5292 | -40.6674 | 51.1838 | -32.4548 | -165.1783 | -47.2291 | 20.1326 | -33.7981 | -131.4362 | -14.3105 | -39.6333 | -8.1444 | -22.8665 | -21.4067 | 56.5017 | -13.6227 | 22.9657 | -31.9036 | 126.6525 | -11.431 | -109.1526 | -15.5871 | -6.7232 | -19.0293 | -35.0315 | -47.7351 | -37.8328 | -32.0242 | -32.5085 | -44.0515 | -31.0007 | -41.7781 | -42.0047 | -31.7 | -30.0789 | -47.0828 | -28.7625 | -31.8947 | 509 | -29.6042 | -29.8871 | -25.7842 | -30.5201 | -26.8375 | -31.01 | -25.5823 | -32.8255 | 509 | -36.793 | -26.4883 | -27.2968 | -38.2539 | -25.2031 | -35.332 | -36.2071 | -25.2539 | -27.6405 | -37.6054 | -26.1327 | -36.9101 | -32.6211 | -26.8125 | -24.8672 | -41.2852 | -22.9649 | -25.4486 | -32.0352 | -25.5781 | -25.2109 | -40.6367 | -23.8945 | -27.0267
510 | -5.1894 | 0 | -5.7692 | 0 | -6.6327 | 0 | -4.9225 | 0 | -36.7561 | -167.7917 | -31.9298 | -114.5229 | -48.0755 | -13.3529 | -30.5831 | -51.4656 | -44.0834 | 108.1371 | -30.04 | -38.5712 | -34.8766 | 91.6873 | -27.7844 | 156.4254 | -43.3122 | 37.0409 | -32.2859 | -175.9527 | -51.4407 | -5.0552 | -32.0314 | -152.221 | -14.758 | -39.8716 | -8.0371 | -32.0099 | -19.2498 | 53.3896 | -13.4305 | 23.5475 | -36.2005 | -2.2178 | -11.6793 | -122.2038 | -14.3291 | -15.8389 | -17.8225 | -32.3135 | -49.5152 | -36.9139 | -32.3182 | -31.9254 | -43.4019 | -30.0936 | -40.5973 | -40.9921 | -31.7714 | -29.6989 | -47.1364 | -28.4218 | -31.9409 | 510 | -30.6155 | -29.4905 | -26.0094 | -29.8069 | -26.9089 | -30.3467 | -25.402 | -31.6734 | 510 | -35.8027 | -26.582 | -26.736 | -37.6327 | -24.3244 | -33.9646 | -35.2229 | -25.1387 | -27.0029 | -36.7692 | -25.1711 | -35.6748 | -31.7245 | -27.1288 | -24.5095 | -41.3672 | -22.6526 | -25.3082 | -31.1447 | -25.6855 | -24.7764 | -40.5037 | -23.4993 | -27.0184
511 | -5.1608 | 0 | -5.6755 | 0 | -6.7713 | 0 | -5.0131 | 0 | -34.7485 | -171.0384 | -32.9522 | -101.014 | -45.9826 | -39.5387 | -30.6617 | -62.2262 | -45.5258 | 99.1384 | -29.7995 | -54.352 | -33.2607 | 85.1822 | -27.7044 | 158.6691 | -46.6136 | 25.5052 | -32.2038 | 175.5776 | -57.9779 | -30.1619 | -31.2858 | -173.067 | -15.3493 | -36.8506 | -8.3596 | -38.13 | -16.7291 | 51.4518 | -12.5007 | 26.2795 | -30.3518 | -44.7825 | -12.3335 | -137.1537 | -13.349 | -26.7694 | -16.2166 | -34.5269 | -52.1129 | -35.9939 | -32.6099 | -31.445 | -43.1637 | -29.2673 | -39.6482 | -40.3065 | -31.8444 | -29.4646 | -46.949 | -28.2557 | -32.1851 | 511 | -30.6196 | -29.1301 | -26.175 | -29.5842 | -26.5949 | -29.6834 | -25.168 | -31.1513 | 511 | -35.1457 | -26.6836 | -26.2842 | -37.4882 | -23.5918 | -32.8769 | -34.631 | -25.0731 | -26.4319 | -36.3924 | -24.2542 | -34.6351 | -30.8331 | -27.4491 | -24.3038 | -41.2735 | -22.5802 | -25.4138 | -30.3184 | -25.8386 | -24.4515 | -40.1777 | -23.2426 | -27.172
512 | -5.1609 | 0 | -5.5745 | 0 | -6.8244 | 0 | -5.0875 | 0 | -33.136 | -179.3693 | -31.8591 | -84.8687 | -44.7921 | -58.4158 | -30.8607 | -74.0321 | -46.9901 | 92.8838 | -30.1548 | -70.3663 | -31.9734 | 76.2774 | -26.9857 | 161.0958 | -53.1132 | 23.0305 | -31.982 | 169.2337 | -74.1631 | -111.6964 | -31.3454 | 168.037 | -15.5662 | -34.8666 | -8.7381 | -45.403 | -15.0961 | 43.9908 | -11.7673 | 24.3491 | -27.4119 | -71.4897 | -13.1793 | -153.0124 | -13.2414 | -36.9021 | -14.8025 | -40.3903 | -54.6251 | -35.3555 | -32.7974 | -31.0822 | -43.0626 | -28.6992 | -38.9925 | -39.9728 | -31.9148 | -29.3284 | -46.5511 | -28.2228 | -32.4023 | 512 | -29.3156 | -28.7747 | -26.1315 | -29.9219 | -25.7814 | -28.9673 | -24.725 | -31.3164 | 512 | -34.8119 | -26.7539 | -25.9213 | -37.4881 | -23.1247 | -32.1681 | -34.3983 | -25.0904 | -25.9947 | -36.2382 | -23.6117 | -33.905 | -30.1946 | -27.6365 | -24.1675 | -40.9766 | -22.6483 | -25.5779 | -29.781 | -25.973 | -24.2409 | -39.7267 | -23.1353 | -27.3148
513 | -5.1728 | 0 | -5.4462 | 0 | -6.8212 | 0 | -5.1611 | 0 | -31.9142 | 170.8161 | -29.3732 | -76.835 | -43.4505 | -75.3845 | -31.1713 | -85.2976 | -48.491 | 90.2019 | -30.9811 | -84.658 | -30.8985 | 66.6142 | -25.6986 | 162.1129 | -55.5122 | 108.0709 | -31.5722 | 161.231 | -60.1577 | 128.0277 | -31.8061 | 152.3404 | -15.574 | -34.2781 | -9.3627 | -52.3351 | -14.0575 | 34.8683 | -11.0466 | 21.214 | -25.8621 | -94.5077 | -14.2947 | -170.3495 | -13.4212 | -47.7158 | -13.6443 | -48.4523 | -53.5672 | -34.8562 | -32.9187 | -30.8484 | -43.0047 | -28.3211 | -38.5947 | -39.9345 | -31.9736 | -29.3173 | -46.0478 | -28.3291 | -32.5985 | 513 | -27.3424 | -28.4731 | -25.6596 | -30.6695 | -24.549 | -28.2092 | -23.9271 | -31.7813 | 513 | -34.7617 | -26.8008 | -25.6756 | -37.5585 | -22.8749 | -31.7735 | -34.4883 | -25.1524 | -25.6873 | -36.1835 | -23.16 | -33.4336 | -29.6834 | -27.7459 | -24.1445 | -40.6016 | -22.8829 | -25.7773 | -29.41 | -26.0975 | -24.1562 | -39.2266 | -23.168 | -27.4374
514 | -5.1937 | 0 | -5.318 | 0 | -6.7706 | 0 | -5.2256 | 0 | -30.985 | 160.1276 | -26.9029 | -78.8789 | -42.1729 | -96.5566 | -31.6831 | -98.0067 | -49.7524 | 92.4643 | -31.7867 | -95.7653 | -30.0714 | 54.7363 | -24.2713 | 158.7658 | -47.3495 | 113.1072 | -31.2225 | 150.5298 | -55.028 | 96.6264 | -32.4242 | 135.7122 | -15.4303 | -35.3174 | -10.1227 | -56.7435 | -13.4883 | 24.7317 | -10.3888 | 16.6849 | -24.9205 | -110.6222 | -16.2849 | 172.1302 | -13.5605 | -58.2124 | -13.0927 | -60.5728 | -50.4155 | -34.5477 | -32.9122 | -30.7201 | -42.9936 | -28.1141 | -38.5016 | -40.0362 | -32.053 | -29.3649 | -45.6852 | -28.4425 | -32.7238 | 514 | -25.3789 | -28.2787 | -24.7085 | -31.3434 | -23.2403 | -27.5908 | -22.9526 | -32.2636 | 514 | -34.8425 | -26.8593 | -25.5264 | -37.6756 | -22.7961 | -31.731 | -34.7182 | -25.2824 | -25.4945 | -36.223 | -22.8885 | -33.276 | -29.354 | -27.7185 | -24.1712 | -40.3672 | -23.1245 | -25.9532 | -29.2297 | -26.1416 | -24.1393 | -38.9146 | -23.2169 | -27.4982
515 | -5.2095 | 0 | -5.2185 | 0 | -6.6692 | 0 | -5.2645 | 0 | -30.4001 | 147.4784 | -24.917 | -85.0732 | -41.711 | -116.0394 | -32.7035 | -109.5719 | -49.5489 | 98.8355 | -32.6709 | -107.7898 | -29.5333 | 41.0879 | -22.9745 | 152.3261 | -43.9081 | 100.711 | -31.1674 | 137.0125 | -53.6932 | 63.0938 | -33.4849 | 118.3768 | -15.7039 | -34.405 | -11.1718 | -58.3584 | -13.1687 | 16.3967 | -9.738 | 12.3997 | -25.0451 | -126.5574 | -19.3958 | 151.3645 | -14.1284 | -68.8515 | -12.6003 | -72.8499 | -47.7534 | -34.2588 | -32.8108 | -30.6909 | -43.0463 | -28.0479 | -38.6364 | -40.1341 | -32.1744 | -29.57 | -45.5739 | -28.4466 | -32.6929 | 515 | -23.7647 | -28.3574 | -23.6648 | -32.0819 | -22.0792 | -27.2538 | -22.0385 | -33.07 | 515 | -34.9246 | -26.9649 | -25.4814 | -37.8278 | -22.8294 | -31.9672 | -34.9156 | -25.5052 | -25.4264 | -36.3771 | -22.7834 | -33.3719 | -29.0493 | -27.6013 | -24.3605 | -40.3554 | -23.2281 | -26.0237 | -29.0403 | -26.1416 | -24.3055 | -38.9047 | -23.1821 | -27.4284
516 | -5.2356 | 0 | -5.1595 | 0 | -6.5114 | 0 | -5.2994 | 0 | -30.2122 | 134.1453 | -23.349 | -94.216 | -41.8895 | -135.356 | -34.4922 | -123.4763 | -48.2762 | 95.5245 | -34.3046 | -122.2251 | -29.3822 | 27.5833 | -21.9022 | 144.6527 | -41.6212 | 91.8586 | -31.5458 | 123.3555 | -55.3363 | 27.0499 | -35.363 | 100.8327 | -16.0444 | -34.6681 | -11.9147 | -58.1559 | -13.2177 | 4.3728 | -9.378 | 5.2757 | -25.4759 | -144.7118 | -23.766 | 129.092 | -15.139 | -79.5795 | -12.3167 | -84.6221 | -45.7999 | -34.0072 | -32.6494 | -30.8897 | -43.378 | -28.1126 | -39.1752 | -40.4918 | -32.2708 | -30.0736 | -45.6791 | -28.4645 | -32.3711 | 516 | -22.4857 | -28.7856 | -22.7153 | -33.4608 | -21.1492 | -27.3135 | -21.2815 | -34.4052 | 516 | -35.2562 | -27.0352 | -25.6541 | -38.2185 | -22.9531 | -32.6638 | -35.3323 | -25.7594 | -25.5903 | -36.8666 | -22.8132 | -33.8758 | -28.7716 | -27.4138 | -24.838 | -40.5196 | -23.305 | -25.8597 | -28.8477 | -26.138 | -24.7742 | -39.1677 | -23.1651 | -27.0717
517 | -5.2706 | 0 | -5.1534 | 0 | -6.3292 | 0 | -5.3292 | 0 | -30.4308 | 120.7351 | -22.1107 | -104.0413 | -41.8052 | -150.5393 | -37.4233 | -133.2271 | -47.4931 | 85.8317 | -36.9436 | -133.1404 | -29.6758 | 11.4198 | -21.0448 | 134.8721 | -39.4382 | 79.6716 | -32.6023 | 108.459 | -61.4592 | -27.2631 | -37.9986 | 86.0151 | -16.4203 | -33.7214 | -12.323 | -55.3001 | -13.7295 | -2.5856 | -9.0163 | -0.3802 | -27.2094 | -155.8469 | -33.3259 | 86.5526 | -16.2223 | -89.4757 | -12.3424 | -99.9115 | -44.5945 | -33.907 | -32.3875 | -31.282 | -44.1219 | -28.2742 | -40.1222 | -41.2159 | -32.3253 | -30.8331 | -46.3409 | -28.5519 | -31.9781 | 517 | -21.4738 | -29.5688 | -21.8483 | -35.4373 | -20.432 | -27.8849 | -20.6704 | -35.6373 | 517 | -35.9453 | -27.0547 | -26.0114 | -38.9685 | -23.1208 | -33.793 | -36.0625 | -25.9961 | -25.9528 | -37.7927 | -22.945 | -34.793 | -28.6364 | -27.1169 | -25.5625 | -41.1875 | -23.3985 | -25.6489 | -28.7536 | -26.0583 | -25.5039 | -40.0117 | -23.2227 | -26.6489
518 | -5.2803 | 0 | -5.1772 | 0 | -6.1581 | 0 | -5.3442 | 0 | -31.0397 | 108.1331 | -21.1952 | -114.7208 | -41.4862 | -168.4011 | -42.256 | -131.6973 | -47.5108 | 73.1166 | -40.1999 | -137.6007 | -30.4289 | -2.2107 | -20.447 | 125.3676 | -37.8027 | 63.4728 | -34.6101 | 90.8747 | -61.9073 | -155.5894 | -40.9637 | 74.2532 | -16.8049 | -30.9318 | -12.1872 | -52.6849 | -14.5628 | -12.9718 | -8.8909 | -7.0091 | -30.0777 | -159.2607 | -29.5625 | -42.5052 | -17.7183 | -99.7148 | -12.5618 | -113.649 | -44.0284 | -33.9585 | -32.069 | -31.8956 | -45.4737 | -28.4429 | -41.4507 | -42.4081 | -32.2881 | -31.7749 | -47.728 | -28.6385 | -31.7134 | 518 | -20.7303 | -30.6332 | -21.1075 | -37.3457 | -19.9595 | -29.0221 | -20.2466 | -36.0801 | 518 | -37.1278 | -27.0078 | -26.6153 | -40.2965 | -23.2657 | -35.2926 | -37.2309 | -26.13 | -26.5514 | -39.3156 | -23.0987 | -36.1065 | -28.6782 | -26.7887 | -26.4946 | -42.5508 | -23.4613 | -25.5553 | -28.7813 | -25.9109 | -26.4307 | -41.5699 | -23.2943 | -26.3692
519 | -5.3062 | 0 | -5.2457 | 0 | -5.9784 | 0 | -5.3453 | 0 | -32.0442 | 96.9888 | -20.6264 | -127.8306 | -41.571 | 171.314 | -45.6885 | -85.6586 | -48.2306 | 59.3334 | -44.0751 | -134.475 | -31.5965 | -15.7438 | -20.0966 | 114.3102 | -36.8765 | 46.7415 | -38.3072 | 75.1849 | -54.4202 | 150.7662 | -44.9923 | 56.2834 | -16.6759 | -28.4511 | -11.5824 | -53.2301 | -15.7658 | -22.4526 | -9.0416 | -16.4416 | -32.6995 | -140.7986 | -22.9416 | -74.9208 | -19.4128 | -107.6038 | -13.019 | -129.4956 | -43.9328 | -34.1928 | -31.7628 | -32.5656 | -47.2961 | -28.7358 | -43.0035 | -44.1268 | -32.1734 | -32.7496 | -49.9371 | -28.7791 | -31.7135 | 519 | -20.2914 | -31.7614 | -20.5934 | -39.0726 | -19.7152 | -30.7383 | -20.0177 | -36.1875 | 519 | -38.8206 | -26.8672 | -27.2594 | -42.0504 | -23.4901 | -37.0251 | -38.8811 | -26.195 | -27.2203 | -41.3177 | -23.3905 | -37.6582 | -28.8866 | -26.4566 | -27.4434 | -44.6914 | -23.5334 | -25.7351 | -28.9471 | -25.7844 | -27.4043 | -43.9587 | -23.4338 | -26.3682
520 | -5.3272 | 0 | -5.3159 | 0 | -5.8781 | 0 | -5.3442 | 0 | -33.4029 | 87.6592 | -20.3991 | -139.3488 | -42.0915 | 155.0559 | -40.4788 | -57.9623 | -49.4933 | 50.5009 | -48.7799 | -105.4563 | -33.2011 | -27.1829 | -19.9928 | 103.8789 | -36.2027 | 32.0093 | -46.4487 | 68.925 | -50.9865 | 118.7776 | -54.0425 | 11.0612 | -16.3865 | -23.2195 | -10.8694 | -55.8487 | -17.5544 | -26.2277 | -9.2058 | -21.9523 | -30.441 | -113.7212 | -19.513 | -97.8292 | -21.6122 | -115.5204 | -13.7015 | -145.1238 | -44.1358 | -34.5847 | -31.5026 | -33.1514 | -49.085 | -29.0808 | -44.6479 | -46.8468 | -31.9952 | -33.4057 | -52.8784 | -28.9484 | -32.1758 | 520 | -20.159 | -32.5369 | -20.3504 | -40.6418 | -19.692 | -32.9317 | -19.9813 | -35.9921 | 520 | -41.5196 | -26.668 | -27.8242 | -43.7691 | -23.7649 | -38.7698 | -41.5309 | -26.1171 | -27.8072 | -43.2069 | -23.7366 | -39.3037 | -29.2575 | -26.1754 | -28.0785 | -47.5625 | -23.6325 | -26.2977 | -29.2688 | -25.6245 | -28.0615 | -47.0003 | -23.6042 | -26.8316
521 | -5.3528 | 0 | -5.388 | 0 | -5.8098 | 0 | -5.3177 | 0 | -35.1877 | 81.2352 | -20.524 | -150.9551 | -42.185 | 141.7993 | -36.4634 | -60.9659 | -50.795 | 45.5717 | -45.74 | -63.7511 | -35.3307 | -36.4477 | -20.1452 | 94.6876 | -35.5743 | 15.7881 | -48.8349 | -175.5094 | -49.528 | 93.1895 | -51.0241 | -120.2538 | -15.7256 | -19.8113 | -10.5126 | -59.8323 | -20.1844 | -16.6944 | -9.6667 | -29.7406 | -26.535 | -108.1671 | -17.4465 | -117.7378 | -24.2854 | -119.075 | -14.567 | -161.7336 | -44.5711 | -35.1531 | -31.3172 | -33.3992 | -50.0985 | -29.4266 | -46.1536 | -51.4583 | -31.7825 | -33.4778 | -55.9036 | -29.1497 | -32.8265 | 521 | -20.3495 | -32.7007 | -20.402 | -40.2018 | -19.8965 | -34.9857 | -20.1358 | -35.2855 | 521 | -46.1055 | -26.4297 | -28.0464 | -44.7105 | -24.0386 | -40.3438 | -46.0703 | -25.9727 | -28.0815 | -44.2887 | -24.1089 | -40.8359 | -29.8003 | -25.9644 | -28.125 | -50.5156 | -23.7617 | -27.0167 | -29.7651 | -25.5074 | -28.1601 | -50.0938 | -23.832 | -27.5088
522 | -5.3853 | 0 | -5.4586 | 0 | -5.8306 | 0 | -5.2707 | 0 | -37.3196 | 79.177 | -21.0472 | -162.9628 | -41.8763 | 122.4601 | -33.9722 | -70.2815 | -51.3809 | 43.4457 | -42.07 | -61.3795 | -38.1631 | -40.7779 | -20.5372 | 85.175 | -35.3878 | -1.9087 | -39.6751 | -175.2969 | -49.4035 | 70.6821 | -44.5183 | -149.2706 | -14.7762 | -19.7451 | -10.1705 | -65.8335 | -21.1252 | -3.818 | -10.2864 | -35.089 | -23.1563 | -118.3005 | -15.8291 | -137.6625 | -26.7475 | -112.3214 | -15.5471 | -179.6283 | -45.2667 | -35.9942 | -31.2325 | -33.2003 | -50.1456 | -29.8575 | -46.9547 | -64.1666 | -31.604 | -33.068 | -57.4899 | -29.4439 | -33.6208 | 522 | -20.911 | -32.2672 | -20.7987 | -38.7198 | -20.3253 | -35.6561 | -20.4674 | -34.7364 | 522 | -58.7813 | -26.2187 | -27.815 | -44.687 | -24.3989 | -41.1241 | -58.708 | -25.7734 | -27.9296 | -44.315 | -24.5868 | -41.684 | -30.6089 | -25.8472 | -27.6827 | -52.0313 | -23.9853 | -27.7902 | -30.5356 | -25.4019 | -27.7973 | -51.6593 | -24.1732 | -28.3501
523 | -5.408 | 0 | -5.5034 | 0 | -5.8873 | 0 | -5.2236 | 0 | -39.3821 | 86.5263 | -21.9424 | -171.6095 | -42.0654 | 100.9828 | -32.3594 | -81.6114 | -51.3618 | 39.3683 | -40.0709 | -62.1222 | -41.7398 | -35.4447 | -21.2166 | 77.4643 | -35.9032 | -19.5309 | -35.8718 | 172.0051 | -50.2879 | 53.7717 | -41.0044 | -164.9277 | -13.9036 | -21.4886 | -10.0162 | -72.9314 | -19.956 | 13.6433 | -11.1269 | -40.3857 | -20.5651 | -131.6672 | -14.6903 | -156.4683 | -26.6831 | -95.994 | -17.5091 | 163.2439 | -46.1904 | -37.1095 | -31.2083 | -32.7529 | -49.8115 | -30.1837 | -46.6128 | -56.2741 | -31.451 | -32.3471 | -57.0307 | -29.6881 | -34.4198 | 523 | -21.8235 | -31.5277 | -21.5039 | -37.751 | -21.0344 | -34.7487 | -21.0265 | -34.6147 | 523 | -50.8661 | -26.043 | -27.3449 | -44.3081 | -24.6803 | -40.7255 | -50.7707 | -25.5637 | -27.5293 | -43.9242 | -24.9601 | -41.3892 | -31.7015 | -25.8003 | -26.9391 | -51.5273 | -24.1847 | -28.5325 | -31.6061 | -25.321 | -27.1235 | -51.1434 | -24.4645 | -29.1962
524 | -5.4608 | 0 | -5.5299 | 0 | -5.9682 | 0 | -5.1552 | 0 | -40.1999 | 102.0515 | -23.2527 | -179.5292 | -42.9658 | 81.6526 | -31.3008 | -92.5396 | -51.489 | 30.6948 | -38.1033 | -65.0609 | -43.8011 | -7.7028 | -22.1408 | 70.1594 | -36.8571 | -34.7433 | -33.6815 | 159.3572 | -51.6416 | 42.8364 | -38.4886 | 179.7462 | -13.2097 | -26.6834 | -9.9764 | -81.3336 | -17.835 | 18.3168 | -12.232 | -44.1817 | -18.9174 | -145.181 | -13.9042 | -174.1282 | -24.5911 | -89.9711 | -19.1555 | 146.209 | -47.4043 | -38.5692 | -31.2728 | -32.2715 | -49.4629 | -30.4286 | -45.4869 | -48.3705 | -31.3983 | -31.5767 | -56.2564 | -29.9565 | -35.114 | 524 | -23.1206 | -30.7377 | -22.4992 | -36.7289 | -21.968 | -33.2155 | -21.7533 | -34.5017 | 524 | -42.9097 | -25.9375 | -26.8107 | -43.933 | -24.8987 | -39.5187 | -42.8406 | -25.4301 | -27.1163 | -43.4947 | -25.2734 | -40.3317 | -33.1084 | -25.812 | -26.1159 | -50.7265 | -24.4266 | -29.1458 | -33.0393 | -25.3046 | -26.4215 | -50.2882 | -24.8013 | -29.9588
525 | -5.4819 | 0 | -5.517 | 0 | -6.0795 | 0 | -5.0912 | 0 | -38.9405 | 114.3799 | -24.8731 | 178.4744 | -43.9425 | 63.8819 | -30.6679 | -105.6202 | -52.0073 | 20.6171 | -36.3822 | -74.6575 | -41.2765 | 15.2367 | -23.2326 | 66.6729 | -37.8773 | -48.3211 | -32.3232 | 146.9214 | -52.8977 | 37.5959 | -37.169 | 160.1852 | -12.829 | -32.2914 | -10.2037 | -89.6814 | -16.0706 | 15.1577 | -13.3721 | -44.7706 | -17.798 | -160.4024 | -13.5894 | 166.6813 | -22.5226 | -99.0375 | -22.2017 | 127.8756 | -49.0516 | -40.161 | -31.3993 | -31.7665 | -49.1454 | -30.5907 | -43.9897 | -44.1342 | -31.3959 | -30.81 | -56.0209 | -30.1381 | -35.706 | 525 | -24.6546 | -30.0376 | -23.6216 | -35.5804 | -23.0207 | -31.7694 | -22.5742 | -34.4361 | 525 | -38.6523 | -25.914 | -26.2846 | -43.6284 | -25.0737 | -37.9102 | -38.6172 | -25.3164 | -26.6753 | -43.0659 | -25.4995 | -38.8985 | -34.6791 | -25.9174 | -25.3281 | -50.5039 | -24.6211 | -29.6265 | -34.644 | -25.3198 | -25.7188 | -49.9414 | -25.0469 | -30.6148
526 | -5.4943 | 0 | -5.4863 | 0 | -6.1886 | 0 | -5.0427 | 0 | -36.8669 | 116.9843 | -26.476 | -178.4082 | -44.5623 | 45.7721 | -30.3525 | -116.8919 | -52.9241 | 10.3111 | -35.5446 | -85.8808 | -38.064 | 18.9013 | -24.2187 | 69.8531 | -39.3336 | -63.1277 | -31.4182 | 135.8493 | -53.7397 | 35.6803 | -36.9701 | 145.3805 | -12.5196 | -40.7044 | -10.6029 | -98.4654 | -14.6969 | 6.0304 | -14.2747 | -42.9674 | -16.9279 | -175.0597 | -13.2766 | 149.5324 | -20.8542 | -114.5818 | -26.6114 | 117.9673 | -50.8998 | -41.1646 | -31.564 | -31.3256 | -49.0678 | -30.6178 | -42.5488 | -41.384 | -31.4904 | -30.1543 | -56.1894 | -30.2824 | -36.1199 | 526 | -26.0348 | -29.4582 | -24.6191 | -34.9616 | -23.9165 | -30.5463 | -23.2718 | -34.9253 | 526 | -35.8897 | -25.9961 | -25.8313 | -43.5815 | -25.1315 | -36.3602 | -35.8977 | -25.3018 | -26.2829 | -42.8792 | -25.5751 | -37.5061 | -35.6703 | -26.0697 | -24.66 | -50.7031 | -24.7961 | -29.9313 | -35.6783 | -25.3754 | -25.1116 | -50.0008 | -25.2397 | -31.0772
527 | -5.5215 | 0 | -5.4215 | 0 | -6.2671 | 0 | -5.0038 | 0 | -35.0423 | 113.8327 | -26.8487 | -166.5591 | -46.729 | 21.05 | -30.1783 | -127.3637 | -54.2182 | 4.2825 | -35.0755 | -93.8975 | -35.7092 | 12.1076 | -24.3824 | 75.1197 | -41.9486 | -70.5096 | -30.724 | 124.279 | -53.8321 | 36.4631 | -36.9079 | 133.5383 | -12.8507 | -46.6708 | -11.2676 | -106.3644 | -13.9634 | -3.532 | -14.4406 | -36.5649 | -16.5854 | 172.2073 | -13.4078 | 132.2086 | -19.7778 | -133.4825 | -41.5014 | 102.3676 | -51.4361 | -40.7203 | -31.7081 | -31.0569 | -49.0323 | -30.5692 | -41.5152 | -39.4335 | -31.617 | -29.7121 | -56.277 | -30.4212 | -36.3506 | 527 | -26.1972 | -28.939 | -24.767 | -34.7392 | -24.0034 | -29.511 | -23.2829 | -35.6577 | 527 | -33.912 | -26.0955 | -25.5354 | -43.6108 | -25.1477 | -35.2481 | -34.012 | -25.3499 | -26.0531 | -42.7652 | -25.5654 | -36.5114 | -35.1988 | -26.1866 | -24.1906 | -50.8555 | -24.9997 | -30.0835 | -35.2988 | -25.441 | -24.7083 | -50.0099 | -25.4174 | -31.3468
528 | -5.5223 | 0 | -5.3591 | 0 | -6.3014 | 0 | -5.0066 | 0 | -33.6102 | 106.8458 | -25.813 | -156.6577 | -48.7752 | -0.0008 | -30.1202 | -138.1277 | -55.3233 | 0.3848 | -34.8522 | -103.8664 | -33.9783 | 2.6083 | -23.711 | 80.1642 | -44.8786 | -75.1338 | -30.159 | 112.6219 | -53.803 | 31.1695 | -37.6313 | 121.2597 | -13.4115 | -52.2233 | -12.0941 | -114.0569 | -13.6258 | -12.9265 | -14.0023 | -32.4417 | -16.6815 | 158.6689 | -13.6072 | 114.6242 | -18.86 | -152.013 | -30.6615 | -120.1413 | -50.398 | -39.331 | -31.8573 | -30.8779 | -49.0109 | -30.5039 | -40.7755 | -37.8821 | -31.7408 | -29.3972 | -56.1314 | -30.551 | -36.3969 | 528 | -25.127 | -28.5043 | -24.0646 | -34.6424 | -23.2905 | -28.6381 | -22.6828 | -36.794 | 528 | -32.3598 | -26.2185 | -25.3556 | -43.6518 | -25.1448 | -34.4741 | -32.523 | -25.4394 | -25.8713 | -42.7095 | -25.4973 | -35.7689 | -33.8087 | -26.335 | -23.8749 | -50.7723 | -25.1919 | -30.0955 | -33.9719 | -25.5559 | -24.3906 | -49.83 | -25.5444 | -31.3903
529 | -5.5054 | 0 | -5.2593 | 0 | -6.3296 | 0 | -5.0328 | 0 | -32.5199 | 98.4288 | -23.9958 | -151.8435 | -53.1857 | -39.5533 | -30.1883 | -149.622 | -56.4742 | -1.4098 | -34.6669 | -111.3111 | -32.7032 | -9.1392 | -22.476 | 82.1829 | -47.937 | -60.208 | -29.7374 | 101.3343 | -53.537 | 25.188 | -38.2336 | 111.9652 | -14.2621 | -57.0212 | -13.0807 | -121.6578 | -13.6326 | -22.7963 | -13.1264 | -30.5677 | -17.0952 | 146.3801 | -13.9855 | 98.7082 | -17.6575 | -170.3773 | -22.9838 | -132.9878 | -48.5907 | -37.5399 | -31.9657 | -30.7665 | -48.9931 | -30.4735 | -40.3218 | -36.6539 | -31.8765 | -29.1734 | -55.7242 | -30.7164 | -36.3783 | 529 | -23.4204 | -28.1827 | -22.7704 | -34.5781 | -22.071 | -27.9496 | -21.6323 | -37.6777 | 529 | -31.1485 | -26.3711 | -25.2611 | -43.7338 | -25.2142 | -33.9922 | -31.3946 | -25.5469 | -25.7337 | -42.6635 | -25.4407 | -35.289 | -32.0345 | -26.4603 | -23.668 | -50.4649 | -25.4571 | -30.0487 | -32.2806 | -25.6361 | -24.1406 | -49.3946 | -25.6836 | -31.3455
530 | -5.506 | 0 | -5.1876 | 0 | -6.2983 | 0 | -5.119 | 0 | -31.8069 | 86.4118 | -22.0978 | -155.8372 | -58.221 | -91.8014 | -30.5457 | -162.6853 | -57.0692 | -3.0679 | -34.8176 | -122.5901 | -31.89 | -23.0251 | -21.0555 | 78.0789 | -48.4957 | -36.7146 | -29.5852 | 88.1307 | -54.3485 | 13.6309 | -39.6217 | 105.8033 | -15.2944 | -59.0824 | -14.1629 | -127.9078 | -13.8374 | -35.4605 | -12.2563 | -34.789 | -18.1104 | 136.5859 | -14.6917 | 80.9465 | -16.8604 | 171.5027 | -19.4376 | -147.7288 | -46.726 | -35.6141 | -32.0249 | -30.7221 | -48.9838 | -30.5594 | -40.254 | -35.7397 | -32.0334 | -29.0938 | -55.1993 | -30.8491 | -36.4643 | 530 | -21.6556 | -28.1148 | -21.319 | -34.7721 | -20.7039 | -27.567 | -20.4327 | -38.9649 | 530 | -30.2337 | -26.5274 | -25.2161 | -43.7962 | -25.3718 | -33.9557 | -30.5521 | -25.7351 | -25.6031 | -42.6855 | -25.4404 | -35.135 | -30.1081 | -26.5189 | -23.5878 | -50.0117 | -25.6615 | -30.166 | -30.4265 | -25.7266 | -23.9748 | -48.901 | -25.7301 | -31.3453
531 | -5.5139 | 0 | -5.1147 | 0 | -6.2155 | 0 | -5.2246 | 0 | -31.4568 | 75.0104 | -20.5154 | -162.4946 | -54.7088 | -160.4313 | -31.2983 | -174.5033 | -57.7634 | -3.2774 | -35.4527 | -131.0114 | -31.4543 | -37.2631 | -19.8221 | 71.436 | -45.2552 | -18.596 | -29.7339 | 74.3765 | -55.9333 | 5.2642 | -40.216 | 107.3255 | -16.5078 | -54.8317 | -15.3753 | -132.1481 | -14.7182 | -45.7718 | -11.4513 | -39.8073 | -19.6497 | 134.9023 | -15.8508 | 65.133 | -16.4303 | 154.2263 | -17.1953 | -163.3991 | -45.407 | -34.0196 | -32.0445 | -30.8016 | -48.993 | -30.7735 | -40.5561 | -35.0866 | -32.1468 | -29.1499 | -54.6889 | -30.9694 | -36.6082 | 531 | -20.1776 | -28.3615 | -20.0404 | -35.3763 | -19.522 | -27.4929 | -19.3642 | -38.9443 | 531 | -29.5727 | -26.6329 | -25.2877 | -43.8783 | -25.6588 | -34.3406 | -29.9719 | -25.9313 | -25.577 | -42.7775 | -25.5489 | -35.3315 | -28.5057 | -26.5306 | -23.636 | -49.5742 | -25.8547 | -30.3927 | -28.9049 | -25.829 | -23.9253 | -48.4734 | -25.7448 | -31.3836
532 | -5.5673 | 0 | -5.0565 | 0 | -6.139 | 0 | -5.3333 | 0 | -31.4677 | 63.0512 | -19.3052 | -171.9943 | -48.9302 | 156.8027 | -32.5333 | 174.0191 | -57.7383 | 0.8725 | -36.121 | -139.3982 | -31.3948 | -51.7159 | -18.8611 | 63.0465 | -41.949 | -24.3287 | -30.3047 | 59.2974 | -58.4298 | -2.9557 | -40.2513 | 104.0067 | -16.9673 | -45.7762 | -16.5168 | -134.7469 | -15.9283 | -57.4793 | -10.9106 | -46.8686 | -21.2464 | 142.5486 | -17.5274 | 49.394 | -16.1016 | 138.4812 | -15.1199 | 179.5268 | -44.3956 | -32.7789 | -32.0509 | -30.9542 | -48.9347 | -31.0719 | -41.1815 | -34.596 | -32.2235 | -29.4822 | -54.4901 | -31.1507 | -36.9184 | 532 | -19.0445 | -28.9519 | -19.018 | -35.871 | -18.6051 | -27.8016 | -18.531 | -37.9682 | 532 | -29.0287 | -26.6562 | -25.3869 | -43.8782 | -26.0154 | -35.0425 | -29.5395 | -26.0845 | -25.6209 | -42.7957 | -25.7386 | -35.8482 | -27.2116 | -26.4836 | -23.9149 | -49.4336 | -26.0942 | -30.7794 | -27.7224 | -25.9119 | -24.1489 | -48.3511 | -25.8174 | -31.5851
533 | -5.6462 | 0 | -5.0212 | 0 | -6.0446 | 0 | -5.4352 | 0 | -31.821 | 51.8172 | -18.4725 | 177.4225 | -45.386 | 126.7851 | -34.3734 | 164.3806 | -56.4195 | 0.6651 | -37.0356 | -147.4807 | -31.6986 | -67.387 | -18.2027 | 53.2438 | -40.2226 | -34.8708 | -31.4541 | 44.1874 | -63.6762 | -2.1533 | -40.9016 | 98.2599 | -16.3085 | -36.5578 | -17.4876 | -136.4427 | -18.02 | -67.905 | -10.6122 | -55.033 | -21.3319 | 153.7479 | -19.9295 | 36.0616 | -15.9745 | 124.3642 | -13.8162 | 163.5371 | -43.8525 | -31.8603 | -32.001 | -31.2588 | -48.9111 | -31.3877 | -42.0641 | -34.2673 | -32.3024 | -29.986 | -54.7048 | -31.279 | -36.9413 | 533 | -18.2677 | -29.8924 | -18.3038 | -36.3995 | -17.9867 | -28.563 | -17.9798 | -37.528 | 533 | -28.6211 | -26.6562 | -25.6126 | -43.8899 | -26.3665 | -36.0195 | -29.2461 | -26.2578 | -25.8236 | -42.8665 | -25.9525 | -36.6289 | -26.2141 | -26.3548 | -24.3398 | -49.6836 | -26.2578 | -30.8967 | -26.8391 | -25.9564 | -24.5508 | -48.6602 | -25.8438 | -31.5061
534 | -5.785 | 0 | -5.0118 | 0 | -5.9378 | 0 | -5.5246 | 0 | -32.4845 | 39.8652 | -17.9555 | 165.7038 | -43.4918 | 102.2679 | -36.9864 | 160.3106 | -55.2428 | -8.9572 | -38.8651 | -155.4507 | -32.3318 | -81.6524 | -17.7904 | 42.379 | -39.0195 | -43.0454 | -33.3491 | 29.2236 | -66.6433 | 63.0538 | -41.5582 | 98.039 | -14.6171 | -35.2701 | -18.0004 | -137.214 | -20.3308 | -78.1625 | -10.5484 | -68.3219 | -19.1494 | 169.2707 | -24.2011 | 26.2414 | -16.0363 | 111.1726 | -12.9658 | 147.5105 | -43.7143 | -31.1519 | -31.9992 | -31.6166 | -49.0072 | -31.6598 | -43.0665 | -34.0901 | -32.3124 | -30.6954 | -55.5509 | -31.3948 | -36.6588 | 534 | -17.7934 | -31.1492 | -17.8669 | -37.5054 | -17.6089 | -29.7995 | -17.6536 | -37.0908 | 534 | -28.3051 | -26.5274 | -25.8316 | -43.9954 | -26.648 | -37.1287 | -29.0783 | -26.3746 | -26.092 | -43.0694 | -26.1352 | -37.5419 | -25.3669 | -26.2142 | -24.9104 | -50.5391 | -26.383 | -30.721 | -26.1401 | -26.0614 | -25.1708 | -49.6131 | -25.8702 | -31.1342
535 | -5.9361 | 0 | -5.0036 | 0 | -5.852 | 0 | -5.5801 | 0 | -33.4094 | 29.7355 | -17.7437 | 154.6062 | -41.9646 | 85.8734 | -39.9779 | 167.3626 | -54.6719 | -19.2129 | -41.2214 | -154.6864 | -33.1945 | -97.1834 | -17.6501 | 30.9727 | -37.7632 | -53.9355 | -36.4034 | 15.4085 | -59.8647 | 81.0424 | -41.5584 | 94.9839 | -13.0929 | -37.2267 | -18.3037 | -139.1968 | -23.6521 | -84.4194 | -10.7053 | -76.6521 | -16.4715 | 167.6864 | -28.9508 | 43.1023 | -16.2009 | 97.2592 | -12.1017 | 134.049 | -43.8115 | -30.7263 | -32.0096 | -32.0185 | -49.1279 | -31.9958 | -43.9607 | -34.0512 | -32.3346 | -31.4021 | -56.9411 | -31.5786 | -36.2332 | 535 | -17.6115 | -32.518 | -17.6985 | -38.4616 | -17.4896 | -31.4925 | -17.5752 | -36.2296 | 535 | -28.1151 | -26.3985 | -26.0824 | -44.1243 | -26.9922 | -38.1087 | -29.0476 | -26.4826 | -26.4384 | -43.2759 | -26.4157 | -38.3806 | -24.7902 | -26.0735 | -25.466 | -51.9375 | -26.575 | -30.3812 | -25.7227 | -26.1576 | -25.822 | -51.0891 | -25.9985 | -30.6531
536 | -6.108 | 0 | -5.0436 | 0 | -5.7538 | 0 | -5.5902 | 0 | -34.5887 | 20.8432 | -17.8425 | 142.7049 | -40.3478 | 68.7385 | -41.224 | -170.6142 | -54.3576 | -28.9463 | -43.0238 | -144.3888 | -34.2974 | -110.8302 | -17.7658 | 20.5639 | -36.9567 | -66.9511 | -41.5802 | 7.8961 | -56.6204 | 77.5421 | -42.2516 | 90.4971 | -11.7862 | -43.0077 | -18.3734 | -142.2918 | -30.5239 | -81.1199 | -11.2174 | -85.419 | -14.1347 | 163.2505 | -29.8623 | 101.6563 | -16.7533 | 89.5434 | -11.811 | 119.0919 | -44.1718 | -30.4992 | -32.0174 | -32.375 | -49.3437 | -32.3078 | -44.7429 | -34.1405 | -32.3424 | -31.9733 | -58.4889 | -31.6718 | -35.7093 | 536 | -17.7278 | -33.6983 | -17.8095 | -38.362 | -17.6194 | -33.5317 | -17.7324 | -35.7964 | 536 | -28.0325 | -26.2344 | -26.267 | -44.3001 | -27.2642 | -38.9891 | -29.0969 | -26.5886 | -26.7848 | -43.5899 | -26.7176 | -39.1527 | -24.3912 | -25.9094 | -25.8653 | -53.4453 | -26.6282 | -29.9555 | -25.4556 | -26.2636 | -26.3831 | -52.7351 | -26.0816 | -30.1191
537 | -6.2674 | 0 | -5.0682 | 0 | -5.7166 | 0 | -5.5643 | 0 | -36.0632 | 11.8814 | -18.1867 | 132.829 | -39.2238 | 48.4408 | -39.4662 | -154.7093 | -54.0499 | -39.0358 | -44.108 | -129.063 | -35.7251 | -125.6452 | -18.1792 | 9.4033 | -36.8444 | -79.4258 | -52.057 | 44.3514 | -54.563 | 74.1541 | -43.9205 | 91.7546 | -10.7917 | -51.6815 | -18.3099 | -147.2488 | -34.3859 | -30.4303 | -11.7177 | -97.3283 | -12.3437 | 155.5565 | -23.8631 | 113.257 | -17.2928 | 81.9455 | -11.7203 | 105.7969 | -44.6182 | -30.5792 | -32.001 | -32.6964 | -49.5323 | -32.5635 | -45.3924 | -34.4666 | -32.3377 | -32.3025 | -59.4666 | -31.9275 | -35.4612 | 537 | -18.0829 | -34.3821 | -18.1435 | -37.8958 | -18.0458 | -35.5701 | -18.1659 | -36.0059 | 537 | -28.1992 | -26.0703 | -26.429 | -44.4641 | -27.4953 | -39.6758 | -29.3984 | -26.6211 | -27.1321 | -43.8157 | -26.9992 | -39.8281 | -24.3118 | -25.7336 | -26.0351 | -54.3984 | -26.8593 | -29.7446 | -25.511 | -26.2844 | -26.7382 | -53.75 | -26.3632 | -29.8969
538 | -6.389 | 0 | -5.0889 | 0 | -5.6826 | 0 | -5.5113 | 0 | -37.8997 | 7.0207 | -18.7954 | 123.4711 | -38.8538 | 29.5368 | -37.1373 | -150.8962 | -54.0172 | -50.5488 | -42.8367 | -108.0352 | -37.632 | -140.9377 | -18.8341 | -0.0455 | -36.8515 | -88.7413 | -43.4854 | 118.5088 | -52.6795 | 69.3186 | -44.2969 | 102.6877 | -10.1345 | -60.8086 | -18.2365 | -153.8553 | -29.306 | 11.3876 | -12.801 | -107.2208 | -10.9564 | 145.3261 | -20.3013 | 106.6089 | -18.0597 | 78.3773 | -11.859 | 92.2302 | -45.346 | -30.967 | -32.0289 | -32.9046 | -49.5648 | -32.9436 | -45.8819 | -35.0459 | -32.3538 | -32.3584 | -59.6045 | -32.1631 | -35.3101 | 538 | -18.7002 | -34.4433 | -18.7154 | -37.3 | -18.7101 | -36.5224 | -18.807 | -36.0373 | 538 | -28.6569 | -25.9648 | -26.5156 | -44.4759 | -27.8547 | -40.1993 | -29.957 | -26.6712 | -27.3933 | -43.8822 | -27.4323 | -40.3706 | -24.578 | -25.6399 | -25.9694 | -54.5156 | -27.0742 | -29.6275 | -25.8781 | -26.3463 | -26.8471 | -53.9219 | -26.6518 | -29.7988
539 | -6.5021 | 0 | -5.1119 | 0 | -5.6864 | 0 | -5.4236 | 0 | -40.0311 | 5.0681 | -19.6921 | 113.0017 | -38.8045 | 12.6529 | -35.2849 | -157.115 | -54.1789 | -61.8893 | -39.8649 | -102.1577 | -40.3714 | -156.8166 | -19.8001 | -8.2614 | -36.6512 | -98.7713 | -37.6699 | 111.4814 | -50.9352 | 61.4917 | -43.5573 | 107.8632 | -9.6447 | -72.7304 | -18.0967 | -161.2763 | -25.3257 | 4.8121 | -13.9161 | -118.3155 | -9.9858 | 135.1437 | -17.9911 | 95.667 | -18.6143 | 77.2059 | -12.3548 | 80.145 | -46.3221 | -31.6545 | -32.0599 | -32.9744 | -49.7049 | -33.217 | -46.1041 | -35.8583 | -32.3732 | -32.2642 | -58.522 | -32.413 | -35.2085 | 539 | -19.5996 | -33.9875 | -19.5335 | -36.222 | -19.6742 | -35.6724 | -19.7118 | -35.7129 | 539 | -29.3562 | -25.8711 | -26.4723 | -44.593 | -28.1051 | -40.4177 | -30.7464 | -26.6868 | -27.5508 | -44.0185 | -27.7934 | -40.6805 | -25.1524 | -25.5578 | -25.7621 | -53.4101 | -27.3011 | -29.5221 | -26.5426 | -26.3735 | -26.8406 | -52.8356 | -26.9894 | -29.7849
540 | -6.5377 | 0 | -5.1193 | 0 | -5.6681 | 0 | -5.3335 | 0 | -42.0281 | 10.7704 | -20.8812 | 107.4299 | -38.6627 | -2.969 | -33.9473 | -163.8834 | -54.0484 | -71.944 | -37.724 | -107.1686 | -44.492 | -173.9033 | -21.0665 | -15.1936 | -36.7019 | -110.858 | -34.6429 | 98.8158 | -49.5697 | 51.2409 | -43.0075 | 112.0718 | -9.4979 | -83.5396 | -17.984 | -169.6436 | -23.3614 | -0.9455 | -15.6306 | -127.1217 | -9.2912 | 124.2473 | -16.5292 | 84.1246 | -18.7148 | 79.9269 | -13.2345 | 69.3876 | -47.8335 | -32.683 | -32.0604 | -32.935 | -49.9155 | -33.351 | -46.0646 | -36.8752 | -32.4205 | -32.0373 | -56.4592 | -32.7853 | -35.1199 | 540 | -20.7767 | -33.2828 | -20.5872 | -35.102 | -20.9303 | -34.0903 | -20.8534 | -35.6102 | 540 | -30.3375 | -25.8828 | -26.3973 | -44.7962 | -28.2317 | -40.3965 | -31.7559 | -26.7524 | -27.6015 | -44.2474 | -28.0175 | -40.7311 | -26.1453 | -25.5227 | -25.4996 | -51.3399 | -27.666 | -29.4518 | -27.5637 | -26.3923 | -26.7038 | -50.7911 | -27.4518 | -29.7864
541 | -6.5253 | 0 | -5.1386 | 0 | -5.6698 | 0 | -5.2362 | 0 | -42.9032 | 20.9052 | -22.3455 | 103.1553 | -38.7207 | -21.2963 | -32.9931 | -172.4473 | -53.9735 | -85.7594 | -36.319 | -113.254 | -52.1606 | 170.4483 | -22.5886 | -18.1964 | -37.1924 | -120.9182 | -32.804 | 85.2609 | -48.6596 | 38.8745 | -41.411 | 116.4386 | -9.5868 | -96.2482 | -17.8008 | -179.1244 | -22.1495 | -15.7872 | -17.7163 | -134.55 | -8.839 | 113.6603 | -15.2499 | 71.6591 | -18.2626 | 83.894 | -14.5457 | 59.995 | -49.6613 | -34.0715 | -31.9894 | -32.884 | -49.9699 | -33.4816 | -45.9081 | -38.1581 | -32.5722 | -31.8456 | -54.705 | -33.2323 | -35.0982 | 541 | -22.2094 | -32.5396 | -21.8293 | -34.2985 | -22.4361 | -32.6438 | -22.1421 | -35.579 | 541 | -31.6328 | -26.0469 | -26.3587 | -44.8313 | -28.343 | -40.2383 | -33.0195 | -26.9024 | -27.6478 | -44.3001 | -28.2454 | -40.6719 | -27.5462 | -25.4641 | -25.3203 | -49.5664 | -28.0937 | -29.4284 | -28.9329 | -26.3196 | -26.6094 | -49.0352 | -27.9961 | -29.862
542 | -6.4668 | 0 | -5.1561 | 0 | -5.681 | 0 | -5.1586 | 0 | -42.2963 | 30.1555 | -23.8261 | 105.2546 | -39.5865 | -42.386 | -32.3197 | 178.7093 | -54.5712 | -101.6448 | -34.9434 | -118.2718 | -63.465 | -43.4228 | -24.1289 | -15.6981 | -37.6255 | -128.2826 | -31.6578 | 71.8426 | -48.3967 | 26.203 | -39.4718 | 113.0547 | -9.96 | -107.6644 | -17.5858 | 171.0573 | -21.802 | -28.546 | -19.9094 | -136.3993 | -8.7081 | 103.338 | -14.6374 | 59.9736 | -17.1139 | 84.5 | -16.3696 | 53.697 | -51.0812 | -35.903 | -31.8489 | -32.8898 | -49.6437 | -33.5514 | -45.7382 | -39.8412 | -32.7481 | -31.7225 | -53.6991 | -33.7474 | -35.2032 | 542 | -23.6526 | -31.8802 | -22.9669 | -33.6265 | -23.9385 | -31.5639 | -23.3159 | -35.2265 | 542 | -33.3744 | -26.2813 | -26.423 | -44.4876 | -28.3953 | -40.0572 | -34.6851 | -27.0671 | -27.7312 | -43.9627 | -28.3928 | -40.5796 | -29.4362 | -25.3821 | -25.2557 | -48.543 | -28.5913 | -29.5222 | -30.7469 | -26.1679 | -26.5639 | -48.0181 | -28.5888 | -30.0446
543 | -6.3734 | 0 | -5.1557 | 0 | -5.6789 | 0 | -5.1324 | 0 | -41.1876 | 32.3275 | -24.637 | 113.6529 | -41.3468 | -59.3248 | -31.8647 | 169.5687 | -55.9268 | -115.685 | -33.7707 | -127.0571 | -49.9262 | -50.7343 | -25.0176 | -7.1214 | -37.858 | -136.7669 | -31.0146 | 58.7783 | -48.834 | 15.1672 | -38.2218 | 104.6698 | -10.6126 | -119.9083 | -17.2999 | 160.8502 | -22.4558 | -40.8675 | -22.5078 | -128.3915 | -8.8252 | 93.2568 | -14.3349 | 48.2477 | -15.8687 | 80.9023 | -18.4894 | 53.8527 | -51.0456 | -38.1352 | -31.6344 | -32.9948 | -49.0925 | -33.7016 | -45.4565 | -42.0851 | -32.9125 | -31.601 | -53.3784 | -34.2414 | -35.4355 | 543 | -24.4522 | -31.3694 | -23.4596 | -33.0488 | -24.7842 | -30.8889 | -23.8809 | -34.8487 | 543 | -35.7117 | -26.5391 | -26.6214 | -43.9368 | -28.5459 | -39.7776 | -36.9294 | -27.2336 | -27.8624 | -43.4136 | -28.5692 | -40.3241 | -31.7618 | -25.261 | -25.2276 | -48.2227 | -29.0857 | -29.7566 | -32.9795 | -25.9555 | -26.4686 | -47.6995 | -29.109 | -30.3031
544 | -6.2703 | 0 | -5.1501 | 0 | -5.7124 | 0 | -5.1087 | 0 | -40.3781 | 28.0958 | -24.0283 | 123.879 | -43.7344 | -76.6811 | -31.5876 | 158.2578 | -57.4536 | -124.3527 | -33.1125 | -137.1158 | -45.8094 | -66.3713 | -24.478 | 2.3282 | -38.4081 | -146.4782 | -30.7501 | 45.0396 | -49.6082 | 9.2518 | -37.1964 | 97.4267 | -11.643 | -131.6333 | -17.0048 | 149.7716 | -23.2979 | -58.2549 | -23.3265 | -110.7986 | -9.1596 | 84.4237 | -14.3515 | 38.0395 | -14.7912 | 75.4141 | -19.9151 | 62.8958 | -49.6025 | -40.239 | -31.3907 | -33.165 | -48.5088 | -33.8914 | -45.154 | -45.1889 | -32.9968 | -31.6189 | -53.529 | -34.5561 | -35.9143 | 544 | -23.8836 | -31.0388 | -22.8926 | -32.7369 | -24.2751 | -30.5623 | -23.3741 | -34.6102 | 544 | -38.9186 | -26.7265 | -26.8947 | -43.3587 | -28.7413 | -39.4416 | -40.0388 | -27.2844 | -28.0563 | -42.7964 | -28.7827 | -40.0453 | -33.9687 | -25.1204 | -25.3486 | -48.3789 | -29.406 | -30.2019 | -35.0889 | -25.6783 | -26.5102 | -47.8166 | -29.4474 | -30.8056
545 | -6.1737 | 0 | -5.1563 | 0 | -5.7227 | 0 | -5.1426 | 0 | -40.1288 | 20.4589 | -22.3826 | 126.0671 | -47.729 | -100.0801 | -31.5469 | 148.0061 | -59.3088 | -133.9084 | -32.7113 | -147.3948 | -43.8689 | -84.1201 | -22.8678 | 6.2828 | -38.9511 | -152.2602 | -30.8664 | 32.2906 | -49.5762 | 6.2809 | -36.2298 | 86.436 | -13.1779 | -142.7526 | -16.735 | 137.6211 | -24.709 | -79.7639 | -22.09 | -99.9313 | -9.8514 | 77.952 | -14.7851 | 27.9827 | -13.9999 | 68.0726 | -20.2824 | 83.9143 | -47.7629 | -40.1161 | -31.147 | -33.4049 | -48.1152 | -34.0594 | -44.854 | -50.3748 | -32.847 | -31.7145 | -53.8092 | -34.6777 | -36.564 | 545 | -22.2978 | -30.9768 | -21.5407 | -32.5674 | -22.7286 | -30.5988 | -22.0592 | -34.2414 | 545 | -44.2011 | -26.6733 | -27.2312 | -42.9589 | -28.9031 | -39.1313 | -45.2185 | -27.1243 | -28.2623 | -42.3925 | -28.9168 | -39.7114 | -33.9424 | -24.9733 | -25.5408 | -48.6529 | -29.5214 | -30.8413 | -34.9598 | -25.4243 | -26.5719 | -48.0865 | -29.5351 | -31.4214
546 | -6.0971 | 0 | -5.1494 | 0 | -5.7596 | 0 | -5.1885 | 0 | -40.326 | 12.3785 | -20.7296 | 123.3717 | -56.5506 | -124.8592 | -31.7273 | 136.6257 | -61.2498 | -133.3847 | -32.6341 | -158.1968 | -43.0266 | -103.627 | -21.2407 | 3.767 | -39.8599 | -161.1341 | -31.2824 | 20.14 | -49.5176 | 2.3253 | -35.7634 | 76.4375 | -15.2767 | -150.5869 | -16.5234 | 125.8097 | -26.2124 | -106.6066 | -20.0264 | -101.4499 | -10.7934 | 73.5206 | -15.2278 | 19.4143 | -13.5318 | 60.2571 | -18.257 | 92.7546 | -46.1865 | -38.2858 | -30.9712 | -33.6284 | -47.9102 | -34.2602 | -44.4889 | -57.0486 | -32.558 | -31.914 | -54.2327 | -34.7614 | -37.3927 | 546 | -20.6811 | -31.1613 | -20.1454 | -32.6106 | -21.1531 | -30.9404 | -20.6933 | -34.2055 | 546 | -50.9515 | -26.4609 | -27.5313 | -42.7608 | -29.1108 | -38.7293 | -51.8992 | -26.7984 | -28.4399 | -42.1506 | -29.0717 | -39.3004 | -32.1887 | -24.8741 | -25.8169 | -49.0833 | -29.612 | -31.6331 | -33.1364 | -25.2116 | -26.7255 | -48.4731 | -29.5729 | -32.2042
547 | -6.0495 | 0 | -5.1515 | 0 | -5.7973 | 0 | -5.2702 | 0 | -40.9308 | 5.7596 | -19.3207 | 118.4323 | -56.5703 | 89.4808 | -32.14 | 125.5214 | -62.7483 | -125.5919 | -32.712 | -166.7678 | -42.9759 | -124.4502 | -19.844 | -3.7469 | -40.9392 | -164.3278 | -31.9816 | 8.2288 | -49.1515 | -4.1271 | -35.3937 | 62.9905 | -18.1954 | -153.0252 | -16.3726 | 114.0755 | -27.4164 | -145.0185 | -18.4172 | -107.3812 | -11.7453 | 71.7245 | -15.8521 | 11.0227 | -13.2395 | 51.8386 | -16.0159 | 92.5686 | -44.9828 | -35.9842 | -30.877 | -33.8148 | -47.8188 | -34.5154 | -44.1593 | -52.2934 | -32.1667 | -32.2218 | -54.8468 | -34.77 | -38.3275 | 547 | -19.29 | -31.5978 | -18.9145 | -32.6899 | -19.7895 | -31.5727 | -19.4738 | -34.1847 | 547 | -46.2439 | -26.1172 | -27.7653 | -42.6673 | -29.3639 | -38.362 | -47.1419 | -26.3694 | -28.5446 | -42.0215 | -29.2452 | -38.8891 | -29.9347 | -24.8275 | -26.1723 | -49.6953 | -29.6185 | -32.5302 | -30.8327 | -25.0797 | -26.9516 | -49.0495 | -29.4998 | -33.0573
548 | -6.0535 | 0 | -5.13 | 0 | -5.8103 | 0 | -5.3155 | 0 | -41.9013 | -1.4751 | -18.3273 | 106.8618 | -47.892 | 43.2057 | -32.8291 | 114.4203 | -61.1366 | -119.3721 | -33.2348 | -176.49 | -43.8337 | -142.9604 | -18.8509 | -13.268 | -42.9002 | -164.7903 | -32.9978 | -1.7543 | -49.5924 | -10.6614 | -35.4574 | 53.3184 | -20.8988 | -139.991 | -16.4146 | 101.4218 | -26.6381 | 176.6829 | -17.181 | -119.1777 | -12.4599 | 75.8926 | -16.6848 | 3.7536 | -13.2207 | 44.5401 | -14.1663 | 87.0459 | -44.2113 | -33.9893 | -30.9513 | -33.8988 | -47.7973 | -34.8917 | -43.8526 | -45.4978 | -31.8856 | -32.5753 | -55.2706 | -34.9861 | -39.1999 | 548 | -18.3035 | -32.3164 | -18.0425 | -33.0819 | -18.8201 | -32.5665 | -18.5965 | -34.5982 | 548 | -39.4443 | -25.8321 | -27.8453 | -42.6673 | -29.7617 | -38.0423 | -40.3678 | -26.0753 | -28.5833 | -41.987 | -29.5762 | -38.5371 | -27.9358 | -24.8978 | -26.5218 | -50.1406 | -29.8561 | -33.3896 | -28.8593 | -25.141 | -27.2598 | -49.4603 | -29.6706 | -33.8844
549 | -6.0919 | 0 | -5.1036 | 0 | -5.8341 | 0 | -5.3888 | 0 | -43.3344 | -8.4865 | -17.6975 | 95.9137 | -44.1778 | 22.805 | -33.7811 | 104.5466 | -59.2741 | -131.2097 | -34.0348 | 176.3092 | -45.2801 | -162.9865 | -18.2493 | -24.3454 | -43.1097 | -150.2127 | -34.2961 | -11.0387 | -50.0126 | -15.1305 | -35.6679 | 40.72 | -20.3878 | -114.707 | -16.6343 | 89.7188 | -25.0602 | 147.7163 | -16.4111 | -131.1595 | -12.2099 | 81.9417 | -17.9055 | 0.1008 | -13.5162 | 37.4102 | -13.0089 | 79.252 | -43.9819 | -32.4936 | -31.0952 | -33.896 | -47.8296 | -35.4233 | -43.6505 | -41.8654 | -31.7482 | -32.9513 | -55.0216 | -35.1036 | -40.0362 | 549 | -17.6759 | -33.3136 | -17.4944 | -33.6218 | -18.2266 | -33.8564 | -18.0666 | -34.815 | 549 | -35.7735 | -25.6563 | -27.8041 | -42.726 | -30.3197 | -37.8164 | -36.7618 | -25.9141 | -28.5072 | -41.9955 | -30.0345 | -38.2617 | -26.4017 | -25.0033 | -26.8594 | -49.918 | -30 | -34.2021 | -27.39 | -25.2611 | -27.5625 | -49.1875 | -29.7148 | -34.6474
550 | -6.1842 | 0 | -5.0894 | 0 | -5.8231 | 0 | -5.452 | 0 | -45.2303 | -10.8904 | -17.4336 | 84.07 | -41.5558 | 8.7114 | -35.0108 | 94.497 | -59.0121 | -148.3999 | -34.7742 | 173.0877 | -47.0797 | 178.3464 | -17.9797 | -35.6875 | -40.8909 | -147.3842 | -35.8709 | -17.1536 | -50.529 | -19.8516 | -36.423 | 27.7253 | -17.2728 | -107.5005 | -17.163 | 79.1521 | -23.1997 | 124.1511 | -15.6436 | -144.5398 | -11.3246 | 85.7213 | -18.8925 | -3.422 | -13.9739 | 31.4805 | -12.3477 | 71.5255 | -44.0536 | -31.4709 | -31.2812 | -33.8348 | -47.9559 | -35.8694 | -43.4488 | -39.5614 | -31.7936 | -33.312 | -54.1714 | -35.3973 | -40.5057 | 550 | -17.4096 | -34.6006 | -17.2804 | -33.9335 | -17.9522 | -35.418 | -17.849 | -34.9732 | 550 | -33.3772 | -25.6094 | -27.6506 | -42.8665 | -30.78 | -37.6257 | -34.472 | -25.9705 | -28.3828 | -42.1328 | -30.4174 | -37.9968 | -25.2867 | -25.097 | -27.1278 | -49.082 | -30.3079 | -34.6826 | -26.3815 | -25.4581 | -27.86 | -48.3483 | -29.9453 | -35.0537
551 | -6.3234 | 0 | -5.0892 | 0 | -5.8223 | 0 | -5.4886 | 0 | -47.2073 | -8.8158 | -17.5028 | 72.9152 | -39.5261 | -7.8283 | -36.5564 | 85.0042 | -59.6853 | -163.6521 | -35.5545 | 170.1127 | -48.9757 | 159.544 | -18.0143 | -47.3635 | -39.5023 | -154.2702 | -37.5787 | -18.6251 | -51.3816 | -21.7482 | -37.7735 | 17.7089 | -14.683 | -110.4289 | -17.892 | 69.684 | -21.7523 | 106.2485 | -15.7825 | -159.2687 | -10.0765 | 85.4744 | -19.9946 | -3.7385 | -14.5701 | 27.8678 | -11.969 | 62.0735 | -44.487 | -30.8139 | -31.4673 | -33.8229 | -48.2722 | -36.4232 | -43.2376 | -37.9707 | -31.9835 | -33.6751 | -53.3119 | -35.6192 | -40.4698 | 551 | -17.471 | -36.1784 | -17.3825 | -34.079 | -17.9801 | -37.1093 | -17.9214 | -35.4304 | 551 | -31.6473 | -25.6601 | -27.4995 | -43.183 | -31.334 | -37.4153 | -32.8815 | -26.1612 | -28.3343 | -42.4499 | -30.9346 | -37.749 | -24.4905 | -25.1439 | -27.3517 | -48.2227 | -30.53 | -34.6475 | -25.7247 | -25.645 | -28.1865 | -47.4896 | -30.1306 | -34.9812
552 | -6.4824 | 0 | -5.0617 | 0 | -5.8092 | 0 | -5.4912 | 0 | -48.9434 | -5.0714 | -17.8524 | 61.9032 | -38.5365 | -27.6987 | -38.5336 | 73.9702 | -60.7684 | 179.9974 | -36.3615 | 169.7181 | -50.633 | 139.5013 | -18.3663 | -58.3678 | -38.626 | -161.4588 | -39.1318 | -18.3108 | -52.0735 | -20.1548 | -39.3391 | 11.2647 | -12.6043 | -122.1259 | -19.0813 | 62.4094 | -21.1738 | 89.9643 | -15.1969 | -173.6355 | -8.849 | 81.8887 | -21.1839 | 0.2494 | -15.1902 | 25.968 | -11.8764 | 53.4158 | -45.2252 | -30.5195 | -31.724 | -33.772 | -48.6705 | -37.0195 | -43.1516 | -36.9107 | -32.2598 | -33.9172 | -52.8391 | -35.8756 | -40.3863 | 552 | -17.8121 | -38.1316 | -17.7552 | -34.2941 | -18.323 | -38.6335 | -18.2958 | -35.8527 | 552 | -30.4283 | -25.7774 | -27.2896 | -43.6088 | -31.9578 | -37.3424 | -31.849 | -26.4506 | -28.2808 | -42.8613 | -31.5283 | -37.6604 | -24.0371 | -25.2416 | -27.4348 | -47.7774 | -30.8139 | -34.5771 | -25.4578 | -25.9148 | -28.426 | -47.0299 | -30.3844 | -34.8951
553 | -6.6584 | 0 | -5.0334 | 0 | -5.799 | 0 | -5.5217 | 0 | -50.6887 | 1.3026 | -18.4547 | 51.2654 | -38.3869 | -42.502 | -41.1849 | 66.1453 | -61.9696 | 163.4176 | -36.5479 | 173.0355 | -51.5189 | 117.4044 | -19.0166 | -70.3663 | -37.6202 | -169.9809 | -40.2099 | -13.9717 | -51.9546 | -16.8733 | -41.2517 | 4.4512 | -11.2253 | -133.3208 | -20.1743 | 59.0391 | -20.5278 | 76.1152 | -15.3176 | 171.2762 | -7.9595 | 76.2888 | -21.848 | 6.3945 | -15.6382 | 25.1588 | -12.0388 | 44.1633 | -45.9234 | -30.4742 | -31.943 | -33.7789 | -49.0523 | -37.3531 | -43.2053 | -36.1857 | -32.5959 | -34.1154 | -53.0451 | -36.2795 | -40.1184 | 553 | -18.4082 | -40.691 | -18.3651 | -34.353 | -18.9547 | -39.6374 | -18.958 | -35.9464 | 553 | -29.5273 | -25.9375 | -27.1205 | -44.0189 | -32.3197 | -37.4063 | -31.1523 | -26.7969 | -28.2572 | -43.2533 | -31.8314 | -37.6836 | -23.8158 | -25.2846 | -27.457 | -48.0117 | -31.2461 | -34.3194 | -25.4408 | -26.144 | -28.5937 | -47.2461 | -30.7578 | -34.5967
554 | -6.8254 | 0 | -5.0325 | 0 | -5.7794 | 0 | -5.5072 | 0 | -52.9169 | 14.021 | -19.2883 | 41.6193 | -38.3361 | -53.7122 | -45.2252 | 61.1401 | -63.4726 | 139.9371 | -36.1979 | 173.5887 | -51.168 | 95.3546 | -19.9661 | -79.4645 | -37.1532 | 177.1101 | -40.9279 | -9.5301 | -51.3043 | -14.0863 | -43.9681 | 5.4007 | -10.1478 | -146.6197 | -21.4195 | 61.7024 | -20.7914 | 63.1417 | -15.6358 | 155.2036 | -7.3106 | 68.9526 | -21.8281 | 12.4915 | -15.8022 | 25.2258 | -12.2516 | 35.7413 | -46.3327 | -30.7124 | -32.1451 | -33.8132 | -49.4265 | -37.8257 | -43.5443 | -35.7169 | -32.927 | -34.3489 | -54.1029 | -36.4943 | -39.7472 | 554 | -19.2327 | -44.4876 | -19.1899 | -34.1214 | -19.8807 | -40.1859 | -19.9143 | -36.1957 | 554 | -28.8915 | -26.1016 | -26.9878 | -44.394 | -32.7932 | -37.7649 | -30.6844 | -27.1476 | -28.306 | -43.6471 | -32.3185 | -38.0371 | -23.887 | -25.3197 | -27.5235 | -49.0704 | -31.4618 | -33.9678 | -25.6799 | -26.3657 | -28.8417 | -48.3235 | -30.9871 | -34.24
555 | -6.9745 | 0 | -5.0448 | 0 | -5.7614 | 0 | -5.5072 | 0 | -54.3253 | 43.1862 | -20.3794 | 34.7458 | -38.02 | -63.0125 | -52.1751 | 73.2282 | -64.4497 | 101.887 | -35.8834 | 174.273 | -49.8859 | 72.8563 | -21.253 | -88.6889 | -37.3849 | 165.0937 | -41.482 | -3.5059 | -50.297 | -16.5617 | -45.554 | 21.4547 | -9.5374 | -159.3538 | -21.508 | 68.7786 | -21.1655 | 54.3581 | -15.9717 | 139.4482 | -6.8189 | 61.5472 | -21.4448 | 19.4232 | -15.781 | 25.8767 | -12.4259 | 29.3645 | -46.1926 | -31.1515 | -32.2708 | -33.9544 | -49.8176 | -38.2179 | -44.1581 | -35.5114 | -33.1737 | -34.5956 | -56.0799 | -36.6403 | -38.8816 | 555 | -20.3035 | -49.9512 | -20.256 | -33.8076 | -21.1426 | -40.4242 | -21.196 | -36.5801 | 555 | -28.5369 | -26.1992 | -26.9799 | -44.7728 | -33.1731 | -38.3967 | -30.4666 | -27.4123 | -28.4472 | -44.0562 | -32.7107 | -38.6509 | -24.177 | -25.2963 | -27.6211 | -51.0351 | -31.5955 | -33.1202 | -26.1067 | -26.5094 | -29.0884 | -50.3185 | -31.1331 | -33.3744
556 | -7.0892 | 0 | -5.0693 | 0 | -5.7719 | 0 | -5.4794 | 0 | -51.5085 | 71.6961 | -21.7059 | 29.0819 | -37.889 | -76.1855 | -53.985 | 156.1169 | -62.0993 | 40.3889 | -35.3778 | 173.1476 | -48.3761 | 53.9182 | -22.896 | -94.7995 | -37.4671 | 158.3369 | -41.8123 | 2.8714 | -49.4802 | -23.1926 | -44.9202 | 32.4939 | -9.0419 | -172.7882 | -20.787 | 75.3042 | -22.5687 | 47.2485 | -16.4998 | 124.7044 | -6.5388 | 53.8293 | -20.6217 | 23.6939 | -15.4977 | 25.009 | -13.2794 | 22.9001 | -45.3851 | -31.7636 | -32.2331 | -34.225 | -50.6508 | -38.4081 | -45.0732 | -35.5337 | -33.2063 | -34.9248 | -57.7373 | -36.6391 | -37.3531 | 556 | -21.5981 | -49.3266 | -21.5209 | -33.4382 | -22.7351 | -40.3769 | -22.8138 | -36.5236 | 556 | -28.4445 | -26.1171 | -27.1358 | -45.5815 | -33.3388 | -39.3013 | -30.4644 | -27.4344 | -28.7456 | -44.8789 | -32.9287 | -39.5938 | -24.6744 | -25.1439 | -27.8356 | -52.668 | -31.5698 | -31.5812 | -26.6943 | -26.4612 | -29.4454 | -51.9654 | -31.1597 | -31.8737
557 | -7.1429 | 0 | -5.0804 | 0 | -5.7991 | 0 | -5.4593 | 0 | -47.8648 | 76.6229 | -23.2631 | 26.7437 | -38.0792 | -89.3564 | -46.3397 | 174.7225 | -56.998 | -17.9071 | -34.6345 | 170.0701 | -47.0173 | 35.9024 | -24.8596 | -98.1343 | -37.1134 | 149.0167 | -41.3847 | 10.7534 | -49.7386 | -33.2612 | -44.5495 | 37.9999 | -8.8129 | 173.8095 | -19.3951 | 76.9499 | -24.8355 | 45.6405 | -17.2893 | 110.8954 | -6.4603 | 46.1029 | -19.4854 | 22.7256 | -15.1845 | 22.2356 | -14.1021 | 17.6006 | -44.4431 | -32.5407 | -32.0876 | -34.7321 | -52.7321 | -38.5407 | -45.9319 | -35.8186 | -32.9515 | -35.3147 | -56.4905 | -36.5257 | -36.2162 | 557 | -23.1076 | -43.8117 | -22.9375 | -32.9963 | -24.5837 | -39.8635 | -24.7186 | -36.1964 | 557 | -28.6757 | -25.8086 | -27.5892 | -47.6517 | -33.4603 | -40.1328 | -30.7382 | -27.1524 | -29.2728 | -46.933 | -33.0814 | -40.4726 | -25.3978 | -24.9447 | -28.1718 | -51.4101 | -31.4453 | -30.4171 | -27.4603 | -26.2885 | -29.8554 | -50.6914 | -31.0664 | -30.7569
558 | -7.1048 | 0 | -5.1236 | 0 | -5.8392 | 0 | -5.4232 | 0 | -45.7927 | 71.6636 | -24.783 | 29.8542 | -38.5055 | -102.5761 | -42.0339 | 168.9339 | -53.1837 | -63.7357 | -34.219 | 162.9891 | -45.9896 | 23.4033 | -26.8995 | -94.5046 | -37.1804 | 136.0682 | -40.3818 | 16.6517 | -50.8405 | -35.9892 | -43.3205 | 47.1663 | -8.7361 | 160.3177 | -18.1437 | 73.3763 | -27.5748 | 58.6292 | -18.3974 | 97.5057 | -6.5487 | 38.6288 | -18.7295 | 21.7977 | -14.9539 | 18.4175 | -15.1821 | 13.4123 | -43.7754 | -33.4402 | -31.9909 | -35.3457 | -56.3457 | -38.3426 | -46.4439 | -36.39 | -32.5383 | -35.9048 | -54.3306 | -36.7298 | -35.643 | 558 | -24.5696 | -40.28 | -24.2419 | -32.8033 | -26.4617 | -39.0308 | -26.6152 | -36.0871 | 558 | -29.2852 | -25.4335 | -28.2409 | -51.2221 | -33.219 | -40.6047 | -31.2664 | -26.6991 | -29.9225 | -50.5065 | -32.9194 | -41.0207 | -26.3354 | -24.8861 | -28.8 | -49.207 | -31.6062 | -29.8038 | -28.3166 | -26.1517 | -30.4816 | -48.4914 | -31.3066 | -30.2198
559 | -7.0089 | 0 | -5.166 | 0 | -5.8897 | 0 | -5.395 | 0 | -44.768 | 68.2434 | -25.6001 | 37.3616 | -39.059 | -115.4602 | -39.351 | 159.5211 | -50.6473 | -99.9513 | -34.3355 | 157.1514 | -45.0427 | 12.8289 | -28.0709 | -81.8919 | -37.9624 | 124.5112 | -39.1171 | 19.8496 | -51.2979 | -28.0583 | -41.3736 | 46.2795 | -8.9564 | 147.6044 | -17.1889 | 66.848 | -26.985 | 86.4643 | -20.0134 | 83.6177 | -6.7968 | 32.1123 | -17.9223 | 16.9179 | -14.9053 | 14.1811 | -15.5441 | 15.9453 | -43.3842 | -34.5493 | -31.9068 | -35.8491 | -59.7045 | -38.0532 | -46.3574 | -37.253 | -32.1378 | -36.6426 | -52.4355 | -37.1827 | -35.2599 | 559 | -25.3585 | -38.0109 | -24.8962 | -32.9989 | -27.5686 | -37.9244 | -27.5581 | -36.1948 | 559 | -30.2441 | -25.1289 | -28.8402 | -54.5385 | -32.8872 | -40.4677 | -32.087 | -26.2481 | -30.4541 | -53.8148 | -32.6582 | -40.9624 | -27.5404 | -24.8979 | -29.6337 | -47.2695 | -32.0167 | -29.3702 | -29.3833 | -26.0171 | -31.2476 | -46.5458 | -31.7877 | -29.8649
560 | -6.8564 | 0 | -5.2077 | 0 | -5.9636 | 0 | -5.3473 | 0 | -44.0552 | 68.0736 | -25.1398 | 46.2207 | -40.4715 | -129.9363 | -37.5862 | 146.7889 | -48.9274 | -131.2628 | -34.5576 | 155.8533 | -43.9117 | 5.7883 | -27.4717 | -69.8251 | -39.0266 | 113.7236 | -37.692 | 19.0637 | -49.862 | -23.9058 | -39.8486 | 41.5163 | -9.4441 | 134.9601 | -16.4731 | 57.723 | -23.3168 | 98.6486 | -21.0272 | 68.7548 | -7.2677 | 25.238 | -17.6442 | 11.3587 | -15.1113 | 8.7551 | -17.3328 | 8.8315 | -43.1564 | -35.8186 | -31.8833 | -36.1603 | -57.6876 | -38.0764 | -45.6921 | -38.4558 | -31.8642 | -37.3796 | -51.4421 | -37.9715 | -34.912 | 560 | -24.9606 | -36.4504 | -24.4532 | -33.4424 | -27.0871 | -36.5543 | -26.8538 | -36.2161 | 560 | -31.5994 | -25.0078 | -29.3039 | -52.4799 | -32.8687 | -39.7285 | -33.2481 | -25.9006 | -30.813 | -51.724 | -32.7291 | -40.3448 | -28.9622 | -25.0269 | -30.5232 | -46.2344 | -32.7638 | -28.9484 | -30.6109 | -25.9197 | -32.0323 | -45.4785 | -32.6242 | -29.5647
561 | -6.6742 | 0 | -5.225 | 0 | -6.0609 | 0 | -5.3422 | 0 | -43.0321 | 69.7227 | -23.8851 | 48.5107 | -43.5517 | -139.8878 | -36.5274 | 133.9353 | -47.8937 | -161.0037 | -34.3427 | 154.7178 | -42.5005 | -2.1669 | -25.7543 | -63.9737 | -40.3625 | 104.7062 | -36.1907 | 15.8585 | -48.2396 | -26.3925 | -38.6503 | 35.4338 | -10.2506 | 122.9557 | -16.2816 | 48.296 | -20.635 | 96.6781 | -24.2003 | 57.6524 | -7.9135 | 19.8281 | -17.2145 | 3.439 | -15.3776 | 3.2929 | -17.949 | 11.8055 | -42.9745 | -37.0213 | -31.8534 | -36.1659 | -54.1073 | -38.2323 | -44.8617 | -40.057 | -31.6468 | -37.6664 | -51.0961 | -38.8109 | -34.4663 | 561 | -23.7865 | -35.3992 | -23.2992 | -33.6827 | -25.5186 | -35.0637 | -25.1785 | -36.1361 | 561 | -33.3828 | -24.9726 | -29.4917 | -48.8823 | -33.0073 | -38.8008 | -34.832 | -25.5859 | -30.8237 | -48.0464 | -32.8901 | -39.5195 | -30.3471 | -25.1792 | -30.9922 | -45.8711 | -33.5859 | -28.4054 | -31.7963 | -25.7925 | -32.3242 | -45.0352 | -33.4687 | -29.1241
562 | -6.49 | 0 | -5.2477 | 0 | -6.1336 | 0 | -5.3351 | 0 | -41.4994 | 71.4614 | -22.5702 | 45.6072 | -47.2355 | -127.8527 | -35.9472 | 120.6639 | -47.16 | 173.0228 | -33.8921 | 153.0616 | -41.0715 | -11.6425 | -23.9616 | -66.4772 | -42.869 | 98.5217 | -34.7631 | 10.078 | -47.0839 | -34.6292 | -37.6474 | 25.786 | -11.5469 | 112.6904 | -16.1881 | 38.8108 | -18.549 | 88.8801 | -26.8681 | 51.5144 | -8.5974 | 16.1426 | -17.4006 | -4.283 | -15.9791 | -1.3151 | -18.1906 | 16.9461 | -42.8995 | -37.5784 | -31.72 | -35.9659 | -51.6847 | -38.5198 | -43.9781 | -42.2703 | -31.5369 | -37.4195 | -50.9781 | -39.4734 | -34.164 | 562 | -22.5004 | -34.6307 | -22.0791 | -33.5042 | -23.8235 | -33.6485 | -23.4464 | -36.1418 | 562 | -35.7803 | -25.0469 | -29.4759 | -46.437 | -33.2721 | -37.8445 | -37.0226 | -25.4033 | -30.6308 | -45.5511 | -33.1847 | -38.643 | -31.0884 | -25.23 | -30.9295 | -45.7304 | -34.2257 | -28.0304 | -32.3307 | -25.5864 | -32.0844 | -44.8445 | -34.1383 | -28.8289
563 | -6.3138 | 0 | -5.2476 | 0 | -6.1812 | 0 | -5.3442 | 0 | -39.7522 | 67.4322 | -21.5234 | 38.0497 | -46.8909 | -103.5284 | -35.7805 | 106.5235 | -46.5528 | 149.1692 | -33.1852 | 150.3959 | -39.8312 | -21.9933 | -22.5516 | -72.4298 | -45.553 | 114.2143 | -33.5725 | 1.2199 | -46.2133 | -42.9969 | -37.1721 | 14.0215 | -13.43 | 106.0402 | -16.9359 | 28.2067 | -17.4317 | 78.4549 | -33.4553 | 58.0786 | -9.52 | 15.0329 | -17.2151 | -12.2009 | -16.4125 | -5.2986 | -18.4362 | 20.4543 | -42.9346 | -37.1183 | -31.5633 | -35.6455 | -50.0283 | -38.6495 | -43.1929 | -45.5289 | -31.4544 | -36.8179 | -50.8335 | -39.8375 | -33.825 | 563 | -21.4462 | -34.0649 | -21.0869 | -32.8163 | -22.4498 | -32.4629 | -22.0845 | -36.1345 | 563 | -39.2151 | -25.1406 | -29.3317 | -44.7807 | -33.4019 | -37.0117 | -40.2813 | -25.2732 | -30.3013 | -43.8471 | -33.3053 | -37.8487 | -30.8045 | -25.2495 | -30.5041 | -45.5859 | -34.5899 | -27.6438 | -31.8707 | -25.3821 | -31.4737 | -44.6523 | -34.4933 | -28.4808
564 | -6.1924 | 0 | -5.2571 | 0 | -6.2266 | 0 | -5.3753 | 0 | -38.1357 | 61.9407 | -20.8362 | 29.1276 | -44.5538 | -92.4192 | -36.0528 | 92.8079 | -46.1087 | 124.779 | -32.2313 | 147.209 | -38.8508 | -32.8575 | -21.5764 | -83.2756 | -43.7925 | 133.7596 | -32.7173 | -8.5462 | -45.7387 | -55.2123 | -37.19 | 3.7591 | -15.8687 | 106.8065 | -17.8021 | 18.9534 | -16.5937 | 68.3285 | -33.6646 | 89.2485 | -10.0744 | 16.5882 | -17.9793 | -20.3312 | -17.348 | -8.6654 | -18.8378 | 21.5973 | -43.2293 | -36.1011 | -31.3833 | -35.2332 | -48.8738 | -38.5855 | -42.5071 | -50.8867 | -31.4385 | -36.1204 | -50.7376 | -39.6445 | -33.6554 | 564 | -20.738 | -33.7032 | -20.412 | -31.8192 | -21.4703 | -31.5998 | -21.1453 | -35.86 | 564 | -44.6943 | -25.2461 | -29.0408 | -43.6167 | -33.3284 | -36.2805 | -45.6296 | -25.2119 | -29.8579 | -42.6472 | -33.2102 | -37.1318 | -29.9087 | -25.1909 | -29.928 | -45.4805 | -34.3874 | -27.4288 | -30.844 | -25.1567 | -30.7451 | -44.511 | -34.2692 | -28.2801
565 | -6.1665 | 0 | -5.2602 | 0 | -6.2172 | 0 | -5.4008 | 0 | -36.8758 | 52.7797 | -20.5675 | 18.8048 | -41.6238 | -90.352 | -36.8968 | 78.6566 | -45.9128 | 101.4194 | -31.3757 | 140.897 | -38.1517 | -44.2938 | -21.0413 | -94.4974 | -41.3214 | 132.8715 | -32.2632 | -21.8478 | -45.7773 | -67.1827 | -37.3871 | -6.3582 | -17.6554 | 121.6247 | -19.0979 | 12.474 | -16.254 | 58.5719 | -29.2071 | 104.3019 | -10.4964 | 20.4571 | -19.6886 | -27.5458 | -18.7789 | -10.2449 | -19.4308 | 23.4899 | -43.7597 | -35.0097 | -31.2519 | -34.8965 | -48.0644 | -38.4941 | -41.9946 | -57.2368 | -31.5649 | -35.4907 | -50.7407 | -38.9985 | -33.6344 | 565 | -20.4339 | -33.6124 | -20.1288 | -30.8463 | -20.9179 | -31.1163 | -20.6326 | -35.4865 | 565 | -51.0703 | -25.3984 | -28.73 | -42.8042 | -33.2339 | -35.7774 | -51.9766 | -25.3477 | -29.4957 | -41.8472 | -33.0933 | -36.5938 | -28.8432 | -25.0854 | -29.3242 | -45.4805 | -33.7383 | -27.4172 | -29.7495 | -25.0347 | -30.0899 | -44.5235 | -33.5977 | -28.2336
566 | -6.2226 | 0 | -5.2497 | 0 | -6.2068 | 0 | -5.4214 | 0 | -36.0154 | 41.5015 | -20.6341 | 8.5795 | -39.0909 | -102.7891 | -38.4688 | 60.0214 | -45.954 | 77.3521 | -30.7747 | 130.384 | -37.6272 | -53.9304 | -20.9081 | -106.5109 | -39.4203 | 127.9851 | -32.1762 | -35.0956 | -46.202 | -77.736 | -37.677 | -14.4553 | -16.3399 | 141.3611 | -21.1921 | 8.2858 | -16.5937 | 48.1719 | -26.8581 | 108.95 | -9.9271 | 23.1885 | -21.3299 | -31.0764 | -19.5031 | -10.4805 | -19.3876 | 27.6918 | -44.5617 | -34.1087 | -31.2026 | -34.6047 | -47.5149 | -38.14 | -41.6911 | -50.4529 | -31.7733 | -35.0348 | -50.8356 | -38.449 | -33.9287 | 566 | -20.4503 | -33.7887 | -20.1681 | -30.0643 | -20.7571 | -30.9553 | -20.5111 | -35.1006 | 566 | -44.2303 | -25.5507 | -28.3821 | -42.2652 | -32.8903 | -35.4843 | -45.2032 | -25.5665 | -29.1833 | -41.3081 | -32.7186 | -36.2697 | -27.8861 | -24.98 | -28.8122 | -45.5859 | -33.1993 | -27.7219 | -28.859 | -24.9958 | -29.6134 | -44.6288 | -33.0276 | -28.5073
567 | -6.3861 | 0 | -5.2675 | 0 | -6.153 | 0 | -5.4346 | 0 | -35.5633 | 31.2966 | -21.0402 | -1.9592 | -37.7746 | -116.736 | -41.1716 | 41.6458 | -46.1901 | 55.5135 | -30.3296 | 121.2977 | -37.2699 | -64.4056 | -21.1209 | -117.3156 | -37.5209 | 118.491 | -32.5399 | -47.7818 | -46.861 | -87.3545 | -38.4597 | -25.1292 | -13.6702 | 146.1329 | -23.3777 | 10.8847 | -17.1282 | 40.6174 | -24.8267 | 100.6887 | -9.2334 | 23.31 | -23.6216 | -28.1882 | -20.7769 | -8.6727 | -19.1414 | 31.4131 | -45.7202 | -33.5159 | -31.2489 | -34.478 | -47.2007 | -37.7268 | -41.5527 | -45.7116 | -32.1165 | -34.7441 | -50.8808 | -37.8093 | -34.7265 | 567 | -20.8015 | -34.2233 | -20.5191 | -29.516 | -20.9207 | -31.1617 | -20.7443 | -34.6833 | 567 | -39.3255 | -25.7304 | -28.0919 | -41.9332 | -32.4593 | -35.3997 | -40.4441 | -25.9635 | -29.0434 | -41.0477 | -32.2922 | -36.1181 | -27.1298 | -24.8628 | -28.358 | -45.6133 | -32.5418 | -28.5735 | -28.2484 | -25.0959 | -29.3095 | -44.7278 | -32.3747 | -29.2919
568 | -6.6238 | 0 | -5.2712 | 0 | -6.1131 | 0 | -5.446 | 0 | -35.5015 | 20.0652 | -21.737 | -11.0533 | -37.2523 | -130.9579 | -46.0177 | 11.3619 | -46.6143 | 31.6922 | -30.1198 | 110.0799 | -37.0851 | -75.1115 | -21.6698 | -131.2569 | -36.166 | 104.1257 | -33.4645 | -62.7467 | -47.9402 | -97.954 | -39.6269 | -31.3273 | -11.2311 | 142.0953 | -25.4964 | 21.4038 | -18.3746 | 33.4466 | -25.6041 | 97.9672 | -8.2592 | 20.2858 | -28.0025 | -13.6388 | -21.7197 | -5.1667 | -18.7964 | 33.3614 | -47.0755 | -33.1244 | -31.3929 | -34.5442 | -47.1224 | -37.5111 | -41.5798 | -42.9217 | -32.4832 | -34.6892 | -50.9431 | -37.324 | -36.0967 | 568 | -21.4427 | -34.8338 | -21.1344 | -29.2707 | -21.3994 | -31.7909 | -21.3269 | -34.3556 | 568 | -36.2979 | -25.8594 | -27.9204 | -41.8512 | -32.2399 | -35.4667 | -37.6505 | -26.3701 | -29.0982 | -41.0093 | -32.0651 | -36.1338 | -26.5006 | -24.7691 | -28.0654 | -45.6719 | -32.0528 | -29.9836 | -27.8532 | -25.2798 | -29.2432 | -44.83 | -31.878 | -30.6507
569 | -6.8736 | 0 | -5.272 | 0 | -6.0572 | 0 | -5.4595 | 0 | -35.7989 | 12.6532 | -22.6935 | -19.4342 | -36.7556 | -141.3129 | -51.7589 | -64.9706 | -47.3785 | 7.8272 | -30.3476 | 98.5574 | -37.127 | -85.668 | -22.5159 | -142.4405 | -35.706 | 87.5247 | -35.1603 | -77.6514 | -49.8635 | -107.0058 | -40.5948 | -35.9215 | -9.6482 | 133.3474 | -25.0663 | 38.0225 | -19.3176 | 33.7795 | -22.5967 | 78.9624 | -7.6762 | 15.1218 | -27.0955 | 16.2159 | -21.6965 | 0.4232 | -18.5961 | 32.8758 | -48.4982 | -32.9552 | -31.5685 | -34.838 | -47.2052 | -37.2247 | -41.7837 | -41.2173 | -32.8697 | -34.9009 | -51.1431 | -37.2095 | -38.5916 | 569 | -22.3266 | -35.4053 | -22.001 | -29.3838 | -22.1714 | -32.934 | -22.2222 | -34.3616 | 569 | -34.3437 | -25.9961 | -27.9644 | -41.9332 | -31.9527 | -35.7265 | -35.9453 | -26.8125 | -29.3785 | -41.148 | -31.7652 | -36.3242 | -26.0816 | -24.6949 | -28.0273 | -45.8711 | -31.9375 | -32.5344 | -27.6832 | -25.5113 | -29.4414 | -45.0859 | -31.75 | -33.1321
570 | -7.1169 | 0 | -5.2954 | 0 | -6.0563 | 0 | -5.4382 | 0 | -36.4068 | 2.684 | -23.8952 | -27.2471 | -36.2947 | -157.0434 | -45.2042 | -137.9421 | -48.5989 | -16.7078 | -30.9942 | 85.6888 | -37.4092 | -94.0403 | -23.7059 | -152.1515 | -35.7324 | 72.8674 | -38.1164 | -94.8871 | -53.0128 | -106.8595 | -41.4757 | -40.2352 | -8.4567 | 123.252 | -24.3292 | 45.5689 | -20.9473 | 34.3136 | -23.9373 | 67.5298 | -7.1584 | 8.9578 | -23.9287 | 32.4706 | -22.3493 | 8.0187 | -17.589 | 34.5754 | -49.8185 | -32.9895 | -31.7337 | -35.3888 | -47.4904 | -37.1653 | -42.1821 | -40.1344 | -33.199 | -35.4321 | -51.2368 | -37.3024 | -42.8602 | 570 | -23.4278 | -35.6431 | -23.0946 | -29.8134 | -23.271 | -34.674 | -23.4819 | -34.6427 | 570 | -33.0175 | -26.0821 | -28.2719 | -42.195 | -31.8699 | -36.1258 | -34.839 | -27.1427 | -29.9506 | -41.4341 | -31.7271 | -36.7439 | -25.8726 | -24.6168 | -28.3152 | -45.9414 | -32.007 | -36.8039 | -27.6941 | -25.6774 | -29.9939 | -45.1805 | -31.8642 | -37.422
571 | -7.3453 | 0 | -5.2963 | 0 | -6.0709 | 0 | -5.4193 | 0 | -37.4238 | -3.0308 | -25.3571 | -31.6487 | -36.3409 | -171.0303 | -40.0917 | -164.2294 | -50.2776 | -42.1473 | -32.0759 | 74.7512 | -38.0134 | -103.4826 | -25.3043 | -162.4014 | -35.7663 | 60.2599 | -44.2327 | -116.7697 | -56.1796 | -86.7843 | -43.1088 | -48.1558 | -7.7025 | 112.6746 | -24.2295 | 46.6754 | -21.3472 | 43.1769 | -23.2999 | 56.6594 | -6.7765 | 1.9389 | -20.7502 | 33.5454 | -22.4529 | 15.0213 | -17.2888 | 32.6942 | -50.5811 | -33.215 | -31.8683 | -36.0968 | -47.7374 | -37.2971 | -42.687 | -39.5631 | -33.4273 | -36.058 | -51.0971 | -37.8795 | -48.5897 | 571 | -24.781 | -35.402 | -24.4002 | -30.6468 | -24.7219 | -37.0302 | -25.1786 | -34.9981 | 571 | -32.2178 | -26.082 | -28.7515 | -42.4411 | -32.0008 | -36.6161 | -34.2668 | -27.3564 | -30.6775 | -41.6665 | -31.8778 | -37.2677 | -25.8697 | -24.523 | -28.7127 | -45.8008 | -32.5832 | -42.5188 | -27.9187 | -25.7974 | -30.6387 | -45.0262 | -32.4602 | -43.1704
572 | -7.4398 | 0 | -5.3025 | 0 | -6.0946 | 0 | -5.3909 | 0 | -38.8135 | -6.9521 | -27.0093 | -35.1675 | -36.8246 | 174.9806 | -36.9047 | 176.3667 | -52.3979 | -71.1119 | -33.7504 | 63.3532 | -38.9871 | -110.1487 | -27.4628 | -172.0594 | -35.9928 | 44.2787 | -54.3372 | 106.2543 | -54.9161 | -55.4598 | -45.679 | -52.0138 | -7.2695 | 101.9386 | -24.7713 | 44.074 | -21.1278 | 48.9727 | -26.7912 | 40.8974 | -6.7124 | -6.1251 | -19.3378 | 33.7777 | -21.6026 | 18.4993 | -16.9052 | 31.5399 | -50.3295 | -33.563 | -31.9512 | -36.9506 | -47.9311 | -37.5396 | -43.2244 | -39.3251 | -33.4866 | -36.6736 | -50.8807 | -39.1259 | -43.1056 | 572 | -26.3261 | -34.6708 | -25.8226 | -31.9711 | -26.6325 | -38.7558 | -27.389 | -35.4994 | 572 | -31.8853 | -26.0468 | -29.5108 | -42.6286 | -32.2371 | -37.1298 | -34.0226 | -27.392 | -31.5597 | -41.8365 | -32.1487 | -37.8335 | -26.1232 | -24.5114 | -29.2338 | -45.5782 | -33.8234 | -37.011 | -28.2605 | -25.8566 | -31.2827 | -44.7861 | -33.735 | -37.7147
573 | -7.4948 | 0 | -5.3307 | 0 | -6.1666 | 0 | -5.3659 | 0 | -40.3334 | -5.4745 | -28.6015 | -33.4822 | -37.3729 | 162.162 | -34.7394 | 160.2298 | -54.5246 | -106.248 | -36.341 | 55.919 | -40.2654 | -110.5468 | -30.4417 | -176.908 | -36.8935 | 28.4547 | -40.7074 | 51.6955 | -51.1986 | -42.6991 | -49.4585 | -50.3303 | -7.0851 | 91.8474 | -25.2747 | 42.1463 | -19.8896 | 50.8652 | -27.817 | 33.2493 | -6.6921 | -13.9382 | -17.9188 | 28.6532 | -21.6582 | 20.8695 | -17.0102 | 29.9342 | -49.3343 | -34.1429 | -32.0296 | -37.7757 | -47.9241 | -38.1507 | -43.819 | -39.4557 | -33.4362 | -37.151 | -50.7213 | -41.2174 | -37.6034 | 573 | -27.8104 | -33.6459 | -27.1043 | -33.7793 | -29.2015 | -37.2902 | -30.0018 | -36.5093 | 573 | -31.9609 | -25.9414 | -30.2809 | -42.5934 | -32.82 | -37.6524 | -34.125 | -27.2696 | -32.4098 | -41.7575 | -32.7848 | -38.4531 | -26.6481 | -24.5348 | -29.6562 | -45.3906 | -35.8867 | -31.4368 | -28.8122 | -25.863 | -31.7851 | -44.5547 | -35.8515 | -32.2375
574 | -7.4485 | 0 | -5.3653 | 0 | -6.2731 | 0 | -5.3471 | 0 | -41.2961 | 5.8346 | -29.7772 | -27.951 | -38.0675 | 149.7143 | -33.2499 | 147.0525 | -55.1091 | -149.3061 | -40.1318 | 59.7903 | -41.2432 | -103.5948 | -34.6555 | -174.6006 | -38.4392 | 14.948 | -35.4637 | 31.8072 | -47.6484 | -46.7238 | -55.3629 | -10.3505 | -7.1485 | 81.8562 | -27.0185 | 46.3861 | -19.0023 | 46.9133 | -29.8761 | 30.9626 | -7.0775 | -23.2595 | -17.2926 | 23.8152 | -21.4011 | 21.1205 | -17.7067 | 25.276 | -47.9353 | -35.0111 | -32.0303 | -38.0486 | -47.4079 | -38.9525 | -44.2871 | -39.8669 | -33.3079 | -37.2442 | -50.4942 | -44.7614 | -33.9482 | 574 | -28.9181 | -32.5929 | -27.8973 | -35.9152 | -32.5128 | -34.2424 | -32.0104 | -37.8691 | 574 | -32.4184 | -25.8594 | -30.6001 | -42.0426 | -33.5872 | -38.014 | -34.5016 | -27.0348 | -32.7015 | -41.1348 | -33.6054 | -38.94 | -27.5626 | -24.5818 | -29.7957 | -45.1289 | -39.3961 | -27.6751 | -29.6458 | -25.7572 | -31.8971 | -44.2211 | -39.4143 | -28.6011
575 | -7.3305 | 0 | -5.3994 | 0 | -6.4036 | 0 | -5.3154 | 0 | -40.4311 | 18.4467 | -30.1757 | -22.3993 | -39.7876 | 137.2303 | -32.127 | 133.9569 | -52.4846 | 167.945 | -41.8691 | 89.5428 | -40.2683 | -92.0602 | -37.5058 | -140.787 | -40.0913 | 1.9314 | -32.4305 | 14.9738 | -45.3386 | -58.8734 | -48.7675 | 32.248 | -7.4227 | 71.8996 | -29.0026 | 69.6693 | -18.4552 | 39.3642 | -31.9355 | 38.6695 | -7.745 | -31.7911 | -16.4191 | 17.9752 | -21.7431 | 24.2127 | -18.7765 | 21.9826 | -46.2316 | -36.1609 | -31.9769 | -37.6059 | -46.3558 | -39.772 | -44.4677 | -40.5784 | -33.0956 | -36.5605 | -50.1989 | -47.5978 | -31.36 | 575 | -29.3707 | -31.4937 | -27.8565 | -37.5527 | -34.3236 | -31.5822 | -31.1788 | -38.5247 | 575 | -33.2479 | -25.7651 | -30.2754 | -40.9564 | -34.3726 | -38.0641 | -35.179 | -26.692 | -32.2905 | -39.9522 | -34.4566 | -39.1523 | -28.8304 | -24.6464 | -29.23 | -44.7995 | -42.1984 | -24.9564 | -30.7615 | -25.5733 | -31.2451 | -43.7953 | -42.2824 | -26.0446
576 | -7.139 | 0 | -5.4564 | 0 | -6.5285 | 0 | -5.313 | 0 | -38.6259 | 25.7262 | -30.0698 | -17.07 | -41.5189 | 126.7642 | -31.1232 | 121.2505 | -49.2148 | 134.3304 | -39.6996 | 114.0268 | -38.0946 | -86.4836 | -35.4995 | -108.5816 | -42.9405 | -3.2825 | -30.3283 | -0.7957 | -43.7955 | -70.5364 | -44.3814 | 37.9904 | -7.9344 | 62.9697 | -27.0273 | 100.6307 | -18.5978 | 29.9925 | -32.7337 | 51.9764 | -8.451 | -38.1501 | -15.849 | 12.4261 | -21.3125 | 26.6687 | -19.0697 | 28.059 | -44.7862 | -37.4282 | -31.8501 | -37.0646 | -45.3643 | -39.841 | -44.2882 | -41.411 | -32.8382 | -35.5109 | -49.9583 | -46.1067 | -29.4991 | 576 | -29.2381 | -30.3559 | -27.2971 | -37.2209 | -33.118 | -29.4923 | -29.0465 | -38.894 | 576 | -34.272 | -25.6992 | -29.9256 | -39.9079 | -34.3846 | -37.7597 | -35.9546 | -26.3097 | -31.7516 | -38.8358 | -34.528 | -38.9752 | -30.2892 | -24.7111 | -28.3719 | -44.5019 | -40.6503 | -22.9706 | -31.9718 | -25.3216 | -30.1979 | -43.4298 | -40.7937 | -24.1861
577 | -6.9206 | 0 | -5.53 | 0 | -6.6589 | 0 | -5.3308 | 0 | -36.549 | 26.5744 | -29.6382 | -15.6196 | -45.0053 | 121.8515 | -30.2848 | 108.1446 | -45.9932 | 104.4554 | -36.5065 | 120.1846 | -35.7547 | -88.5012 | -31.8706 | -99.5792 | -45.9187 | -7.5561 | -28.8133 | -17.1501 | -42.9845 | -84.2508 | -41.4717 | 32.6527 | -8.8376 | 54.6848 | -22.8909 | 109.9557 | -19.2199 | 19.9488 | -29.7099 | 62.825 | -9.7866 | -46.8454 | -15.7706 | 7.4262 | -21.1457 | 30.9354 | -19.4879 | 35.3014 | -43.7954 | -38.5064 | -31.6665 | -36.5532 | -44.772 | -38.8462 | -43.5808 | -42.3464 | -32.6355 | -34.3972 | -49.9324 | -42.7253 | -28.1739 | 577 | -28.7295 | -29.27 | -26.4841 | -35.5241 | -30.2622 | -27.8773 | -26.9132 | -38.3224 | 577 | -35.4258 | -25.7149 | -29.6326 | -39.242 | -33.3162 | -36.9219 | -36.8164 | -25.9766 | -31.2224 | -38.1131 | -33.5154 | -38.25 | -31.5858 | -24.7459 | -27.4766 | -44.4024 | -37.1953 | -21.515 | -32.9764 | -25.0076 | -29.0664 | -43.2735 | -37.3945 | -22.8431
578 | -6.6838 | 0 | -5.605 | 0 | -6.7829 | 0 | -5.3783 | 0 | -34.4387 | 21.4933 | -29.2316 | -17.0006 | -47.9724 | 129.9115 | -29.863 | 93.4513 | -43.7239 | 76.7963 | -33.8711 | 113.9039 | -33.7859 | -97.7847 | -29.5093 | -105.7302 | -48.9313 | 18.3664 | -27.8686 | -32.6365 | -42.4578 | -94.1309 | -39.0197 | 27.7366 | -10.1294 | 48.9292 | -19.7279 | 110.203 | -21.2483 | 8.1505 | -29.6755 | 56.2696 | -11.5049 | -51.7932 | -15.7721 | 2.4931 | -21.1021 | 35.0955 | -19.4325 | 42.1878 | -43.3313 | -38.8413 | -31.5078 | -35.6087 | -44.6009 | -37.1498 | -42.3276 | -43.5914 | -32.5276 | -33.5425 | -50.148 | -40.3102 | -27.3681 | 578 | -28.0428 | -28.4335 | -25.791 | -33.2931 | -28.0949 | -26.7601 | -25.4083 | -37.102 | 578 | -36.9076 | -25.8438 | -28.9249 | -38.9959 | -31.5448 | -35.5447 | -37.9864 | -25.7447 | -30.2304 | -37.818 | -31.7715 | -36.9493 | -32.1575 | -24.824 | -26.8587 | -44.543 | -34.7052 | -20.5852 | -33.2363 | -24.7249 | -28.1642 | -43.3651 | -34.9319 | -21.9898
579 | -6.446 | 0 | -5.6566 | 0 | -6.888 | 0 | -5.4129 | 0 | -32.6713 | 13.3921 | -29.1398 | -20.2542 | -50.0273 | 158.6554 | -29.8356 | 80.5999 | -42.1391 | 52.3974 | -32.0108 | 104.462 | -32.3269 | -107.9656 | -28.2824 | -114.8007 | -46.4899 | 38.3774 | -27.4237 | -47.8771 | -41.8692 | -103.6375 | -36.7568 | 18.2191 | -11.5051 | 48.0105 | -17.2645 | 101.7863 | -24.5583 | 1.2589 | -27.7507 | 48.4665 | -13.5052 | -49.9287 | -15.5388 | -1.8811 | -20.3294 | 37.3632 | -18.6246 | 48.0567 | -43.3596 | -38.5949 | -31.3208 | -34.4611 | -44.5822 | -35.6652 | -40.9691 | -45.4935 | -32.446 | -32.9496 | -50.3519 | -38.7201 | -26.9811 | 579 | -27.5213 | -27.8508 | -25.3955 | -31.5463 | -26.7928 | -26.0906 | -24.552 | -35.2508 | 579 | -39.0475 | -26 | -28.0151 | -38.9256 | -30.0086 | -34.0811 | -39.8369 | -25.558 | -29.0482 | -37.6942 | -30.2523 | -35.5562 | -32.1489 | -24.8748 | -26.5036 | -44.6953 | -33.0635 | -20.0931 | -32.9383 | -24.4328 | -27.5367 | -43.4639 | -33.3072 | -21.5682
580 | -6.3229 | 0 | -5.7268 | 0 | -6.9451 | 0 | -5.4829 | 0 | -31.3483 | 1.7988 | -29.4337 | -24.6475 | -46.1351 | -175.6739 | -30.1007 | 66.8841 | -41.0606 | 30.2629 | -30.6123 | 92.2735 | -31.3018 | -120.4096 | -27.8348 | -125.7467 | -44.2449 | 41.0974 | -27.3777 | -62.6471 | -41.3475 | -115.005 | -35.3201 | 4.1277 | -12.8447 | 51.3907 | -15.8805 | 92.6496 | -30.2007 | 7.4709 | -28.6325 | 24.4863 | -15.4979 | -43.2666 | -15.4778 | -5.9 | -19.5838 | 38.8799 | -17.6249 | 49.3152 | -43.6641 | -38.1324 | -31.2329 | -33.3321 | -44.5 | -34.5582 | -39.7463 | -48.5154 | -32.5104 | -32.5627 | -50.9416 | -37.3787 | -26.9093 | 580 | -27.2199 | -27.4751 | -25.2508 | -30.127 | -26.1529 | -25.7784 | -24.2375 | -33.9286 | 580 | -42.1925 | -26.1875 | -27.0092 | -38.7732 | -28.8314 | -32.8012 | -42.7886 | -25.5653 | -27.8492 | -37.5549 | -29.0753 | -34.2634 | -31.8095 | -24.91 | -26.2398 | -45.2148 | -31.6519 | -19.9642 | -32.4056 | -24.2878 | -27.0798 | -43.9965 | -31.8958 | -21.4264
581 | -6.2723 | 0 | -5.741 | 0 | -6.9793 | 0 | -5.5301 | 0 | -30.4874 | -10.1924 | -30.1099 | -26.6907 | -42.0137 | -179.8261 | -30.6681 | 54.6978 | -40.4234 | 10.2641 | -29.5827 | 79.5487 | -30.5903 | -131.7191 | -27.8972 | -132.8662 | -41.895 | 41.5387 | -27.6632 | -77.1301 | -40.9119 | -126.4021 | -34.6319 | -8.1919 | -12.9274 | 60.2256 | -15.0343 | 82.8759 | -33.7547 | 79.5727 | -29.3395 | 7.8915 | -15.6237 | -27.8701 | -15.4273 | -10.0514 | -18.6808 | 39.3367 | -16.1215 | 49.7658 | -44.1394 | -37.5651 | -31.1589 | -32.4284 | -44.3151 | -33.7331 | -38.784 | -52.6746 | -32.6473 | -32.1629 | -51.6512 | -36.0574 | -27.1974 | 581 | -27.1405 | -27.3472 | -25.3265 | -29.0154 | -25.9169 | -25.7403 | -24.3418 | -33.0989 | 581 | -46.4023 | -26.375 | -26.1561 | -38.5741 | -27.9921 | -31.8047 | -46.9336 | -25.668 | -26.8983 | -37.3358 | -28.203 | -33.2539 | -31.2928 | -24.8866 | -25.8906 | -45.9102 | -30.3164 | -20.2181 | -31.8241 | -24.1796 | -26.6328 | -44.6719 | -30.5273 | -21.6673
582 | -6.3115 | 0 | -5.7606 | 0 | -6.9532 | 0 | -5.6146 | 0 | -30.0139 | -22.9416 | -30.8976 | -27.6797 | -39.671 | 169.3172 | -31.5835 | 42.4069 | -40.0179 | -9.1014 | -28.9921 | 63.7124 | -30.1231 | -143.843 | -28.288 | -140.2864 | -39.2748 | 31.3692 | -28.2808 | -90.5305 | -40.5909 | -138.8176 | -34.1222 | -19.6389 | -12.1144 | 65.5964 | -14.3257 | 72.0249 | -26.1528 | 102.0475 | -30.1357 | -37.0344 | -13.9807 | -18.2057 | -15.272 | -12.9224 | -18.1193 | 40.0254 | -15.2926 | 43.3775 | -44.7995 | -36.8828 | -31.1161 | -31.7683 | -44.1785 | -33.0508 | -38.1317 | -52.9415 | -32.8779 | -31.7918 | -51.1942 | -35.0079 | -27.7846 | 582 | -27.1716 | -27.4694 | -25.5768 | -28.3307 | -25.8949 | -25.9431 | -24.7419 | -32.273 | 582 | -46.63 | -26.5664 | -25.4568 | -38.4179 | -27.2902 | -31.1785 | -47.1809 | -25.9247 | -26.1537 | -37.2253 | -27.4362 | -32.5171 | -30.5713 | -24.8046 | -25.4803 | -45.4336 | -29.2473 | -20.8314 | -31.1222 | -24.1629 | -26.1772 | -44.241 | -29.3933 | -22.17
583 | -6.4333 | 0 | -5.7845 | 0 | -6.8836 | 0 | -5.6569 | 0 | -29.8597 | -36.1328 | -31.4809 | -24.0954 | -38.0788 | 157.0029 | -32.9833 | 30.2736 | -39.8127 | -27.9541 | -28.9039 | 46.4447 | -29.888 | -155.7981 | -28.9054 | -146.0074 | -37.6323 | 15.9775 | -29.3274 | -103.1922 | -40.528 | -152.3523 | -33.6899 | -31.2513 | -11.1148 | 66.2686 | -15.1008 | 62.4262 | -22.0362 | 96.2951 | -26.4513 | -86.5399 | -12.5752 | -20.8309 | -15.4481 | -15.7067 | -17.2885 | 37.9884 | -14.0575 | 42.1017 | -45.4953 | -36.2859 | -31.1324 | -31.3703 | -44.1555 | -32.5827 | -37.8235 | -48.9187 | -33.0934 | -31.6048 | -49.8899 | -34.2937 | -28.7501 | 583 | -27.2135 | -27.8506 | -26.0184 | -28.1047 | -26.0463 | -26.4165 | -25.4035 | -31.6202 | 583 | -42.4854 | -26.6601 | -24.937 | -38.371 | -26.7982 | -30.9399 | -43.1342 | -26.2098 | -25.7134 | -37.2719 | -26.9258 | -32.1666 | -29.8526 | -24.6991 | -25.1715 | -44.1054 | -28.5092 | -21.8665 | -30.5014 | -24.2488 | -25.9479 | -43.0063 | -28.6368 | -23.0932
584 | -6.5694 | 0 | -5.7761 | 0 | -6.792 | 0 | -5.6937 | 0 | -30.0262 | -46.9392 | -31.4604 | -19.3478 | -36.5598 | 142.9543 | -35.1513 | 20.3502 | -39.8307 | -44.6486 | -29.2724 | 32.0648 | -29.8697 | -167.6549 | -29.7273 | -149.4191 | -36.584 | 2.2609 | -31.0077 | -115.5017 | -41.0654 | -167.7422 | -33.8903 | -43.1809 | -9.9362 | 61.3533 | -15.2195 | 55.14 | -19.4132 | 83.8821 | -28.6074 | -117.8809 | -11.3804 | -27.0662 | -16.2338 | -19.2251 | -16.3226 | 34.3795 | -13.1867 | 39.0589 | -46.3455 | -35.9239 | -31.0717 | -31.2916 | -44.3164 | -32.2915 | -37.7858 | -45.7977 | -33.2024 | -31.5261 | -48.5484 | -33.9573 | -30.0405 | 584 | -27.1462 | -28.5283 | -26.5714 | -28.2184 | -26.3548 | -27.2088 | -26.4474 | -31.5112 | 584 | -39.2283 | -26.633 | -24.7222 | -38.5403 | -26.5154 | -30.9938 | -40.0216 | -26.4104 | -25.5979 | -37.5244 | -26.5978 | -32.0921 | -29.3545 | -24.5023 | -24.9567 | -42.7723 | -28.1812 | -23.2485 | -30.1478 | -24.2797 | -25.8324 | -41.7564 | -28.2636 | -24.3468
585 | -6.6979 | 0 | -5.7938 | 0 | -6.6883 | 0 | -5.7216 | 0 | -30.4535 | -58.725 | -31.0757 | -16.3426 | -35.791 | 128.3932 | -38.3965 | 15.692 | -40.261 | -63.1155 | -29.883 | 14.9884 | -30.028 | -178.3415 | -30.7161 | -151.1587 | -35.733 | -14.7326 | -33.5026 | -123.7179 | -41.776 | 178.0618 | -34.1137 | -56.061 | -9.1457 | 55.0903 | -16.6274 | 51.1263 | -18.1547 | 72.1323 | -24.9099 | -146.6834 | -10.6593 | -35.2446 | -16.9145 | -19.7713 | -15.8538 | 30.4075 | -12.7985 | 31.9343 | -47.2095 | -35.7743 | -31.0184 | -31.4371 | -44.6499 | -32.206 | -37.8985 | -43.6003 | -33.2724 | -31.5496 | -47.4346 | -33.8583 | -31.6037 | 585 | -27.1108 | -29.4322 | -27.0939 | -28.5854 | -26.7599 | -28.2205 | -27.7412 | -31.4184 | 585 | -36.9024 | -26.5745 | -24.7392 | -38.8561 | -26.4122 | -31.2102 | -37.8065 | -26.5841 | -25.7155 | -37.9616 | -26.4844 | -32.1769 | -29.0764 | -24.3205 | -24.8517 | -41.6408 | -28.0645 | -24.9154 | -29.9805 | -24.3301 | -25.828 | -40.7463 | -28.1367 | -25.8821
586 | -6.833 | 0 | -5.8204 | 0 | -6.5898 | 0 | -5.7485 | 0 | -31.1768 | -69.2148 | -30.5067 | -15.4931 | -35.0505 | 112.99 | -43.3649 | 28.1238 | -40.9921 | -80.4402 | -30.9418 | -0.8827 | -30.3724 | 170.1566 | -31.8978 | -150.6596 | -35.1821 | -29.9586 | -37.3243 | -125.84 | -43.0293 | 163.158 | -35.1042 | -70.0667 | -8.5382 | 48.3659 | -17.6376 | 54.4947 | -17.2984 | 59.9562 | -22.7693 | -176.5281 | -10.2272 | -44.4627 | -17.551 | -17.965 | -15.6361 | 25.8246 | -12.4947 | 26.0104 | -48.1055 | -35.8164 | -30.9541 | -31.8087 | -45.2266 | -32.3008 | -38.1797 | -42.0664 | -33.2666 | -31.6641 | -46.4688 | -33.9648 | -33.386 | 586 | -27.0662 | -30.5144 | -27.592 | -29.2184 | -27.2884 | -29.3825 | -29.4314 | -31.793 | 586 | -35.2334 | -26.4336 | -24.9757 | -39.4062 | -26.4804 | -31.5899 | -36.246 | -26.6768 | -26.0602 | -38.6368 | -26.5523 | -32.4312 | -28.9834 | -24.1211 | -24.8311 | -40.6484 | -28.1444 | -26.7962 | -29.996 | -24.3643 | -25.9156 | -39.879 | -28.2163 | -27.6375
587 | -6.8791 | 0 | -5.9023 | 0 | -6.5006 | 0 | -5.7582 | 0 | -32.3347 | -79.1959 | -30.0876 | -20.7683 | -35.0173 | 97.6797 | -43.449 | 77.259 | -42.6227 | -100.4043 | -32.4126 | -21.6601 | -30.9795 | 160.5312 | -33.1113 | -144.284 | -34.8819 | -48.9216 | -41.4161 | -97.6055 | -44.6833 | 149.8544 | -36.6423 | -83.3179 | -8.4826 | 39.9548 | -19.3828 | 68.59 | -17.7738 | 45.5598 | -20.5108 | 170.3138 | -10.3309 | -55.8305 | -16.6186 | -8.7293 | -15.5161 | 20.8233 | -12.344 | 21.1603 | -48.9531 | -36.0319 | -30.8596 | -32.3945 | -46.1796 | -32.6842 | -38.5663 | -40.9811 | -33.1838 | -31.8983 | -45.6562 | -34.3834 | -35.332 | 587 | -27.2604 | -31.6493 | -27.9615 | -30.253 | -27.9276 | -30.437 | -31.0939 | -32.3987 | 587 | -34.102 | -26.3047 | -25.5154 | -40.2773 | -26.7819 | -32.0657 | -35.0788 | -26.6832 | -26.6363 | -39.679 | -26.926 | -32.8081 | -29.1528 | -23.9805 | -25.0192 | -39.7539 | -28.4811 | -28.8314 | -30.1296 | -24.359 | -26.1401 | -39.1556 | -28.6252 | -29.5738
588 | -6.9021 | 0 | -6.0229 | 0 | -6.4709 | 0 | -5.7364 | 0 | -33.9548 | -85.6927 | -30.1503 | -26.1451 | -34.9994 | 83.6246 | -38.3122 | 91.835 | -45.356 | -118.1284 | -34.6896 | -43.0987 | -31.8677 | 151.8987 | -33.7632 | -131.5072 | -35.1004 | -66.9386 | -38.5223 | -59.9175 | -47.33 | 134.8823 | -39.7501 | -96.1611 | -8.6299 | 32.3127 | -17.733 | 85.4535 | -19.1234 | 32.1811 | -19.135 | 152.5798 | -10.9177 | -70.1346 | -15.6974 | -3.6246 | -15.2903 | 17.7173 | -12.5376 | 14.3683 | -49.7105 | -36.2288 | -30.8006 | -33.023 | -47.7105 | -33.3577 | -39.019 | -40.1623 | -33.0153 | -32.3042 | -44.7417 | -34.9709 | -37.6265 | 588 | -27.7352 | -32.3739 | -28.3769 | -31.6427 | -28.6015 | -30.9178 | -31.7596 | -33.6309 | 588 | -33.2602 | -26.1132 | -26.1209 | -41.6876 | -27.3348 | -32.5481 | -34.1394 | -26.5444 | -27.2866 | -41.2396 | -27.6213 | -33.2826 | -29.3267 | -23.8985 | -25.4021 | -38.7188 | -28.948 | -31.1556 | -30.2059 | -24.3297 | -26.5678 | -38.2708 | -29.2345 | -31.8901
589 | -6.8506 | 0 | -6.1748 | 0 | -6.4952 | 0 | -5.71 | 0 | -35.9598 | -86.0414 | -31.0179 | -30.8827 | -35.2634 | 66.4042 | -34.7759 | 87.739 | -50.1454 | -137.5414 | -37.8934 | -71.4167 | -33.0584 | 145.1814 | -33.1129 | -117.9163 | -35.4271 | -84.4047 | -34.2842 | -55.1548 | -52.5554 | 121.5085 | -46.1869 | -97.0934 | -9.0794 | 24.0626 | -15.3402 | 90.9494 | -21.8886 | 18.2853 | -18.2185 | 135.4608 | -11.9125 | -81.0114 | -14.5139 | -3.6509 | -15.6798 | 14.3073 | -12.6428 | 8.0721 | -50.4132 | -36.2414 | -30.714 | -33.5382 | -49.9562 | -34.4874 | -39.4873 | -39.4209 | -32.7413 | -32.9483 | -43.8116 | -35.8545 | -40.1078 | 589 | -28.7218 | -32.2463 | -28.906 | -33.2816 | -28.9639 | -30.5902 | -30.5292 | -35.0001 | 589 | -32.5703 | -25.8907 | -26.6876 | -43.7814 | -28.3126 | -32.9921 | -33.2461 | -26.2461 | -27.8282 | -43.461 | -28.7774 | -33.7773 | -29.3908 | -23.8634 | -26.0977 | -37.6368 | -29.6797 | -33.6126 | -30.0666 | -24.2188 | -27.2383 | -37.3164 | -30.1445 | -34.3978
590 | -6.7626 | 0 | -6.3394 | 0 | -6.5937 | 0 | -5.652 | 0 | -37.5495 | -75.8731 | -32.7649 | -31.6422 | -36.3529 | 48.0199 | -32.3949 | 77.4712 | -65.0769 | -169.3563 | -41.4646 | -109.9288 | -34.6479 | 143.0081 | -31.256 | -108.5894 | -35.6944 | -102.9835 | -31.3284 | -61.2622 | -66.0267 | 174.1273 | -50.6287 | -17.2148 | -9.2957 | 19.4349 | -12.6557 | 87.0367 | -25.7118 | 21.067 | -16.6966 | 115.2616 | -12.9354 | -98.1051 | -13.4245 | -8.4077 | -16.0614 | 12.6424 | -12.9208 | 3.745 | -51.156 | -36.129 | -30.5791 | -33.6091 | -52.2028 | -36.129 | -39.7691 | -38.8281 | -32.4032 | -33.7965 | -42.8355 | -36.9882 | -39.8547 | 590 | -30.2851 | -31.2364 | -29.2939 | -35.1817 | -28.6605 | -29.6671 | -28.2565 | -35.5533 | 590 | -32.0655 | -25.6406 | -26.8465 | -45.8634 | -29.7896 | -33.1754 | -32.4887 | -25.8095 | -27.9571 | -45.6091 | -30.477 | -34.1171 | -29.3664 | -23.8165 | -27.0339 | -36.4961 | -30.6488 | -33.261 | -29.7896 | -23.9854 | -28.1445 | -36.2418 | -31.3362 | -34.2027
591 | -6.654 | 0 | -6.5355 | 0 | -6.738 | 0 | -5.6004 | 0 | -37.2607 | -63.0189 | -34.9903 | -20.143 | -38.2895 | 31.7829 | -30.6919 | 67.0958 | -52.8291 | 12.1322 | -42.2375 | -170.531 | -36.2207 | 148.9764 | -29.1759 | -106.0792 | -36.4036 | -124.0395 | -29.3727 | -71.7121 | -52.5217 | -118.4007 | -42.0008 | 8.3364 | -10.2156 | 12.6715 | -11.3447 | 79.5807 | -31.9803 | 60.8095 | -17.5745 | 101.6299 | -15.6246 | -106.1936 | -11.6193 | -10.3999 | -15.8135 | 13.736 | -13.2932 | 2.5569 | -51.8833 | -35.7968 | -30.4472 | -33.3833 | -51.7076 | -38.3163 | -39.6644 | -38.4373 | -32.0251 | -34.6332 | -41.9183 | -38.0701 | -36.9132 | 591 | -31.8502 | -29.8053 | -29.1031 | -36.7117 | -27.7557 | -28.5396 | -26.1485 | -35.264 | 591 | -31.7833 | -25.3711 | -26.7293 | -45.1721 | -31.7808 | -32.9264 | -31.9018 | -25.2871 | -27.7829 | -44.9696 | -32.7159 | -34.064 | -29.1428 | -23.7932 | -27.9792 | -35.3828 | -31.5346 | -30.1752 | -29.2613 | -23.7092 | -29.0328 | -35.1803 | -32.4697 | -31.3128
592 | -6.5298 | 0 | -6.726 | 0 | -6.9274 | 0 | -5.5658 | 0 | -35.3848 | -53.8674 | -34.8825 | 7.5826 | -40.8292 | 19.1113 | -29.4001 | 55.9982 | -45.9713 | -9.7707 | -39.4622 | 145.5697 | -36.6129 | 159.6455 | -27.3587 | -107.826 | -37.9287 | -147.3086 | -28.1038 | -84.9885 | -46.4031 | -131.6508 | -37.0327 | 1.1719 | -10.8561 | 10.4898 | -9.8351 | 71.0916 | -25.7443 | 104.7573 | -17.0501 | 86.5227 | -18.5249 | -121.0352 | -11.1746 | -22.965 | -15.8685 | 13.7092 | -13.7502 | 3.3027 | -52.3395 | -35.4823 | -30.3073 | -32.8786 | -48.6715 | -40.3377 | -39.0541 | -38.193 | -31.6313 | -34.9487 | -41.1088 | -38.8844 | -34.4345 | 592 | -31.5681 | -28.3481 | -27.9964 | -36.5544 | -26.5437 | -27.4752 | -24.458 | -34.179 | 592 | -31.6632 | -25.1015 | -26.3488 | -41.9455 | -33.6117 | -32.1267 | -31.467 | -24.7039 | -27.3128 | -41.7441 | -34.7719 | -33.4883 | -28.9525 | -23.7775 | -28.4189 | -34.3828 | -32.1584 | -27.5071 | -28.7563 | -23.3799 | -29.3829 | -34.1814 | -33.3186 | -28.8687
593 | -6.4171 | 0 | -6.8703 | 0 | -7.1671 | 0 | -5.5578 | 0 | -33.3151 | -55.4668 | -31.7331 | 23.3511 | -44.6351 | 8.18 | -28.5175 | 42.8676 | -42.489 | -27.9021 | -36.823 | 117.4921 | -35.1003 | 170.9421 | -25.8791 | -112.1861 | -40.0467 | -168.1554 | -27.3391 | -95.0555 | -42.8452 | -149.5757 | -33.8853 | -10.5246 | -11.5242 | 10.0703 | -8.7374 | 62.2998 | -21.1494 | 105.9446 | -17.4785 | 73.5036 | -25.0829 | -127.5635 | -10.2322 | -28.6521 | -15.3253 | 14.1505 | -14.004 | 1.544 | -52.7767 | -35.2064 | -30.2181 | -32.2572 | -45.6986 | -40.2494 | -38.0343 | -38.0695 | -31.3039 | -34.4484 | -40.2765 | -38.796 | -32.8657 | 593 | -29.3127 | -27.1459 | -26.4099 | -35.2491 | -25.2422 | -26.5633 | -23.1543 | -32.521 | 593 | -31.6524 | -24.8868 | -25.8401 | -38.8283 | -33.3791 | -30.8672 | -31.1992 | -24.1368 | -26.6994 | -38.5315 | -34.6916 | -32.4765 | -28.7893 | -23.801 | -28.0313 | -33.4062 | -31.9257 | -25.6986 | -28.3361 | -23.051 | -28.8906 | -33.1094 | -33.2382 | -27.3079
594 | -6.3603 | 0 | -6.9828 | 0 | -7.3877 | 0 | -5.5458 | 0 | -31.6444 | -62.7462 | -28.5613 | 24.0381 | -54.3369 | 12.0279 | -27.9913 | 27.686 | -40.3311 | -46.1084 | -34.9481 | 95.4242 | -32.8823 | 171.5375 | -24.6693 | -117.8412 | -42.4215 | 169.0187 | -26.9554 | -108.3939 | -40.6294 | -169.0131 | -31.8375 | -23.9313 | -12.1928 | 8.8168 | -8.3602 | 52.2886 | -18.6965 | 98.4179 | -19.1053 | 60.6393 | -35.8576 | -15.1178 | -9.8529 | -38.5865 | -14.5592 | 12.9674 | -14.2425 | 5.0543 | -52.0573 | -35.0988 | -30.1965 | -31.6666 | -43.2604 | -38.2863 | -36.9476 | -38.0439 | -31.0947 | -33.432 | -39.6117 | -38.0048 | -31.8284 | 594 | -26.8168 | -26.2607 | -24.8138 | -33.8052 | -23.996 | -25.8214 | -22.1586 | -30.9757 | 594 | -31.6836 | -24.7344 | -25.3063 | -36.2776 | -31.3035 | -29.5599 | -31.0611 | -23.707 | -26.1208 | -35.8727 | -32.7405 | -31.4018 | -28.7385 | -23.8362 | -27.0717 | -32.6289 | -31.022 | -24.4407 | -28.116 | -22.8088 | -27.8862 | -32.224 | -32.459 | -26.2826
595 | -6.3056 | 0 | -7.0274 | 0 | -7.6202 | 0 | -5.5992 | 0 | -30.3674 | -71.7892 | -26.1497 | 18.4733 | -49.1918 | 112.1849 | -27.8082 | 13.8476 | -38.8448 | -63.0209 | -33.5378 | 77.4371 | -30.8667 | 166.0598 | -23.681 | -123.8881 | -45.964 | 133.9142 | -26.8605 | -119.8794 | -39.3703 | 169.8516 | -30.2725 | -36.4721 | -12.5636 | 7.692 | -8.1695 | 42.3771 | -16.8978 | 88.2539 | -21.2081 | 53.5643 | -24.6711 | -1.4151 | -9.7631 | -50.1495 | -14.0183 | 9.709 | -14.1576 | 3.0015 | -50.6332 | -35.2611 | -30.2629 | -30.9808 | -41.5316 | -35.7533 | -35.8165 | -37.9952 | -31.0166 | -32.1251 | -39.0821 | -36.8155 | -31.1312 | 595 | -24.7396 | -25.677 | -23.4428 | -32.326 | -22.8997 | -25.2359 | -21.3763 | -29.6653 | 595 | -31.6896 | -24.711 | -24.6752 | -34.5042 | -28.7259 | -28.1963 | -30.9678 | -23.3964 | -25.3816 | -33.9114 | -30.1541 | -30.2173 | -28.9555 | -23.9573 | -25.8195 | -32.0547 | -29.7881 | -23.511 | -28.2337 | -22.6427 | -26.5259 | -31.4619 | -31.2163 | -25.532
596 | -6.299 | 0 | -6.9967 | 0 | -7.8141 | 0 | -5.6426 | 0 | -29.4268 | -82.2202 | -24.3886 | 10.8289 | -42.3172 | 100.9554 | -28.0466 | 0.7769 | -37.8713 | -79.2883 | -32.5658 | 59.4312 | -29.3032 | 156.4023 | -22.8959 | -131.4034 | -50.7556 | 64.765 | -27.0434 | -130.9154 | -38.7892 | 148.1765 | -29.0127 | -50.0305 | -12.6267 | 7.1742 | -8.0707 | 34.0442 | -15.6837 | 78.7393 | -25.7123 | 52.6899 | -20.6894 | -12.9419 | -9.9871 | -60.5904 | -13.4037 | 5.7595 | -13.9518 | 3.7352 | -48.7314 | -35.4316 | -30.4829 | -30.3759 | -40.3485 | -33.5605 | -34.7818 | -38.0563 | -31.131 | -30.9537 | -38.7584 | -35.4704 | -30.5634 | 596 | -23.1515 | -25.4177 | -22.3941 | -31.1025 | -21.9957 | -24.8391 | -20.7758 | -28.5517 | 596 | -31.7573 | -24.832 | -24.0769 | -33.3518 | -26.5638 | -26.9677 | -31.0596 | -23.3169 | -24.7333 | -32.5344 | -27.9179 | -29.1392 | -29.1326 | -24.1839 | -24.6547 | -31.7617 | -28.4737 | -22.7493 | -28.4349 | -22.6688 | -25.3111 | -30.9443 | -29.8278 | -24.9208
597 | -6.2844 | 0 | -6.9055 | 0 | -7.9211 | 0 | -5.7454 | 0 | -28.7637 | -92.0226 | -23.0322 | 2.2739 | -39.3401 | 85.9825 | -28.7093 | -13.6428 | -37.4337 | -96.0383 | -32.1653 | 42.5656 | -28.2187 | 145.6373 | -22.2129 | -137.3718 | -48.5472 | -19.2414 | -27.4324 | -140.2091 | -38.6112 | 129.9032 | -28.175 | -64.6762 | -12.4096 | 6.2898 | -8.1497 | 26.412 | -14.8704 | 68.6101 | -26.0994 | 89.2657 | -17.8459 | -22.1774 | -10.5858 | -68.9344 | -13.1382 | -0.0237 | -13.6532 | 5.0357 | -46.8863 | -35.4761 | -30.8433 | -29.7886 | -39.5504 | -31.8668 | -33.9719 | -38.3118 | -31.3196 | -29.9914 | -38.5852 | -34.3977 | -29.9947 | 597 | -21.9243 | -25.4425 | -21.5937 | -30.4366 | -21.2328 | -24.6207 | -20.2983 | -27.7626 | 597 | -32.0274 | -25.0352 | -23.5042 | -32.6449 | -24.9613 | -26.0508 | -31.4063 | -23.3985 | -24.0432 | -31.6293 | -26.1214 | -28.2265 | -29.1917 | -24.5589 | -23.707 | -31.6797 | -27.4922 | -22.0736 | -28.5706 | -22.9222 | -24.246 | -30.6641 | -28.6523 | -24.2493
598 | -6.3089 | 0 | -6.7482 | 0 | -7.9816 | 0 | -5.8249 | 0 | -28.3822 | -103.9998 | -21.9508 | -7.0211 | -37.5196 | 71.3189 | -29.7933 | -26.5834 | -37.5269 | -112.3262 | -32.3892 | 23.7547 | -27.5458 | 132.8836 | -21.5651 | -143.9229 | -44.7854 | -62.2931 | -27.9029 | -148.4607 | -38.7626 | 108.8601 | -27.8975 | -81.3176 | -12.7238 | -0.2421 | -8.5208 | 19.9867 | -14.8717 | 57.1458 | -24.9969 | 121.5822 | -16.7255 | -41.1993 | -11.3078 | -83.0982 | -13.0658 | -7.5152 | -13.0298 | 1.8872 | -45.4009 | -35.4194 | -31.2897 | -29.3618 | -39.0767 | -30.5639 | -33.3927 | -38.7745 | -31.6253 | -29.3498 | -38.6506 | -33.5519 | -29.8559 | 598 | -20.9637 | -25.7238 | -20.9653 | -30.3122 | -20.5715 | -24.5428 | -19.9065 | -27.4741 | 598 | -32.4656 | -25.3164 | -23.0529 | -32.3285 | -23.8157 | -25.4111 | -32.0263 | -23.6437 | -23.5369 | -31.0951 | -24.739 | -27.5678 | -29.1105 | -24.9808 | -23.0409 | -31.9024 | -26.8037 | -21.8743 | -28.6712 | -23.3081 | -23.5249 | -30.669 | -27.727 | -24.031
599 | -6.3191 | 0 | -6.5608 | 0 | -7.9164 | 0 | -5.9244 | 0 | -28.2329 | -115.584 | -21.0826 | -15.1195 | -36.0608 | 55.9724 | -31.1007 | -34.054 | -37.9792 | -125.8953 | -33.212 | 6.1729 | -27.13 | 121.2545 | -20.9802 | -150.1485 | -42.3096 | -86.6867 | -28.3526 | -156.0248 | -39.2957 | 90.2725 | -28.0817 | -97.0295 | -12.6356 | -1.2485 | -9.1996 | 13.2632 | -14.9218 | 46.1425 | -19.4583 | 118.6699 | -16.3983 | -45.5796 | -12.6332 | -93.8803 | -13.0677 | -13.6306 | -12.6862 | 1.2326 | -44.194 | -35.448 | -31.6983 | -29.0807 | -38.7721 | -29.6745 | -33.0999 | -39.389 | -31.8698 | -28.9046 | -38.9671 | -32.9007 | -30.0602 | 599 | -20.2029 | -26.1305 | -20.4349 | -30.5342 | -20.011 | -24.5403 | -19.5876 | -27.6152 | 599 | -33.0699 | -25.5507 | -22.7616 | -32.2113 | -23.1137 | -25.1835 | -32.8282 | -23.9534 | -23.1563 | -30.8557 | -23.7501 | -27.1755 | -29.1289 | -25.3792 | -22.5855 | -32.4063 | -26.3399 | -22.1438 | -28.8872 | -23.7819 | -22.9802 | -31.0507 | -26.9763 | -24.1358
600 | -6.3201 | 0 | -6.3776 | 0 | -7.7967 | 0 | -5.999 | 0 | -28.2806 | -126.861 | -20.4793 | -26.6696 | -35.2231 | 39.5606 | -32.3573 | -40.0719 | -38.6184 | -139.2098 | -34.665 | -12.6675 | -26.9272 | 109.5788 | -20.5052 | -158.7048 | -40.2193 | -107.3344 | -28.8321 | -163.2997 | -40.215 | 71.3792 | -28.6146 | -111.1503 | -13.1306 | -5.7075 | -10.0862 | 9.1321 | -15.5866 | 35.275 | -16.7564 | 111.9003 | -16.6659 | -65.1377 | -14.953 | -101.7907 | -13.2338 | -19.4457 | -12.2184 | -1.5819 | -43.3389 | -35.7072 | -32.0861 | -28.9209 | -38.5186 | -29.1838 | -33.0377 | -40.2615 | -32.035 | -28.5338 | -39.4909 | -32.5467 | -30.6632 | 600 | -19.6895 | -26.5673 | -20.0534 | -31.0822 | -19.5759 | -24.6436 | -19.3606 | -28.0521 | 600 | -33.9414 | -25.7149 | -22.6008 | -32.141 | -22.8062 | -25.241 | -33.8839 | -24.2383 | -22.9219 | -30.7219 | -23.1848 | -27.0387 | -29.3871 | -25.766 | -22.2137 | -33.1133 | -26.1691 | -22.8665 | -29.3296 | -24.2894 | -22.5348 | -31.6942 | -26.5477 | -24.6642
601 | -6.2962 | 0 | -6.222 | 0 | -7.6361 | 0 | -6.097 | 0 | -28.555 | -137.6528 | -20.1648 | -36.7553 | -35.1196 | 23.9067 | -33.4993 | -45.09 | -39.5214 | -150.4725 | -37.0268 | -32.7355 | -26.9013 | 97.2127 | -20.2268 | -167.1384 | -38.6954 | -130.1191 | -29.4571 | -171.3181 | -41.3544 | 53.9757 | -29.5153 | -125.9904 | -13.8108 | -9.2313 | -10.8435 | 10.2234 | -16.5549 | 28.4541 | -14.1936 | 101.7729 | -17.2758 | -84.178 | -17.1128 | -112.5613 | -13.5298 | -23.5448 | -11.5543 | -7.4154 | -42.906 | -36.3357 | -32.2498 | -28.9333 | -38.3318 | -28.9958 | -33.1986 | -41.5228 | -32.0931 | -28.2728 | -40.347 | -32.2454 | -31.4635 | 601 | -19.4577 | -27.0926 | -19.8832 | -32.093 | -19.3303 | -24.8845 | -19.3024 | -28.7735 | 601 | -35.2266 | -25.7969 | -22.6371 | -32.1098 | -22.7738 | -25.5625 | -35.3008 | -24.457 | -22.8363 | -30.6957 | -22.8988 | -27.1016 | -30.0395 | -25.9536 | -21.9766 | -34.125 | -26.0234 | -23.8274 | -30.1137 | -24.6137 | -22.1758 | -32.7109 | -26.1484 | -25.3665
602 | -6.2926 | 0 | -6.1774 | 0 | -7.4333 | 0 | -6.1956 | 0 | -29.1191 | -149.6323 | -20.2168 | -47.9103 | -35.2838 | 8.7672 | -35.169 | -55.4534 | -40.8494 | -160.0689 | -41.1833 | -59.6782 | -27.1498 | 84.0777 | -20.2298 | -176.2241 | -37.9443 | -150.5573 | -30.4516 | -178.4408 | -42.5038 | 35.9303 | -31.0492 | -142.0339 | -14.8413 | -14.88 | -11.6143 | 10.6756 | -18.6699 | 20.7979 | -13.0866 | 89.5189 | -20.504 | -85.3807 | -22.8043 | -98.738 | -14.3424 | -32.4201 | -11.2842 | -11.9942 | -42.92 | -37.1057 | -32.2931 | -28.9122 | -38.2755 | -29.1213 | -33.693 | -43.3669 | -31.9958 | -28.1227 | -41.5134 | -32.1248 | -32.3428 | 602 | -19.5726 | -27.9283 | -20.0466 | -33.4236 | -19.3656 | -25.3985 | -19.519 | -29.9909 | 602 | -37.0743 | -25.7032 | -22.6196 | -32.0981 | -22.9439 | -26.2597 | -37.1895 | -24.5625 | -22.7166 | -30.8422 | -22.9257 | -27.4974 | -30.8131 | -26.0005 | -21.8301 | -35.336 | -25.9474 | -24.9095 | -30.9283 | -24.8598 | -21.9271 | -34.0801 | -25.9292 | -26.1472
603 | -6.2588 | 0 | -6.2113 | 0 | -7.2599 | 0 | -6.2452 | 0 | -30.0874 | -158.967 | -20.6687 | -56.292 | -35.3204 | -3.6813 | -38.4323 | -58.8099 | -42.1789 | -164.2799 | -49.0814 | -114.2778 | -27.7455 | 70.794 | -20.5208 | 176.2201 | -37.4875 | -167.763 | -31.9824 | 175.4906 | -43.5462 | 18.3594 | -33.5626 | -153.3097 | -15.0763 | -3.5027 | -10.7329 | 21.9036 | -20.835 | 28.9661 | -11.322 | 80.4798 | -22.0986 | -103.5402 | -23.4735 | -46.6893 | -14.9766 | -30.1207 | -10.8087 | -20.347 | -43.2352 | -37.7565 | -32.1421 | -28.8055 | -38.5555 | -29.5143 | -34.4574 | -46.2482 | -31.8096 | -28.2269 | -43.0277 | -32.1974 | -33.3568 | 603 | -20.0671 | -29.2661 | -20.5905 | -34.3576 | -19.6945 | -26.2741 | -20.0245 | -31.786 | 603 | -39.9894 | -25.5508 | -22.5467 | -32.3442 | -23.303 | -27.1975 | -40.0369 | -24.5497 | -22.5603 | -31.2956 | -23.2691 | -28.2122 | -31.4977 | -25.8833 | -21.9681 | -36.8164 | -25.9861 | -26.0969 | -31.5452 | -24.8822 | -21.9817 | -35.7678 | -25.9522 | -27.1116
604 | -6.2265 | 0 | -6.3663 | 0 | -7.076 | 0 | -6.2891 | 0 | -31.5589 | -167.5899 | -21.5857 | -66.1782 | -35.5628 | -21.6455 | -43.7877 | -43.3971 | -43.3259 | -169.4503 | -45.9815 | 138.9854 | -28.8249 | 58.4182 | -21.1072 | 169.108 | -36.8109 | 176.3881 | -34.0413 | 174.2606 | -44.5937 | -1.1256 | -37.4256 | -159.8983 | -16.1576 | -9.6771 | -10.2772 | 19.5849 | -23.1343 | 44.9527 | -10.9768 | 66.7976 | -24.9429 | -104.553 | -18.3683 | -38.9843 | -15.9185 | -35.7417 | -10.5417 | -26.7396 | -43.9215 | -38.1468 | -31.8051 | -28.6911 | -39.2184 | -30.2796 | -35.4952 | -52.1542 | -31.4374 | -28.6202 | -44.6671 | -32.412 | -34.2901 | 604 | -21.0142 | -31.0419 | -21.544 | -34.5654 | -20.3298 | -27.595 | -20.7962 | -33.726 | 604 | -45.9277 | -25.2109 | -22.4646 | -32.8521 | -23.9133 | -28.4192 | -45.7879 | -24.3614 | -22.402 | -32.1424 | -23.9905 | -29.2061 | -31.9203 | -25.5786 | -22.3937 | -38.3008 | -26.0457 | -27.2141 | -31.7805 | -24.7291 | -22.3311 | -37.5911 | -26.1229 | -28.001
605 | -6.226 | 0 | -6.6127 | 0 | -6.933 | 0 | -6.2963 | 0 | -33.4025 | -169.9626 | -22.9574 | -69.0162 | -36.3513 | -36.4604 | -42.1244 | 10.947 | -44.8622 | -171.5384 | -40.3748 | 107.5507 | -30.5539 | 49.1392 | -21.9704 | 165.289 | -36.0995 | 157.9249 | -35.9098 | -175.9294 | -45.6182 | -25.0229 | -43.3788 | -147.2897 | -15.8164 | -0.7117 | -8.7891 | 22.0058 | -20.4155 | 67.3467 | -10.0861 | 59.6904 | -29.4112 | -78.0545 | -14.7061 | -41.4777 | -16.3614 | -32.8116 | -10.0896 | -35.539 | -45.1405 | -38.0976 | -31.3788 | -28.6288 | -40.3905 | -31.4413 | -36.6556 | -60.808 | -31.0814 | -29.3783 | -45.6283 | -32.9994 | -35.3697 | 605 | -22.4035 | -32.5902 | -22.828 | -34.485 | -21.2619 | -29.3399 | -21.7684 | -34.964 | 605 | -54.582 | -24.8554 | -22.4028 | -33.7778 | -24.8286 | -29.7226 | -54.1953 | -24.1484 | -22.3325 | -33.4575 | -25.145 | -30.3593 | -31.8716 | -25.1528 | -23.1523 | -39.0156 | -26.3867 | -28.4367 | -31.4849 | -24.4458 | -23.082 | -38.6953 | -26.7031 | -29.0734
606 | -6.2055 | 0 | -6.9053 | 0 | -6.886 | 0 | -6.2481 | 0 | -34.9694 | -165.9882 | -24.4939 | -68.7031 | -37.4855 | -54.1127 | -36.6634 | 16.3366 | -46.6921 | -168.1939 | -37.3266 | 89.4143 | -33.0457 | 41.7346 | -22.8673 | 163.9875 | -35.8282 | 139.9931 | -35.985 | -159.7039 | -46.3707 | -54.5675 | -44.0649 | -82.0495 | -15.6563 | -2.5462 | -8.0979 | 14.3075 | -17.9122 | 68.1245 | -10.2645 | 44.4909 | -27.2585 | -55.4235 | -12.393 | -51.6911 | -16.2793 | -36.4727 | -10.1753 | -43.1017 | -47.0817 | -37.8514 | -30.96 | -28.6285 | -42.1285 | -33.1131 | -37.5264 | -48.2962 | -30.686 | -30.4483 | -45.0733 | -33.7727 | -36.4516 | 606 | -23.9254 | -32.5533 | -24.0299 | -34.1464 | -22.2734 | -31.1291 | -22.6291 | -34.8998 | 606 | -42.0907 | -24.4805 | -22.423 | -35.2232 | -26.2078 | -30.6404 | -41.3909 | -23.8 | -22.3804 | -35.2425 | -26.865 | -31.2783 | -31.6459 | -24.7545 | -24.2428 | -38.168 | -26.8674 | -29.5656 | -30.9461 | -24.074 | -24.2002 | -38.1873 | -27.5246 | -30.2035
607 | -6.2174 | 0 | -7.2078 | 0 | -6.8986 | 0 | -6.1822 | 0 | -35.2626 | -157.9177 | -25.1813 | -57.2372 | -38.7389 | -73.1311 | -33.4153 | 6.8329 | -47.007 | -151.0292 | -35.3441 | 76.1267 | -36.1151 | 46.2176 | -23.2968 | 170.4944 | -35.8415 | 124.1822 | -34.3015 | -147.9694 | -46.7403 | -89.8656 | -37.3428 | -64.6119 | -15.1432 | -2.4265 | -7.3987 | 7.974 | -15.8535 | 60.6435 | -10.2973 | 35.3563 | -23.7382 | -29.3967 | -11.205 | -60.6864 | -15.614 | -30.1048 | -11.0782 | -50.506 | -50.1927 | -37.5242 | -30.5852 | -28.7552 | -44.6654 | -35.3484 | -37.7586 | -42.8283 | -30.2877 | -31.6922 | -43.3914 | -34.9611 | -37.9564 | 607 | -24.6038 | -31.1178 | -24.2244 | -33.5091 | -22.8517 | -31.9572 | -22.8095 | -33.3153 | 607 | -36.6109 | -24.0703 | -22.5378 | -37.4576 | -28.1406 | -30.86 | -35.6205 | -23.3891 | -22.573 | -37.7668 | -29.1662 | -31.5764 | -31.3068 | -24.3678 | -25.4748 | -36.1836 | -27.7533 | -31.0578 | -30.3164 | -23.6866 | -25.51 | -36.4928 | -28.7789 | -31.7742
608 | -6.2591 | 0 | -7.4708 | 0 | -7.0355 | 0 | -6.0787 | 0 | -34.391 | -151.7596 | -24.1154 | -46.314 | -40.6405 | -96.0042 | -31.4911 | -4.8452 | -45.0406 | -140.2418 | -33.9133 | 65.8706 | -37.6967 | 67.1674 | -22.7847 | 175.2892 | -35.7528 | 107.4059 | -32.257 | -147.2816 | -46.4009 | -133.2075 | -33.3571 | -74.0854 | -14.6747 | -3.4883 | -6.841 | 3.0912 | -14.4306 | 51.9442 | -10.648 | 26.3241 | -21.2776 | -48.2201 | -10.1447 | -77.2689 | -14.9587 | -38.1379 | -10.7951 | -59.5932 | -55.4636 | -37.4384 | -30.3691 | -29.0144 | -48.5027 | -37.9072 | -37.3849 | -39.5433 | -29.9622 | -32.9903 | -41.5958 | -36.5003 | -40.0932 | 608 | -23.6383 | -29.5681 | -23.0171 | -32.8088 | -22.4394 | -31.0372 | -21.9908 | -31.2469 | 608 | -33.2842 | -23.7031 | -22.7553 | -41.0319 | -30.4364 | -30.3494 | -32.0725 | -22.9267 | -22.9357 | -41.4672 | -31.8285 | -31.3062 | -31.1793 | -24.11 | -26.7312 | -34.125 | -29.0295 | -33.0577 | -29.9676 | -23.3336 | -26.9116 | -34.5603 | -30.4216 | -34.0145
609 | -6.2846 | 0 | -7.6244 | 0 | -7.226 | 0 | -5.9799 | 0 | -33.2904 | -153.1417 | -22.214 | -44.4461 | -44.249 | -132.751 | -30.337 | -18.4042 | -42.5916 | -143.1924 | -32.6456 | 55.7058 | -35.8191 | 85.3511 | -21.5041 | 178.5591 | -35.7424 | 88.7168 | -30.3996 | -151.2754 | -45.4361 | -175.1096 | -30.9016 | -85.4335 | -14.7339 | -10.935 | -6.6626 | -6.4682 | -14.1099 | 39.4268 | -11.3384 | 16.5772 | -20.1616 | -54.6477 | -9.481 | -91.5506 | -14.5529 | -41.2197 | -11.8225 | -66.2179 | -70.418 | -37.8985 | -30.2852 | -29.3907 | -55.3438 | -39.5782 | -36.7025 | -37.2768 | -29.6947 | -33.8705 | -40.0307 | -38.4057 | -44.3423 | 609 | -21.8625 | -28.3888 | -21.2637 | -31.9623 | -21.1912 | -29.1989 | -20.5565 | -29.5559 | 609 | -30.9922 | -23.4101 | -23.1061 | -47.7194 | -31.9538 | -29.4765 | -29.6524 | -22.4687 | -23.4108 | -48.1178 | -33.5983 | -30.7226 | -31.6139 | -24.0006 | -27.5859 | -32.4063 | -30.7813 | -37.1163 | -30.2741 | -23.0592 | -27.8906 | -32.8047 | -32.4258 | -38.3624
610 | -6.311 | 0 | -7.6956 | 0 | -7.4548 | 0 | -5.9129 | 0 | -32.3665 | -157.4593 | -20.4435 | -47.3747 | -49.1787 | 168.011 | -29.7206 | -31.3366 | -40.5289 | -150.6432 | -31.4511 | 45.0709 | -33.1888 | 87.8026 | -20.0273 | 177.505 | -36.4564 | 69.0039 | -28.8798 | -158.1153 | -44.3494 | 147.1617 | -29.2109 | -98.294 | -15.1395 | -20.1499 | -6.5301 | -16.0064 | -14.0139 | 28.3133 | -12.2518 | 7.6733 | -19.0535 | -71.0686 | -9.4909 | -104.4516 | -14.3885 | -52.8499 | -12.5244 | -73.0818 | -57.8603 | -38.8695 | -30.3975 | -29.79 | -73.9111 | -38.7641 | -36.1057 | -35.6072 | -29.5649 | -33.9651 | -38.8909 | -40.8962 | -54.6492 | 610 | -20.1677 | -27.6073 | -19.6611 | -30.88 | -19.7292 | -27.4212 | -19.055 | -28.3502 | 610 | -29.2962 | -23.2539 | -23.479 | -66.2155 | -31.0685 | -28.6509 | -27.9116 | -22.1101 | -23.8771 | -66.4563 | -32.8512 | -30.1928 | -32.5585 | -24.0865 | -27.6541 | -31.1953 | -33.2006 | -47.1944 | -31.1739 | -22.9427 | -28.0522 | -31.4361 | -34.9833 | -48.7363
611 | -6.3243 | 0 | -7.6786 | 0 | -7.6635 | 0 | -5.8194 | 0 | -31.6087 | -160.5548 | -19.0352 | -53.1544 | -48.4011 | 91.2522 | -29.4639 | -44.1099 | -39.0509 | -162.6922 | -30.507 | 34.1741 | -31.1797 | 83.3024 | -18.6651 | 171.7407 | -37.9235 | 51.3105 | -27.7201 | -168.1836 | -43.354 | 111.5528 | -28.0529 | -110.6106 | -15.8461 | -22.4333 | -6.5073 | -19.7567 | -14.0394 | 21.7552 | -13.5729 | 6.4693 | -18.8126 | -84.0749 | -9.4418 | -118.0447 | -14.6694 | -61.0927 | -14.1202 | -77.5312 | -51.7652 | -40.2775 | -30.6219 | -30.1011 | -54.6324 | -36.6212 | -35.702 | -34.3471 | -29.5548 | -33.3505 | -38.1434 | -43.3744 | -49.1547 | 611 | -18.7967 | -27.108 | -18.3837 | -29.8771 | -18.3798 | -26.0228 | -17.7328 | -27.5124 | 611 | -28.0228 | -23.2305 | -23.7768 | -46.9538 | -28.9426 | -28.0385 | -26.6685 | -21.8913 | -24.2817 | -46.9689 | -30.8018 | -29.8826 | -33.9532 | -24.2976 | -27.0262 | -30.4648 | -35.6958 | -41.4912 | -32.5989 | -22.9584 | -27.5311 | -30.4799 | -37.555 | -43.3353
612 | -6.3671 | 0 | -7.5892 | 0 | -7.8584 | 0 | -5.8487 | 0 | -30.8619 | -166.4915 | -17.9665 | -62.333 | -44.346 | 52.4411 | -29.4911 | -55.8568 | -38.2762 | -178.6813 | -29.9564 | 20.8247 | -29.6608 | 74.7971 | -17.5567 | 165.0775 | -39.6135 | 39.4833 | -26.8723 | -178.5823 | -42.757 | 76.4092 | -27.3729 | -124.5702 | -17.0513 | -25.7636 | -6.6065 | -26.8168 | -14.3787 | 13.2203 | -14.7106 | 5.8011 | -20.2429 | -87.5525 | -9.8125 | -131.6641 | -14.8034 | -73.7026 | -15.8346 | -79.0729 | -48.4883 | -41.6599 | -30.9342 | -30.3204 | -49.8633 | -34.8162 | -35.4955 | -33.378 | -29.7147 | -32.1791 | -37.7728 | -46.2608 | -42.541 | 612 | -17.7396 | -26.7922 | -17.4218 | -29.2242 | -17.2717 | -24.9634 | -16.6882 | -27.0041 | 612 | -27.0109 | -23.3476 | -23.9533 | -42.2741 | -27.227 | -27.6371 | -25.7888 | -21.8563 | -24.4717 | -42.0049 | -28.9675 | -29.6468 | -35.2928 | -24.5671 | -25.812 | -30.1836 | -38.6716 | -34.6826 | -34.0707 | -23.0758 | -26.3304 | -29.9144 | -40.4121 | -36.6923
613 | -6.3901 | 0 | -7.433 | 0 | -8.015 | 0 | -5.7807 | 0 | -30.1595 | -173.9583 | -17.141 | -70.7331 | -41.2664 | 28.1971 | -29.8852 | -66.9926 | -38.1977 | 166.459 | -29.8294 | 9.826 | -28.5442 | 64.2834 | -16.6952 | 156.135 | -41.5713 | 28.4367 | -26.3948 | 170.3939 | -42.588 | 43.8873 | -27.0974 | -137.0268 | -18.6851 | -18.6842 | -6.9738 | -31.2773 | -14.7716 | 9.7438 | -15.5837 | 20.8369 | -23.2089 | -87.5535 | -10.2434 | -146.2117 | -15.7448 | -82.1366 | -17.3546 | -74.9751 | -46.3478 | -41.4025 | -31.3673 | -30.3087 | -47.383 | -33.5353 | -35.3666 | -32.6361 | -29.9877 | -30.851 | -37.7729 | -47.5775 | -39.471 | 613 | -16.9135 | -26.6915 | -16.6995 | -28.975 | -16.4071 | -24.2632 | -15.9095 | -26.8282 | 613 | -26.246 | -23.5976 | -23.9186 | -39.95 | -26.1023 | -27.3516 | -25.2031 | -21.9727 | -24.528 | -39.368 | -27.7546 | -29.5859 | -35.0124 | -24.9772 | -24.4609 | -30.3399 | -40.1445 | -31.456 | -33.9695 | -23.3523 | -25.0703 | -29.7579 | -41.7968 | -33.6903
614 | -6.4219 | 0 | -7.1951 | 0 | -8.0797 | 0 | -5.8386 | 0 | -29.5482 | 177.6335 | -16.5045 | -78.5022 | -39.3173 | 3.8181 | -30.6253 | -78.3614 | -38.5647 | 153.3576 | -30.0912 | -3.5265 | -27.736 | 53.0105 | -16.0362 | 146.7423 | -44.4994 | 23.5562 | -26.2601 | 156.9617 | -42.8254 | 11.9088 | -27.017 | -150.2048 | -20.184 | -10.4443 | -7.1812 | -38.1195 | -15.359 | 3.6685 | -14.876 | 29.1671 | -23.5146 | -92.0474 | -10.8534 | -161.0347 | -16.5429 | -92.6852 | -17.4315 | -65.62 | -44.6763 | -39.4671 | -31.8132 | -30.1138 | -45.9341 | -32.5414 | -35.3044 | -32.0797 | -30.3125 | -29.6599 | -38.074 | -46.0211 | -37.3598 | 614 | -16.2726 | -26.7475 | -16.1602 | -29.0819 | -15.7463 | -23.8698 | -15.3367 | -26.8296 | 614 | -25.6578 | -23.8906 | -23.6919 | -38.739 | -25.3463 | -27.2247 | -24.8846 | -22.2328 | -24.2752 | -37.8544 | -26.7028 | -29.4658 | -33.0452 | -25.3913 | -23.238 | -30.8789 | -38.826 | -29.2801 | -32.272 | -23.7335 | -23.8213 | -29.9943 | -40.1825 | -31.5212
615 | -6.4638 | 0 | -6.9849 | 0 | -8.0463 | 0 | -5.8742 | 0 | -29.1395 | 166.9211 | -16.0438 | -88.5107 | -38.5707 | -19.2775 | -31.6383 | -87.528 | -39.1147 | 141.2788 | -30.7624 | -15.0568 | -27.2295 | 40.3921 | -15.6004 | 136.6927 | -46.872 | 39.3315 | -26.4042 | 145.3331 | -43.3204 | -18.3712 | -27.1799 | -163.7156 | -20.5183 | 5.3509 | -7.696 | -42.4095 | -16.2619 | -3.7341 | -13.4478 | 30.0564 | -23.8246 | -85.5991 | -11.9689 | -176.9766 | -18.2022 | -101.0585 | -16.946 | -60.0568 | -43.513 | -37.6369 | -32.2654 | -29.9036 | -45.0404 | -32.0627 | -35.3169 | -31.7065 | -30.6474 | -28.813 | -38.688 | -44.3901 | -36.0452 | 615 | -15.8129 | -26.9304 | -15.7853 | -29.5838 | -15.3087 | -23.7389 | -14.9836 | -27.0303 | 615 | -25.2427 | -24.1836 | -23.4398 | -38.0555 | -25.0778 | -27.2706 | -24.7216 | -22.6011 | -24.0294 | -36.9941 | -26.1885 | -29.4427 | -31.1731 | -25.8016 | -22.3492 | -31.7031 | -37.4052 | -27.9989 | -30.652 | -24.2191 | -22.9388 | -30.6417 | -38.5159 | -30.171
616 | -6.4833 | 0 | -6.7401 | 0 | -7.9257 | 0 | -5.9566 | 0 | -28.9563 | 155.8189 | -15.7915 | -99.3368 | -38.6555 | -38.4886 | -32.853 | -96.1179 | -39.7811 | 129.6167 | -31.7418 | -24.0037 | -27.0009 | 27.6054 | -15.3696 | 126.7525 | -45.4937 | 52.891 | -26.7888 | 133.321 | -43.8247 | -47.9077 | -27.7013 | -176.337 | -19.1309 | 19.1513 | -8.0232 | -48.4665 | -17.3516 | -10.2466 | -11.9493 | 28.9601 | -21.9635 | -83.7658 | -13.7191 | 163.5757 | -19.2395 | -110.6086 | -15.1892 | -58.7698 | -42.8307 | -36.364 | -32.6755 | -29.6823 | -44.4049 | -31.8132 | -35.4823 | -31.4647 | -30.8661 | -28.1659 | -39.4393 | -42.7616 | -35.0299 | 616 | -15.5655 | -27.2233 | -15.6 | -30.4045 | -15.0772 | -23.8395 | -14.8366 | -27.5266 | 616 | -24.9814 | -24.3828 | -23.199 | -37.6648 | -25.0731 | -27.5566 | -24.7246 | -22.9404 | -23.7257 | -36.4792 | -25.8566 | -29.5257 | -29.8807 | -26.1922 | -21.6826 | -32.6992 | -36.0215 | -27.1042 | -29.6239 | -24.7498 | -22.2093 | -31.5136 | -36.805 | -29.0733
617 | -6.5541 | 0 | -6.5658 | 0 | -7.7768 | 0 | -6.0854 | 0 | -29.0711 | 144.9355 | -15.7397 | -108.9575 | -38.9562 | -54.8843 | -34.4382 | -101.7681 | -40.7472 | 117.9978 | -32.9602 | -29.5169 | -27.0382 | 14.3418 | -15.3666 | 116.8956 | -43.9789 | 52.037 | -27.4475 | 120.9855 | -44.305 | -77.754 | -28.6123 | 170.8737 | -16.7647 | 26.3311 | -8.8075 | -47.9858 | -18.6748 | -4.2383 | -10.6555 | 24.9635 | -20.2032 | -82.0952 | -16.0487 | 142.2969 | -21.1725 | -116.4359 | -13.6686 | -64.4565 | -42.5745 | -35.4768 | -33.0745 | -29.5315 | -43.9729 | -31.5588 | -35.8471 | -31.4018 | -31.1205 | -27.6752 | -40.3627 | -41.1752 | -34.7013 | 617 | -15.5228 | -27.7403 | -15.601 | -31.4438 | -15.0751 | -24.1853 | -14.9161 | -28.3756 | 617 | -24.8477 | -24.5664 | -22.9774 | -37.4071 | -24.993 | -28.0703 | -24.836 | -23.3437 | -23.4461 | -36.1961 | -25.4734 | -29.7617 | -28.9227 | -26.5204 | -21.1211 | -33.7969 | -34.6094 | -26.9245 | -28.911 | -25.2977 | -21.5898 | -32.5859 | -35.0898 | -28.6159
618 | -6.6038 | 0 | -6.4094 | 0 | -7.5687 | 0 | -6.1953 | 0 | -29.5546 | 131.6068 | -15.9214 | -119.1259 | -39.3763 | -72.9795 | -36.6921 | -107.2927 | -42.06 | 108.9011 | -34.4351 | -33.4902 | -27.4406 | -0.1476 | -15.6295 | 106.2158 | -42.8127 | 49.9251 | -28.565 | 108.9658 | -44.8921 | -107.2415 | -29.9692 | 160.3241 | -15.2418 | 20.4434 | -8.7464 | -52.3805 | -19.2358 | -7.1643 | -9.6468 | 17.2056 | -17.6143 | -90.8194 | -20.1672 | 120.2126 | -22.3926 | -118.0835 | -12.1561 | -71.583 | -42.7345 | -34.7727 | -33.3234 | -29.3517 | -43.7345 | -31.5618 | -36.3977 | -31.4633 | -31.264 | -27.2571 | -41.4758 | -40.1781 | -34.9034 | 618 | -15.7185 | -28.5873 | -15.825 | -32.6936 | -15.3445 | -24.9124 | -15.2645 | -29.6183 | 618 | -24.8595 | -24.6602 | -22.7479 | -37.3251 | -25.1524 | -28.829 | -25.0539 | -23.6953 | -23.1564 | -36.1658 | -25.3665 | -30.2024 | -28.1689 | -26.7196 | -20.6533 | -35.0664 | -33.7687 | -27.3347 | -28.3633 | -25.7547 | -21.0618 | -33.9071 | -33.9828 | -28.7081
619 | -6.6545 | 0 | -6.3426 | 0 | -7.3177 | 0 | -6.2935 | 0 | -30.4533 | 121.8444 | -16.3992 | -128.4599 | -40.4039 | -92.4612 | -39.612 | -101.2821 | -43.5126 | 100.3572 | -35.8561 | -29.4948 | -28.3078 | -14.3017 | -16.1467 | 97.3952 | -41.3109 | 44.6649 | -30.2655 | 97.5307 | -45.7388 | -135.1912 | -31.8682 | 151.2388 | -13.2692 | 20.9047 | -9.1534 | -49.9987 | -19.5046 | 2.7144 | -9.0292 | 11.5776 | -17.0062 | -97.6695 | -24.8601 | 69.3824 | -24.0451 | -110.7974 | -11.2133 | -80.2338 | -43.2185 | -34.2874 | -33.2804 | -29.2263 | -43.6325 | -31.678 | -37.2098 | -31.8138 | -31.385 | -27.0262 | -42.784 | -39.3021 | -35.6992 | 619 | -16.2151 | -29.7684 | -16.3298 | -34.0306 | -15.8779 | -26.1193 | -15.8711 | -31.2435 | 619 | -25.1593 | -24.7305 | -22.5718 | -37.2899 | -25.3354 | -29.8921 | -25.4712 | -24.0673 | -22.9328 | -36.3148 | -25.3845 | -30.9163 | -27.6329 | -26.6259 | -20.3717 | -36.4414 | -32.9595 | -28.3815 | -27.9448 | -25.9627 | -20.7327 | -35.4663 | -33.0086 | -29.4057
620 | -6.7025 | 0 | -6.4046 | 0 | -7.0712 | 0 | -6.3987 | 0 | -31.7979 | 111.0435 | -17.1825 | -137.9487 | -42.38 | -111.1104 | -41.5777 | -77.7001 | -45.2856 | 93.2987 | -36.4419 | -21.5931 | -29.737 | -27.6725 | -16.9631 | 87.9455 | -40.3942 | 35.0811 | -32.7792 | 91.3873 | -46.7404 | -158.177 | -34.5655 | 147.2481 | -12.1949 | 11.6788 | -8.833 | -51.1238 | -18.7975 | 5.7454 | -8.4763 | 2.7316 | -14.9435 | -111.6242 | -24.7792 | -38.2219 | -25.4768 | -100.6789 | -10.9257 | -93.0593 | -44.1867 | -34.1932 | -33.0355 | -29.1828 | -43.7648 | -32.158 | -38.1311 | -32.4227 | -31.433 | -27.0296 | -44.2444 | -38.786 | -36.6986 | 620 | -17.0223 | -31.1909 | -17.1157 | -35.0265 | -16.721 | -27.9292 | -16.7779 | -33.3535 | 620 | -25.7202 | -24.7305 | -22.4803 | -37.3602 | -25.7534 | -31.0599 | -26.0181 | -24.3618 | -22.7841 | -36.6936 | -25.7593 | -31.7324 | -27.4907 | -26.333 | -20.3271 | -37.8398 | -32.3814 | -29.6274 | -27.7886 | -25.9643 | -20.6309 | -37.1732 | -32.3873 | -30.2999
621 | -6.7299 | 0 | -6.5306 | 0 | -6.8744 | 0 | -6.4564 | 0 | -33.5549 | 105.7788 | -18.348 | -144.3326 | -44.6177 | -124.6251 | -39.4067 | -52.2142 | -47.6858 | 91.9999 | -35.7413 | -11.7213 | -31.8645 | -39.257 | -18.0494 | 82.626 | -40.2346 | 26.5819 | -36.3526 | 92.0437 | -47.3685 | -172.4635 | -37.7296 | 156.2943 | -11.2093 | 5.6281 | -8.6445 | -50.9123 | -17.7664 | 7.9526 | -8.217 | -4.5907 | -13.6612 | -125.0506 | -19.14 | -73.2557 | -22.1195 | -100.435 | -10.7452 | -108.1201 | -45.6058 | -34.4769 | -32.6761 | -29.2386 | -44.1371 | -32.9613 | -39.14 | -33.4252 | -31.4603 | -27.2377 | -45.4799 | -38.7181 | -37.6424 | 621 | -18.209 | -32.4204 | -18.2363 | -34.9733 | -17.8475 | -30.4533 | -17.9399 | -35.5015 | 621 | -26.6953 | -24.7304 | -22.5087 | -37.6065 | -26.4307 | -32.2656 | -26.8946 | -24.5859 | -22.7822 | -37.2627 | -26.5049 | -32.6836 | -27.747 | -25.9462 | -20.5078 | -38.9493 | -32.1875 | -30.768 | -27.9463 | -25.8017 | -20.7813 | -38.6055 | -32.2617 | -31.186
622 | -6.7459 | 0 | -6.7345 | 0 | -6.7351 | 0 | -6.5099 | 0 | -35.5348 | 104.5084 | -19.8091 | -147.3238 | -46.2784 | -143.5319 | -36.0135 | -48.6047 | -50.012 | 100.9582 | -34.4613 | -9.744 | -34.9522 | -45.8615 | -19.4138 | 81.1663 | -39.8469 | 24.3459 | -39.5918 | 118.2462 | -47.0686 | 175.7464 | -38.4056 | -178.9518 | -10.651 | -3.3591 | -7.8721 | -56.7315 | -16.8074 | 3.2415 | -7.9923 | -13.4503 | -13.8376 | -142.1382 | -16.6099 | -98.4877 | -21.0092 | -110.7459 | -10.5865 | -122.6774 | -47.4933 | -35.2322 | -32.2195 | -29.3839 | -44.7785 | -33.8416 | -39.9103 | -34.7429 | -31.4177 | -27.6681 | -46.0353 | -38.6726 | -38.7023 | 622 | -19.6849 | -32.6763 | -19.5633 | -34.0725 | -19.2561 | -33.4754 | -19.3184 | -35.7254 | 622 | -27.997 | -24.6718 | -22.638 | -38.044 | -27.1071 | -33.1752 | -28.0084 | -24.6826 | -22.874 | -38.0434 | -27.3317 | -33.4004 | -28.4863 | -25.4736 | -20.9222 | -39.3008 | -31.9381 | -31.9672 | -28.4977 | -25.4844 | -21.1582 | -39.3002 | -32.1627 | -32.1924
623 | -6.7367 | 0 | -6.9446 | 0 | -6.6573 | 0 | -6.4688 | 0 | -36.7986 | 112.4008 | -21.0358 | -142.5876 | -49.2281 | -177.0899 | -33.4381 | -53.2411 | -50.1025 | 114.9402 | -33.2843 | -11.0158 | -38.6335 | -35.8561 | -20.5286 | 83.6279 | -39.0678 | 15.7796 | -36.7815 | 145.4316 | -46.0848 | 161.9212 | -36.4289 | -167.6321 | -10.4027 | -10.3014 | -7.7517 | -59.2175 | -16.1744 | -3.7734 | -8.1398 | -19.9936 | -12.943 | -154.5963 | -14.6718 | -123.4788 | -19.3386 | -126.7567 | -10.8717 | -135.7034 | -50.0412 | -36.6965 | -31.8682 | -29.7276 | -45.8913 | -35.1198 | -40.0272 | -36.3864 | -31.3323 | -28.1102 | -45.8337 | -39.094 | -39.8279 | 623 | -20.9157 | -31.7272 | -20.5549 | -33.0879 | -20.4025 | -34.3012 | -20.3192 | -34.2465 | 623 | -29.6497 | -24.5956 | -22.9909 | -38.9467 | -28.1752 | -33.3699 | -29.4418 | -24.675 | -23.2588 | -39.234 | -28.651 | -33.5584 | -29.9598 | -25.1315 | -21.3735 | -38.8891 | -32.1494 | -33.1706 | -29.7519 | -25.2109 | -21.6414 | -39.1764 | -32.6252 | -33.3591
624 | -6.7304 | 0 | -7.1567 | 0 | -6.6587 | 0 | -6.4301 | 0 | -36.9648 | 120.9192 | -21.3735 | -133.573 | -50.5834 | 147.9174 | -31.6749 | -62.7388 | -48.828 | 125.2142 | -32.0785 | -14.2802 | -40.0201 | -10.9736 | -20.8139 | 91.1237 | -38.2257 | 9.627 | -33.2281 | 151.607 | -44.6667 | 145.0098 | -34.2109 | -164.5377 | -10.3926 | -18.7844 | -7.4495 | -65.0028 | -15.7012 | -12.1564 | -8.4758 | -26.5445 | -12.9265 | -170.8112 | -13.1549 | -143.4437 | -18.1251 | -143.2849 | -11.2269 | -148.8536 | -52.8479 | -38.883 | -31.5093 | -30.1573 | -47.5208 | -36.6142 | -39.6572 | -38.2113 | -31.2732 | -28.5362 | -45.4576 | -39.7287 | -41.1823 | 624 | -21.2502 | -30.4854 | -20.6609 | -31.9281 | -20.6849 | -32.1522 | -20.3878 | -32.4884 | 624 | -31.4809 | -24.5428 | -23.4269 | -40.3641 | -29.4575 | -32.9985 | -31.0546 | -24.6145 | -23.7272 | -40.8621 | -30.1841 | -33.2271 | -32.1526 | -24.7789 | -21.8058 | -38.3009 | -32.572 | -34.5236 | -31.7263 | -24.8506 | -22.1061 | -38.7989 | -33.2986 | -34.7522
625 | -6.7064 | 0 | -7.2806 | 0 | -6.722 | 0 | -6.3392 | 0 | -36.201 | 126.1235 | -20.5152 | -125.647 | -49.4703 | 91.0293 | -30.4742 | -73.6071 | -47.3191 | 125.8895 | -31.0511 | -19.5879 | -37.6304 | 9.4508 | -20.0184 | 99.2132 | -37.5263 | 0.0938 | -30.5873 | 145.1924 | -43.5231 | 124.2646 | -32.5009 | -167.6075 | -10.4429 | -29.0436 | -6.8131 | -73.0748 | -15.6088 | -18.3955 | -8.6913 | -33.6226 | -13.0899 | 169.4961 | -12.4312 | -164.4688 | -17.9914 | -170.3145 | -11.2807 | -165.8878 | -53.5786 | -41.852 | -31.1801 | -30.5434 | -49.7934 | -38.4497 | -38.9524 | -40.0579 | -31.1556 | -28.804 | -44.9837 | -40.6087 | -42.7435 | 625 | -20.3941 | -29.3744 | -19.7621 | -30.8891 | -19.8687 | -29.6237 | -19.4334 | -31.0601 | 625 | -33.3515 | -24.4492 | -23.837 | -42.5128 | -31.1691 | -32.2304 | -32.7773 | -24.4336 | -24.2042 | -43.0714 | -32.1105 | -32.6132 | -35.1456 | -24.4737 | -22.0976 | -37.7031 | -33.3281 | -36.0215 | -34.5714 | -24.4581 | -22.4648 | -38.2617 | -34.2695 | -36.4043

## 14m_channel_Conn2
[62 empty] | Parameter | [8 empty] | Parameter
[62 empty] | Frequency | [8 empty] | Frequency
Parameter | Insertion loss Magnitude in dB | [7 empty] | NEXT loss near Magnitude in dB | [11 empty] | NEXT loss far Magnitude in dB | [11 empty] | Return loss nearMagnitude in dB | [7 empty] | Return loss farMagnitude in dB | [8 empty] | FEXT loss
Frequency | '45 | '45 | '12 | '12 | '36 | '36 | '78 | '78 | '12-45 | '12-45 | '36-45 | '36-45 | '45-78 | '45-78 | '12-36 | '12-36 | '12-78 | '12-78 | '36-78 | '36-78 | '12-45 | '12-45 | '36-45 | '36-45 | '45-78 | '45-78 | '12-36 | '12-36 | '12-78 | '12-78 | '36-78 | '36-78 | '45 | '45 | '12 | '12 | '36 | '36 | '78 | '78 | '45 | '45 | '12 | '12 | '36 | '36 | '78 | '78 |  | '12-45 | '36-45 | '45-78 | '12-36 | '12-78 | '36-78 | '45-12 | '45-36 | '78-45 | '36-12 | '78-12 | '78-36 |  | Pr1 PSNEXT | Pr2 PSNEXT | Pr3 PSNEXT | Pr4 PSNEXT | Pr1 PSNEXT | Pr2 PSNEXT | Pr3 PSNEXT | Pr4 PSNEXT |  | 12-1ELFEXT | 13-1ELFEXT | 14-1ELFEXT | 23-2ELFEXT | 24-2ELFEXT | 34-3ELFEXT | 12-2ELFEXT | 13-3ELFEXT | 14-4ELFEXT | 23-3ELFEXT | 24-4ELFEXT | 34-4ELFEXT | 21-1ELFEXT | 31-1ELFEXT | 41-1ELFEXT | 32-2ELFEXT | 42-2ELFEXT | 43-3ELFEXT | 21-2ELFEXT | 31-3ELFEXT | 41-4ELFEXT | 32-3ELFEXT | 42-4ELFEXT | 43-4ELFEXT
1 | -0.2968 | 0 | -0.2851 | 0 | -0.328 | 0 | -0.3319 | 0 | -97.6912 | 47.3085 | -86.8157 | -141.3195 | -96.7788 | 67.1463 | -100.0137 | -82.2913 | -100.5861 | 39.7175 | -96.2342 | -134.3053 | -100.3529 | 81.7638 | -87.4702 | -123.9775 | -97.2489 | 48.8469 | -96.349 | -179.8596 | -101.8744 | 81.8899 | -97.806 | -144.081 | -33.3152 | 1.5424 | -32.5385 | -21.7651 | -33.3759 | -3.9204 | -33.4004 | -34.3655 | -33.4272 | -15.1036 | -32.4783 | -32.5707 | -28.5629 | 20.0601 | -32.3119 | -15.0474 | -83.2808 | -87.8199 | -85.0542 | -80.9175 | -94.3472 | -85.5738 | -83.289 | -87.7421 | -85.0194 | -80.8788 | -94.4023 | -85.5546 | -81.9025 | 1 | -86.0873 | -94.4705 | -86.1628 | -92.7138 | -86.8379 | -94.1012 | -86.5994 | -93.7769 | 1 | -87.4453 | -84.7226 | -80.6207 | -94.0621 | -85.2887 | -82.961 | -87.457 | -84.6914 | -80.5856 | -94.0192 | -85.2419 | -82.9571 | -87.5231 | -84.7574 | -80.582 | -94.1172 | -85.2695 | -81.5745 | -87.5348 | -84.7262 | -80.5469 | -94.0743 | -85.2227 | -81.5706
2 | -0.3621 | 0 | -0.3503 | 0 | -0.3855 | 0 | -0.4089 | 0 | -94.309 | -10.482 | -83.6349 | 176.9076 | -94.4892 | 38.5785 | -95.0406 | -69.8523 | -94.5409 | -8.2505 | -96.3378 | -164.7145 | -97.3093 | 47.5019 | -85.4607 | -130.8764 | -94.3388 | 12.9012 | -87.9185 | 127.7432 | -95.2081 | 75.803 | -98.7152 | -171.5495 | -25.9749 | -0.9691 | -27.0932 | -9.8488 | -25.6956 | -1.4291 | -27.9807 | -11.86 | -26.4038 | -4.9965 | -27.4144 | -11.8128 | -23.5431 | -2.2571 | -26.635 | -12.356 | -77.5964 | -84.948 | -79.2449 | -75.6707 | -87.991 | -80.7957 | -77.5339 | -84.6355 | -79.1707 | -75.6902 | -88.1277 | -80.7332 | -75.1989 | 2 | -82.9613 | -89.8483 | -83.1195 | -90.2707 | -84.6877 | -86.7733 | -83.3787 | -90.947 | 2 | -84.2734 | -78.8086 | -75.3086 | -87.6407 | -80.4454 | -77.1484 | -84.2852 | -78.7852 | -75.2618 | -87.6055 | -80.3868 | -77.125 | -84.5859 | -78.8828 | -75.3281 | -87.7774 | -80.3829 | -74.8134 | -84.5977 | -78.8594 | -75.2813 | -87.7422 | -80.3243 | -74.79
3 | -0.4356 | 0 | -0.4238 | 0 | -0.459 | 0 | -0.4473 | 0 | -93.5148 | -60.4562 | -82.6116 | 133.4735 | -95.5962 | 50.0017 | -87.6524 | -71.4945 | -91.4041 | -54.9028 | -97.974 | 165.8367 | -98.3298 | 52.6644 | -84.1727 | -126.4943 | -95.7109 | -29.4741 | -83.8744 | 90.2251 | -91.9874 | 74.9484 | -105.4805 | -142.2681 | -25.4862 | -28.5398 | -26.8317 | -36.2725 | -25.1696 | -27.7625 | -27.3871 | -39.4065 | -25.5434 | -31.0355 | -26.8955 | -38.1136 | -23.3854 | -33.9399 | -26.5264 | -41.6055 | -74.3654 | -83.3849 | -75.9044 | -72.5685 | -84.4318 | -77.9279 | -74.3145 | -82.9004 | -75.8887 | -72.5528 | -84.6387 | -77.8301 | -71.5581 | 3 | -82.075 | -85.3972 | -81.3329 | -89.3597 | -83.7251 | -83.118 | -80.9952 | -90.3171 | 3 | -82.4648 | -75.4531 | -72.1329 | -84.008 | -77.5041 | -73.8555 | -82.4766 | -75.4297 | -72.1212 | -83.9728 | -77.4806 | -73.8672 | -82.9493 | -75.4688 | -72.1172 | -84.2149 | -77.4063 | -71.0991 | -82.9611 | -75.4454 | -72.1055 | -84.1797 | -77.3828 | -71.1108
4 | -0.4938 | 0 | -0.4938 | 0 | -0.5289 | 0 | -0.5406 | 0 | -92.7741 | -113.6742 | -82.3951 | 81.9489 | -92.8796 | 63.4836 | -83.0395 | -94.4678 | -90.3127 | -98.0564 | -100.8585 | 105.0833 | -94.6589 | 76.8905 | -81.7105 | -117.6152 | -99.283 | -101.5129 | -81.878 | 59.3561 | -88.8641 | 76.8026 | -95.2217 | -102.5608 | -27.2207 | -50.6349 | -29.3129 | -60.7158 | -27.0102 | -48.7215 | -29.6166 | -67.4544 | -26.8886 | -53.7328 | -29.2225 | -63.9862 | -25.4614 | -60.7219 | -29.1239 | -70.014 | -72.1071 | -82.1618 | -73.5524 | -70.3297 | -81.9391 | -75.775 | -72.0328 | -81.4625 | -73.5719 | -70.318 | -81.9586 | -75.7477 | -69.1206 | 4 | -81.6723 | -81.9213 | -79.662 | -88.1591 | -81.4239 | -80.8989 | -78.6856 | -87.6513 | 4 | -80.9687 | -73.0781 | -69.8359 | -81.4453 | -75.2812 | -71.5039 | -80.9687 | -73.043 | -69.7891 | -81.4102 | -75.2344 | -71.4922 | -81.668 | -73.0586 | -69.8242 | -81.4648 | -75.2539 | -68.5917 | -81.668 | -73.0235 | -69.7774 | -81.4297 | -75.2071 | -68.58
5 | -0.5637 | 0 | -0.5637 | 0 | -0.5989 | 0 | -0.5872 | 0 | -91.3426 | -172.4167 | -81.7951 | 22.7507 | -88.9583 | 70.8624 | -80.5199 | -119.1573 | -89.4725 | -139.4499 | -95.7343 | 23.2199 | -90.1929 | 81.3364 | -78.9638 | -115.4062 | -92.6199 | 176.6159 | -81.5686 | 33.4419 | -86.4733 | 72.6604 | -89.2429 | -111.7968 | -30.3548 | -63.0376 | -34.8938 | -77.9861 | -30.2259 | -58.0389 | -35.0401 | -94.7105 | -29.6888 | -68.7911 | -34.7858 | -84.1039 | -29.6506 | -78.6556 | -35.2451 | -97.8501 | -70.3878 | -80.9504 | -71.755 | -68.6378 | -80.091 | -74.1535 | -70.3372 | -80.0286 | -71.7512 | -68.6223 | -79.97 | -74.2083 | -67.2886 | 5 | -80.6452 | -79.692 | -78.0263 | -85.7394 | -78.4777 | -79.9235 | -76.8082 | -83.9903 | 5 | -79.4649 | -71.1875 | -68.0741 | -79.5273 | -73.5898 | -69.7383 | -79.4649 | -71.1523 | -68.0506 | -79.4921 | -73.5663 | -69.75 | -80.3867 | -71.1913 | -68.0586 | -79.4063 | -73.6446 | -66.6897 | -80.3867 | -71.1561 | -68.0351 | -79.3711 | -73.6211 | -66.7014
6 | -0.6338 | 0 | -0.6221 | 0 | -0.6689 | 0 | -0.6455 | 0 | -88.6038 | 134.9253 | -79.2475 | -35.507 | -86.326 | 69.9654 | -80.1946 | -143.0279 | -88.327 | 163.6779 | -88.3923 | -17.57 | -87.358 | 74.6278 | -76.3229 | -121.1366 | -86.7292 | 141.1209 | -83.4387 | 6.4844 | -84.713 | 65.8737 | -85.2075 | -131.8604 | -33.3472 | -56.7911 | -44.6315 | -26.205 | -32.555 | -48.4506 | -60.0348 | -117.3839 | -32.8745 | -67.2515 | -46.6197 | -32.6999 | -35.0482 | -66.7723 | -56.2791 | 48.9131 | -68.989 | -79.8093 | -70.3172 | -67.2859 | -78.7156 | -72.7976 | -68.9736 | -78.8291 | -70.3252 | -67.2705 | -78.415 | -72.9971 | -65.7457 | 6 | -78.0684 | -79.062 | -76.4013 | -82.7999 | -75.6416 | -80.1117 | -75.1055 | -80.6973 | 6 | -78.1953 | -69.6914 | -66.6521 | -78.0935 | -72.1755 | -68.3047 | -78.207 | -69.6563 | -66.6404 | -78.0467 | -72.1521 | -68.3281 | -79.1755 | -69.6834 | -66.6367 | -77.7929 | -72.375 | -65.0768 | -79.1872 | -69.6483 | -66.625 | -77.7461 | -72.3516 | -65.1002
7 | -0.6688 | 0 | -0.6923 | 0 | -0.7157 | 0 | -0.704 | 0 | -85.3431 | 93.9703 | -76.5615 | -83.0381 | -83.6065 | 57.2537 | -82.1092 | -164.7986 | -86.7159 | 112.1112 | -84.4753 | -42.2787 | -85.0102 | 66.5429 | -74.5105 | -131.2804 | -82.8857 | 112.3782 | -88.1939 | -17.5641 | -83.5874 | 59.3202 | -82.5413 | -150.9533 | -32.8714 | -46.412 | -35.5782 | 12.1722 | -31.5705 | -42.2734 | -37.3099 | 31.6897 | -33.0236 | -55.0402 | -35.7104 | 11.0859 | -33.2669 | -38.3237 | -35.0443 | 27.7089 | -67.8482 | -78.5709 | -69.1295 | -66.1802 | -77.5982 | -71.6451 | -67.868 | -77.7235 | -69.0673 | -66.1415 | -77.1454 | -72.0673 | -64.3005 | 7 | -75.3235 | -79.5058 | -74.9766 | -79.9753 | -73.5956 | -80.4343 | -73.718 | -78.2121 | 7 | -77.0547 | -68.3985 | -65.5114 | -76.9059 | -70.9528 | -67.1523 | -77.0312 | -68.3516 | -65.4762 | -76.8825 | -70.9411 | -67.164 | -77.9021 | -68.4607 | -65.4727 | -76.4531 | -71.375 | -63.5848 | -77.8786 | -68.4138 | -65.4375 | -76.4297 | -71.3633 | -63.5965
8 | -0.7274 | 0 | -0.7391 | 0 | -0.7625 | 0 | -0.7391 | 0 | -82.5537 | 59.9816 | -74.5155 | -123.3853 | -81.5406 | 46.5557 | -88.9903 | -174.3392 | -83.892 | 61.7773 | -81.0359 | -70.4234 | -82.5733 | 59.7649 | -73.3147 | -143.7093 | -79.9947 | 85.4311 | -109.641 | 119.8626 | -82.694 | 56.6814 | -80.5104 | -169.3474 | -31.4076 | -54.5804 | -31.7334 | -4.6978 | -30.358 | -53.9295 | -32.6311 | 5.7086 | -31.1889 | -59.378 | -31.5695 | -8.2307 | -30.1619 | -48.1586 | -30.7544 | 1.5677 | -66.895 | -77.5043 | -68.1293 | -65.1684 | -76.7153 | -70.5981 | -66.9031 | -76.9344 | -68.0203 | -65.1063 | -75.9344 | -71.3016 | -63.1365 | 8 | -73.1946 | -79.6268 | -73.5169 | -77.2187 | -72.0651 | -79.6186 | -72.5557 | -76.1473 | 8 | -76.207 | -67.2929 | -64.441 | -75.9762 | -69.859 | -66.1406 | -76.1953 | -67.2578 | -64.4293 | -75.9528 | -69.859 | -66.164 | -76.7769 | -67.4019 | -64.3789 | -75.1953 | -70.5625 | -62.374 | -76.7652 | -67.3668 | -64.3672 | -75.1719 | -70.5625 | -62.3974
9 | -0.7857 | 0 | -0.774 | 0 | -0.8092 | 0 | -0.7857 | 0 | -80.3496 | 29.4145 | -73.4621 | -160.037 | -80.2093 | 34.318 | -90.5552 | -76.5815 | -81.6893 | 20.2907 | -79.135 | -97.6809 | -80.4814 | 50.0581 | -72.9627 | -156.5977 | -78.368 | 61.7638 | -85.4682 | 110.272 | -81.5205 | 55.2042 | -79.6141 | 171.3784 | -31.1959 | -74.4192 | -30.7495 | -26.5224 | -30.6457 | -75.4712 | -31.3405 | -19.9481 | -30.1836 | -76.6969 | -30.333 | -32.1676 | -29.161 | -71.6907 | -29.427 | -24.8813 | -66.0002 | -76.633 | -67.2384 | -64.215 | -75.7033 | -69.6955 | -66.0123 | -76.5826 | -67.0943 | -64.1412 | -74.7818 | -70.5396 | -62.1248 | 9 | -71.9507 | -77.7252 | -72.355 | -75.4499 | -71.304 | -77.2501 | -71.9166 | -74.8763 | 9 | -75.7969 | -66.3086 | -63.4293 | -74.9293 | -68.9215 | -65.2031 | -75.8086 | -66.2851 | -63.4293 | -74.8941 | -68.9098 | -65.2266 | -75.8473 | -66.4527 | -63.3555 | -74.0078 | -69.7656 | -61.3156 | -75.859 | -66.4292 | -63.3555 | -73.9726 | -69.7539 | -61.3391
10 | -0.8557 | 0 | -0.8323 | 0 | -0.8557 | 0 | -0.8206 | 0 | -78.9642 | -1.6667 | -73.4537 | 165.7784 | -79.1048 | 18.8226 | -80.9045 | -78.6101 | -79.9919 | -14.15 | -78.1298 | -127.6136 | -78.4996 | 36.9659 | -73.3979 | -168.5311 | -77.4331 | 34.2541 | -79.4432 | 84.3597 | -79.9592 | 47.4447 | -79.1101 | 152.5212 | -32.7561 | -100.4423 | -31.8645 | -48.8963 | -32.8619 | -103.641 | -32.1854 | -45.2471 | -30.4902 | -99.4577 | -30.9252 | -57.4673 | -29.8003 | -99.3154 | -29.7536 | -51.7693 | -65.2146 | -75.9139 | -66.4725 | -63.3318 | -74.7264 | -68.9061 | -65.2229 | -76.7346 | -66.2581 | -63.2581 | -73.7581 | -69.7268 | -61.3865 | 10 | -71.541 | -75.11 | -71.6336 | -74.2377 | -71.0837 | -74.4868 | -71.5881 | -73.9332 | 10 | -75.8789 | -65.4024 | -62.4761 | -73.8941 | -68.0738 | -64.3672 | -75.9023 | -65.4024 | -62.5112 | -73.8707 | -68.0855 | -64.4023 | -75.0582 | -65.6168 | -62.4024 | -72.9258 | -68.8945 | -60.5308 | -75.0816 | -65.6168 | -62.4375 | -72.9024 | -68.9062 | -60.5659
11 | -0.8907 | 0 | -0.879 | 0 | -0.9024 | 0 | -0.8673 | 0 | -78.2223 | -31.2134 | -74.5676 | 131.4423 | -78.8736 | 6.1864 | -76.6226 | -95.4064 | -79.5567 | -48.1976 | -78.6318 | -161.3508 | -77.1652 | 21.802 | -74.7033 | -176.9577 | -77.3548 | 7.784 | -76.442 | 57.5007 | -79.0123 | 36.8887 | -80.0873 | 137.7866 | -36.9941 | -131.5493 | -35.4959 | -69.501 | -38.45 | -139.1015 | -35.5375 | -70.1851 | -32.2864 | -123.3697 | -33.3223 | -83.7401 | -32.2529 | -129.0771 | -31.6982 | -79.9925 | -64.4605 | -75.2574 | -65.6715 | -62.5309 | -73.7262 | -68.1637 | -64.4454 | -77.2032 | -65.4571 | -62.4728 | -72.8556 | -68.879 | -60.7029 | 11 | -72.0099 | -73.1969 | -71.5242 | -74.2321 | -71.4597 | -72.64 | -71.7817 | -73.8996 | 11 | -76.3125 | -64.5664 | -61.6402 | -72.8472 | -67.2847 | -63.543 | -76.3242 | -64.5547 | -61.6636 | -72.8238 | -67.2964 | -63.5781 | -74.3667 | -64.7808 | -61.5821 | -71.9766 | -68 | -59.8005 | -74.3784 | -64.7691 | -61.6055 | -71.9532 | -68.0117 | -59.8356
12 | -0.9259 | 0 | -0.9024 | 0 | -0.9493 | 0 | -0.9142 | 0 | -78.1589 | -59.7666 | -77.5611 | 94.4895 | -79.6759 | -7.1672 | -74.5164 | -114.165 | -79.7243 | -80.8313 | -80.6091 | 156.057 | -76.3996 | 4.3216 | -77.047 | -178.2324 | -78.2183 | -21.3579 | -74.9618 | 28.4164 | -78.8809 | 25.0003 | -82.0172 | 134.7109 | -50.2397 | 164.4749 | -45.6106 | -69.2627 | -48.9436 | 96.0392 | -45.4257 | -92.5331 | -36.2773 | -143.3084 | -38.5177 | -111.8701 | -37.5985 | -159.7291 | -35.7401 | -111.4574 | -63.734 | -74.5855 | -64.9683 | -61.7926 | -72.8433 | -67.5543 | -63.7071 | -77.8751 | -64.7657 | -61.754 | -72.1134 | -68.0782 | -60.0427 | 12 | -73.6063 | -72.1266 | -72.1061 | -75.2112 | -72.3867 | -71.6908 | -72.3714 | -74.6476 | 12 | -76.9492 | -63.8398 | -60.8667 | -71.9409 | -66.6519 | -62.7578 | -76.9727 | -63.8164 | -60.8784 | -71.894 | -66.6401 | -62.7929 | -73.6596 | -64.0424 | -60.8281 | -71.211 | -67.1758 | -59.0934 | -73.6831 | -64.019 | -60.8398 | -71.1641 | -67.164 | -59.1285
13 | -0.9729 | 0 | -0.9612 | 0 | -0.9846 | 0 | -0.9377 | 0 | -78.796 | -89.0337 | -84.3622 | 32.4214 | -80.8336 | -13.8975 | -73.655 | -130.7419 | -81.9902 | -111.7547 | -82.2491 | 89.791 | -76.4514 | -13.4906 | -79.4967 | -157.8309 | -81.3645 | -53.228 | -74.7493 | -2.1548 | -80.0031 | 14.5757 | -83.4875 | 153.581 | -39.5535 | 6.3879 | -40.6688 | 32.2802 | -37.0307 | 7.8399 | -42.6383 | 53.774 | -43.4748 | -124.098 | -54.962 | -170.5858 | -59.0359 | -144.3286 | -44.0082 | -164.073 | -63.0973 | -73.8903 | -64.2966 | -61.2028 | -72.1872 | -67.0114 | -63.0354 | -78.6408 | -64.1643 | -61.1877 | -71.5822 | -67.3869 | -59.2693 | 13 | -76.0014 | -72.0328 | -72.78 | -76.875 | -73.854 | -71.7958 | -73.0794 | -76.6201 | 13 | -77.6679 | -63.1914 | -60.2299 | -71.226 | -66.0502 | -62.0508 | -77.6796 | -63.1797 | -60.2651 | -71.2026 | -66.0737 | -62.0977 | -72.9174 | -63.3237 | -60.2148 | -70.621 | -66.4257 | -58.2847 | -72.9291 | -63.312 | -60.25 | -70.5976 | -66.4492 | -58.3316
14 | -0.9809 | 0 | -0.9926 | 0 | -1.0278 | 0 | -0.9926 | 0 | -80.4672 | -123.2099 | -80.7805 | -92.4699 | -82.5184 | -10.574 | -73.8237 | -144.3777 | -87.8553 | -145.0387 | -79.3263 | 19.192 | -77.7022 | -29.9612 | -76.6293 | -128.7663 | -86.7776 | -103.1909 | -75.7245 | -37.3909 | -82.498 | 12.7701 | -79.6198 | 171.787 | -33.024 | -33.9679 | -33.8931 | 17.7705 | -32.2603 | -33.8507 | -34.4661 | 30.401 | -37.442 | -78.1915 | -42.4248 | 30.4282 | -38.2721 | -57.0501 | -43.4602 | 68.5224 | -62.4765 | -73.164 | -63.6991 | -60.7109 | -71.6601 | -66.6015 | -62.3989 | -79.3794 | -63.6098 | -60.6919 | -71.2153 | -66.8091 | -58.4647 | 14 | -76.3951 | -72.8334 | -72.1117 | -77.2316 | -73.8929 | -73.0659 | -72.2615 | -77.2953 | 14 | -78.3985 | -62.6289 | -59.73 | -70.6675 | -65.6089 | -61.3711 | -78.3868 | -62.582 | -59.7183 | -70.6323 | -65.6089 | -61.4063 | -72.1831 | -62.7182 | -59.711 | -70.2227 | -65.8165 | -57.4369 | -72.1714 | -62.6713 | -59.6993 | -70.1875 | -65.8165 | -57.4721
15 | -1.0514 | 0 | -1.028 | 0 | -1.0514 | 0 | -1.028 | 0 | -83.7104 | -165.0642 | -73.7371 | -141.9552 | -81.5135 | 5.5297 | -75.0307 | -150.3943 | -94.4199 | 54.6206 | -75.1505 | -29.7268 | -80.2721 | -39.0588 | -72.3712 | -127.5706 | -88.9179 | 145.823 | -77.8478 | -84.2527 | -84.9329 | 36.4602 | -75.7363 | 164.0244 | -29.7328 | -71.1667 | -31.1362 | -4.7857 | -29.8027 | -73.5056 | -31.383 | 5.9419 | -31.6691 | -96.1086 | -37.514 | 0.1699 | -32.2851 | -90.8879 | -37.3077 | 21.8778 | -61.8633 | -72.4219 | -63.2383 | -60.3126 | -71.211 | -66.2969 | -61.7975 | -79.3561 | -63.1842 | -60.2701 | -70.8639 | -66.3366 | -57.6093 | 15 | -72.7077 | -74.4349 | -69.8196 | -74.2062 | -71.6366 | -75.3733 | -69.9554 | -75.0604 | 15 | -78.3047 | -62.1328 | -59.2612 | -70.183 | -65.2689 | -60.7461 | -78.3281 | -62.1328 | -59.2846 | -70.1596 | -65.2689 | -60.7695 | -71.3705 | -62.1869 | -59.2187 | -69.8359 | -65.3086 | -56.5579 | -71.3939 | -62.1869 | -59.2421 | -69.8125 | -65.3086 | -56.5813
16 | -1.0983 | 0 | -1.0631 | 0 | -1.1217 | 0 | -1.0397 | 0 | -85.6045 | 124.6545 | -69.8114 | -178.6399 | -79.5239 | 8.5681 | -75.7033 | -142.1117 | -82.0049 | 2.9255 | -72.4277 | -65.7685 | -83.3338 | -24.1654 | -69.539 | -138.4174 | -81.409 | 84.1912 | -78.9472 | -148.9979 | -81.0882 | 60.8028 | -72.4932 | 149.1894 | -27.6198 | -108.8648 | -30.4281 | -29.3686 | -28.1862 | -114.3879 | -30.3166 | -19.35 | -28.2521 | -123.6712 | -36.28 | -28.4923 | -29.0542 | -125.7439 | -35.2232 | -10.1889 | -61.2891 | -71.7305 | -62.793 | -59.9844 | -70.7422 | -66.0626 | -61.2467 | -78.485 | -62.7389 | -59.86 | -70.5006 | -66.0319 | -56.9726 | 16 | -69.2684 | -74.4432 | -67.2466 | -71.2703 | -69.0985 | -75.9915 | -67.4409 | -71.467 | 16 | -77.3867 | -61.6406 | -58.8861 | -69.6791 | -64.9995 | -60.125 | -77.4219 | -61.6172 | -58.9447 | -69.6205 | -65.0229 | -60.207 | -70.6322 | -61.6947 | -58.7617 | -69.4375 | -64.9688 | -55.8509 | -70.6674 | -61.6713 | -58.8203 | -69.3789 | -64.9922 | -55.9329
17 | -1.1334 | 0 | -1.0866 | 0 | -1.1686 | 0 | -1.0983 | 0 | -81.8023 | 54.7083 | -67.6229 | 148.0556 | -77.172 | 3.896 | -73.8108 | -132.7495 | -76.3652 | -26.2993 | -70.7127 | -97.2294 | -80.8071 | 3.1977 | -67.811 | -152.7578 | -77.4952 | 49.7368 | -76.3457 | 147.2601 | -76.7962 | 58.7254 | -70.7764 | 130.998 | -26.1385 | -146.3265 | -31.2836 | -55.4504 | -27.0332 | -154.5514 | -30.8513 | -45.4032 | -26.1472 | -153.3389 | -37.1641 | -58.6826 | -27.0714 | -160.5509 | -35.1182 | -40.2895 | -60.7227 | -71.1524 | -62.3359 | -59.5703 | -70.2227 | -65.8281 | -60.6686 | -77.2155 | -62.235 | -59.4108 | -69.9108 | -65.7741 | -56.4453 | 17 | -67.0192 | -71.4703 | -65.2387 | -68.9573 | -67.175 | -72.8057 | -65.6485 | -69.1242 | 17 | -76.0821 | -61.1016 | -58.4369 | -69.1361 | -64.7415 | -59.5 | -76.1289 | -61.0664 | -58.472 | -69.0541 | -64.7298 | -59.5703 | -70.019 | -61.2025 | -58.2774 | -68.8242 | -64.6875 | -55.2767 | -70.0658 | -61.1673 | -58.3125 | -68.7422 | -64.6758 | -55.347
18 | -1.1803 | 0 | -1.1374 | 0 | -1.2038 | 0 | -1.1335 | 0 | -77.8777 | 9.9915 | -66.7267 | 115.8585 | -75.7318 | -12.2641 | -71.255 | -136.6011 | -73.1855 | -53.9336 | -70.1522 | -128.2885 | -76.5515 | 1.2856 | -67.0156 | -167.1836 | -75.4734 | 14.4336 | -72.9597 | 101.5291 | -74.0115 | 44.5974 | -69.882 | 112.2729 | -25.2254 | 177.1312 | -34.0543 | -84.2038 | -26.2429 | 166.7896 | -33.1755 | -71.6297 | -25.0056 | 176.9381 | -39.8913 | -94.3277 | -26.0278 | 166.3341 | -36.4441 | -71.5693 | -60.1719 | -70.6484 | -61.8594 | -59.1484 | -69.6836 | -65.4844 | -60.1569 | -76.0163 | -61.6921 | -58.9108 | -69.2702 | -65.4655 | -56.125 | 18 | -65.926 | -68.5627 | -64.1573 | -67.6625 | -66.0329 | -69.4918 | -64.5327 | -67.6747 | 18 | -74.836 | -60.5118 | -57.9681 | -68.5462 | -64.347 | -58.9531 | -74.8789 | -60.4883 | -58.0149 | -68.4798 | -64.3509 | -59.0234 | -69.4681 | -60.6791 | -57.7305 | -68.1328 | -64.3281 | -54.9212 | -69.511 | -60.6556 | -57.7773 | -68.0664 | -64.332 | -54.9915
19 | -1.2038 | 0 | -1.1726 | 0 | -1.2273 | 0 | -1.1452 | 0 | -75.2012 | -23.5815 | -66.8611 | 83.6408 | -74.5704 | -24.9019 | -69.5366 | -147.2529 | -71.3134 | -79.2617 | -70.4534 | -159.7359 | -73.6465 | -14.8858 | -67.0131 | 179.4742 | -74.65 | -20.3548 | -70.618 | 64.2855 | -72.418 | 27.8426 | -69.701 | 91.3562 | -24.9369 | 141.2599 | -40.5925 | -122.8002 | -26.1766 | 129.6241 | -38.9861 | -98.9203 | -24.6718 | 147.3608 | -44.357 | -153.5813 | -25.9175 | 134.0598 | -39.4444 | -110.1352 | -59.6524 | -70.3164 | -61.2969 | -58.6406 | -69.1094 | -65.0117 | -59.6608 | -74.8288 | -61.1296 | -58.4148 | -68.5749 | -64.9851 | -55.8672 | 19 | -65.6685 | -66.6685 | -63.9002 | -67.0137 | -65.5848 | -67.2763 | -64.0584 | -67.0178 | 19 | -73.625 | -59.9258 | -57.4368 | -67.9368 | -63.8391 | -58.4335 | -73.6562 | -59.9023 | -57.4954 | -67.8821 | -63.8665 | -58.5156 | -69.1126 | -60.0931 | -57.211 | -67.4023 | -63.8125 | -54.6399 | -69.1438 | -60.0696 | -57.2696 | -67.3476 | -63.8399 | -54.722
20 | -1.2429 | 0 | -1.2234 | 0 | -1.2781 | 0 | -1.2038 | 0 | -73.76 | -53.613 | -67.8878 | 50.3836 | -74.9322 | -40.2034 | -68.6605 | -160.3652 | -70.4816 | -105.0661 | -72.4078 | 165.4623 | -72.1032 | -35.2418 | -67.7317 | 168.3434 | -75.1698 | -57.4106 | -69.3063 | 29.375 | -71.7409 | 12.0627 | -70.3978 | 74.504 | -25.4734 | 106.2797 | -45.282 | 104.882 | -27.1219 | 93.5629 | -56.1262 | 96.8043 | -25.4523 | 118.8368 | -43.8399 | 128.8658 | -27.1273 | 102.7523 | -42.6314 | -162.0048 | -59.1836 | -70.0195 | -60.7656 | -58.1719 | -68.5664 | -64.4961 | -59.157 | -73.864 | -60.5749 | -57.9695 | -67.8835 | -64.5163 | -55.668 | 20 | -66.2556 | -65.7234 | -64.483 | -67.4699 | -65.84 | -66.0923 | -64.2348 | -67.2438 | 20 | -72.6211 | -59.332 | -56.929 | -67.343 | -63.2727 | -57.8789 | -72.6406 | -59.2968 | -56.9681 | -67.2883 | -63.2923 | -57.9532 | -68.7766 | -59.5227 | -56.7266 | -66.6601 | -63.2929 | -54.3899 | -68.7961 | -59.4875 | -56.7657 | -66.6054 | -63.3125 | -54.4642
21 | -1.2706 | 0 | -1.2354 | 0 | -1.2667 | 0 | -1.2354 | 0 | -73.1844 | -82.7991 | -70.1302 | 11.6864 | -76.1376 | -51.291 | -68.6338 | -171.5892 | -70.5741 | -129.7696 | -76.4726 | 118.5732 | -71.5966 | -58.0918 | -69.1617 | 163.3703 | -76.0341 | -98.5815 | -68.6912 | -7.3369 | -71.7771 | -8.4986 | -72.6884 | 59.1388 | -27.251 | 70.2414 | -36.2685 | 47.862 | -29.8281 | 55.984 | -37.0426 | 38.9504 | -27.8076 | 90.9783 | -40.7074 | 82.236 | -30.5558 | 71.414 | -43.0799 | 138.6672 | -58.7504 | -69.8325 | -60.2543 | -57.7153 | -68.0981 | -63.9184 | -58.7159 | -73.298 | -60.0987 | -57.5518 | -67.4854 | -63.9854 | -55.3985 | 21 | -67.7104 | -65.6444 | -65.9084 | -68.7134 | -66.6665 | -65.6731 | -65.0821 | -68.3807 | 21 | -72.0274 | -58.8281 | -56.4447 | -66.8627 | -62.683 | -57.4492 | -72.0626 | -58.832 | -56.4799 | -66.8314 | -62.683 | -57.4805 | -68.5619 | -58.9837 | -56.2812 | -66.25 | -62.75 | -54.1318 | -68.5971 | -58.9876 | -56.3164 | -66.2187 | -62.75 | -54.1631
22 | -1.2903 | 0 | -1.259 | 0 | -1.302 | 0 | -1.2434 | 0 | -73.6643 | -111.8056 | -73.4723 | -43.6393 | -78.218 | -53.9057 | -69.0676 | -179.2156 | -71.6847 | -152.9738 | -79.7934 | 32.8579 | -72.4081 | -82.783 | -70.2811 | 168.3479 | -77.2666 | -150.1637 | -69.0097 | -45.1483 | -72.9969 | -24.9049 | -77.6976 | 58.0107 | -31.2581 | 25.7863 | -32.5975 | 15.9636 | -36.4344 | -2.1411 | -32.087 | 10.8098 | -33.6595 | 62.8165 | -39.2909 | 50.0593 | -40.9934 | 26.8411 | -42.6178 | 97.5918 | -58.3717 | -69.774 | -59.7779 | -57.3482 | -67.7193 | -63.4498 | -58.2981 | -73.2043 | -59.7121 | -57.2161 | -67.2395 | -63.5911 | -55.1094 | 22 | -69.8701 | -66.2929 | -67.462 | -70.2962 | -67.6972 | -66.3227 | -66.2647 | -70.6595 | 22 | -71.914 | -58.4218 | -56.0579 | -66.4603 | -62.1908 | -56.9961 | -71.9453 | -58.4101 | -56.1048 | -66.4173 | -62.2064 | -57.0547 | -68.4837 | -58.4876 | -55.9258 | -65.9805 | -62.3321 | -53.8074 | -68.515 | -58.4759 | -55.9727 | -65.9375 | -62.3477 | -53.866
23 | -1.3021 | 0 | -1.2904 | 0 | -1.3607 | 0 | -1.2943 | 0 | -75.6055 | -142.5658 | -73.5456 | -124.8775 | -79.5631 | -43.5244 | -69.6793 | 178.3835 | -74.3824 | -173.0166 | -74.2085 | -45.7045 | -74.8083 | -107.8926 | -69.3362 | 178.9514 | -76.9441 | 155.39 | -70.0389 | -88.285 | -76.0648 | -42.3859 | -79.3708 | 113.3154 | -36.3427 | -66.6311 | -31.374 | -11.6878 | -34.512 | -129.6834 | -29.9097 | -16.4014 | -45.1989 | -146.1305 | -40.261 | 27.6792 | -34.3998 | -148.601 | -43.2068 | 77.1253 | -58.0632 | -69.7859 | -59.4499 | -57.0632 | -67.4109 | -63.1648 | -57.9779 | -73.7123 | -59.4584 | -56.9896 | -67.2318 | -63.3295 | -54.7735 | 23 | -70.8214 | -67.6542 | -67.2168 | -70.6825 | -67.7012 | -68.0436 | -66.4363 | -72.4782 | 23 | -72.4102 | -58.1563 | -55.7611 | -66.1205 | -61.8744 | -56.6172 | -72.4219 | -58.0977 | -55.7689 | -66.0502 | -61.8705 | -56.6836 | -68.4838 | -58.1478 | -55.6875 | -65.9414 | -62.0391 | -53.4128 | -68.4955 | -58.0892 | -55.6953 | -65.8711 | -62.0352 | -53.4792
24 | -1.3647 | 0 | -1.3296 | 0 | -1.3725 | 0 | -1.3179 | 0 | -80.2821 | 179.5608 | -69.3889 | 174.6445 | -78.06 | -29.3212 | -69.7262 | -179.1414 | -80.6927 | 177.0048 | -70.0646 | -86.5256 | -80.7588 | -137.4393 | -67.0711 | 178.5514 | -75.0841 | 109.2454 | -71.1892 | -137.6259 | -81.7117 | -43.491 | -71.7874 | 124.1663 | -29.386 | -152.3652 | -31.7352 | -39.5522 | -26.9178 | -179.3593 | -29.142 | -44.0682 | -29.212 | -171.4845 | -43.4391 | 13.1819 | -26.5291 | 178.3981 | -44.8213 | 85.0221 | -57.8328 | -69.786 | -59.243 | -56.9032 | -67.1219 | -63.0711 | -57.7241 | -74.2163 | -59.31 | -56.8296 | -67.2358 | -63.2827 | -54.3985 | 24 | -68.5353 | -69.0516 | -64.9466 | -69.1122 | -66.2764 | -70.4007 | -64.7032 | -69.8288 | 24 | -72.8516 | -57.9453 | -55.5385 | -65.7923 | -61.7415 | -56.3516 | -72.8867 | -57.9375 | -55.5853 | -65.7494 | -61.7532 | -56.4062 | -68.4213 | -57.8783 | -55.4649 | -65.9062 | -61.9531 | -53.026 | -68.4564 | -57.8705 | -55.5117 | -65.8633 | -61.9648 | -53.0806
25 | -1.4 | 0 | -1.3531 | 0 | -1.4312 | 0 | -1.3296 | 0 | -87.0737 | 74.4551 | -66.3329 | 133.7322 | -75.9339 | -27.1012 | -68.7209 | -177.4347 | -84.9955 | -102.3429 | -67.5671 | -120.5477 | -92.4296 | 61.731 | -65.1956 | 169.4552 | -74.3098 | 73.5872 | -71.3653 | 167.3033 | -83.4067 | 22.327 | -67.7278 | 108.9584 | -24.32 | 167.1879 | -33.8822 | -68.7995 | -22.9626 | 147.7906 | -29.5261 | -72.6916 | -24.0287 | 162.5098 | -50.6641 | 31.0051 | -22.7729 | 150.5457 | -42.463 | 102.1691 | -57.622 | -69.7275 | -59.079 | -56.7392 | -66.7353 | -63.165 | -57.5367 | -74.1226 | -59.1695 | -56.6304 | -67.2242 | -63.3882 | -54.129 | 25 | -65.8483 | -68.5581 | -62.66 | -66.9086 | -64.6859 | -71.0701 | -62.6435 | -66.7701 | 25 | -72.7226 | -57.7695 | -55.3392 | -65.3822 | -61.8119 | -56.1055 | -72.7695 | -57.7383 | -55.4096 | -65.3041 | -61.8354 | -56.2071 | -68.3275 | -57.679 | -55.2304 | -65.8711 | -62.0351 | -52.6978 | -68.3744 | -57.6478 | -55.3008 | -65.793 | -62.0586 | -52.7994
26 | -1.4352 | 0 | -1.3883 | 0 | -1.4821 | 0 | -1.3649 | 0 | -77.7453 | -7.7634 | -64.7085 | 99.9631 | -73.712 | -33.924 | -67.3483 | 178.8735 | -75.1509 | -93.246 | -66.1878 | -151.3056 | -77.0799 | 7.174 | -64.1179 | 155.8736 | -73.292 | 33.1096 | -70.4499 | 114.5418 | -76.2061 | 32.5663 | -65.4351 | 91.3909 | -21.4256 | 135.3972 | -39.0624 | -105.8788 | -20.8308 | 118.5408 | -31.0844 | -103.9078 | -21.2641 | 137.0771 | -47.2503 | 98.9125 | -20.7819 | 124.6928 | -38.3771 | 101.3494 | -57.4424 | -69.5557 | -58.8564 | -56.54 | -66.2861 | -63.2666 | -57.3493 | -73.3024 | -59.0055 | -56.361 | -67.0719 | -63.4977 | -53.9103 | 26 | -64.0063 | -66.3545 | -61.1754 | -65.0357 | -63.4305 | -68.7386 | -61.1709 | -64.4746 | 26 | -71.8672 | -57.5703 | -55.1048 | -64.8978 | -61.8783 | -55.8672 | -71.9141 | -57.5234 | -55.1751 | -64.804 | -61.9017 | -55.9844 | -68.1205 | -57.4212 | -54.9258 | -65.6836 | -62.1094 | -52.4282 | -68.1674 | -57.3743 | -54.9961 | -65.5898 | -62.1328 | -52.5454
27 | -1.4587 | 0 | -1.4002 | 0 | -1.4939 | 0 | -1.4002 | 0 | -72.6672 | -43.8391 | -64.183 | 69.1551 | -72.8467 | -44.5715 | -66.3905 | 170.272 | -70.7864 | -112.3516 | -65.7409 | 176.9368 | -71.9145 | -20.9848 | -63.8094 | 140.3844 | -74.4763 | -0.835 | -69.1011 | 67.2492 | -72.6721 | 19.0101 | -64.2566 | 72.4723 | -19.9349 | 106.5071 | -46.1488 | 145.7252 | -19.9815 | 91.0485 | -33.8552 | -140.6128 | -19.8721 | 112.3885 | -41.0902 | 102.6058 | -20.0052 | 100.0871 | -35.445 | 89.5988 | -57.2316 | -69.1573 | -58.5636 | -56.2706 | -65.8058 | -63.173 | -57.158 | -72.2595 | -58.783 | -56.0173 | -66.7673 | -63.3572 | -53.672 | 27 | -63.1184 | -64.3517 | -60.5656 | -63.9579 | -62.8736 | -66.1727 | -60.3894 | -63.3256 | 27 | -70.8008 | -57.3243 | -54.8119 | -64.4056 | -61.7728 | -55.6641 | -70.8593 | -57.2891 | -54.8704 | -64.3119 | -61.7728 | -55.7578 | -67.6986 | -57.1049 | -54.5586 | -65.3671 | -61.957 | -52.1781 | -67.7571 | -57.0697 | -54.6171 | -65.2734 | -61.957 | -52.2718
28 | -1.494 | 0 | -1.4354 | 0 | -1.5175 | 0 | -1.4237 | 0 | -69.7399 | -74.6295 | -64.7891 | 39.7195 | -72.1431 | -57.6705 | -66.1938 | 160.7405 | -68.4764 | -133.2427 | -66.2735 | 142.3643 | -69.2737 | -47.2998 | -64.3708 | 124.5984 | -77.6915 | -32.19 | -68.1129 | 22.9394 | -70.6922 | 2.8366 | -63.5851 | 54.1527 | -19.5577 | 79.2345 | -37.0888 | 68.0842 | -20.3249 | 64.7282 | -37.7446 | 167.5078 | -19.5885 | 88.4259 | -37.8068 | 96.0112 | -20.3811 | 76.5374 | -34.0143 | 74.1174 | -57.0598 | -68.6418 | -58.2082 | -55.9856 | -65.3723 | -62.8449 | -56.994 | -71.5175 | -58.4901 | -55.6893 | -66.3417 | -62.9667 | -53.4962 | 28 | -63.0174 | -63.1121 | -60.9256 | -63.576 | -63.0038 | -64.4625 | -60.1865 | -62.6737 | 28 | -70.0235 | -56.9961 | -54.4916 | -63.9369 | -61.4095 | -55.4765 | -70.0821 | -56.9726 | -54.5619 | -63.8548 | -61.4212 | -55.5703 | -67.1478 | -56.7142 | -54.1953 | -64.9063 | -61.5313 | -51.9787 | -67.2064 | -56.6907 | -54.2656 | -64.8242 | -61.543 | -52.0725
29 | -1.5059 | 0 | -1.4434 | 0 | -1.5293 | 0 | -1.459 | 0 | -68.1722 | -103.64 | -66.614 | 10.5772 | -72.2244 | -65.896 | -66.6658 | 154.0958 | -67.3904 | -155.082 | -67.7011 | 102.719 | -67.9959 | -73.334 | -66.0877 | 110.6983 | -85.3264 | -91.3613 | -67.5439 | -21.6825 | -69.6615 | -16.9489 | -63.7512 | 35.1944 | -20.337 | 52.8657 | -32.5806 | 34.8691 | -22.0946 | 39.3432 | -38.9846 | 94.4269 | -20.42 | 65.7603 | -35.6394 | 88.7953 | -22.0841 | 55.4314 | -33.7144 | 58.3175 | -56.8294 | -68.0521 | -57.8334 | -55.6537 | -65.0248 | -62.2552 | -56.791 | -71.2246 | -58.1582 | -55.3574 | -65.7871 | -62.3574 | -53.3205 | 29 | -63.6621 | -62.5949 | -62.1944 | -63.8503 | -63.8962 | -63.5381 | -60.7377 | -62.7358 | 29 | -69.7187 | -56.6523 | -54.1478 | -63.5814 | -60.8118 | -55.2617 | -69.7812 | -56.6289 | -54.1947 | -63.4955 | -60.7962 | -55.332 | -66.5462 | -56.3275 | -53.8515 | -64.3437 | -60.914 | -51.7912 | -66.6087 | -56.3041 | -53.8984 | -64.2578 | -60.8984 | -51.8615
30 | -1.5177 | 0 | -1.4787 | 0 | -1.5412 | 0 | -1.4709 | 0 | -67.7219 | -131.8711 | -70.6456 | -20.978 | -72.6036 | -66.8887 | -67.2908 | 153.0719 | -67.3771 | -175.9957 | -69.8917 | 51.9461 | -67.9495 | -99.9624 | -69.4333 | 104.6377 | -81.6996 | 136.308 | -67.1917 | -68.4537 | -69.871 | -38.367 | -65.1395 | 18.2519 | -22.6557 | 27.4383 | -30.4618 | 6.9843 | -26.3201 | 16.129 | -36.7019 | 36.1831 | -22.7311 | 45.5972 | -33.9154 | 81.5659 | -25.9049 | 40.9892 | -34.7287 | 45.4805 | -56.6069 | -67.5093 | -57.4819 | -55.3726 | -64.814 | -61.5015 | -56.6037 | -71.5412 | -57.842 | -55.0763 | -65.2834 | -61.6506 | -53.1213 | 30 | -65.0855 | -62.6881 | -64.256 | -64.6805 | -65.5123 | -63.4269 | -62.139 | -63.809 | 30 | -70.0235 | -56.3243 | -53.8549 | -63.3353 | -60.0228 | -55.0625 | -70.0625 | -56.3008 | -53.9017 | -63.2728 | -60.0306 | -55.1328 | -65.9916 | -55.9642 | -53.5586 | -63.8047 | -60.1719 | -51.5801 | -66.0306 | -55.9407 | -53.6054 | -63.7422 | -60.1797 | -51.6504
31 | -1.5413 | 0 | -1.5023 | 0 | -1.5765 | 0 | -1.5062 | 0 | -68.2665 | -160.3251 | -81.9119 | -79.8479 | -70.7429 | -67.8563 | -67.2386 | 158.3837 | -68.5862 | 165.2691 | -70.5783 | -10.0697 | -69.0849 | -126.4074 | -72.8676 | 128.4752 | -73.7791 | 94.3563 | -66.799 | -117.0831 | -71.3755 | -60.5581 | -67.8981 | 9.9277 | -28.0711 | 4.3818 | -29.7873 | -19.3828 | -40.002 | 19.0889 | -35.0376 | -4.6485 | -27.6444 | 34.6897 | -32.4805 | 73.0643 | -32.6703 | 64.565 | -36.9165 | 39.7471 | -56.3844 | -67.111 | -57.2555 | -55.1383 | -64.65 | -60.8571 | -56.4046 | -72.5413 | -57.5609 | -54.8616 | -64.8929 | -61.0882 | -52.9104 | 31 | -66.202 | -63.2203 | -65.4847 | -65.0824 | -66.6351 | -63.9224 | -63.7376 | -65.5753 | 31 | -71 | -56.0196 | -53.597 | -63.1477 | -59.3548 | -54.8281 | -71.039 | -55.9844 | -53.6321 | -63.0735 | -59.3509 | -54.8984 | -65.5697 | -55.7142 | -53.3203 | -63.3906 | -59.5859 | -51.3339 | -65.6087 | -55.679 | -53.3554 | -63.3164 | -59.582 | -51.4042
32 | -1.5582 | 0 | -1.5265 | 0 | -1.59 | 0 | -1.5206 | 0 | -70.106 | 170.1481 | -73.5595 | 129.9391 | -70.0891 | -71.1342 | -65.8661 | 160.9142 | -71.1791 | 152.7114 | -68.5058 | -67.4744 | -71.8623 | -152.866 | -69.5133 | 155.9743 | -69.7117 | 64.6661 | -66.2483 | -165.3632 | -74.8371 | -82.5031 | -70.478 | 22.4574 | -45.9547 | 92.5268 | -30.2681 | -44.9396 | -28.9241 | 128.6317 | -34.904 | -39.893 | -33.6347 | 85.1129 | -31.4017 | 62.283 | -27.5089 | 114.2684 | -39.204 | 50.6231 | -56.1859 | -66.773 | -57.1552 | -54.9477 | -64.5336 | -60.4683 | -56.2179 | -73.9768 | -57.3199 | -54.7218 | -64.6241 | -60.7619 | -52.6544 | 32 | -66.2048 | -63.6365 | -63.5244 | -65.0133 | -65.4691 | -64.7471 | -63.5787 | -66.3965 | 32 | -72.4186 | -55.7617 | -53.3895 | -63.0071 | -58.9418 | -54.6279 | -72.4503 | -55.7299 | -53.4271 | -62.9436 | -58.9477 | -54.6973 | -65.2148 | -55.597 | -53.1636 | -63.0976 | -59.2354 | -51.0644 | -65.2465 | -55.5652 | -53.2012 | -63.0341 | -59.2413 | -51.1338
33 | -1.598 | 0 | -1.552 | 0 | -1.6368 | 0 | -1.5368 | 0 | -73.8585 | 137.8652 | -66.9102 | 94.1267 | -68.5866 | -82.8134 | -64.2009 | 157.3288 | -74.6886 | 160.387 | -65.8877 | -109.9978 | -78.251 | 179.1998 | -65.4768 | 151.6561 | -67.2293 | 38.566 | -65.5057 | 149.334 | -85.4216 | -102.2707 | -68.4209 | 41.2466 | -26.5848 | 121.8685 | -32.0646 | -70.3165 | -22.4073 | 108.559 | -36.4124 | -76.2027 | -25.7546 | 115.3521 | -30.9255 | 49.9013 | -22.166 | 106.6579 | -38.5585 | 72.0051 | -56.02 | -66.515 | -57.1364 | -54.8208 | -64.4536 | -60.3861 | -56.0676 | -75.7774 | -57.1331 | -54.5715 | -64.4387 | -60.7266 | -52.4745 | 33 | -64.1647 | -63.4179 | -60.7491 | -63.6632 | -63.1196 | -65.239 | -61.4956 | -64.7368 | 33 | -74.1794 | -55.5351 | -53.2228 | -62.9016 | -58.8341 | -54.4308 | -74.2254 | -55.4963 | -53.284 | -62.8168 | -58.8493 | -54.5308 | -64.917 | -55.5384 | -52.9735 | -62.8867 | -59.1746 | -50.8377 | -64.963 | -55.4996 | -53.0347 | -62.8019 | -59.1898 | -50.9377
34 | -1.6283 | 0 | -1.5855 | 0 | -1.6785 | 0 | -1.5571 | 0 | -81.8938 | 76.5182 | -63.7407 | 64.492 | -68.0093 | -96.7587 | -62.9189 | 147.9557 | -74.6463 | -170.6177 | -63.9943 | -145.8331 | -89.4303 | 0.6467 | -63.1091 | 136.2083 | -65.7492 | 13.1677 | -64.9191 | 106.7794 | -80.3482 | 42.7024 | -65.5676 | 38.8986 | -21.2661 | 99.2724 | -35.6759 | -95.7766 | -19.423 | 85.2714 | -39.7279 | -121.5444 | -21.0588 | 101.831 | -31.2694 | 36.8607 | -19.3515 | 88.4775 | -36.0698 | 78.5634 | -55.8426 | -66.2013 | -57.0963 | -54.702 | -64.2645 | -60.4981 | -55.8745 | -76.8895 | -56.9173 | -54.4409 | -64.2027 | -60.909 | -52.3404 | 34 | -62.312 | -62.5853 | -58.7554 | -62.2835 | -61.2147 | -64.7815 | -59.6321 | -62.574 | 34 | -75.2612 | -55.289 | -53.0737 | -62.679 | -58.9126 | -54.196 | -75.304 | -55.2388 | -53.1449 | -62.586 | -58.941 | -54.3174 | -64.573 | -55.468 | -52.8126 | -62.6172 | -59.3235 | -50.6619 | -64.6158 | -55.4178 | -52.8838 | -62.5242 | -59.3519 | -50.7833
35 | -1.6564 | 0 | -1.6036 | 0 | -1.6899 | 0 | -1.5864 | 0 | -77.9604 | -44.1466 | -62.2655 | 36.9279 | -67.4803 | -109.772 | -62.3453 | 136.4671 | -70.5987 | -164.8962 | -62.8538 | -176.938 | -74.5295 | -43.371 | -62.0038 | 117.9404 | -65.0008 | -12.0722 | -64.7685 | 65.9249 | -72.8196 | 23.3993 | -63.6835 | 24.8751 | -18.6988 | 75.4608 | -43.8029 | -122.8448 | -18.125 | 61.7784 | -42.688 | 160.9282 | -18.6583 | 82.6941 | -32.7785 | 26.1564 | -18.0824 | 68.4279 | -34.2562 | 74.6062 | -55.6264 | -65.8728 | -56.9838 | -54.5443 | -64.0326 | -60.6892 | -55.6466 | -77.2875 | -56.6994 | -54.2833 | -64.0333 | -61.0961 | -52.1642 | 35 | -61.0338 | -61.6377 | -57.7093 | -61.0563 | -60.0797 | -63.7569 | -58.5631 | -60.9875 | 35 | -75.6311 | -55.043 | -52.8879 | -62.429 | -59.0856 | -53.9567 | -75.6839 | -55.0095 | -52.9579 | -62.3427 | -59.1028 | -54.0602 | -64.2164 | -55.3274 | -52.6269 | -62.4297 | -59.4925 | -50.4743 | -64.2692 | -55.2939 | -52.6969 | -62.3434 | -59.5097 | -50.5778
36 | -1.7009 | 0 | -1.6213 | 0 | -1.7378 | 0 | -1.6223 | 0 | -71.4111 | -86.5479 | -61.9546 | 10.5437 | -67.5099 | -124.633 | -62.5538 | 125.2789 | -67.6721 | -173.8856 | -62.5145 | 151.5871 | -69.6754 | -70.8781 | -61.888 | 97.8419 | -65.075 | -36.4232 | -65.0817 | 23.8968 | -69.161 | 1.0951 | -62.4965 | 9.6569 | -17.5895 | 51.8163 | -49.1197 | 44.7649 | -18.098 | 38.7513 | -38.6281 | 87.8034 | -17.5679 | 62.3468 | -35.6569 | 24.9574 | -17.9972 | 48.3007 | -33.4386 | 69.375 | -55.3862 | -65.4754 | -56.7939 | -54.3628 | -63.8159 | -60.8895 | -55.4182 | -76.6792 | -56.5095 | -54.1135 | -63.9572 | -61.2261 | -52.0246 | 36 | -60.5194 | -60.9767 | -57.561 | -60.4153 | -59.7224 | -62.6808 | -58.1799 | -60.0221 | 36 | -74.9783 | -54.8086 | -52.6619 | -62.1946 | -59.2682 | -53.6804 | -75.0579 | -54.7717 | -52.7405 | -62.0781 | -59.2672 | -53.7959 | -63.7745 | -55.093 | -52.4126 | -62.3359 | -59.6048 | -50.2868 | -63.8541 | -55.0561 | -52.4912 | -62.2194 | -59.6038 | -50.4023
37 | -1.713 | 0 | -1.6401 | 0 | -1.7585 | 0 | -1.6456 | 0 | -68.0921 | -117.5713 | -62.8004 | -14.7552 | -68.0828 | -139.1969 | -63.4794 | 117.9584 | -65.9762 | 170.9875 | -62.89 | 122.4465 | -67.2752 | -97.9649 | -62.9726 | 77.3844 | -65.586 | -59.5862 | -65.8186 | -22.4221 | -67.1825 | -21.3244 | -62.2787 | -6.7733 | -17.6496 | 28.7209 | -38.5072 | 13.8118 | -19.3835 | 16.9201 | -34.729 | 45.777 | -17.5772 | 42.3481 | -37.8944 | 49.4016 | -19.0692 | 29.5697 | -33.095 | 67.0689 | -55.1237 | -64.9648 | -56.5247 | -54.1706 | -63.6237 | -61.0039 | -55.1205 | -75.3483 | -56.3458 | -53.933 | -63.9018 | -61.1765 | -51.8928 | 37 | -60.781 | -60.6725 | -58.2751 | -60.3522 | -60.1415 | -61.9349 | -58.671 | -59.7495 | 37 | -73.6353 | -54.6328 | -52.4576 | -61.9836 | -59.3638 | -53.362 | -73.7082 | -54.5873 | -52.525 | -61.8652 | -59.3583 | -53.4749 | -63.2518 | -54.8117 | -52.22 | -62.2617 | -59.5364 | -50.1343 | -63.3247 | -54.7662 | -52.2874 | -62.1433 | -59.5309 | -50.2472
38 | -1.7523 | 0 | -1.6556 | 0 | -1.7744 | 0 | -1.6596 | 0 | -66.3954 | -145.9233 | -64.9293 | -38.3209 | -68.9998 | -151.0791 | -64.6281 | 118.568 | -65.2318 | 154.5557 | -64.3549 | 93.2298 | -66.2674 | -125.0544 | -65.5924 | 58.3029 | -67.1256 | -81.5383 | -66.433 | -76.0247 | -66.4757 | -44.3989 | -62.6438 | -25.7622 | -18.8963 | 6.515 | -34.909 | -12.0827 | -22.442 | -1.6589 | -32.4978 | 13.6644 | -18.6418 | 23.7806 | -34.6241 | 72.8399 | -21.6493 | 15.0907 | -32.4501 | 68.5356 | -54.8131 | -64.4299 | -56.2418 | -53.9518 | -63.4869 | -60.9495 | -54.8138 | -73.7509 | -56.2152 | -53.7669 | -63.8724 | -60.9522 | -51.7622 | 38 | -61.6964 | -60.5868 | -59.8599 | -61.0097 | -61.5124 | -61.6199 | -59.7994 | -60.1638 | 38 | -71.9986 | -54.4629 | -52.1995 | -61.8313 | -59.2939 | -53.0394 | -72.0953 | -54.4408 | -52.2922 | -61.7125 | -59.2899 | -53.1542 | -62.6776 | -54.4895 | -52.0146 | -62.2168 | -59.2966 | -49.9878 | -62.7743 | -54.4674 | -52.1073 | -62.098 | -59.2926 | -50.1026
39 | -1.7513 | 0 | -1.6923 | 0 | -1.7828 | 0 | -1.6665 | 0 | -65.8724 | -173.2127 | -69.4387 | -58.4646 | -70.2594 | -162.7271 | -64.6352 | 126.4521 | -65.325 | 139.2088 | -66.9003 | 62.5409 | -66.4049 | -151.9583 | -71.2194 | 47.1384 | -69.962 | -102.3535 | -65.7227 | -133.9805 | -66.6441 | -69.2904 | -64.4827 | -44.7662 | -21.7835 | -13.1324 | -33.5058 | -37.8963 | -28.8439 | -3.905 | -31.4246 | -14.8003 | -21.0658 | 9.2089 | -30.8853 | 69.8145 | -26.1708 | 16.5313 | -31.0895 | 68.4167 | -54.5041 | -63.9422 | -55.983 | -53.7834 | -63.4181 | -60.7293 | -54.4892 | -72.3902 | -56.0443 | -53.6279 | -63.7666 | -60.6851 | -51.5478 | 39 | -63.3098 | -60.4767 | -61.7921 | -62.2783 | -63.923 | -61.4682 | -61.5521 | -61.7155 | 39 | -70.6389 | -54.293 | -52.0321 | -61.7258 | -59.037 | -52.7064 | -70.6979 | -54.2615 | -52.1169 | -61.6353 | -59.0628 | -52.8227 | -62.1909 | -54.2317 | -51.8766 | -62.0743 | -58.9928 | -49.765 | -62.2499 | -54.2002 | -51.9614 | -61.9838 | -59.0186 | -49.8813
40 | -1.7747 | 0 | -1.7137 | 0 | -1.787 | 0 | -1.6932 | 0 | -66.3706 | 159.9673 | -80.433 | -34.93 | -71.7956 | -170.8017 | -63.0206 | 131.014 | -66.2499 | 126.5199 | -72.4803 | 26.0448 | -67.6353 | -179.6109 | -78.172 | 112.2424 | -74.7822 | -119.8501 | -63.997 | 173.9345 | -68.2743 | -95.3926 | -67.851 | -54.7951 | -27.8349 | -21.3887 | -33.4137 | -63.8671 | -30.114 | 64.5222 | -31.2522 | -40.7718 | -25.244 | 7.9598 | -28.5893 | 56.8425 | -27.5023 | 57.1881 | -29.523 | 62.3717 | -54.2207 | -63.5479 | -55.7973 | -53.6582 | -63.3223 | -60.5128 | -54.1707 | -71.4354 | -55.8919 | -53.5027 | -63.577 | -60.5135 | -51.3351 | 40 | -65.1452 | -60.1475 | -62.4845 | -64.4398 | -66.5589 | -61.4294 | -62.3835 | -64.6085 | 40 | -69.6607 | -54.1172 | -51.8835 | -61.6086 | -58.7991 | -52.3837 | -69.7217 | -54.1049 | -51.965 | -61.5353 | -58.8196 | -52.4775 | -61.7732 | -54.0226 | -51.728 | -61.8633 | -58.7998 | -49.5481 | -61.8342 | -54.0103 | -51.8095 | -61.79 | -58.8203 | -49.6419
41 | -1.7733 | 0 | -1.7417 | 0 | -1.8216 | 0 | -1.7257 | 0 | -68.2804 | 131.7981 | -71.4838 | 35.9442 | -73.4728 | -176.2604 | -61.05 | 126.5574 | -67.7883 | 120.8392 | -83.0814 | -77.5479 | -70.3775 | 150.5324 | -69.1821 | 137.7851 | -85.628 | -116.4049 | -62.2781 | 129.9753 | -71.4205 | -125.6145 | -73.8332 | -42.5662 | -32.1504 | 48.6023 | -34.4875 | -91.2436 | -22.9699 | 69.5331 | -31.9471 | -65.1634 | -27.4523 | 42.9942 | -27.5703 | 40.7871 | -22.5709 | 69.7335 | -28.3516 | 50.8133 | -54.0027 | -63.3364 | -55.6553 | -53.5886 | -63.2331 | -60.3833 | -53.9058 | -70.931 | -55.7108 | -53.3511 | -63.3238 | -60.513 | -51.2055 | 41 | -65.7743 | -59.5852 | -60.6489 | -66.65 | -66.6729 | -61.2171 | -61.2268 | -69.3476 | 41 | -69.1577 | -53.9375 | -51.8153 | -61.4914 | -58.6416 | -52.0842 | -69.1893 | -53.8892 | -51.8629 | -61.4115 | -58.6576 | -52.1801 | -61.5631 | -53.882 | -51.5778 | -61.5821 | -58.7713 | -49.3839 | -61.5947 | -53.8337 | -51.6254 | -61.5022 | -58.7873 | -49.4798
42 | -1.7884 | 0 | -1.7734 | 0 | -1.8683 | 0 | -1.7566 | 0 | -72.1597 | 102.5656 | -65.8369 | 18.0898 | -75.1268 | 175.5143 | -59.605 | 115.9783 | -68.914 | 126.3022 | -71.955 | -179.0487 | -75.762 | 115.0157 | -64.841 | 123.0577 | -80.653 | -9.6274 | -61.1625 | 91.5292 | -77.9974 | -174.026 | -72.0117 | 6.889 | -23.8436 | 62.2579 | -36.8109 | -121.3437 | -19.4374 | 52.4719 | -33.5792 | -86.3392 | -23.0242 | 60.8713 | -27.7222 | 24.5039 | -19.2558 | 58.5278 | -28.0284 | 35.5724 | -53.7999 | -63.2972 | -55.6119 | -53.5031 | -63.1007 | -60.3675 | -53.7031 | -70.6574 | -55.515 | -53.207 | -63.0625 | -60.6144 | -51.0803 | 42 | -64.5305 | -58.9128 | -58.4778 | -66.5194 | -64.399 | -60.9283 | -59.37 | -70.5855 | 42 | -68.869 | -53.7266 | -51.7147 | -61.3273 | -58.5941 | -51.8348 | -68.884 | -53.6467 | -51.7465 | -61.2324 | -58.6109 | -51.9465 | -61.5088 | -53.8235 | -51.4186 | -61.2891 | -58.841 | -49.212 | -61.5238 | -53.7436 | -51.4504 | -61.1942 | -58.8578 | -49.3237
43 | -1.8579 | 0 | -1.7888 | 0 | -1.9203 | 0 | -1.7888 | 0 | -81.9536 | 51.1701 | -63.3666 | -4.9713 | -76.5385 | 175.682 | -58.8434 | 102.6896 | -67.7425 | 132.7696 | -66.236 | 144.778 | -85.0877 | 7.2754 | -62.831 | 103.8056 | -73.7189 | -20.5657 | -60.7923 | 55.6913 | -77.9001 | 74.6722 | -66.809 | 12.6783 | -19.8209 | 45.9553 | -40.7045 | -161.356 | -17.8286 | 31.8361 | -35.8973 | -102.7747 | -19.5384 | 52.1181 | -29.1029 | 10.4774 | -17.5883 | 41.6904 | -28.7595 | 18.3867 | -53.6474 | -63.3961 | -55.572 | -53.4325 | -62.9364 | -60.3492 | -53.5036 | -70.5922 | -55.3931 | -53.0076 | -62.8396 | -60.7836 | -50.9916 | 43 | -63.1053 | -58.2983 | -56.9817 | -63.6829 | -62.4669 | -60.6928 | -58.0609 | -65.7318 | 43 | -68.7343 | -53.5352 | -51.5746 | -61.1476 | -58.5604 | -51.5833 | -68.8034 | -53.4728 | -51.6437 | -61.0161 | -58.5604 | -51.7148 | -61.5382 | -53.7141 | -51.1497 | -61.0508 | -58.9948 | -49.0713 | -61.6073 | -53.6517 | -51.2188 | -60.9193 | -58.9948 | -49.2028
44 | -1.9072 | 0 | -1.803 | 0 | -1.9748 | 0 | -1.8127 | 0 | -76.9087 | -96.6736 | -62.5316 | -28.9166 | -77.696 | 163.7264 | -58.8194 | 88.6942 | -65.8791 | 129.3023 | -63.6342 | 115.4597 | -75.1001 | -80.6764 | -62.1776 | 83.5644 | -71.2221 | -33.7081 | -61.1909 | 20.7222 | -70.6895 | 23.2829 | -63.6481 | -4.5185 | -17.8941 | 25.5296 | -44.7076 | 130.216 | -17.537 | 10.2366 | -38.7887 | -106.2068 | -17.6873 | 36.3997 | -31.9067 | 4.6223 | -17.1227 | 23.4409 | -31.177 | 0.2634 | -53.5053 | -63.556 | -55.4923 | -53.3178 | -62.7514 | -60.3919 | -53.3499 | -70.5139 | -55.2431 | -52.8577 | -62.6077 | -60.885 | -50.8819 | 44 | -62.2502 | -57.9832 | -56.3757 | -61.4974 | -61.4749 | -60.573 | -57.4532 | -62.2731 | 44 | -68.6067 | -53.3359 | -51.4106 | -60.9484 | -58.5889 | -51.3751 | -68.7109 | -53.2683 | -51.5051 | -60.7766 | -58.5792 | -51.5372 | -61.6488 | -53.5851 | -50.9505 | -60.8047 | -59.082 | -48.9071 | -61.753 | -53.5175 | -51.045 | -60.6329 | -59.0723 | -49.0692
45 | -1.9772 | 0 | -1.831 | 0 | -1.9955 | 0 | -1.8284 | 0 | -69.7199 | -132.8938 | -63.0317 | -53.4221 | -83.3113 | 160.7716 | -59.5796 | 76.0691 | -64.5104 | 118.5304 | -62.3863 | 87.0174 | -70.2341 | -116.776 | -62.7959 | 63.6443 | -69.5729 | -49.7689 | -62.5313 | -15.689 | -67.301 | -5.4056 | -61.798 | -18.8309 | -17.2756 | 4.2091 | -42.154 | 53.8185 | -18.4348 | -11.1521 | -39.7559 | -95.4417 | -16.9507 | 18.6536 | -34.7355 | 21.708 | -17.7064 | 5.7742 | -36.9476 | -15.8422 | -53.3575 | -63.6118 | -55.3748 | -53.1935 | -62.588 | -60.3657 | -53.2021 | -70.3939 | -55.149 | -52.7217 | -62.4795 | -60.8588 | -50.7736 | 45 | -62.1548 | -58.0624 | -56.6225 | -60.2878 | -61.3645 | -60.7612 | -57.583 | -60.1886 | 45 | -68.4167 | -53.1718 | -51.2163 | -60.757 | -58.5347 | -51.2066 | -68.5629 | -53.1535 | -51.3651 | -60.5925 | -58.5373 | -51.3737 | -61.6346 | -53.3976 | -50.7445 | -60.6485 | -59.0278 | -48.7781 | -61.7808 | -53.3793 | -50.8933 | -60.484 | -59.0304 | -48.9452
46 | -2.0116 | 0 | -1.837 | 0 | -2.0158 | 0 | -1.8515 | 0 | -66.3036 | -160.7641 | -65.0609 | -77.4037 | -88.7617 | -160.9857 | -61.0473 | 67.3832 | -63.9383 | 105.8983 | -61.7214 | 58.0181 | -67.873 | -147.4276 | -64.9475 | 45.3634 | -68.8817 | -62.7858 | -64.9864 | -58.2712 | -65.1832 | -31.9089 | -60.8491 | -36.6514 | -17.7563 | -16.9743 | -38.2794 | 7.9495 | -20.8053 | -31.088 | -37.5764 | -91.2063 | -17.2505 | 0.9138 | -32.5596 | 46.5765 | -19.4741 | -9.3375 | -48.2269 | 96.4316 | -53.1994 | -63.5853 | -55.2334 | -53.0471 | -62.4768 | -60.3509 | -53.0792 | -70.2971 | -55.1014 | -52.6104 | -62.4151 | -60.6213 | -50.6063 | 46 | -62.6171 | -58.4656 | -57.5195 | -59.6742 | -62.128 | -61.0592 | -58.3573 | -59.0137 | 46 | -68.2855 | -53.0898 | -51.0355 | -60.6398 | -58.5139 | -51.0634 | -68.4601 | -53.0856 | -51.1956 | -60.461 | -58.4994 | -51.2277 | -61.5737 | -53.2218 | -50.5988 | -60.5781 | -58.7843 | -48.5905 | -61.7483 | -53.2176 | -50.7589 | -60.3993 | -58.7698 | -48.7548
47 | -1.9984 | 0 | -1.8622 | 0 | -2.0003 | 0 | -1.8842 | 0 | -64.502 | 173.6905 | -69.6618 | -100.1304 | -85.881 | -114.7376 | -62.9299 | 67.3954 | -63.8816 | 91.3673 | -61.9951 | 29.4602 | -66.872 | -177.6292 | -69.4744 | 36.2819 | -68.0755 | -73.9836 | -68.0946 | -117.6273 | -64.4118 | -57.3825 | -60.3448 | -56.3024 | -19.4624 | -37.1959 | -35.8415 | -26.5504 | -25.682 | -44.3476 | -35.024 | -103.2522 | -18.5731 | -15.1515 | -28.9578 | 45.1798 | -22.6027 | -16.1522 | -33.2976 | 106.4347 | -53.0254 | -63.4174 | -55.0561 | -52.9317 | -62.3731 | -60.265 | -52.9521 | -70.3401 | -55.0413 | -52.5653 | -62.37 | -60.3596 | -50.4384 | 47 | -63.3224 | -58.9514 | -59.034 | -59.8157 | -63.2411 | -61.4106 | -59.2386 | -58.4118 | 47 | -68.3417 | -53.0429 | -50.9333 | -60.5109 | -58.4028 | -50.9518 | -68.4779 | -53.041 | -51.0475 | -60.3728 | -58.3808 | -51.0679 | -61.419 | -53.0577 | -50.5669 | -60.5078 | -58.4974 | -48.4381 | -61.5552 | -53.0558 | -50.6811 | -60.3697 | -58.4754 | -48.5542
48 | -1.9891 | 0 | -1.9164 | 0 | -1.9998 | 0 | -1.8975 | 0 | -63.7777 | 149.7186 | -87.7839 | -93.4977 | -80.7062 | -110.7132 | -63.731 | 77.6276 | -64.7065 | 78.203 | -62.9969 | -0.5687 | -66.8563 | 151.0909 | -74.4613 | 78.6057 | -68.309 | -84.4277 | -67.7897 | 165.7433 | -64.8033 | -83.102 | -61.4685 | -74.9065 | -22.9236 | -53.7737 | -34.3185 | -57.9342 | -33.8944 | -4.5683 | -33.2291 | -121.5005 | -21.1064 | -26.4336 | -26.6839 | 31.5527 | -25.8328 | 0.3124 | -28.3087 | 87.5034 | -52.9155 | -63.1356 | -54.953 | -52.8687 | -62.2749 | -60.2411 | -52.8774 | -70.6365 | -54.9852 | -52.5492 | -62.2602 | -60.2068 | -50.2737 | 48 | -63.6736 | -59.2779 | -60.3303 | -60.7141 | -64.0933 | -61.5275 | -60.3846 | -59.2388 | 48 | -68.6474 | -52.9961 | -50.8796 | -60.3585 | -58.3247 | -50.8776 | -68.7201 | -52.9854 | -50.9712 | -60.2751 | -58.3436 | -50.9799 | -61.1465 | -52.9639 | -50.5601 | -60.3438 | -58.2904 | -48.2739 | -61.2192 | -52.9532 | -50.6517 | -60.2604 | -58.3093 | -48.3762
49 | -1.9829 | 0 | -1.9362 | 0 | -2.0125 | 0 | -1.9288 | 0 | -63.9413 | 126.9301 | -71.097 | 20.4754 | -78.438 | -120.9161 | -62.3864 | 85.7857 | -66.3352 | 69.8849 | -65.228 | -32.9078 | -67.6879 | 117.1935 | -68.0771 | 107.1983 | -68.6114 | -92.6844 | -64.5252 | 108.9341 | -66.3986 | -109.4987 | -63.1902 | -90.1897 | -29.6734 | -51.2483 | -33.5014 | -88.6786 | -26.36 | 41.1956 | -32.1271 | -142.2478 | -24.7934 | -22.4424 | -25.6976 | 13.5817 | -24.0313 | 24.6883 | -25.7449 | 66.7576 | -52.8182 | -62.8788 | -54.8883 | -52.8299 | -62.1307 | -60.3397 | -52.8386 | -71.2703 | -54.897 | -52.5456 | -62.0456 | -60.2195 | -50.1456 | 49 | -63.0493 | -59.1603 | -60.2001 | -62.6208 | -63.3379 | -61.2366 | -60.0517 | -60.7235 | 49 | -69.2874 | -52.9141 | -50.847 | -60.1945 | -58.4035 | -50.8261 | -69.3341 | -52.8845 | -50.9011 | -60.1182 | -58.4109 | -50.9098 | -60.8959 | -52.9054 | -50.5627 | -60.1094 | -58.2833 | -48.1331 | -60.9426 | -52.8758 | -50.6168 | -60.0331 | -58.2907 | -48.2168
50 | -1.9828 | 0 | -1.954 | 0 | -2.0647 | 0 | -1.9578 | 0 | -65.0592 | 106.4054 | -65.1667 | -1.7819 | -78.3232 | -119.0411 | -60.5501 | 83.4134 | -67.9728 | 71.5201 | -69.5622 | -75.5078 | -69.2855 | 77.8587 | -63.7514 | 94.9424 | -68.9226 | -98.867 | -62.1063 | 67.9182 | -70.0749 | -138.1191 | -66.0795 | -98.2869 | -29.8729 | 15.7456 | -33.0939 | -119.6928 | -21.5792 | 28.7189 | -31.4554 | -163.6859 | -25.6699 | 6.0028 | -25.8306 | -5.9013 | -20.7346 | 23.5128 | -24.6011 | 45.5329 | -52.7187 | -62.7083 | -54.8647 | -52.8007 | -61.8789 | -60.4622 | -52.8095 | -72.2639 | -54.7797 | -52.4813 | -61.7821 | -60.4241 | -50.0453 | 50 | -61.9999 | -58.6888 | -58.8741 | -65.4545 | -61.7548 | -60.7994 | -58.9147 | -63.2507 | 50 | -70.2811 | -52.7969 | -50.8179 | -59.9249 | -58.5082 | -50.7448 | -70.3099 | -52.715 | -50.8429 | -59.8142 | -58.5044 | -50.8517 | -60.7255 | -52.8819 | -50.4985 | -59.8281 | -58.4701 | -47.9806 | -60.7543 | -52.8 | -50.5235 | -59.7174 | -58.4663 | -48.0875
51 | -2.0251 | 0 | -1.969 | 0 | -2.1188 | 0 | -1.9914 | 0 | -67.043 | 90.2206 | -62.4509 | -24.211 | -78.7548 | -117.9024 | -59.272 | 74.1368 | -68.0786 | 84.0118 | -74.7996 | -153.6732 | -71.2186 | 29.0045 | -61.5889 | 75.5454 | -68.9785 | -101.8032 | -60.8994 | 32.9297 | -78.5585 | 176.3202 | -68.9708 | -88.8263 | -23.3376 | 18.4894 | -33.1258 | -150.809 | -19.3961 | 8.9018 | -31.2458 | 175.4548 | -22.2126 | 16.865 | -27.1398 | -25.5756 | -18.7989 | 10.4484 | -24.5457 | 24.1776 | -52.7103 | -62.6922 | -54.8602 | -52.7806 | -61.6712 | -60.5867 | -52.8362 | -73.861 | -54.7048 | -52.3557 | -61.5628 | -60.7126 | -49.9119 | 51 | -61.0812 | -58.1369 | -57.4852 | -66.9447 | -60.4786 | -60.4459 | -57.8694 | -65.7317 | 51 | -71.8359 | -52.6797 | -50.7555 | -59.7022 | -58.6177 | -50.7174 | -71.892 | -52.586 | -50.7892 | -59.5524 | -58.5953 | -50.8448 | -60.6671 | -52.8351 | -50.3306 | -59.5938 | -58.7436 | -47.7931 | -60.7232 | -52.7414 | -50.3643 | -59.444 | -58.7212 | -47.9205
52 | -2.0789 | 0 | -1.9867 | 0 | -2.1489 | 0 | -1.9834 | 0 | -70.0389 | 84.1109 | -61.3123 | -46.1424 | -79.8094 | -127.4874 | -58.7777 | 62.4613 | -66.1347 | 85.4325 | -70.3164 | 117.4188 | -71.8482 | -29.4754 | -60.8158 | 53.4749 | -68.675 | -103.6362 | -60.8041 | 0.0785 | -76.0046 | 31.4464 | -68.5653 | -69.0737 | -20.1039 | 2.1041 | -33.5017 | 178.0184 | -18.7333 | -12.4553 | -31.3726 | 155.1269 | -19.502 | 8.2285 | -30.1285 | -44.1531 | -18.0876 | -6.3281 | -25.5588 | 3.6621 | -52.6968 | -62.6324 | -54.8436 | -52.7319 | -61.4585 | -60.6207 | -52.8657 | -76.1489 | -54.6531 | -52.2211 | -61.3578 | -61.0474 | -49.7426 | 52 | -60.7121 | -57.7789 | -56.661 | -64.5975 | -59.8726 | -60.3555 | -57.45 | -65.23 | 52 | -74.07 | -52.5742 | -50.653 | -59.4718 | -58.634 | -50.7168 | -74.1622 | -52.5042 | -50.7485 | -59.3096 | -58.6373 | -50.8823 | -60.5535 | -52.7647 | -50.1422 | -59.3711 | -59.0607 | -47.5937 | -60.6457 | -52.6947 | -50.2377 | -59.2089 | -59.064 | -47.7592
53 | -2.1328 | 0 | -2.011 | 0 | -2.1719 | 0 | -2.0109 | 0 | -72.2129 | 97.2558 | -61.3215 | -66.3882 | -78.5733 | -120.9425 | -58.996 | 51.1403 | -64.3095 | 77.18 | -65.6563 | 74.1102 | -70.5922 | -84.4764 | -61.2191 | 30.1471 | -67.7476 | -107.4051 | -61.8394 | -33.0125 | -68.5348 | -7.7489 | -66.1231 | -63.1557 | -18.6539 | -18.0184 | -34.4269 | 147.9049 | -19.3214 | -34.0399 | -31.8165 | 136.3207 | -18.0683 | -6.871 | -36.291 | -54.4389 | -18.4905 | -23.7553 | -27.9277 | -15.818 | -52.6859 | -62.3936 | -54.8428 | -52.6507 | -61.2953 | -60.5968 | -52.8782 | -79.2969 | -54.6367 | -52.1048 | -61.218 | -61.3438 | -49.5506 | 53 | -60.9065 | -57.7189 | -56.4405 | -61.8277 | -59.9547 | -60.5448 | -57.8143 | -62.5785 | 53 | -77.1641 | -52.5039 | -50.5179 | -59.2843 | -58.5858 | -50.7063 | -77.2859 | -52.4648 | -50.6398 | -59.1234 | -58.5859 | -50.8673 | -60.2608 | -52.71 | -49.972 | -59.207 | -59.3328 | -47.3787 | -60.3826 | -52.6709 | -50.0939 | -59.0461 | -59.3329 | -47.5397
54 | -2.134 | 0 | -2.0057 | 0 | -2.1469 | 0 | -2.0192 | 0 | -70.5136 | 112.7015 | -62.3715 | -83.8619 | -78.1111 | -120.3841 | -59.9175 | 42.861 | -63.4894 | 63.7511 | -63.124 | 44.0634 | -69.0112 | -128.523 | -62.9242 | 5.7804 | -66.7606 | -113.4079 | -64.4203 | -68.1872 | -64.7847 | -35.1397 | -63.4456 | -75.9765 | -18.4151 | -39.1872 | -36.2786 | 117.8798 | -21.2692 | -54.9234 | -32.5781 | 119.2395 | -17.7233 | -24.1717 | -43.4853 | 20.5315 | -20.037 | -39.9893 | -32.4133 | -30.4501 | -52.5869 | -61.8648 | -54.7971 | -52.5517 | -61.2158 | -60.5601 | -52.8143 | -83.5766 | -54.591 | -52.0174 | -61.1307 | -61.4712 | -49.3381 | 54 | -61.6525 | -58.0805 | -56.8079 | -60.2214 | -60.7242 | -60.8658 | -58.7821 | -60.0198 | 54 | -81.4426 | -52.457 | -50.4177 | -59.2101 | -58.5544 | -50.6674 | -81.5709 | -52.4441 | -50.5325 | -59.0689 | -58.5409 | -50.7951 | -59.7308 | -52.6631 | -49.8834 | -59.125 | -59.4655 | -47.1912 | -59.8591 | -52.6502 | -49.9982 | -58.9838 | -59.452 | -47.3189
55 | -2.1496 | 0 | -2.0458 | 0 | -2.1612 | 0 | -2.034 | 0 | -67.799 | 107.9595 | -64.4108 | -93.7594 | -77.1338 | -120.6857 | -61.2009 | 39.4461 | -63.4328 | 47.3623 | -61.7928 | 14.7465 | -67.7326 | -166.8692 | -66.8364 | -22.156 | -65.7787 | -122.8477 | -69.432 | -117.7602 | -62.9978 | -60.9638 | -62.2711 | -90.8869 | -19.2956 | -60.4894 | -39.8349 | 88.4989 | -25.2314 | -72.0887 | -33.6603 | 103.5572 | -18.3644 | -41.4522 | -33.864 | 42.0504 | -23.0444 | -50.3076 | -40.9924 | -11.7749 | -52.5214 | -61.1486 | -54.8011 | -52.498 | -61.1738 | -60.5392 | -52.7255 | -85.5557 | -54.5012 | -52.0575 | -61.0614 | -61.5205 | -49.282 | 55 | -62.616 | -58.6073 | -57.49 | -59.4509 | -61.9378 | -61.057 | -60.3909 | -58.6693 | 55 | -83.4061 | -52.3516 | -50.3484 | -59.128 | -58.4934 | -50.5643 | -83.5099 | -52.34 | -50.464 | -59.0126 | -58.5052 | -50.6915 | -58.999 | -52.6515 | -49.9079 | -59.0156 | -59.4747 | -47.1208 | -59.1028 | -52.6399 | -50.0235 | -58.9002 | -59.4865 | -47.248
56 | -2.1546 | 0 | -2.0828 | 0 | -2.1637 | 0 | -2.0755 | 0 | -65.8722 | 94.1664 | -66.4362 | -88.8658 | -77.7749 | -133.0846 | -62.0303 | 44.4718 | -64.4189 | 31.4111 | -61.5455 | -11.9823 | -67.2777 | 157.9637 | -76.3773 | -73.3648 | -64.3903 | -137.9972 | -72.1063 | 142.1928 | -62.3901 | -86.349 | -62.0249 | -107.2392 | -21.4821 | -80.8624 | -48.8195 | 60.0361 | -33.3338 | -64.8034 | -35.0724 | 89.8679 | -20.1081 | -57.0105 | -29.8133 | 26.7774 | -27.1914 | -41.662 | -36.9047 | 55.0315 | -52.3754 | -60.3235 | -54.7519 | -52.4457 | -61.0199 | -60.6165 | -52.575 | -84.4489 | -54.3148 | -52.1141 | -60.8641 | -61.4137 | -49.2477 | 56 | -62.9881 | -59.0422 | -58.0846 | -59.6707 | -62.4102 | -60.8329 | -61.4755 | -58.0466 | 56 | -82.2943 | -52.1602 | -50.2911 | -58.9371 | -58.5337 | -50.4113 | -82.3661 | -52.1511 | -50.3702 | -58.8562 | -58.541 | -50.4995 | -58.1689 | -52.5973 | -49.9595 | -58.7813 | -59.3309 | -47.084 | -58.2407 | -52.5882 | -50.0386 | -58.7004 | -59.3382 | -47.1722
57 | -2.1157 | 0 | -2.0352 | 0 | -2.1437 | 0 | -2.0604 | 0 | -64.93 | 75.5038 | -65.7557 | -76.2415 | -81.9661 | -147.1501 | -61.3094 | 51.0643 | -66.9402 | 20.3131 | -62.2794 | -41.7162 | -67.5371 | 122.483 | -71.6904 | 145.5206 | -63.7816 | -153.6581 | -65.7869 | 73.9791 | -62.9596 | -111.4214 | -62.4744 | -122.8383 | -25.7289 | -96.8566 | -48.2542 | -140.054 | -30.878 | 7.744 | -37.0883 | 76.397 | -23.2383 | -66.2741 | -28.1458 | 7.1395 | -27.0454 | -9.7766 | -31.8615 | 48.1261 | -52.1865 | -59.6075 | -54.5951 | -52.4091 | -60.7451 | -60.6543 | -52.3399 | -81.0226 | -53.9946 | -52.1055 | -60.4884 | -61.175 | -49.2341 | 57 | -62.2662 | -58.9847 | -57.9667 | -60.9675 | -61.7867 | -60.2411 | -60.4709 | -58.2676 | 57 | -78.9069 | -51.8789 | -50.2934 | -58.7099 | -58.6191 | -50.1962 | -78.9874 | -51.8509 | -50.3487 | -58.6014 | -58.5939 | -50.2795 | -57.4918 | -52.4794 | -49.9898 | -58.4532 | -59.1398 | -47.0904 | -57.5723 | -52.4514 | -50.0451 | -58.3447 | -59.1146 | -47.1737
58 | -2.1308 | 0 | -2.0666 | 0 | -2.1813 | 0 | -2.0644 | 0 | -64.9227 | 55.8676 | -63.3839 | -77.5257 | -85.0959 | -16.4769 | -59.7466 | 50.4294 | -70.612 | 28.2247 | -64.447 | -70.972 | -68.5302 | 85.8575 | -64.6412 | 108.8941 | -63.7445 | -170.552 | -61.9143 | 35.8139 | -65.0567 | -138.2053 | -63.7126 | -139.3666 | -34.4015 | -82.4713 | -39.0715 | -171.864 | -24.718 | 1.9187 | -39.8922 | 65.5515 | -27.3828 | -54.7472 | -27.914 | -12.2246 | -23.36 | -3.7327 | -29.8235 | 31.1592 | -52.0851 | -59.1958 | -54.3601 | -52.4483 | -60.4327 | -60.7466 | -52.1721 | -77.3336 | -53.6815 | -52.1369 | -60.1682 | -61.0954 | -49.2944 | 58 | -61.058 | -58.3302 | -57.263 | -63.4764 | -60.4289 | -59.6022 | -58.5006 | -59.3565 | 58 | -75.2028 | -51.5507 | -50.3175 | -58.3661 | -58.68 | -49.9908 | -75.267 | -51.5002 | -50.3839 | -58.2514 | -58.6822 | -50.1077 | -57.065 | -52.2293 | -50.0061 | -58.1016 | -59.0288 | -47.1131 | -57.1292 | -52.1788 | -50.0725 | -57.9869 | -59.031 | -47.23
59 | -2.1567 | 0 | -2.0825 | 0 | -2.2019 | 0 | -2.0811 | 0 | -65.7392 | 36.1379 | -61.4907 | -89.6283 | -73.374 | -30.2629 | -58.4307 | 42.8126 | -70.3397 | 54.9795 | -68.6141 | -103.209 | -70.2287 | 47.8733 | -61.4734 | 81.942 | -64.858 | 166.0333 | -59.9021 | 4.0404 | -69.7846 | -170.757 | -66.0661 | -148.1262 | -30.0978 | -12.0866 | -35.1483 | 160.0509 | -22.0097 | -17.8379 | -43.7801 | 63.2991 | -26.665 | -23.0482 | -29.0243 | -30.1137 | -20.9884 | -15.2318 | -29.8556 | 12.5458 | -51.9212 | -59.0171 | -54.0774 | -52.429 | -60.1321 | -60.8609 | -51.9536 | -74.6706 | -53.52 | -52.0473 | -59.9028 | -61.1511 | -49.1971 | 59 | -59.9047 | -57.4606 | -56.4162 | -65.5901 | -59.4542 | -59.1266 | -57.0279 | -61.6799 | 59 | -72.5139 | -51.3633 | -50.2723 | -58.0496 | -58.7784 | -49.7517 | -72.5881 | -51.3181 | -50.3479 | -57.9302 | -58.7798 | -49.8725 | -56.8604 | -51.9207 | -49.8906 | -57.8203 | -59.0686 | -46.9952 | -56.9346 | -51.8755 | -49.9662 | -57.7009 | -59.07 | -47.116
60 | -2.1618 | 0 | -2.1044 | 0 | -2.2367 | 0 | -2.1063 | 0 | -67.5207 | 17.8708 | -60.5215 | -106.5695 | -68.1251 | -55.0494 | -57.686 | 31.9888 | -66.8745 | 61.4639 | -76.924 | -163.6696 | -72.5583 | 6.5044 | -60.0695 | 57.2178 | -66.7201 | 145.7902 | -59.1623 | -25.4109 | -80.3787 | 95.0213 | -67.8414 | -148.4617 | -24.2518 | -20.3786 | -33.3023 | 132.602 | -21.0673 | -40.689 | -48.8105 | 85.1683 | -22.9579 | -19.1983 | -31.5437 | -43.6029 | -19.9716 | -31.6353 | -31.8513 | -4.7186 | -51.779 | -59.005 | -53.8481 | -52.404 | -59.9782 | -61.0871 | -51.749 | -73.0727 | -53.5368 | -51.8935 | -59.8545 | -61.3969 | -48.9618 | 60 | -59.1442 | -56.8067 | -55.8321 | -64.2059 | -59.0225 | -58.9367 | -56.2686 | -64.1301 | 60 | -70.9109 | -51.375 | -50.2422 | -57.8738 | -58.9827 | -49.5123 | -70.9683 | -51.3001 | -50.2977 | -57.7415 | -58.9808 | -49.6427 | -56.8432 | -51.6863 | -49.7317 | -57.7501 | -59.2925 | -46.7251 | -56.9006 | -51.6114 | -49.7872 | -57.6178 | -59.2906 | -46.8555
61 | -2.1972 | 0 | -2.1154 | 0 | -2.2528 | 0 | -2.133 | 0 | -70.7134 | 2.3341 | -60.533 | -126.0211 | -64.9923 | -77.9513 | -57.5445 | 20.0519 | -64.125 | 51.287 | -73.5862 | 80.8174 | -75.523 | -44.2609 | -59.92 | 34.0157 | -69.7661 | 119.935 | -59.5264 | -53.7688 | -69.6104 | -9.1294 | -68.2942 | -139.8905 | -21.5664 | -40.0601 | -32.9157 | 104.5644 | -21.4119 | -65.4824 | -47.9595 | 133.3127 | -20.609 | -31.4293 | -35.6639 | -41.7213 | -20.0703 | -49.4951 | -37.1616 | -12.9462 | -51.5672 | -59.021 | -53.8014 | -52.3329 | -59.9774 | -61.2906 | -51.5021 | -72.5731 | -53.7246 | -51.7521 | -59.9943 | -61.8114 | -48.5554 | 61 | -58.9071 | -56.5134 | -55.705 | -61.2645 | -59.3849 | -59.0217 | -56.417 | -64.4006 | 61 | -70.3759 | -51.5274 | -50.1357 | -57.862 | -59.1752 | -49.2493 | -70.4577 | -51.4718 | -50.1999 | -57.7246 | -59.1576 | -49.3691 | -56.8238 | -51.6042 | -49.5549 | -57.8789 | -59.696 | -46.3026 | -56.9056 | -51.5486 | -49.6191 | -57.7415 | -59.6784 | -46.4224
62 | -2.2566 | 0 | -2.1465 | 0 | -2.2615 | 0 | -2.1416 | 0 | -77.1058 | 0.2626 | -61.622 | -146.1288 | -62.8996 | -96.1665 | -58.0072 | 8.1673 | -62.4518 | 35.0479 | -66.6915 | 41.035 | -77.8459 | -112.0658 | -60.9116 | 12.7432 | -74.7651 | 70.8076 | -61.1422 | -80.6928 | -63.9568 | -40.8874 | -66.9724 | -139.7504 | -20.5247 | -62.6377 | -33.9388 | 75.4517 | -23.0068 | -92.3529 | -43.1766 | 146.9544 | -19.6044 | -48.3283 | -36.9462 | -8.4815 | -21.2067 | -66.6481 | -43.0594 | 54.0456 | -51.3639 | -58.8656 | -53.8841 | -52.2936 | -60.0553 | -61.7093 | -51.2637 | -73.781 | -53.948 | -51.6895 | -60.2364 | -62.4685 | -48.2471 | 62 | -59.1339 | -56.6347 | -56.0471 | -58.8748 | -60.6527 | -59.2546 | -57.4953 | -61.9636 | 62 | -71.5244 | -51.6914 | -50.037 | -57.9088 | -59.5628 | -49.0022 | -71.6345 | -51.6865 | -50.152 | -57.7938 | -59.5677 | -49.1221 | -56.609 | -51.6275 | -49.4329 | -58.0899 | -60.322 | -45.9856 | -56.7191 | -51.6226 | -49.5479 | -57.9749 | -60.3269 | -46.1055
63 | -2.2813 | 0 | -2.1561 | 0 | -2.2858 | 0 | -2.1615 | 0 | -78.5685 | 70.7141 | -64.2975 | -164.2558 | -61.5516 | -115.8415 | -59.1427 | -1.6157 | -61.9073 | 15.8534 | -63.0467 | 12.9336 | -76.6423 | 172.2945 | -63.1018 | -6.2123 | -78.2541 | -45.1278 | -64.5932 | -106.2071 | -61.077 | -66.8375 | -65.7709 | -151.2948 | -20.6187 | -86.5105 | -37.1087 | 40.654 | -26.1989 | -122.6193 | -40.2269 | 144.9803 | -19.5937 | -67.1517 | -32.8849 | 2.8768 | -23.4139 | -80.8525 | -33.9364 | 77.4886 | -51.1742 | -58.4523 | -54.065 | -52.3148 | -60.1 | -62.4757 | -51.0311 | -77.4147 | -54.0469 | -51.7616 | -60.4257 | -63.3873 | -48.103 | 63 | -59.6448 | -57.266 | -56.8073 | -57.3519 | -62.7886 | -59.3956 | -59.5796 | -59.7465 | 63 | -75.1334 | -51.7656 | -50.0335 | -57.9439 | -60.3196 | -48.7453 | -75.2586 | -51.7611 | -50.1533 | -57.8142 | -60.3142 | -48.8696 | -56.171 | -51.7837 | -49.4803 | -58.2696 | -61.2312 | -45.8172 | -56.2962 | -51.7792 | -49.6001 | -58.1399 | -61.2258 | -45.9415
64 | -2.3063 | 0 | -2.1819 | 0 | -2.2999 | 0 | -2.1823 | 0 | -71.3644 | 75.1038 | -69.2953 | -168.7787 | -60.6275 | -137.462 | -60.8739 | -5.773 | -62.5106 | -5.3349 | -61.433 | -13.5577 | -73.452 | 112.8054 | -67.4103 | -20.4658 | -70.157 | -99.4293 | -72.7371 | -127.1259 | -59.4937 | -92.643 | -64.8353 | -168.372 | -21.8015 | -111.5127 | -44.0279 | -26.1678 | -32.0596 | -165.7513 | -38.0964 | 140.5302 | -20.6556 | -86.0132 | -29.8891 | -7.94 | -26.6885 | -86.7193 | -29.3828 | 63.2397 | -51.0593 | -57.8413 | -54.2032 | -52.3639 | -59.8796 | -63.3452 | -50.842 | -78.0381 | -53.7399 | -51.9475 | -60.2756 | -64.0108 | -48.1794 | 64 | -59.7629 | -58.3811 | -57.8139 | -56.6849 | -64.9059 | -59.1291 | -62.4931 | -58.1008 | 64 | -75.7318 | -51.4336 | -50.0576 | -57.6977 | -61.1633 | -48.5421 | -75.8562 | -51.44 | -50.1816 | -57.5797 | -61.1629 | -48.6597 | -55.535 | -51.8969 | -49.6412 | -58.0937 | -61.8289 | -45.8795 | -55.6594 | -51.9033 | -49.7652 | -57.9757 | -61.8285 | -45.9971
65 | -2.3009 | 0 | -2.1992 | 0 | -2.3169 | 0 | -2.2034 | 0 | -68.1611 | 57.9135 | -72.1241 | -127.9495 | -60.6543 | -160.5936 | -62.2711 | 0.0893 | -64.8446 | -24.0437 | -61.0619 | -36.5536 | -71.1825 | 65.6116 | -76.0727 | 1.3741 | -65.6463 | -130.6861 | -75.1491 | 4.826 | -59.0559 | -119.6234 | -64.4217 | 169.1831 | -24.2593 | -137.8945 | -38.6718 | -136.262 | -36.4093 | 94.0115 | -36.5966 | 136.9125 | -22.8301 | -103.7348 | -28.2795 | -26.1221 | -29.681 | -74.8807 | -27.2189 | 43.9032 | -51.0491 | -57.3622 | -53.9984 | -52.4475 | -59.3264 | -63.6786 | -50.7734 | -72.7623 | -53.004 | -52.1601 | -59.6289 | -63.6724 | -48.4854 | 65 | -59.6892 | -59.693 | -58.4249 | -57.0532 | -64.2786 | -58.6981 | -63.8036 | -57.2663 | 65 | -70.4614 | -50.7031 | -50.1466 | -57.1272 | -61.4794 | -48.4565 | -70.5631 | -50.6871 | -50.2441 | -57.0095 | -61.4752 | -48.57 | -55.0613 | -51.6975 | -49.8592 | -57.4297 | -61.4732 | -46.1685 | -55.163 | -51.6815 | -49.9567 | -57.312 | -61.469 | -46.282
66 | -2.2981 | 0 | -2.2345 | 0 | -2.3364 | 0 | -2.227 | 0 | -66.6607 | 42.7725 | -67.3732 | -114.733 | -62.3928 | 176.7643 | -61.9099 | 8.3848 | -68.7056 | -28.4775 | -61.5492 | -57.4203 | -69.9295 | 28.4838 | -70.3753 | 67.7281 | -65.3704 | -155.4946 | -64.917 | -14.2701 | -59.9197 | -147.3597 | -65.3364 | 139.8148 | -28.7446 | -167.5093 | -32.3041 | -176.3674 | -30.696 | 25.5516 | -35.1261 | 133.4043 | -26.5657 | -116.6965 | -27.7116 | -46.9076 | -29.1728 | -59.1078 | -26.4239 | 23.2109 | -51.1195 | -57.2058 | -53.5034 | -52.5062 | -58.7445 | -63.4089 | -50.8321 | -69.6294 | -52.3059 | -52.2892 | -58.8751 | -62.7505 | -48.9267 | 66 | -60.1089 | -60.0233 | -58.1609 | -58.5045 | -63.1539 | -58.4085 | -61.5076 | -57.9542 | 66 | -67.3313 | -50.0078 | -50.2081 | -56.51 | -61.1744 | -48.4957 | -67.3949 | -49.9695 | -50.2792 | -56.4081 | -61.1819 | -48.6051 | -54.9077 | -51.2053 | -49.9911 | -56.6406 | -60.516 | -46.5903 | -54.9713 | -51.167 | -50.0622 | -56.5387 | -60.5235 | -46.6997
67 | -2.3048 | 0 | -2.2563 | 0 | -2.3502 | 0 | -2.2455 | 0 | -65.4776 | 28.3725 | -64.7498 | -126.8285 | -65.9415 | 167.5332 | -60.642 | 9.5293 | -71.2873 | -8.3309 | -62.4331 | -73.3957 | -69.1228 | -0.3201 | -64.7346 | 58.4901 | -64.9689 | -170.0269 | -60.9128 | -40.6196 | -62.415 | -174.9894 | -67.705 | 107.9567 | -38.0329 | 141.3669 | -28.734 | 154.3421 | -27.8705 | -9.9736 | -33.4904 | 128.4054 | -32.2703 | -110.1557 | -27.8824 | -69.8448 | -27.493 | -61.333 | -26.8454 | 1.0996 | -51.1177 | -57.2429 | -53.0842 | -52.481 | -58.4537 | -62.8523 | -50.8657 | -68.0572 | -52.0548 | -52.2172 | -58.4633 | -61.8853 | -49.1905 | 67 | -60.5905 | -59.1356 | -57.5236 | -60.4575 | -61.0956 | -58.221 | -58.8067 | -59.7405 | 67 | -65.7524 | -49.75 | -50.1762 | -56.1974 | -60.596 | -48.5155 | -65.8009 | -49.7046 | -50.2355 | -56.1035 | -60.6068 | -48.6202 | -54.9381 | -50.7794 | -49.9124 | -56.207 | -59.629 | -46.8403 | -54.9866 | -50.734 | -49.9717 | -56.1131 | -59.6398 | -46.945
68 | -2.317 | 0 | -2.2657 | 0 | -2.3615 | 0 | -2.2725 | 0 | -64.4294 | 11.6587 | -63.8741 | -142.4648 | -67.6172 | 172.1685 | -59.6053 | 4.8897 | -70.0629 | 10.8326 | -64.2335 | -91.3459 | -68.3506 | -25.0047 | -62.275 | 39.2946 | -64.1865 | 176.1572 | -59.057 | -67.8541 | -67.4743 | 155.3179 | -72.7425 | 72.0367 | -36.5211 | 3.5728 | -26.7466 | 128.6409 | -27.2352 | -40.3427 | -32.0615 | 121.9124 | -33.2004 | -66.1435 | -28.8427 | -94.4075 | -27.0442 | -72.9817 | -28.5457 | -21.1352 | -50.9748 | -57.4221 | -52.9088 | -52.338 | -58.4552 | -62.0549 | -50.7931 | -67.6701 | -52.1256 | -51.9806 | -58.4142 | -61.2599 | -49.0576 | 68 | -60.2524 | -58.0846 | -57.2533 | -61.8781 | -59.5085 | -58.0477 | -57.2401 | -62.1223 | 68 | -65.3531 | -49.8086 | -50.021 | -56.1895 | -59.7892 | -48.4316 | -65.4044 | -49.7641 | -50.0655 | -56.0937 | -59.7824 | -48.5206 | -55.1051 | -50.5918 | -49.6636 | -56.1485 | -58.9942 | -46.6961 | -55.1564 | -50.5473 | -49.7081 | -56.0527 | -58.9874 | -46.7851
69 | -2.345 | 0 | -2.2725 | 0 | -2.3773 | 0 | -2.2911 | 0 | -63.9416 | -8.092 | -63.9496 | -158.0763 | -67.4463 | 178.1102 | -58.8927 | -1.6009 | -66.7535 | 11.8163 | -67.7586 | -102.7686 | -67.9366 | -48.5248 | -61.8534 | 18.6438 | -63.6881 | 157.2765 | -58.6257 | -95.4962 | -80.1323 | 77.6144 | -81.736 | 58.4514 | -30.4291 | -38.9621 | -25.7118 | 105.0687 | -28.4028 | -69.749 | -30.5493 | 113.3461 | -29.1899 | -59.0675 | -30.3564 | -121.4594 | -27.7271 | -87.8773 | -32.0265 | -46.92 | -50.7822 | -57.7659 | -52.8548 | -52.1689 | -58.6377 | -61.2933 | -50.6592 | -68.7796 | -52.3529 | -51.7178 | -58.6084 | -61.0179 | -48.4409 | 69 | -60.0599 | -57.2008 | -57.3032 | -62.5277 | -59.0616 | -58.117 | -56.9217 | -63.5247 | 69 | -66.4346 | -50.0079 | -49.8239 | -56.3652 | -59.0208 | -48.2819 | -66.5071 | -49.9756 | -49.8778 | -56.2604 | -59.0022 | -48.3681 | -55.4209 | -50.5098 | -49.3728 | -56.3359 | -58.7454 | -46.0636 | -55.4934 | -50.4775 | -49.4267 | -56.2311 | -58.7268 | -46.1498
70 | -2.3559 | 0 | -2.3043 | 0 | -2.4068 | 0 | -2.2954 | 0 | -64.2759 | -29.4165 | -65.0705 | -174.6972 | -67.4009 | 174.258 | -58.3617 | -9.7539 | -64.2971 | 1.8452 | -76.1164 | -111.6785 | -68.2047 | -70.2626 | -63.1946 | 0.701 | -65.0061 | 142.0259 | -59.4867 | -122.7723 | -69.3301 | -42.2393 | -88.4952 | 125.5121 | -28.2268 | -70.0243 | -25.6553 | 82.7137 | -31.5054 | -101.6948 | -29.403 | 103.2687 | -27.2019 | -71.4526 | -32.3869 | -152.6003 | -29.9529 | -101.1736 | -39.2456 | -88.9798 | -50.6031 | -58.2055 | -52.8773 | -52.1304 | -58.9859 | -60.9829 | -50.5153 | -72.7466 | -52.6841 | -51.5621 | -59.0153 | -61.4927 | -47.7519 | 70 | -60.6215 | -56.5686 | -57.4622 | -62.3794 | -60.2402 | -58.5595 | -57.9423 | -63.6263 | 70 | -70.3907 | -50.3282 | -49.7745 | -56.6816 | -58.6786 | -48.1085 | -70.4423 | -50.2773 | -49.835 | -56.5791 | -58.6875 | -48.2199 | -55.8496 | -50.5214 | -49.2062 | -56.711 | -59.1884 | -45.3451 | -55.9012 | -50.4705 | -49.2667 | -56.6085 | -59.1973 | -45.4565
71 | -2.387 | 0 | -2.3179 | 0 | -2.4113 | 0 | -2.3121 | 0 | -65.6472 | -48.3687 | -68.4252 | 172.9529 | -67.0054 | 175.8978 | -58.2035 | -20.0684 | -62.4818 | -16.5053 | -70.8472 | -21.8745 | -69.73 | -87.5438 | -66.3295 | -8.3907 | -67.1563 | 130.6789 | -61.8032 | -149.194 | -63.3379 | -71.7864 | -78.3364 | 118.3483 | -28.0405 | -100.1875 | -26.4571 | 63.8204 | -38.3024 | -149.9892 | -28.4249 | 93.1266 | -26.9337 | -88.5808 | -34.5953 | 169.2801 | -33.488 | -105.2029 | -39.9722 | 151.7636 | -50.4174 | -58.1749 | -53.1896 | -52.2729 | -59.3744 | -61.7374 | -50.3765 | -86.923 | -53.0902 | -51.6343 | -59.4781 | -63.216 | -47.2528 | 71 | -62.1082 | -56.2903 | -57.5987 | -60.725 | -62.7431 | -59.0999 | -60.4205 | -61.734 | 71 | -84.536 | -50.7032 | -49.8859 | -57.0565 | -59.4195 | -47.9652 | -84.6051 | -50.6789 | -49.9608 | -56.9631 | -59.4253 | -48.0644 | -55.7879 | -50.8026 | -49.2473 | -57.1602 | -60.8981 | -44.8415 | -55.857 | -50.7783 | -49.3222 | -57.0668 | -60.9039 | -44.9407
72 | -2.4027 | 0 | -2.3323 | 0 | -2.4436 | 0 | -2.325 | 0 | -67.2021 | -58.5762 | -73.3303 | -158.461 | -65.4925 | 172.6246 | -58.8917 | -29.727 | -61.6059 | -40.9461 | -64.6585 | -31.8805 | -71.8295 | -81.8948 | -70.7124 | 6.6109 | -68.0504 | 149.4422 | -66.3603 | -176.6843 | -60.2339 | -96.4689 | -78.1956 | 92.7886 | -29.3741 | -131.6309 | -28.0717 | 50.0459 | -39.4823 | 88.115 | -27.5654 | 81.63 | -27.9505 | -106.2795 | -35.8883 | 123.1661 | -36.5663 | -86.3701 | -32.5804 | 108.7402 | -50.3497 | -57.2462 | -53.7013 | -52.6778 | -59.4278 | -64.1134 | -50.3206 | -73.5608 | -53.2816 | -51.9768 | -59.6096 | -66.7874 | -47.1798 | 72 | -62.8464 | -56.6313 | -57.7488 | -58.8097 | -65.1264 | -59.0505 | -64.7989 | -59.5102 | 72 | -71.1581 | -50.8789 | -50.2751 | -57.0955 | -61.7811 | -47.877 | -71.2285 | -50.838 | -50.3528 | -56.9842 | -61.7884 | -47.9956 | -54.8435 | -51.2986 | -49.5741 | -57.2773 | -64.4551 | -44.7362 | -54.9139 | -51.2577 | -49.6518 | -57.166 | -64.4624 | -44.8548
73 | -2.4055 | 0 | -2.3471 | 0 | -2.4663 | 0 | -2.351 | 0 | -67.0393 | -73.3279 | -67.7925 | -127.5866 | -64.3764 | 147.4027 | -59.9272 | -31.8819 | -62.5911 | -70.457 | -62.8021 | -50.8785 | -68.2161 | -74.741 | -69.4625 | 48.7941 | -63.812 | 149.2807 | -79.2994 | 123.0391 | -58.7192 | -123.0904 | -73.0207 | 84.2214 | -32.2028 | -169.373 | -30.2756 | 45.0785 | -32.8427 | 35.2758 | -26.8634 | 69.1138 | -30.47 | -123.1064 | -35.6947 | 77.3425 | -34.9171 | -69.4127 | -29.021 | 85.6425 | -50.6809 | -56.0462 | -53.7276 | -53.1848 | -58.5364 | -68.5306 | -50.5932 | -68.4468 | -52.5227 | -52.5463 | -58.6713 | -70.7397 | -47.5424 | 73 | -61.3725 | -57.5318 | -57.6759 | -58.4155 | -61.6769 | -58.223 | -67.5744 | -57.4265 | 73 | -66.0413 | -50.1172 | -50.7793 | -56.1893 | -66.1835 | -48.1269 | -66.0997 | -50.0564 | -50.8338 | -56.0701 | -66.1796 | -48.2422 | -53.6407 | -51.3221 | -50.1408 | -56.3242 | -68.3926 | -45.0761 | -53.6991 | -51.2613 | -50.1953 | -56.205 | -68.3887 | -45.1914
74 | -2.4176 | 0 | -2.3694 | 0 | -2.4861 | 0 | -2.369 | 0 | -68.841 | -109.1237 | -62.9364 | -143.2679 | -67.961 | 107.0154 | -59.7599 | -30.2111 | -65.5227 | -92.4155 | -61.8934 | -65.0365 | -65.7255 | -98.8674 | -64.4404 | 57.4729 | -62.2474 | 123.9204 | -68.3707 | -27.0311 | -59.0844 | -147.3228 | -68.7369 | 62.0227 | -35.7744 | 135.9761 | -31.5236 | 53.9601 | -30.2646 | 3.3863 | -26.407 | 55.7284 | -34.503 | -134.7246 | -34.8859 | 38.1648 | -32.6874 | -77.9799 | -27.0932 | 67.9601 | -51.3634 | -55.3004 | -53.0443 | -53.5118 | -57.336 | -73.8316 | -51.2053 | -66.5135 | -51.6402 | -53.0491 | -57.3889 | -68.2986 | -48.3981 | 74 | -60.9741 | -58.3333 | -56.552 | -59.638 | -59.1246 | -57.831 | -61.945 | -57.0675 | 74 | -64.0959 | -49.2226 | -51.0942 | -54.9666 | -71.4622 | -48.7192 | -64.1441 | -49.1541 | -51.1428 | -54.8499 | -71.4626 | -48.8363 | -52.8828 | -50.6267 | -50.6315 | -55.0195 | -65.9292 | -45.912 | -52.931 | -50.5582 | -50.6801 | -54.9028 | -65.9296 | -46.0291
75 | -2.4185 | 0 | -2.3805 | 0 | -2.5103 | 0 | -2.3684 | 0 | -75.5562 | -163.0918 | -60.9272 | -169.9708 | -82.4424 | -24.4062 | -58.921 | -34.821 | -68.591 | -108.8598 | -60.4549 | -74.7667 | -66.1888 | -122.1269 | -60.6864 | 49.1136 | -62.1955 | 103.662 | -61.785 | -60.2668 | -60.8043 | -165.4745 | -65.4612 | 24.2561 | -36.0288 | 67.4379 | -30.15 | 62.1628 | -29.9907 | -24.4842 | -26.1267 | 41.0283 | -40.8441 | -127.3575 | -34.1549 | 2.2125 | -32.2232 | -96.9375 | -26.0205 | 52.6068 | -51.6908 | -54.7034 | -52.7288 | -53.4643 | -56.8276 | -69.7777 | -51.5562 | -65.7603 | -51.4771 | -53.107 | -56.8687 | -64.1978 | -49.7151 | 75 | -60.7506 | -58.3918 | -55.2428 | -59.8106 | -57.7019 | -57.6085 | -57.4445 | -57.6485 | 75 | -63.3418 | -49.0586 | -51.0458 | -54.4471 | -67.3972 | -49.0459 | -63.3798 | -48.9668 | -51.0959 | -54.3173 | -67.4093 | -49.1878 | -52.2849 | -50.3103 | -50.6885 | -54.4882 | -61.8173 | -47.2048 | -52.3229 | -50.2185 | -50.7386 | -54.3584 | -61.8294 | -47.3467
76 | -2.442 | 0 | -2.3918 | 0 | -2.5157 | 0 | -2.3852 | 0 | -76.711 | 61.9525 | -60.8416 | 163.88 | -68.8152 | -119.4021 | -58.5595 | -44.7139 | -72.4544 | -130.6397 | -59.821 | -91.6485 | -67.7173 | -135.3568 | -58.2869 | 32.6521 | -62.7766 | 96.855 | -58.6915 | -89.0486 | -63.3897 | -174.4694 | -64.1106 | -13.7936 | -34.2018 | 18.0534 | -28.169 | 56.2314 | -31.4634 | -51.6395 | -26.1556 | 25.1598 | -42.985 | -86.0413 | -33.9 | -32.2839 | -33.3154 | -121.2765 | -25.4319 | 39.0399 | -51.6436 | -54.2011 | -52.6821 | -53.0186 | -56.71 | -64.2206 | -51.5793 | -65.8243 | -51.5944 | -52.7317 | -56.7746 | -61.2735 | -50.7204 | 76 | -60.1032 | -58.3225 | -54.8689 | -59.1 | -56.6147 | -57.0357 | -54.917 | -58.6204 | 76 | -63.3823 | -49.1524 | -50.5766 | -54.3182 | -61.8288 | -49.0636 | -63.4325 | -49.0787 | -50.6334 | -54.1943 | -61.8354 | -49.1941 | -51.7591 | -50.2401 | -50.2897 | -54.3828 | -58.8817 | -48.2047 | -51.8093 | -50.1664 | -50.3465 | -54.2589 | -58.8883 | -48.3352
77 | -2.4644 | 0 | -2.4117 | 0 | -2.5238 | 0 | -2.4203 | 0 | -69.1632 | 6.1985 | -61.7702 | 141.7763 | -64.3572 | -147.7796 | -59.1702 | -54.6914 | -80.4911 | -171.7346 | -60.1288 | -114.7653 | -69.2293 | -138.362 | -57.2462 | 12.912 | -62.4174 | 81.8964 | -57.4225 | -117.3566 | -66.272 | -169.1458 | -64.1706 | -49.8582 | -33.53 | -14.1652 | -26.9585 | 43.229 | -35.4995 | -78.4853 | -26.5604 | 6.8417 | -42.0452 | -72.8009 | -33.9704 | -68.3316 | -36.3353 | -148.6447 | -25.1986 | 26.9589 | -51.4056 | -53.9807 | -52.5814 | -52.3645 | -56.8587 | -60.823 | -51.3941 | -66.7267 | -51.7164 | -52.0796 | -56.9214 | -59.3379 | -50.1537 | 77 | -59.3811 | -58.7266 | -55.4568 | -58.7083 | -55.8874 | -56.6441 | -53.8951 | -59.2378 | 77 | -64.2623 | -49.252 | -49.9001 | -54.447 | -58.4113 | -48.8703 | -64.315 | -49.1926 | -49.9442 | -54.3349 | -58.4027 | -48.9738 | -51.5163 | -50.117 | -49.6152 | -54.5097 | -56.9262 | -47.6299 | -51.569 | -50.0576 | -49.6593 | -54.3976 | -56.9176 | -47.7334
78 | -2.4818 | 0 | -2.4237 | 0 | -2.5453 | 0 | -2.4324 | 0 | -65.692 | -30.271 | -62.7156 | 120.9196 | -63.0812 | -165.8358 | -60.0634 | -57.6419 | -80.3924 | 57.5341 | -62.8165 | -135.938 | -69.3954 | -133.8831 | -57.6293 | -5.8525 | -62.1857 | 61.1856 | -57.7145 | -143.9785 | -66.5792 | -150.4084 | -66.9271 | -83.4965 | -34.6311 | -36.4901 | -26.7037 | 27.2354 | -46.6178 | -119.3722 | -27.5607 | -13.3353 | -43.7923 | -66.4323 | -34.2586 | -108.0211 | -42.061 | 179.9776 | -25.2925 | 15.3439 | -51.0093 | -54.2364 | -52.3585 | -51.7515 | -57.273 | -59.0038 | -51.0155 | -68.1346 | -51.8333 | -51.4295 | -57.3201 | -58.5004 | -48.9935 | 78 | -58.8717 | -58.9815 | -56.8964 | -59.8976 | -56.1161 | -56.9307 | -54.411 | -59.8831 | 78 | -65.6528 | -49.3515 | -49.2697 | -54.8493 | -56.5801 | -48.4702 | -65.7109 | -49.288 | -49.3191 | -54.7277 | -56.5714 | -48.5831 | -51.7546 | -49.8767 | -48.9477 | -54.8964 | -56.0767 | -46.4482 | -51.8127 | -49.8132 | -48.9971 | -54.7748 | -56.068 | -46.5611
79 | -2.4866 | 0 | -2.446 | 0 | -2.548 | 0 | -2.4429 | 0 | -64.4285 | -63.8001 | -63.9232 | 91.1189 | -61.8522 | 178.4137 | -59.685 | -59.1885 | -71.714 | 12.4008 | -68.5937 | -136.0371 | -68.3495 | -135.3508 | -59.1225 | -18.8032 | -62.9753 | 31.6269 | -59.5188 | -166.2417 | -64.6598 | -142.4274 | -72.2577 | -87.6685 | -37.8135 | -43.4894 | -27.4592 | 11.7686 | -41.2068 | 75.3536 | -29.408 | -35.5715 | -44.895 | -27.6192 | -34.3647 | -150.5092 | -57.2105 | 142.0103 | -25.7109 | 4.2185 | -50.6273 | -54.7879 | -52.1719 | -51.6156 | -57.9515 | -58.6199 | -50.6101 | -69.1964 | -52.0491 | -51.1413 | -57.9616 | -58.9308 | -48.1312 | 79 | -58.4811 | -58.2295 | -57.9084 | -60.663 | -57.2719 | -57.9442 | -56.1969 | -60.4311 | 79 | -66.7098 | -49.5625 | -49.129 | -55.5055 | -56.1739 | -48.0621 | -66.7504 | -49.5011 | -49.1727 | -55.4035 | -56.177 | -48.1672 | -52.3013 | -49.6853 | -48.6547 | -55.5156 | -56.4848 | -45.5832 | -52.3419 | -49.6239 | -48.6984 | -55.4136 | -56.4879 | -45.6883
80 | -2.5162 | 0 | -2.443 | 0 | -2.5703 | 0 | -2.4662 | 0 | -64.7551 | -92.1219 | -67.0754 | 45.5065 | -61.0072 | 162.2643 | -59.5098 | -69.8363 | -67.3806 | -25.0505 | -68.943 | -94.989 | -68.1306 | -142.9475 | -61.0671 | -22.6384 | -65.2775 | -4.6503 | -62.5753 | 179.942 | -62.7298 | -142.0624 | -72.0183 | -61.6703 | -39.8591 | -17.1645 | -29.2764 | -0.5003 | -34.3061 | 47.7768 | -32.3757 | -62.0681 | -39.561 | -4.4802 | -34.1857 | 166.6467 | -50.8596 | -75.8441 | -26.5015 | -6.1085 | -50.3195 | -55.0679 | -52.3575 | -52.0813 | -58.5266 | -59.8062 | -50.2203 | -69.6093 | -52.4693 | -51.361 | -58.6266 | -61.0468 | -47.5638 | 80 | -58.7822 | -57.8599 | -58.4069 | -59.5729 | -59.0918 | -59.0664 | -58.546 | -60.4922 | 80 | -67.0931 | -49.9531 | -49.5651 | -56.0836 | -57.3632 | -47.65 | -67.1663 | -49.899 | -49.6151 | -55.9563 | -57.34 | -47.7541 | -52.5517 | -49.8413 | -48.8448 | -56.1836 | -58.6038 | -44.9935 | -52.6249 | -49.7872 | -48.8948 | -56.0563 | -58.5806 | -45.0976
81 | -2.5083 | 0 | -2.478 | 0 | -2.5935 | 0 | -2.4834 | 0 | -65.5436 | -111.2658 | -71.7942 | -31.4802 | -60.2782 | 148.4595 | -61.0359 | -79.9372 | -65.3737 | -67.5606 | -65.4027 | -91.6759 | -69.0769 | -137.8457 | -62.8492 | -17.1554 | -71.191 | -66.5166 | -67.0581 | -179.5334 | -60.2803 | -147.121 | -70.3877 | -54.0195 | -35.9574 | 0.2137 | -31.9786 | -3.7927 | -31.624 | 26.4989 | -37.2457 | -100.1437 | -35.4594 | -14.1077 | -33.9637 | 124.4211 | -44.3272 | -125.8882 | -27.6677 | -14.9505 | -50.1201 | -54.4309 | -53.041 | -53.0342 | -58.7256 | -62.8176 | -49.9038 | -69.6794 | -52.813 | -52.0171 | -59.2163 | -65.6091 | -47.4232 | 81 | -58.9173 | -58.6743 | -59.4227 | -58.1921 | -61.4352 | -59.003 | -60.93 | -59.5665 | 81 | -67.1711 | -50.3047 | -50.5259 | -56.2476 | -60.3396 | -47.3103 | -67.2014 | -50.2195 | -50.5508 | -56.1321 | -60.3342 | -47.4204 | -51.9226 | -50.5327 | -49.5088 | -56.7383 | -63.1311 | -44.8297 | -51.9529 | -50.4475 | -49.5337 | -56.6228 | -63.1257 | -44.9398
82 | -2.5316 | 0 | -2.4874 | 0 | -2.6256 | 0 | -2.4844 | 0 | -64.0521 | -133.1154 | -69.5746 | -119.5936 | -59.6628 | 123.0805 | -62.6072 | -70.8911 | -66.5645 | -114.1749 | -62.8146 | -101.8066 | -64.7378 | -124.7031 | -62.6447 | -2.1655 | -68.3883 | 179.8794 | -70.0486 | -133.1122 | -58.3241 | -164.8473 | -68.9638 | -53.16 | -32.8866 | -7.191 | -33.9176 | 10.6526 | -30.897 | 9.2551 | -41.2538 | -177.562 | -34.022 | -32.5095 | -34.0424 | 84.2119 | -39.7232 | 176.8163 | -29.1936 | -21.8849 | -50.4224 | -53.3222 | -53.572 | -54.2193 | -57.7701 | -68.9043 | -49.8664 | -68.9107 | -52.0004 | -52.9796 | -58.5187 | -75.9654 | -48.0103 | 82 | -58.0014 | -59.3458 | -59.2739 | -57.3889 | -59.8938 | -57.1994 | -61.1365 | -57.5875 | 82 | -66.3791 | -49.4688 | -51.6877 | -55.2827 | -66.4169 | -47.2408 | -66.4233 | -49.3748 | -51.7349 | -55.1445 | -66.4199 | -47.382 | -50.7906 | -51.0404 | -50.448 | -56.0313 | -73.478 | -45.3847 | -50.8348 | -50.9464 | -50.4952 | -55.8931 | -73.481 | -45.5259
83 | -2.5502 | 0 | -2.4939 | 0 | -2.6597 | 0 | -2.4958 | 0 | -63.788 | 179.2449 | -65.8912 | -178.5645 | -63.7505 | 90.7729 | -60.5263 | -65.9803 | -69.8096 | -146.8968 | -62.4452 | -105.2065 | -61.3775 | -153.0823 | -60.7586 | 5.0344 | -65.832 | 114.1409 | -62.6976 | -112.1294 | -58.9634 | 174.6116 | -65.239 | -45.0369 | -31.5458 | -18.5696 | -32.2118 | 25.8274 | -31.3201 | -0.7289 | -36.8451 | 114.1793 | -34.8041 | -52.9755 | -34.8712 | 42.2273 | -35.5307 | 132.2004 | -31.0864 | -24.6065 | -51.2061 | -52.5711 | -52.7312 | -55.1788 | -56.2843 | -74.6883 | -50.5174 | -66.4527 | -50.976 | -54.0096 | -56.8689 | -69.9683 | -49.7127 | 83 | -59.597 | -58.5128 | -57.6626 | -59.6034 | -57.3778 | -55.96 | -57.7563 | -57.3756 | 83 | -63.9025 | -48.4258 | -52.6286 | -53.7904 | -72.1944 | -47.8577 | -63.9588 | -48.3163 | -52.683 | -53.6246 | -72.1925 | -48.0216 | -50.0209 | -50.181 | -51.4594 | -54.375 | -67.4744 | -47.053 | -50.0772 | -50.0715 | -51.5138 | -54.2092 | -67.4725 | -47.2169
84 | -2.5667 | 0 | -2.4906 | 0 | -2.6848 | 0 | -2.5213 | 0 | -65.697 | 123.338 | -65.2794 | 127.2203 | -72.4177 | 108.7637 | -58.7042 | -79.7086 | -70.3715 | -178.4319 | -59.8275 | -114.8718 | -61.6832 | -179.8942 | -58.1528 | 2.9803 | -64.6608 | 89.9584 | -58.0324 | -128.9192 | -60.5066 | 164.7452 | -60.9306 | -60.3223 | -31.3608 | -29.284 | -29.6752 | 22.0393 | -31.769 | -1.6858 | -33.5543 | 79.3939 | -39.3135 | -71.3905 | -36.1429 | -8.2335 | -32.3497 | 94.0053 | -32.9847 | -20.6711 | -51.2183 | -51.8774 | -52.4897 | -54.98 | -55.8511 | -65.4009 | -50.7601 | -63.0442 | -50.9338 | -54.2874 | -56.3226 | -62.4114 | -52.539 | 84 | -62.0539 | -57.6731 | -55.711 | -59.2459 | -55.9334 | -55.0283 | -54.0779 | -56.906 | 84 | -60.4775 | -48.3671 | -52.4133 | -53.3605 | -62.9103 | -48.0753 | -60.5536 | -48.249 | -52.4587 | -53.1663 | -62.8796 | -48.2388 | -49.3107 | -49.923 | -51.7207 | -53.832 | -59.9208 | -49.8542 | -49.3868 | -49.8049 | -51.7661 | -53.6378 | -59.8901 | -50.0177
85 | -2.5717 | 0 | -2.5314 | 0 | -2.7046 | 0 | -2.5126 | 0 | -66.6486 | 56.4667 | -67.1656 | 71.7434 | -68.4227 | 147.4657 | -58.6677 | -101.6078 | -69.5738 | 143.844 | -57.7228 | -138.6494 | -63.6003 | 162.5576 | -56.1498 | -10.4643 | -62.6464 | 68.6064 | -55.5832 | -153.3973 | -61.6371 | 164.5288 | -58.4036 | -89.3048 | -32.1533 | -31.0853 | -28.1849 | 9.8167 | -30.8589 | 2.0275 | -31.9522 | 54.6276 | -54.1685 | 32.145 | -36.6926 | -70.4116 | -30.1557 | 59.9352 | -34.1501 | -14.0991 | -50.8567 | -51.2878 | -52.4869 | -53.6458 | -55.845 | -60.069 | -50.6017 | -60.2398 | -51.0092 | -53.5197 | -56.3048 | -58.2632 | -53.7546 | 85 | -62.5791 | -57.7322 | -54.894 | -57.1143 | -54.6764 | -54.1035 | -51.781 | -55.7286 | 85 | -57.6681 | -48.4375 | -51.0741 | -53.3136 | -57.5376 | -47.8971 | -57.7084 | -48.3046 | -51.1332 | -53.1404 | -57.5564 | -48.0891 | -48.7161 | -49.9152 | -50.948 | -53.7734 | -55.7318 | -51.05 | -48.7564 | -49.7823 | -51.0071 | -53.6002 | -55.7506 | -51.242
86 | -2.6007 | 0 | -2.5642 | 0 | -2.6982 | 0 | -2.5397 | 0 | -64.9319 | -9.3748 | -70.1618 | 14.7672 | -66.9108 | 146.8282 | -61.1425 | -121.7858 | -67.7682 | 104.3516 | -57.6911 | -169.2321 | -66.4737 | 159.5915 | -55.8513 | -28.4206 | -61.1507 | 42.0121 | -54.9756 | 179.4335 | -61.8791 | 164.9867 | -58.1016 | -126.2764 | -31.7312 | -22.7649 | -27.6867 | -5.823 | -28.9832 | -3.2566 | -31.8596 | 34.902 | -35.4859 | 48.3518 | -34.2416 | -128.1911 | -29.1767 | 24.6713 | -34.7799 | -9.9912 | -50.3504 | -51.211 | -52.258 | -51.9481 | -56.2176 | -57.0664 | -50.1541 | -58.6435 | -50.9796 | -52.1423 | -56.5603 | -55.8935 | -52.0805 | 86 | -62.0674 | -59.0063 | -55.9062 | -56.8349 | -54.4468 | -53.9211 | -51.3503 | -55.2808 | 86 | -56.0428 | -48.3789 | -49.3474 | -53.6534 | -54.5022 | -47.4559 | -56.0793 | -48.2814 | -49.4084 | -53.5194 | -54.5267 | -47.6144 | -48.6103 | -49.6573 | -49.5416 | -53.9961 | -53.3293 | -49.3823 | -48.6468 | -49.5598 | -49.6026 | -53.8621 | -53.3538 | -49.5408
87 | -2.6166 | 0 | -2.5805 | 0 | -2.7084 | 0 | -2.5555 | 0 | -62.6932 | -61.3355 | -70.4473 | -26.5033 | -65.684 | 145.7069 | -64.9236 | -118.5623 | -65.6563 | 68.1366 | -60.3432 | 158.9003 | -67.0942 | 176.9043 | -57.2823 | -40.5265 | -61.0538 | 8.8435 | -56.3428 | 154.5081 | -61.2723 | 160.5695 | -61.4334 | -157.6985 | -29.4329 | -18.7152 | -28.2589 | -21.2755 | -27.8722 | -15.2488 | -33.1524 | 23.5365 | -29.4522 | 26.1159 | -31.723 | -172.588 | -29.2943 | -11.2178 | -35.7567 | -1.4233 | -49.812 | -51.9242 | -51.7777 | -50.8706 | -57.0112 | -55.8188 | -49.5922 | -58.7006 | -50.972 | -51.1117 | -57.0844 | -55.0678 | -50.267 | 87 | -60.4661 | -59.4631 | -58.7417 | -58.3385 | -55.4523 | -54.8644 | -53.0893 | -56.4792 | 87 | -56.084 | -48.3554 | -48.254 | -54.4307 | -53.2383 | -46.8838 | -56.1201 | -48.2636 | -48.3151 | -54.3028 | -53.2633 | -47.0367 | -49.3076 | -49.1611 | -48.4951 | -54.5039 | -52.4873 | -47.5586 | -49.3437 | -49.0693 | -48.5562 | -54.376 | -52.5123 | -47.7115
88 | -2.6358 | 0 | -2.594 | 0 | -2.7166 | 0 | -2.5682 | 0 | -61.3215 | -102.9005 | -66.1907 | -60.3861 | -63.3393 | 144.5755 | -64.4303 | -110.6631 | -64.2246 | 27.7752 | -66.0794 | 141.1725 | -64.4305 | -178.512 | -58.8275 | -37.8349 | -61.8251 | -25.446 | -59.4986 | 140.2439 | -61.6725 | 153.3352 | -70.2389 | -156.4633 | -26.7914 | -26.7035 | -29.6723 | -34.3101 | -27.5335 | -29.0775 | -34.5416 | 25.9561 | -26.4457 | 3.1471 | -29.7512 | 151.0099 | -30.859 | -52.3788 | -36.5222 | 18.4109 | -49.4817 | -53.2019 | -51.4532 | -50.8215 | -57.8801 | -55.9441 | -49.1917 | -60.8142 | -51.1749 | -50.8049 | -57.6213 | -55.6189 | -49.2638 | 88 | -58.4116 | -58.3084 | -60.7181 | -59.6329 | -56.3314 | -56.6488 | -55.974 | -58.4408 | 88 | -58.1784 | -48.5391 | -48.1857 | -55.2861 | -53.3501 | -46.4751 | -58.2202 | -48.4583 | -48.2533 | -55.1635 | -53.3759 | -46.6235 | -50.5661 | -48.8174 | -48.1691 | -55.0273 | -53.0249 | -46.5472 | -50.6079 | -48.7366 | -48.2367 | -54.9047 | -53.0507 | -46.6956
89 | -2.684 | 0 | -2.5913 | 0 | -2.7194 | 0 | -2.6056 | 0 | -60.6867 | -137.045 | -62.0045 | -99.725 | -62.3837 | 134.6768 | -64.9476 | -127.9473 | -64.0475 | -14.4473 | -70.3603 | 166.5965 | -62.3706 | 172.2862 | -58.3711 | -30.4356 | -62.9949 | -64.3624 | -62.8886 | 147.7672 | -62.8213 | 153.8107 | -67.2849 | -102.4703 | -25.0293 | -41.8964 | -31.9164 | -40.6813 | -27.9232 | -41.9076 | -33.7178 | 40.0064 | -24.8534 | -21.5568 | -28.8268 | 118.5101 | -33.2982 | -104.343 | -33.8283 | 35.5791 | -49.3032 | -54.2945 | -51.513 | -51.5727 | -58.393 | -57.2242 | -48.9312 | -66.0748 | -51.6332 | -51.1187 | -58.021 | -57.4772 | -48.5286 | 89 | -56.8578 | -58.0477 | -59.8196 | -59.733 | -55.9581 | -57.9161 | -56.6632 | -59.169 | 89 | -63.3908 | -48.9492 | -48.8887 | -55.8017 | -54.6329 | -46.2118 | -63.4835 | -48.9138 | -48.9671 | -55.6736 | -54.6186 | -46.3256 | -51.6105 | -48.829 | -48.4347 | -55.4297 | -54.8859 | -45.8092 | -51.7032 | -48.7936 | -48.5131 | -55.3016 | -54.8716 | -45.923
90 | -2.7154 | 0 | -2.5995 | 0 | -2.7515 | 0 | -2.6149 | 0 | -60.3416 | -164.8333 | -59.7019 | -141.2163 | -61.6718 | 127.7183 | -71.3816 | -146.9306 | -65.2746 | -63.912 | -70.0259 | 176.2704 | -61.4156 | 160.7749 | -57.0531 | -29.055 | -64.2006 | -116.8735 | -62.8732 | 168.7548 | -62.3292 | 161.3711 | -63.3176 | -110.3129 | -24.1899 | -60.248 | -33.9368 | -34.5173 | -28.8182 | -51.8661 | -30.4869 | 41.6635 | -24.4547 | -46.7695 | -29.0075 | 87.5028 | -34.2288 | -172.036 | -30.2167 | 35.6174 | -49.2137 | -54.2328 | -51.9975 | -52.8934 | -58.6668 | -59.7836 | -48.8573 | -91.2476 | -52.231 | -51.8417 | -58.4628 | -61.0132 | -48.4555 | 90 | -55.7253 | -58.8808 | -59.0546 | -59.6789 | -55.1244 | -57.3927 | -55.2975 | -58.444 | 90 | -88.5322 | -49.5156 | -50.178 | -56.0673 | -57.1841 | -46.1058 | -88.6481 | -49.4795 | -50.2785 | -55.9153 | -57.1687 | -46.2424 | -51.5174 | -49.2821 | -49.1263 | -55.8633 | -58.4137 | -45.704 | -51.6333 | -49.246 | -49.2268 | -55.7113 | -58.3983 | -45.8406
91 | -2.7126 | 0 | -2.6115 | 0 | -2.763 | 0 | -2.6232 | 0 | -59.2822 | 171.2527 | -59.414 | 177.9525 | -60.1297 | 112.358 | -71.9101 | -32.0897 | -67.9418 | -134.5784 | -71.0678 | -172.1819 | -60.5423 | 156.3473 | -55.4116 | -31.87 | -64.3738 | -178.2034 | -60.5167 | 179.1098 | -60.2301 | 159.4794 | -62.256 | -124.5035 | -24.4486 | -79.4262 | -33.8833 | -22.1495 | -30.1682 | -56.1243 | -27.5197 | 30.7318 | -25.3162 | -72.6367 | -30.5509 | 56.7323 | -31.8722 | 127.9753 | -27.4472 | 24.6525 | -49.2959 | -52.7755 | -52.7955 | -54.7647 | -58.3624 | -64.631 | -48.8576 | -66.2356 | -52.3572 | -52.842 | -58.6271 | -68.3645 | -49.8188 | 91 | -54.8218 | -58.524 | -58.904 | -59.1743 | -53.8466 | -55.6562 | -53.6061 | -57.1931 | 91 | -63.523 | -49.6446 | -52.0521 | -55.7509 | -62.0195 | -46.0946 | -63.6241 | -49.5942 | -52.1415 | -55.5994 | -62.0078 | -46.2344 | -50.0629 | -50.0829 | -50.1294 | -56.0156 | -65.753 | -47.0558 | -50.164 | -50.0325 | -50.2188 | -55.8641 | -65.7413 | -47.1956
92 | -2.7219 | 0 | -2.6268 | 0 | -2.8013 | 0 | -2.6364 | 0 | -57.5833 | 134.78 | -60.6737 | 139.5526 | -61.849 | 85.9426 | -62.8321 | -60.527 | -70.3763 | 144.3197 | -68.3837 | -155.0218 | -57.7031 | 140.7258 | -53.9599 | -40.628 | -64.258 | 112.0869 | -56.959 | 177.9723 | -60.084 | 143.2191 | -61.5405 | -128.3338 | -25.8939 | -96.9663 | -32.3507 | -20.0963 | -30.896 | -53.2243 | -25.5028 | 13.4365 | -27.9584 | -98.9795 | -34.4078 | 25.6068 | -29.1386 | 84.7811 | -25.572 | 8.4568 | -50.2174 | -51.1458 | -52.6407 | -56.6627 | -56.5924 | -72.9466 | -49.6971 | -60.7349 | -51.3079 | -54.4002 | -56.9861 | -76.4106 | -53.5839 | 92 | -54.8757 | -56.2761 | -58.1749 | -60.5058 | -52.1537 | -53.2864 | -51.7176 | -56.8669 | 92 | -58.013 | -48.586 | -53.9408 | -53.9656 | -70.3198 | -46.8958 | -58.1081 | -48.5066 | -54.0263 | -53.7911 | -70.3102 | -47.0607 | -48.4239 | -49.9188 | -51.6783 | -54.3593 | -73.7838 | -50.7826 | -48.519 | -49.8394 | -51.7638 | -54.1848 | -73.7742 | -50.9475
93 | -2.7364 | 0 | -2.661 | 0 | -2.8573 | 0 | -2.67 | 0 | -58.0807 | 90.9288 | -64.5191 | 93.8865 | -63.9996 | 87.3449 | -61.5364 | -95.5694 | -68.4906 | 103.2945 | -63.0111 | -166.9004 | -57.4088 | 110.9498 | -52.6361 | -51.7554 | -64.1116 | 71.6407 | -53.8415 | 160.8483 | -61.0343 | 141.7948 | -59.0579 | -134.6204 | -28.9609 | -106.9118 | -31.0212 | -27.0018 | -29.8441 | -49.4976 | -24.1453 | -6.813 | -34.1 | -127.142 | -43.9581 | -34.3409 | -27.6593 | 48.5933 | -24.5535 | -11.6457 | -50.65 | -49.9792 | -52.5497 | -55.7203 | -55.8024 | -64.7956 | -50.3055 | -57.2284 | -51.0294 | -54.9149 | -56.1844 | -62.1581 | -60.98 | 93 | -56.3693 | -56.1991 | -58.0821 | -59.8313 | -51.1611 | -51.7178 | -49.6572 | -56.1648 | 93 | -54.492 | -48.293 | -52.9839 | -53.1414 | -62.1346 | -47.4482 | -54.5674 | -48.1721 | -53.0503 | -52.9451 | -62.1256 | -47.6355 | -47.2428 | -49.8133 | -52.1785 | -53.5234 | -59.4971 | -58.1227 | -47.3182 | -49.6924 | -52.2449 | -53.3271 | -59.4881 | -58.31
94 | -2.7428 | 0 | -2.6858 | 0 | -2.8786 | 0 | -2.7075 | 0 | -59.9251 | 45.468 | -75.966 | 36.2421 | -64.173 | 81.8816 | -65.5503 | -123.2636 | -65.5846 | 76.6798 | -59.3193 | 158.3255 | -59.2721 | 84.7646 | -51.8917 | -69.4836 | -63.4957 | 35.4107 | -52.1075 | 135.44 | -60.1023 | 142.5435 | -57.3792 | -159.6572 | -33.1896 | -92.2215 | -30.7053 | -37.2008 | -28.028 | -56.0905 | -23.6331 | -27.942 | -46.4016 | 51.5766 | -38.4087 | -172.1585 | -27.1555 | 14.1205 | -24.3312 | -34.4733 | -50.3936 | -49.2348 | -52.6733 | -52.8272 | -55.6865 | -58.7739 | -50.26 | -55.277 | -50.942 | -53.3186 | -56.1858 | -56.8864 | -64.4467 | 94 | -58.461 | -58.0344 | -58.3162 | -57.3787 | -50.916 | -50.8016 | -48.4005 | -54.8781 | 94 | -52.5342 | -48.1992 | -50.0844 | -53.0007 | -56.0881 | -47.3814 | -52.5912 | -48.0634 | -50.1197 | -52.8079 | -56.0664 | -47.5525 | -46.492 | -49.9305 | -50.5758 | -53.5 | -54.2006 | -61.5681 | -46.549 | -49.7947 | -50.6111 | -53.3072 | -54.1789 | -61.7392
95 | -2.7691 | 0 | -2.709 | 0 | -2.8826 | 0 | -2.741 | 0 | -63.0021 | -7.4255 | -80.3479 | -152.1494 | -67.2988 | 77.5562 | -70.1762 | -62.5185 | -62.6689 | 53.0988 | -58.5437 | 109.998 | -63.382 | 64.7385 | -52.7875 | -89.3044 | -63.631 | -3.2665 | -52.0623 | 105.8146 | -58.8433 | 133.7894 | -58.4649 | 164.032 | -30.689 | -57.7435 | -31.0489 | -45.9756 | -26.7649 | -71.5798 | -23.7725 | -49.605 | -30.5923 | 8.6476 | -31.8146 | 147.5898 | -27.7164 | -22.2037 | -24.7993 | -59.6793 | -49.9128 | -49.3326 | -52.3948 | -50.5925 | -55.9909 | -55.813 | -49.9199 | -55.0311 | -50.816 | -51.4121 | -56.5527 | -54.4334 | -58.0758 | 95 | -61.5712 | -59.4391 | -58.2285 | -56.7253 | -52.1073 | -50.9779 | -48.8918 | -54.9996 | 95 | -52.262 | -48.0469 | -47.8234 | -53.2819 | -53.104 | -47.0373 | -52.3221 | -47.9334 | -47.8515 | -53.1083 | -53.072 | -47.1789 | -46.5635 | -49.6257 | -48.643 | -53.8437 | -51.7244 | -55.1932 | -46.6236 | -49.5122 | -48.6711 | -53.6701 | -51.6924 | -55.3348
96 | -2.7902 | 0 | -2.7106 | 0 | -2.8824 | 0 | -2.7517 | 0 | -65.8152 | -75.3488 | -80.6427 | -92.9253 | -68.0323 | 108.7419 | -61.6972 | -65.9516 | -60.7086 | 25.8488 | -60.422 | 62.3602 | -71.2069 | 73.1973 | -55.2525 | -100.1678 | -63.9275 | -39.5099 | -53.8989 | 77.2335 | -58.6446 | 119.0388 | -64.6224 | 128.8691 | -26.1328 | -60.7135 | -31.8063 | -50.2484 | -26.7404 | -90.6413 | -24.5591 | -69.8712 | -25.868 | -18.8755 | -28.5163 | 118.0756 | -29.7063 | -63.0479 | -26.2276 | -88.7907 | -49.5629 | -50.2503 | -51.9472 | -49.6801 | -56.4535 | -54.6605 | -49.5817 | -56.3629 | -50.8371 | -50.3903 | -56.9294 | -53.7379 | -54.8881 | 96 | -63.6851 | -57.4761 | -57.9791 | -57.1802 | -54.604 | -52.5831 | -51.3057 | -56.7448 | 96 | -53.5727 | -48.0469 | -46.8899 | -53.7429 | -51.9499 | -46.6993 | -53.6523 | -47.9547 | -46.9284 | -53.5711 | -51.9088 | -46.83 | -47.4601 | -49.157 | -47.6001 | -54.2188 | -51.0273 | -52.0057 | -47.5397 | -49.0648 | -47.6386 | -54.047 | -50.9862 | -52.1364
97 | -2.8306 | 0 | -2.7338 | 0 | -2.8712 | 0 | -2.7596 | 0 | -64.8404 | -143.8294 | -66.2563 | -103.6501 | -65.0309 | 114.4821 | -59.6236 | -93.799 | -60.0756 | -4.6444 | -63.6664 | 21.0977 | -69.0693 | 141.376 | -57.4738 | -95.2432 | -65.2347 | -95.0653 | -57.7081 | 52.9032 | -59.6521 | 104.6453 | -72.2812 | -80.5354 | -23.3002 | -77.1829 | -31.8267 | -49.7158 | -27.7461 | -108.1253 | -26.0007 | -87.9667 | -23.5559 | -45.9527 | -27.1258 | 89.5233 | -32.7606 | -115.3702 | -28.4966 | -124.1835 | -49.4298 | -51.5438 | -51.6906 | -49.7736 | -56.7697 | -54.579 | -49.4526 | -58.8673 | -51.0884 | -50.1909 | -57.0815 | -54.1876 | -53.4082 | 97 | -60.5609 | -56.1955 | -57.5517 | -57.628 | -56.5511 | -55.3725 | -54.506 | -58.4099 | 97 | -56.0367 | -48.2578 | -46.943 | -54.0359 | -51.8452 | -46.5814 | -56.1335 | -48.2172 | -47.014 | -53.8985 | -51.8194 | -46.693 | -48.7132 | -48.86 | -47.3603 | -54.3477 | -51.4538 | -50.537 | -48.81 | -48.8194 | -47.4313 | -54.2103 | -51.428 | -50.6486
98 | -2.8615 | 0 | -2.7304 | 0 | -2.8614 | 0 | -2.7659 | 0 | -62.2955 | 168.5586 | -60.6308 | -141.0619 | -63.4228 | 113.4076 | -60.776 | -115.9888 | -61.0324 | -36.4025 | -69.9692 | -15.7978 | -62.9342 | 140.0491 | -57.4376 | -85.8429 | -65.6404 | -143.7864 | -64.7594 | 39.8192 | -62.2133 | 96.5323 | -61.8253 | -122.2641 | -21.9075 | -97.1744 | -30.9415 | -49.8391 | -29.7329 | -118.9516 | -28.3181 | -101.2221 | -22.5497 | -72.4809 | -27.0384 | 60.7872 | -34.8733 | 175.6266 | -31.4515 | -172.0805 | -49.403 | -52.6043 | -51.6513 | -50.4616 | -56.9655 | -55.2059 | -49.4296 | -62.4239 | -51.4474 | -50.4609 | -57.0351 | -55.4278 | -53.1326 | 98 | -57.192 | -56.5477 | -57.4427 | -58.7166 | -55.8742 | -58.4049 | -55.536 | -58.1518 | 98 | -59.5624 | -48.5859 | -47.6001 | -54.2351 | -52.4755 | -46.5682 | -59.6935 | -48.586 | -47.6957 | -54.1041 | -52.44 | -46.6637 | -49.7428 | -48.7898 | -47.5994 | -54.3047 | -52.6974 | -50.2712 | -49.8739 | -48.7899 | -47.695 | -54.1737 | -52.6619 | -50.3667
99 | -2.859 | 0 | -2.7573 | 0 | -2.8879 | 0 | -2.7698 | 0 | -60.2039 | 133.5135 | -58.3341 | -179.5558 | -61.8595 | 107.9157 | -63.8386 | -118.1433 | -64.1236 | -70.8476 | -71.7884 | 19.9642 | -59.7374 | 124.6062 | -56.5794 | -83.6555 | -64.0439 | 169.7647 | -73.3282 | 117.9754 | -65.2666 | 106.1384 | -59.2212 | -152.5781 | -21.64 | -118.3044 | -29.7338 | -56.0564 | -31.9974 | -119.5101 | -31.0131 | -103.6977 | -22.7446 | -99.7124 | -28.3061 | 30.4316 | -32.9407 | 110.0665 | -32.0987 | 125.9569 | -49.4338 | -52.7596 | -51.7698 | -51.6565 | -57.2737 | -56.4315 | -49.4175 | -66.7277 | -51.8356 | -51.0855 | -57.0698 | -57.4972 | -53.6587 | 99 | -55.1238 | -57.5591 | -57.1064 | -59.5668 | -54.3716 | -58.5195 | -54.6331 | -57.2402 | 99 | -63.8687 | -48.9766 | -48.7975 | -54.5164 | -53.6742 | -46.5296 | -63.9704 | -48.9477 | -48.8867 | -54.3858 | -53.6617 | -46.6477 | -49.9006 | -48.9108 | -48.2265 | -54.3125 | -54.7399 | -50.7708 | -50.0023 | -48.8819 | -48.3157 | -54.1819 | -54.7274 | -50.8889
100 | -2.8514 | 0 | -2.7705 | 0 | -2.9324 | 0 | -2.7745 | 0 | -58.7698 | 103.5829 | -58.5622 | 140.082 | -60.5985 | 99.1251 | -63.1602 | -98.6709 | -72.3957 | -130.43 | -66.7672 | 7.2881 | -58.167 | 107.0171 | -55.5519 | -83.2377 | -61.9837 | 124.7955 | -63.4895 | 144.8055 | -64.501 | 131.3071 | -58.9486 | -173.492 | -22.4699 | -139.0458 | -28.6489 | -66.5664 | -32.3858 | -106.8069 | -31.9831 | -91.2853 | -24.1403 | -126.4285 | -31.1145 | -5.9495 | -30.8402 | 61.543 | -30.2568 | 71.3661 | -49.4391 | -51.7651 | -52.1138 | -53.3258 | -57.7399 | -58.562 | -49.3955 | -68.6511 | -52.203 | -52.0283 | -57.3212 | -60.9519 | -56.6209 | 100 | -54.4476 | -57.286 | -56.8069 | -59.4333 | -53.0598 | -56.3309 | -53.4615 | -56.4551 | 100 | -65.7997 | -49.3516 | -50.4744 | -54.9694 | -55.7915 | -46.4631 | -65.8806 | -49.2706 | -50.5513 | -54.8075 | -55.7875 | -46.621 | -48.9137 | -49.2624 | -49.1769 | -54.5507 | -58.1814 | -53.6885 | -48.9946 | -49.1814 | -49.2538 | -54.3888 | -58.1774 | -53.8464
101 | -2.878 | 0 | -2.8 | 0 | -2.9696 | 0 | -2.79 | 0 | -57.646 | 75.3467 | -62.2303 | 96.4908 | -59.0707 | 83.5758 | -59.9102 | -105.93 | -68.0024 | 84.5365 | -65.9633 | -28.5398 | -57.4578 | 91.6289 | -53.9157 | -87.6812 | -60.0585 | 86.0032 | -58.7702 | 135.7584 | -61.006 | 130.3985 | -59.6968 | 178.7137 | -24.5813 | -156.8962 | -28.0757 | -80.1965 | -30.0463 | -100.8833 | -30.0338 | -87.0452 | -27.1779 | -154.5575 | -35.3408 | -63.93 | -29.6353 | 20.8638 | -28.283 | 29.2536 | -49.5467 | -50.1148 | -52.7263 | -55.4842 | -57.6834 | -62.5679 | -49.4015 | -64.8563 | -52.2882 | -53.1984 | -57.4328 | -67.9969 | -63.7828 | 101 | -54.4898 | -55.3778 | -57.2756 | -57.8243 | -51.6486 | -54.0713 | -51.8985 | -55.4483 | 101 | -61.9783 | -49.4102 | -52.6062 | -54.8834 | -59.7679 | -46.4319 | -62.0563 | -49.3186 | -52.6942 | -54.7138 | -59.7779 | -46.6115 | -47.2368 | -49.8483 | -50.3204 | -54.6328 | -65.1969 | -60.8132 | -47.3148 | -49.7567 | -50.4084 | -54.4632 | -65.2069 | -60.9928
102 | -2.8827 | 0 | -2.8065 | 0 | -3.015 | 0 | -2.8062 | 0 | -56.9123 | 40.8269 | -74.8516 | 20.7467 | -59.5248 | 63.8703 | -59.4798 | -131.0118 | -62.0681 | 40.2359 | -69.2475 | -59.7658 | -56.7637 | 73.7867 | -52.68 | -100.4693 | -59.5721 | 41.0921 | -55.2051 | 116.7903 | -59.9265 | 118.7483 | -59.8742 | 174.4139 | -28.7939 | -164.8949 | -28.1394 | -93.3049 | -27.5028 | -106.9814 | -27.9736 | -95.5635 | -34.2141 | 173.3631 | -34.7124 | -147.8217 | -29.0317 | -17.8916 | -27.2265 | -5.8526 | -49.9283 | -48.6797 | -53.0279 | -55.4087 | -56.3619 | -69.8672 | -49.7245 | -60.683 | -51.6718 | -54.1581 | -56.4628 | -75.3314 | -66.8163 | 102 | -54.9698 | -54.2201 | -58.9317 | -57.3149 | -50.6522 | -52.1181 | -50.2499 | -55.0169 | 102 | -57.8003 | -48.7891 | -52.526 | -53.5554 | -67.0607 | -46.7095 | -57.8765 | -48.6568 | -52.6025 | -53.3469 | -67.061 | -46.9183 | -45.797 | -50.1452 | -51.2754 | -53.6563 | -72.5249 | -63.8013 | -45.8732 | -50.0129 | -51.3519 | -53.4478 | -72.5252 | -64.0101
103 | -2.886 | 0 | -2.8299 | 0 | -3.0531 | 0 | -2.8279 | 0 | -57.9937 | 0.6687 | -66.3834 | -132.3963 | -60.4595 | 53.2703 | -63.7507 | -145.5341 | -59.6195 | 14.6757 | -75.4208 | 8.2586 | -57.7994 | 52.0833 | -52.5641 | -117.2612 | -60.1972 | 0.9089 | -53.3868 | 87.7739 | -59.1683 | 113.9287 | -58.9651 | 154.3743 | -32.6575 | -131.3331 | -28.6542 | -105.3792 | -25.3797 | -121.4881 | -26.6668 | -112.9342 | -40.8342 | -3.2603 | -30.5722 | 159.5432 | -28.7069 | -57.6972 | -27.0833 | -37.6028 | -49.7407 | -47.9991 | -53.1131 | -52.4907 | -55.6079 | -65.0967 | -49.7948 | -57.3813 | -51.3196 | -53.3221 | -55.8729 | -61.9672 | -60.28 | 103 | -55.6595 | -55.0858 | -61.673 | -56.9468 | -50.885 | -51.2751 | -49.4329 | -54.6398 | 103 | -54.4953 | -48.4336 | -49.6047 | -52.778 | -62.2668 | -46.7417 | -54.5514 | -48.2665 | -49.6628 | -52.5548 | -62.2688 | -46.9669 | -45.1131 | -50.2271 | -50.4361 | -53.043 | -59.1373 | -57.2269 | -45.1692 | -50.06 | -50.4942 | -52.8198 | -59.1393 | -57.4521
104 | -2.9128 | 0 | -2.8428 | 0 | -3.0534 | 0 | -2.8455 | 0 | -61.0395 | -44.9928 | -62.3938 | -163.498 | -62.6896 | 43.6889 | -64.9199 | -105.7389 | -57.9626 | -6.0523 | -63.6245 | 10.4119 | -60.75 | 39.8638 | -54.0995 | -131.2337 | -61.3056 | -39.4689 | -53.6404 | 55.3909 | -58.0858 | 102.462 | -61.2886 | 124.0076 | -27.6258 | -105.7107 | -29.5634 | -113.6555 | -24.2194 | -139.7171 | -26.3704 | -132.6839 | -29.0848 | -46.8238 | -27.8947 | 125.802 | -28.3774 | -101.9916 | -27.7358 | -69.9705 | -49.2614 | -48.1438 | -53.0111 | -50.2965 | -55.4098 | -59.7961 | -49.421 | -55.487 | -51.2058 | -51.7491 | -55.8038 | -57.6042 | -57.1433 | 104 | -57.2085 | -55.6738 | -58.7535 | -55.899 | -52.618 | -51.7263 | -50.4775 | -55.1748 | 104 | -52.5742 | -48.293 | -47.3837 | -52.567 | -56.9533 | -46.3676 | -52.6442 | -48.1524 | -47.451 | -52.3564 | -56.9506 | -46.5755 | -45.231 | -50.0983 | -48.8363 | -52.961 | -54.7614 | -54.0899 | -45.301 | -49.9577 | -48.9036 | -52.7504 | -54.7587 | -54.2978
105 | -2.9605 | 0 | -2.859 | 0 | -3.0472 | 0 | -2.8558 | 0 | -65.0022 | -109.7463 | -60.3855 | -172.0891 | -64.543 | 54.2634 | -60.3012 | -108.464 | -57.0255 | -27.4286 | -59.9287 | -25.818 | -64.2239 | 51.9268 | -56.2898 | -131.0358 | -62.2687 | -84.9132 | -55.97 | 22.5717 | -57.9213 | 86.1844 | -74.0555 | 82.8012 | -23.4142 | -115.6974 | -30.1864 | -117.0617 | -23.9193 | -158.5572 | -26.9613 | -154.0933 | -24.6421 | -75.7534 | -26.7764 | 95.6302 | -28.1122 | -144.5924 | -29.3279 | -102.0078 | -48.8986 | -48.8993 | -52.672 | -49.3596 | -55.426 | -57.4149 | -49.0153 | -54.7894 | -51.23 | -50.777 | -55.8434 | -55.844 | -55.5822 | 105 | -58.0067 | -54.9044 | -55.4293 | -54.7477 | -54.7874 | -53.4474 | -53.0818 | -56.4854 | 105 | -51.8289 | -48.2695 | -46.3991 | -52.567 | -54.5559 | -45.9681 | -51.9304 | -48.1828 | -46.5038 | -52.3788 | -54.5591 | -46.1595 | -45.9388 | -49.7115 | -47.8165 | -52.9844 | -52.985 | -52.535 | -46.0403 | -49.6248 | -47.9212 | -52.7962 | -52.9882 | -52.7264
106 | -2.9908 | 0 | -2.8753 | 0 | -3.04 | 0 | -2.8778 | 0 | -63.7654 | 170.579 | -57.1268 | 177.7114 | -63.7338 | 65.9172 | -59.3402 | -125.9042 | -56.9685 | -50.3206 | -59.4401 | -53.1889 | -62.5893 | 78.4533 | -56.3112 | -121.2975 | -62.4591 | -135.9283 | -61.156 | -11.8529 | -58.8351 | 69.4311 | -63.3073 | -117.5412 | -21.0185 | -133.8716 | -29.9353 | -119.3078 | -24.3947 | -174.399 | -28.6497 | -175.5466 | -22.3548 | -103.6673 | -26.9131 | 68.8517 | -27.9199 | 174.7915 | -31.9929 | -136.4997 | -48.6804 | -50.0092 | -52.2413 | -49.2351 | -55.4656 | -56.396 | -48.676 | -55.0166 | -51.3345 | -50.3479 | -55.7893 | -55.2978 | -55.2 | 106 | -55.5575 | -54.4441 | -53.7268 | -54.4725 | -54.6133 | -55.809 | -54.4716 | -56.3037 | 106 | -52.0258 | -48.3437 | -46.2443 | -52.5903 | -53.5207 | -45.636 | -52.1413 | -48.2945 | -46.3573 | -52.4256 | -53.5182 | -45.7982 | -47.0184 | -49.2505 | -47.3571 | -52.914 | -52.4225 | -52.16 | -47.1339 | -49.2013 | -47.4701 | -52.7493 | -52.42 | -52.3222
107 | -3.0087 | 0 | -2.8931 | 0 | -3.0318 | 0 | -2.8962 | 0 | -59.642 | 120.9044 | -54.4602 | 156.4888 | -62.4761 | 65.1704 | -60.7674 | -134.6465 | -58.1312 | -73.139 | -60.0669 | -68.4868 | -58.6908 | 78.5222 | -54.7384 | -121.6983 | -61.5505 | 174.8023 | -74.6407 | -86.9831 | -61.1641 | 54.8289 | -56.9687 | -150.4126 | -19.8857 | -154.0148 | -29.1452 | -124.254 | -25.406 | 174.8027 | -32.0859 | 163.017 | -21.3469 | -130.642 | -28.3101 | 42.3327 | -28.1536 | 137.7062 | -36.1425 | -176.1144 | -48.499 | -51.0557 | -51.8841 | -49.6044 | -55.6474 | -56.126 | -48.4126 | -56.0279 | -51.5165 | -50.3657 | -55.7368 | -55.4498 | -55.7973 | 107 | -52.8132 | -54.6071 | -52.6732 | -55.1034 | -52.6679 | -56.6735 | -52.6739 | -54.5913 | 107 | -53.0192 | -48.5078 | -46.5957 | -52.7543 | -53.2329 | -45.3808 | -53.1348 | -48.4847 | -46.7082 | -52.6156 | -53.2298 | -45.5164 | -48.047 | -48.8754 | -47.357 | -52.8437 | -52.5567 | -52.7655 | -48.1626 | -48.8523 | -47.4695 | -52.705 | -52.5536 | -52.9011
108 | -3.0232 | 0 | -2.9196 | 0 | -3.0444 | 0 | -2.8943 | 0 | -56.6701 | 86.99 | -53.2645 | 129.8078 | -60.6755 | 64.1215 | -61.4143 | -123.2918 | -61.2591 | -94.8359 | -59.901 | -69.41 | -55.9635 | 65.3922 | -53.7025 | -130.3405 | -60.0364 | 132.8141 | -64.1592 | 140.0943 | -65.7101 | 52.8913 | -54.7224 | -179.1368 | -19.7168 | -174.0871 | -28.2494 | -132.9565 | -26.2582 | 171.0602 | -40.2303 | 144.9793 | -21.2624 | -157.2118 | -31.3591 | 12.4234 | -29.3565 | 102.0789 | -44.5222 | 126.4304 | -48.42 | -51.6463 | -51.5939 | -50.3731 | -55.9825 | -56.3377 | -48.2282 | -58.1577 | -51.7654 | -50.6852 | -55.8102 | -56.1342 | -57.6577 | 108 | -51.1213 | -54.4092 | -51.8971 | -55.8048 | -51.0857 | -54.9684 | -50.9593 | -53.3431 | 108 | -55.1345 | -48.7422 | -47.3499 | -53.0629 | -53.4181 | -45.1838 | -55.2381 | -48.721 | -47.4788 | -52.9381 | -53.4434 | -45.3339 | -48.6231 | -48.5707 | -47.662 | -52.8906 | -53.2146 | -54.6133 | -48.7267 | -48.5495 | -47.7909 | -52.7658 | -53.2399 | -54.7634
109 | -3.0335 | 0 | -2.916 | 0 | -3.0705 | 0 | -2.9042 | 0 | -54.7783 | 57.8327 | -53.8555 | 102.0322 | -59.0391 | 56.4216 | -58.8451 | -117.6696 | -68.7522 | -103.9424 | -57.6393 | -74.6416 | -54.4128 | 46.9665 | -53.3347 | -140.1567 | -58.7093 | 97.3338 | -58.7145 | 107.7101 | -68.8099 | 93.7667 | -54.4811 | 156.4438 | -20.4418 | 167.3112 | -27.5772 | -144.7871 | -26.3723 | 172.5204 | -43.5109 | -73.4551 | -22.0884 | 176.4742 | -37.5957 | -31.8278 | -31.8518 | 66.7414 | -43.3465 | -20.6602 | -48.3226 | -51.2622 | -51.4244 | -51.5921 | -56.4827 | -57.1411 | -48.1074 | -62.8283 | -52.0999 | -51.3418 | -56.0918 | -57.6408 | -61.5199 | 109 | -50.6092 | -53.2186 | -51.4615 | -55.0821 | -50.1744 | -52.9276 | -50.2008 | -52.9747 | 109 | -59.7948 | -49.0664 | -48.5586 | -53.5667 | -54.2251 | -45.0369 | -59.9123 | -49.0294 | -48.6879 | -53.4122 | -54.2369 | -45.2032 | -48.2287 | -48.3909 | -48.3083 | -53.1758 | -54.7248 | -58.4494 | -48.3462 | -48.3539 | -48.4376 | -53.0213 | -54.7366 | -58.6157
110 | -3.0355 | 0 | -2.9292 | 0 | -3.1031 | 0 | -2.9187 | 0 | -53.7339 | 29.8392 | -56.6913 | 79.4157 | -57.4073 | 46.5319 | -56.8505 | -128.1478 | -68.6862 | -1.9005 | -55.5445 | -96.5466 | -53.8806 | 26.9414 | -53.1754 | -150.549 | -57.9237 | 65.322 | -56.108 | 81.0903 | -63.2957 | 116.3125 | -55.4695 | 138.1487 | -22.2099 | 151.8277 | -27.4085 | -157.5581 | -25.5485 | 172.8833 | -32.9132 | -85.1812 | -24.0665 | 150.1847 | -39.9763 | -140.46 | -36.3786 | 17.8212 | -35.4173 | -72.458 | -48.1911 | -50.1306 | -51.4966 | -53.0114 | -56.8786 | -58.8767 | -48.0229 | -83.4273 | -52.4691 | -52.2338 | -56.4995 | -60.5796 | -62.67 | 110 | -50.8664 | -51.9158 | -51.5509 | -53.2407 | -49.7805 | -51.5426 | -49.956 | -53.0809 | 110 | -80.3918 | -49.4336 | -49.9759 | -53.9494 | -55.9475 | -44.9198 | -80.4981 | -49.366 | -50.0927 | -53.7755 | -55.958 | -45.1042 | -47.0951 | -48.4611 | -49.1983 | -53.5703 | -57.6504 | -59.5669 | -47.2014 | -48.3935 | -49.3151 | -53.3964 | -57.6609 | -59.7513
111 | -3.0226 | 0 | -2.9463 | 0 | -3.15 | 0 | -2.936 | 0 | -53.647 | 2.461 | -61.3187 | 80.6969 | -56.29 | 29.6222 | -56.4517 | -139.1707 | -60.0739 | -13.1624 | -55.9661 | -122.9095 | -54.2801 | 7.5 | -53.5056 | -164.4407 | -57.5887 | 32.1798 | -54.6235 | 54.2588 | -59.4977 | 105.9308 | -56.4912 | 125.9536 | -24.9895 | 146.5076 | -27.5245 | -169.8456 | -24.078 | 169.9839 | -28.602 | -104.561 | -28.1453 | 125.1745 | -33.2011 | 166.5206 | -37.3238 | -77.9977 | -30.995 | -112.0589 | -48.0441 | -49.0368 | -51.9525 | -53.4152 | -56.7082 | -62.2165 | -48.0284 | -63.4117 | -52.5031 | -53.0362 | -56.751 | -66.5757 | -59.3775 | 111 | -51.3042 | -51.2119 | -52.57 | -52.3178 | -50.028 | -50.8073 | -49.9341 | -52.9173 | 111 | -60.3891 | -49.4805 | -50.3926 | -53.7619 | -59.2702 | -44.8784 | -60.4654 | -49.3531 | -50.4792 | -53.5582 | -59.2805 | -45.0924 | -46.0142 | -48.9299 | -50.0136 | -53.8047 | -63.6294 | -56.2275 | -46.0905 | -48.8025 | -50.1002 | -53.601 | -63.6397 | -56.4415
112 | -3.053 | 0 | -2.9711 | 0 | -3.18 | 0 | -2.9608 | 0 | -54.7836 | -24.2065 | -61.6749 | 103.5837 | -56.8362 | 9.5038 | -56.2184 | -143.2687 | -56.6078 | -34.5358 | -58.4056 | -139.4971 | -55.5269 | -11.3483 | -55.43 | -177.3897 | -58.1926 | -4.3316 | -54.0508 | 23.4667 | -57.7168 | 89.62 | -57.5413 | 110.2988 | -27.1355 | 161.5551 | -27.8651 | 179.1544 | -22.6217 | 161.845 | -26.3548 | -122.8336 | -39.5152 | 107.0401 | -29.8286 | 139.0331 | -30.9939 | -136.2643 | -28.1938 | -146.2315 | -47.9868 | -48.5707 | -52.4905 | -52.1821 | -56.0766 | -67.305 | -48.0766 | -57.9417 | -52.178 | -53.2602 | -56.4242 | -70.0628 | -56.6542 | 112 | -52.164 | -51.0257 | -53.456 | -52.4417 | -51.438 | -50.743 | -50.6751 | -53.0371 | 112 | -54.8887 | -49.125 | -49.1291 | -53.1055 | -64.3339 | -44.8966 | -54.9706 | -48.998 | -49.2213 | -52.8966 | -64.3442 | -45.1158 | -45.5177 | -49.4375 | -50.2072 | -53.4531 | -67.0917 | -53.4742 | -45.5996 | -49.3105 | -50.2994 | -53.2442 | -67.102 | -53.6934
113 | -3.0676 | 0 | -2.9685 | 0 | -3.1823 | 0 | -2.9879 | 0 | -57.456 | -47.8011 | -60.276 | 109.9274 | -58.329 | -4.1682 | -55.0538 | -148.1078 | -55.07 | -56.2705 | -61.3533 | -130.1749 | -58.213 | -28.4319 | -58.7465 | -173.6556 | -59.8832 | -41.6224 | -54.5306 | -12.5984 | -56.8331 | 73.9811 | -62.0742 | 92.6692 | -25.0207 | 179.2162 | -28.3067 | 170.5014 | -21.5256 | 150.7219 | -25.0422 | -139.1653 | -33.5768 | -116.3214 | -28.2416 | 118.3389 | -26.7819 | -170.8206 | -26.1778 | -178.9911 | -47.9372 | -48.7018 | -52.8332 | -50.7809 | -55.5544 | -68.2448 | -48.0856 | -55.8268 | -51.8527 | -52.8708 | -56.0114 | -63.2799 | -54.7664 | 113 | -53.7633 | -50.9521 | -53.193 | -52.7464 | -54.1219 | -51.4839 | -52.6137 | -54.2934 | 113 | -52.7592 | -48.7851 | -47.7133 | -52.5859 | -65.2763 | -44.9033 | -52.8583 | -48.6704 | -47.793 | -52.3721 | -65.2569 | -45.0977 | -45.6342 | -49.7656 | -49.8032 | -53.0429 | -60.3114 | -51.5841 | -45.7333 | -49.6509 | -49.8829 | -52.8291 | -60.292 | -51.7785
114 | -3.0975 | 0 | -2.9922 | 0 | -3.1908 | 0 | -3.005 | 0 | -62.8587 | -62.8559 | -58.4477 | 115.6794 | -60.7533 | -9.1095 | -54.1576 | -159.7154 | -54.4617 | -76.1975 | -59.0527 | -119.2939 | -63.5345 | -33.2424 | -58.4683 | -149.7304 | -63.2766 | -87.0856 | -56.014 | -54.1715 | -56.5285 | 55.8396 | -71.4885 | 155.0206 | -21.8874 | 176.3964 | -28.674 | 163.2164 | -21.0566 | 138.3316 | -24.4177 | -153.4169 | -25.7608 | -137.0495 | -27.8937 | 101.3844 | -24.3712 | 161.1933 | -24.9032 | 150.4703 | -47.9608 | -49.3118 | -52.9099 | -49.91 | -55.2733 | -64.4915 | -48.1328 | -55.2572 | -51.7069 | -52.3203 | -55.7148 | -59.7846 | -53.5061 | 114 | -55.5468 | -51.0037 | -51.8625 | -52.4687 | -56.3147 | -52.8642 | -53.9819 | -55.5825 | 114 | -52.1597 | -48.6094 | -46.8125 | -52.2811 | -61.4993 | -44.942 | -52.265 | -48.5161 | -46.905 | -52.0825 | -61.4865 | -45.1278 | -46.2143 | -49.8124 | -49.2228 | -52.7226 | -56.7924 | -50.3153 | -46.3196 | -49.7191 | -49.3153 | -52.524 | -56.7796 | -50.5011
115 | -3.1184 | 0 | -2.9972 | 0 | -3.1936 | 0 | -3.0145 | 0 | -71.0133 | -9.5494 | -55.4918 | 111.7124 | -62.2723 | -1.4516 | -54.3347 | -172.8182 | -54.6951 | -95.7009 | -56.7187 | -131.4695 | -67.2631 | 23.4746 | -55.3067 | -148.4687 | -65.3621 | -147.7802 | -57.8384 | -104.2604 | -57.0839 | 34.6119 | -59.7183 | -173.1019 | -19.6743 | 163.5433 | -28.9634 | 155.7719 | -21.024 | 127.0023 | -24.1046 | -165.3373 | -22.0959 | -160.7858 | -28.3897 | 88.634 | -23.1368 | 136.3803 | -24.2523 | 120.8726 | -48.0478 | -50.1973 | -52.8018 | -49.5283 | -55.1963 | -61.7793 | -48.1965 | -55.5881 | -51.6575 | -51.8176 | -55.4855 | -57.9982 | -52.861 | 115 | -54.5649 | -51.4525 | -50.6357 | -52.137 | -54.6529 | -54.2138 | -52.4729 | -54.7951 | 115 | -52.4697 | -48.5391 | -46.4099 | -52.1991 | -58.7821 | -45.0029 | -52.5909 | -48.4639 | -46.5138 | -52.0027 | -58.7648 | -45.182 | -47.0789 | -49.6834 | -48.6992 | -52.4883 | -55.001 | -49.6674 | -47.2001 | -49.6082 | -48.8031 | -52.2919 | -54.9837 | -49.8465
116 | -3.1467 | 0 | -3.0235 | 0 | -3.1826 | 0 | -3.0265 | 0 | -61.7904 | 27.0849 | -53.1044 | 96.1501 | -61.8137 | 7.0523 | -55.3383 | 179.36 | -55.7996 | -113.7242 | -55.973 | -146.162 | -60.0322 | 42.2287 | -53.5069 | -161.2079 | -63.3769 | 148.1222 | -58.5829 | -161.8688 | -58.9135 | 13.6733 | -54.9864 | 167.6078 | -18.4203 | 147.6052 | -29.2801 | 149.112 | -21.4273 | 117.7152 | -23.8694 | -174.3638 | -20.0874 | 175.5751 | -29.6695 | 80.733 | -23.0793 | 113.2584 | -24.412 | 92.2418 | -48.1501 | -51.2537 | -52.5604 | -49.5603 | -55.3161 | -60.089 | -48.2696 | -56.6534 | -51.6974 | -51.457 | -55.336 | -57.1669 | -52.7745 | 116 | -52.0666 | -52.0635 | -49.8524 | -52.3533 | -52.2827 | -54.362 | -50.449 | -53.0839 | 116 | -53.5067 | -48.5507 | -46.4136 | -52.2926 | -57.0655 | -45.087 | -53.6299 | -48.5148 | -46.5338 | -52.1335 | -57.0625 | -45.2431 | -48.107 | -49.4137 | -48.3103 | -52.3125 | -54.1434 | -49.5919 | -48.2302 | -49.3778 | -48.4305 | -52.1534 | -54.1404 | -49.748
117 | -3.1583 | 0 | -3.0499 | 0 | -3.1882 | 0 | -3.0197 | 0 | -56.7192 | 13.0407 | -51.979 | 74.5715 | -60.4574 | 6.5844 | -56.0913 | 179.8379 | -58.1126 | -128.33 | -55.6039 | -157.0336 | -55.8118 | 28.7949 | -53.0826 | -176.4074 | -60.0364 | 106.8653 | -57.9267 | 144.9267 | -62.8456 | -8.9872 | -52.95 | 144.6348 | -17.9599 | 130.6082 | -29.8689 | 142.559 | -22.0687 | 111.1493 | -23.6157 | 177.7368 | -19.0917 | 152.5194 | -31.2423 | 81.0901 | -24.1708 | 92.6037 | -25.2723 | 61.5781 | -48.3171 | -52.0645 | -52.2281 | -50.0509 | -55.6821 | -59.1543 | -48.3428 | -58.49 | -51.8379 | -51.2725 | -55.3448 | -57.1255 | -53.0327 | 117 | -50.2832 | -52.1236 | -49.3736 | -52.8432 | -50.6894 | -53.2291 | -49.3557 | -51.8172 | 117 | -55.3317 | -48.6796 | -46.8926 | -52.6322 | -56.1044 | -45.1546 | -55.4401 | -48.6497 | -47.0312 | -52.4939 | -56.1346 | -45.3231 | -48.9062 | -49.0698 | -48.1142 | -52.2949 | -54.0756 | -49.8445 | -49.0146 | -49.0399 | -48.2528 | -52.1566 | -54.1058 | -50.013
118 | -3.157 | 0 | -3.0428 | 0 | -3.2121 | 0 | -3.0353 | 0 | -53.9359 | -7.3369 | -52.2644 | 51.7565 | -58.8595 | 1.3012 | -55.5872 | -178.6044 | -61.9588 | -130.5432 | -55.3722 | -167.4601 | -53.494 | 9.7414 | -53.5126 | 171.3668 | -57.9404 | 73.8856 | -57.1013 | 100.9302 | -73.7094 | -31.9224 | -52.6628 | 126.0609 | -18.207 | 114.5248 | -30.6793 | 139.803 | -22.7889 | 109.0702 | -23.1117 | 170.756 | -18.9917 | 129.8731 | -32.266 | 90.5914 | -26.8126 | 77.0065 | -26.9833 | 27.5894 | -48.433 | -51.9773 | -52.0042 | -51.0072 | -56.1244 | -59.0203 | -48.4295 | -61.5012 | -52.1531 | -51.3123 | -55.5428 | -58.0442 | -53.3387 | 118 | -49.4779 | -51.2845 | -49.3547 | -53.1517 | -49.7742 | -51.8944 | -49.2739 | -51.5083 | 118 | -58.3442 | -48.9961 | -47.8502 | -53.0816 | -55.9775 | -45.2174 | -58.4584 | -48.941 | -47.9719 | -52.9123 | -55.985 | -45.3942 | -48.8203 | -48.8472 | -48.1553 | -52.5 | -55.0014 | -50.1266 | -48.9345 | -48.7921 | -48.277 | -52.3307 | -55.0089 | -50.3034
119 | -3.1665 | 0 | -3.049 | 0 | -3.231 | 0 | -3.0438 | 0 | -52.5309 | -29.4635 | -53.9455 | 30.963 | -57.7325 | -7.9416 | -54.8933 | 176.8504 | -63.8278 | -99.6689 | -54.7118 | 178.3238 | -52.4435 | -11.4241 | -54.2673 | 161.1428 | -56.4718 | 45.4971 | -56.7962 | 62.5651 | -69.5014 | 120.5921 | -52.7683 | 113.5843 | -19.2089 | 99.3477 | -31.3573 | 139.7265 | -23.1163 | 110.1063 | -22.6476 | 161.9908 | -19.7899 | 108.8311 | -31.5683 | 102.1377 | -32.0719 | 78.5738 | -29.0284 | -13.7426 | -48.4391 | -51.043 | -52.0605 | -52.1774 | -56.4352 | -59.8984 | -48.5177 | -66.8208 | -52.5649 | -51.6584 | -55.8693 | -60.2935 | -53.2761 | 119 | -49.469 | -50.3439 | -49.7259 | -52.613 | -49.3204 | -51.0235 | -49.5385 | -51.1623 | 119 | -63.6543 | -49.3984 | -49.0109 | -53.3862 | -56.8494 | -45.2867 | -63.7718 | -49.3339 | -49.1336 | -53.2042 | -56.8546 | -45.4739 | -47.8765 | -48.894 | -48.4919 | -52.8203 | -57.2445 | -50.0451 | -47.994 | -48.8295 | -48.6146 | -52.6383 | -57.2497 | -50.2323
120 | -3.1623 | 0 | -3.0586 | 0 | -3.2685 | 0 | -3.041 | 0 | -52.2146 | -51.4815 | -57.034 | 14.5618 | -57.2016 | -22.2521 | -54.594 | 171.6912 | -60.04 | -84.8186 | -55.1064 | 158.8197 | -52.4695 | -32.566 | -55.6884 | 152.8757 | -56.388 | 15.5787 | -57.1588 | 23.4235 | -61.8175 | 99.0364 | -53.1425 | 100.8085 | -21.0119 | 90.204 | -30.5982 | 145.414 | -22.4817 | 114.6818 | -22.0749 | 153.4311 | -21.7933 | 90.7484 | -29.7471 | 109.3956 | -32.3506 | 137.6594 | -30.5353 | -69.3295 | -48.3549 | -50.0335 | -52.3727 | -52.8003 | -56.4565 | -61.9359 | -48.5743 | -84.581 | -52.8888 | -52.1953 | -56.1602 | -64.3193 | -52.8219 | 120 | -50.0481 | -49.8012 | -50.6866 | -52.232 | -49.7228 | -50.8382 | -50.2354 | -51.0761 | 120 | -81.4187 | -49.7265 | -49.638 | -53.3979 | -58.8773 | -45.3058 | -81.5224 | -49.6203 | -49.7593 | -53.188 | -58.8949 | -45.5333 | -46.8712 | -49.2104 | -49.033 | -53.1016 | -61.2607 | -49.5534 | -46.9749 | -49.1042 | -49.1543 | -52.8917 | -61.2783 | -49.7809
121 | -3.1447 | 0 | -3.0756 | 0 | -3.3113 | 0 | -3.0466 | 0 | -52.9104 | -72.0317 | -63.1442 | 5.738 | -57.7983 | -40.4778 | -54.3057 | 167.4349 | -57.0271 | -92.4862 | -57.1701 | 144.8155 | -53.5326 | -52.9574 | -57.8872 | 155.7773 | -57.7152 | -13.2736 | -58.0815 | -22.1151 | -58.6671 | 76.271 | -53.7123 | 87.5242 | -23.3717 | 90.5637 | -29.1442 | 144.661 | -21.0894 | 114.7425 | -21.8107 | 143.8702 | -25.5887 | 80.4599 | -27.851 | 107.4284 | -25.6086 | 143.7632 | -29.3222 | -123.8573 | -48.2429 | -49.338 | -52.8276 | -52.4656 | -56.1922 | -65.049 | -48.5795 | -69.0183 | -53.0236 | -52.8022 | -56.224 | -69.1707 | -51.8535 | 121 | -51.3898 | -49.6619 | -52.1368 | -52.5479 | -51.1057 | -51.3383 | -51.2867 | -51.3636 | 121 | -65.8736 | -49.8789 | -49.3209 | -53.1166 | -61.9734 | -45.2682 | -65.9427 | -49.7123 | -49.419 | -52.8809 | -62.0024 | -45.5329 | -46.1933 | -49.6829 | -49.6575 | -53.1484 | -66.0951 | -48.5422 | -46.2624 | -49.5163 | -49.7556 | -52.9127 | -66.1241 | -48.8069
122 | -3.1602 | 0 | -3.0981 | 0 | -3.3359 | 0 | -3.0493 | 0 | -54.6133 | -89.3332 | -68.7117 | 97.337 | -59.9236 | -52.3882 | -53.931 | 162.0905 | -55.1638 | -106.6546 | -59.7389 | 143.41 | -56.0193 | -70.8192 | -57.5205 | 172.9291 | -61.9153 | -36.7745 | -58.6997 | -78.2192 | -57.2661 | 53.7613 | -55.5749 | 74.7684 | -24.2925 | 104.5064 | -27.8681 | 136.1996 | -19.6495 | 108.2136 | -21.7002 | 133.5533 | -30.4357 | 105.5427 | -26.4551 | 101.36 | -21.6499 | 128.2504 | -26.8707 | -165.7565 | -48.16 | -49.0345 | -53.2533 | -51.6756 | -55.7654 | -68.9407 | -48.5552 | -62.375 | -53.0625 | -53.2583 | -56.0356 | -67.375 | -50.7381 | 122 | -53.3639 | -49.7688 | -52.8056 | -52.9031 | -53.0856 | -52.4211 | -52.2995 | -52.7652 | 122 | -59.2148 | -49.9023 | -48.5154 | -52.6673 | -65.8426 | -45.2193 | -59.2769 | -49.7266 | -48.6263 | -52.4295 | -65.8914 | -45.5059 | -45.8743 | -50.0931 | -50.0981 | -52.9375 | -64.2769 | -47.4022 | -45.9364 | -49.9174 | -50.209 | -52.6997 | -64.3257 | -47.6888
123 | -3.1868 | 0 | -3.1052 | 0 | -3.3953 | 0 | -3.0732 | 0 | -57.4634 | -99.3422 | -57.6986 | 107.841 | -62.8487 | -51.8965 | -53.9077 | 155.7055 | -54.3513 | -122.4217 | -60.5267 | 152.4332 | -60.8424 | -79.7756 | -54.4495 | 173.6814 | -71.0617 | -62.4298 | -57.4909 | -137.785 | -57.017 | 30.6411 | -59.4238 | 79.0914 | -22.3177 | 116.519 | -27.1735 | 124.4901 | -18.6506 | 98.8459 | -21.7636 | 123.4647 | -26.22 | 141.4898 | -25.6267 | 92.5363 | -19.5759 | 107.7829 | -25.0263 | 162.8471 | -48.1318 | -49.1172 | -53.5649 | -50.9521 | -55.2802 | -70.4102 | -48.527 | -58.6609 | -52.9836 | -53.4567 | -55.6989 | -63.4929 | -49.798 | 123 | -53.9674 | -50.2083 | -51.771 | -52.9444 | -53.476 | -53.3789 | -51.8618 | -54.9381 | 123 | -55.4741 | -49.7968 | -47.7653 | -52.175 | -67.305 | -45.1317 | -55.5557 | -49.5883 | -47.8789 | -51.8849 | -67.337 | -45.4538 | -45.9304 | -50.3781 | -50.2699 | -52.5937 | -60.3877 | -46.4027 | -46.012 | -50.1696 | -50.3835 | -52.3036 | -60.4197 | -46.7248
124 | -3.2338 | 0 | -3.0989 | 0 | -3.4044 | 0 | -3.1091 | 0 | -60.9853 | -90.8641 | -52.9109 | 87.0389 | -64.2833 | -29.9121 | -54.2069 | 152.1327 | -54.506 | -137.8346 | -58.8454 | 157.6307 | -66.6173 | -34.6072 | -52.2982 | 158.6756 | -68.0247 | 82.6585 | -55.2587 | 172.4155 | -57.6819 | 6.7613 | -59.0559 | 110.5908 | -19.768 | 112.1349 | -27.4575 | 108.5811 | -18.1774 | 86.2176 | -22.0324 | 112.3821 | -21.3765 | 136.4277 | -25.4913 | 85.0479 | -18.8155 | 87.0344 | -23.9606 | 137.9156 | -48.1372 | -49.5716 | -53.6471 | -50.4418 | -54.8754 | -67.5638 | -48.509 | -56.295 | -52.7963 | -53.2942 | -55.3411 | -61.0685 | -49.1749 | 124 | -52.0164 | -50.8958 | -49.9071 | -52.8227 | -52.0298 | -53.0957 | -49.9512 | -55.0783 | 124 | -53.0612 | -49.5625 | -47.208 | -51.7765 | -64.4649 | -45.1046 | -53.1961 | -49.3919 | -47.3327 | -51.471 | -64.4547 | -45.3999 | -46.3378 | -50.4133 | -50.0604 | -52.2422 | -57.9696 | -45.7705 | -46.4727 | -50.2427 | -50.1851 | -51.9367 | -57.9594 | -46.0658
125 | -3.2672 | 0 | -3.1106 | 0 | -3.4061 | 0 | -3.1221 | 0 | -60.526 | -62.5085 | -50.6396 | 63.1493 | -61.4249 | -17.1094 | -54.107 | 152.8555 | -55.3407 | -151.0147 | -57.5185 | 152.0542 | -59.5926 | -1.497 | -51.6522 | 137.8311 | -59.1115 | 62.123 | -53.4605 | 131.1418 | -59.7582 | -19.998 | -54.7784 | 115.2527 | -17.9098 | 101.4296 | -28.9169 | 98.5991 | -18.4225 | 75.0498 | -22.6142 | 102.757 | -18.6041 | 119.0472 | -25.8403 | 77.7044 | -19.1511 | 64.9329 | -23.8291 | 114.6812 | -48.1723 | -50.3623 | -53.4891 | -50.2778 | -54.6489 | -64.6709 | -48.4739 | -54.9569 | -52.6188 | -52.8138 | -55.095 | -59.9061 | -48.9664 | 125 | -49.8984 | -51.1386 | -48.451 | -52.6643 | -50.3806 | -51.7631 | -48.3354 | -52.5088 | 125 | -51.6897 | -49.3516 | -47.0106 | -51.5383 | -61.5603 | -45.0678 | -51.8463 | -49.2127 | -47.1557 | -51.2428 | -61.5488 | -45.3518 | -47.0951 | -50.2219 | -49.5466 | -51.9844 | -56.7955 | -45.5603 | -47.2517 | -50.083 | -49.6917 | -51.6889 | -56.784 | -45.8443
126 | -3.316 | 0 | -3.1245 | 0 | -3.3763 | 0 | -3.1372 | 0 | -56.7165 | -57.3525 | -50.0709 | 38.3975 | -58.5517 | -20.277 | -53.0952 | 151.3353 | -56.7456 | -158.2973 | -56.6059 | 145.9299 | -54.8608 | -12.1749 | -52.4546 | 116.9788 | -55.4941 | 38.5496 | -52.532 | 94.9803 | -64.1922 | -55.2877 | -52.2676 | 102.4065 | -16.8474 | 86.238 | -31.7037 | 95.7883 | -19.2484 | 64.4695 | -23.4926 | 93.0551 | -17.0935 | 100.3929 | -26.6653 | 78.0108 | -20.9532 | 45.6716 | -24.3831 | 96.7827 | -48.1862 | -51.188 | -53.151 | -50.4323 | -54.6276 | -62.9731 | -48.4175 | -54.6224 | -52.5738 | -52.312 | -54.9917 | -59.9115 | -49.0779 | 126 | -48.7407 | -50.3864 | -47.7144 | -52.4441 | -49.2922 | -50.3488 | -47.6454 | -50.3926 | 126 | -51.3064 | -49.2578 | -47.1163 | -51.5031 | -59.8486 | -45.0412 | -51.4979 | -49.1975 | -47.2951 | -51.2513 | -59.8359 | -45.2803 | -47.872 | -49.835 | -48.996 | -51.8672 | -56.787 | -45.7016 | -48.0635 | -49.7747 | -49.1748 | -51.6154 | -56.7743 | -45.9407
127 | -3.3451 | 0 | -3.1456 | 0 | -3.3679 | 0 | -3.1432 | 0 | -53.848 | -68.6548 | -50.9654 | 16.7953 | -56.0912 | -31.0173 | -52.0222 | 143.8016 | -57.8148 | -157.0341 | -55.1313 | 134.1943 | -52.2522 | -30.0064 | -54.6211 | 98.6411 | -53.2764 | 14.2064 | -52.4329 | 61.2488 | -70.1717 | -135.2344 | -50.8403 | 86.8011 | -16.5656 | 70.3849 | -33.4653 | 122.4745 | -20.7833 | 60.1726 | -24.8118 | 85.5374 | -16.6313 | 80.5632 | -26.8609 | 85.1469 | -24.9131 | 31.9973 | -25.875 | 82.215 | -48.1135 | -51.4178 | -52.8638 | -50.8752 | -54.7463 | -62.5155 | -48.3214 | -55.3874 | -52.6381 | -52.0714 | -55.0128 | -61.2312 | -49.41 | 127 | -48.3596 | -49.1886 | -47.6064 | -51.4377 | -48.5057 | -49.2957 | -47.5939 | -48.8473 | 127 | -52.0423 | -49.293 | -47.5301 | -51.6007 | -59.3699 | -44.9535 | -52.2418 | -49.2702 | -47.732 | -51.3784 | -59.3723 | -45.1782 | -48.0727 | -49.5187 | -48.7263 | -51.8672 | -58.0856 | -46.0421 | -48.2722 | -49.4959 | -48.9282 | -51.6449 | -58.088 | -46.2668
128 | -3.3541 | 0 | -3.1518 | 0 | -3.377 | 0 | -3.1457 | 0 | -52.1563 | -85.484 | -53.0388 | 0.1092 | -54.8915 | -48.5586 | -51.6307 | 133.0725 | -57.6023 | -152.3289 | -54.1357 | 120.2387 | -50.8836 | -49.9465 | -58.682 | 87.1118 | -52.2755 | -9.4269 | -53.1973 | 27.0454 | -64.7714 | 136.3401 | -50.2851 | 71.6151 | -17.0545 | 54.7676 | -29.291 | 142.1816 | -22.064 | 65.8393 | -26.6133 | 82.2758 | -17.0621 | 60.729 | -25.3701 | 91.3342 | -31.6348 | 56.0804 | -28.0093 | 73.9495 | -47.9439 | -50.9425 | -52.6618 | -51.3071 | -54.9165 | -63.0323 | -48.1401 | -57.127 | -52.7643 | -52.187 | -55.0424 | -64.0294 | -49.7596 | 128 | -48.4478 | -48.3289 | -48.0423 | -50.5366 | -48.1148 | -48.7675 | -48.0943 | -48.0633 | 128 | -53.7729 | -49.4102 | -47.953 | -51.7647 | -59.8805 | -44.7631 | -53.9752 | -49.3873 | -48.1614 | -51.5395 | -59.8866 | -44.9944 | -47.5884 | -49.3077 | -48.8329 | -51.8906 | -60.8776 | -46.3826 | -47.7907 | -49.2848 | -49.0413 | -51.6654 | -60.8837 | -46.6139
129 | -3.3346 | 0 | -3.1591 | 0 | -3.3912 | 0 | -3.1543 | 0 | -51.4542 | -104.5375 | -56.5777 | -7.8964 | -54.1825 | -67.0327 | -51.9648 | 123.1652 | -56.3906 | -154.1413 | -53.6786 | 97.7578 | -50.4711 | -70.0669 | -65.9855 | 112.2108 | -52.2885 | -33.6837 | -54.9592 | -10.6907 | -59.407 | 99.7376 | -50.2222 | 56.0699 | -18.4183 | 41.1766 | -25.2922 | 134.8462 | -21.429 | 76.8645 | -28.3645 | 87.293 | -18.7829 | 43.5435 | -23.3312 | 92.1585 | -26.3201 | 110.4512 | -30.7463 | 82.713 | -47.6894 | -50.2184 | -52.5719 | -51.5488 | -55.1113 | -64.234 | -47.8661 | -59.3522 | -52.8971 | -52.6161 | -55.0966 | -69.2858 | -49.8448 | 129 | -48.8039 | -48.0103 | -48.912 | -49.8297 | -48.2022 | -48.7581 | -48.8788 | -47.8116 | 129 | -56.0176 | -49.5625 | -48.2142 | -51.9522 | -61.0749 | -44.4749 | -56.1931 | -49.5059 | -48.3945 | -51.7201 | -61.0797 | -44.7118 | -46.8838 | -49.2373 | -49.2815 | -51.9375 | -66.1267 | -46.4536 | -47.0593 | -49.1807 | -49.4618 | -51.7054 | -66.1315 | -46.6905
130 | -3.3198 | 0 | -3.1875 | 0 | -3.4473 | 0 | -3.1597 | 0 | -51.6398 | -123.8444 | -61.3207 | 13.7224 | -54.5661 | -85.4687 | -52.8296 | 116.6166 | -55.2205 | -161.9895 | -54.4889 | 79.8331 | -50.9617 | -90.1848 | -60.1821 | 168.6017 | -53.225 | -57.3049 | -57.7137 | -59.8161 | -56.7338 | 71.6009 | -50.8812 | 41.5476 | -20.91 | 34.1549 | -22.6943 | 119.4893 | -19.4701 | 78.3489 | -28.7772 | 101.0054 | -21.8833 | 31.9676 | -21.4006 | 82.2645 | -20.9103 | 99.4512 | -30.5353 | 103.1812 | -47.4639 | -49.6729 | -52.5689 | -51.6163 | -55.3428 | -66.0401 | -47.625 | -60.3731 | -53.0346 | -53.3281 | -55.1485 | -78.4668 | -49.4679 | 130 | -49.5517 | -48.2179 | -50.2194 | -49.9751 | -48.6228 | -49.2709 | -49.6596 | -48.2264 | 130 | -57.0533 | -49.7148 | -48.2965 | -52.1553 | -62.8526 | -44.1777 | -57.1856 | -49.5873 | -48.4566 | -51.8955 | -62.8804 | -44.4653 | -46.3531 | -49.2491 | -50.0083 | -51.961 | -75.2793 | -46.0206 | -46.4854 | -49.1216 | -50.1684 | -51.7012 | -75.3071 | -46.3082
131 | -3.3029 | 0 | -3.2154 | 0 | -3.5125 | 0 | -3.1653 | 0 | -52.7387 | -142.976 | -57.7352 | 55.1488 | -55.8473 | -102.8452 | -53.7705 | 115.7174 | -54.546 | -173.4672 | -56.2602 | 61.6502 | -52.452 | -108.3279 | -54.2691 | 158.5112 | -55.6861 | -79.4893 | -59.2209 | -129.0094 | -55.5058 | 46.0887 | -52.2908 | 28.1468 | -23.5336 | 43.0148 | -21.2712 | 99.4595 | -17.7474 | 69.5613 | -27.2282 | 108.3479 | -26.8197 | 45.7715 | -20.3856 | 69.5684 | -18.3573 | 80.5413 | -27.8925 | 111.0173 | -47.316 | -49.4608 | -52.5989 | -51.6676 | -55.5348 | -68.2381 | -47.3794 | -58.9539 | -53.1701 | -54.1294 | -55.2583 | -70.6804 | -48.7719 | 131 | -50.1732 | -48.8504 | -50.8368 | -50.7169 | -49.1621 | -50.1336 | -49.65 | -49.425 | 131 | -55.651 | -49.8672 | -48.3647 | -52.3194 | -65.0227 | -43.8669 | -55.7385 | -49.6576 | -48.5023 | -52.0223 | -65.0728 | -44.2141 | -46.1579 | -49.296 | -50.8265 | -52.0429 | -67.465 | -45.2594 | -46.2454 | -49.0864 | -50.9641 | -51.7458 | -67.5151 | -45.6066
132 | -3.32 | 0 | -3.2581 | 0 | -3.5604 | 0 | -3.1757 | 0 | -55.043 | -159.0302 | -52.4303 | 50.6283 | -58.1993 | -116.6562 | -54.0403 | 120.1593 | -54.5912 | 173.9936 | -59.0783 | 51.137 | -55.2623 | -121.3079 | -51.2432 | 136.6842 | -60.8176 | -95.6653 | -56.6881 | 165.7119 | -55.3575 | 21.463 | -54.7332 | 23.0276 | -22.9658 | 65.2776 | -20.858 | 79.2983 | -16.9656 | 57.2216 | -25.5504 | 105.2286 | -24.7359 | 85.1904 | -19.9622 | 53.9921 | -17.2531 | 58.2409 | -25.6001 | 104.5892 | -47.2884 | -49.7548 | -52.7214 | -51.8275 | -55.6361 | -70.8056 | -47.2464 | -57.0057 | -53.2106 | -54.8206 | -55.4065 | -65.576 | -48.0431 | 132 | -49.8467 | -49.7675 | -49.6277 | -52.0589 | -49.4631 | -50.9511 | -48.8548 | -51.4853 | 132 | -53.6857 | -49.8906 | -48.5075 | -52.378 | -67.5475 | -43.686 | -53.7476 | -49.6502 | -48.6518 | -52.0757 | -67.6299 | -44.0707 | -46.4348 | -49.4014 | -51.5006 | -52.1484 | -62.3179 | -44.4827 | -46.4967 | -49.161 | -51.6449 | -51.8461 | -62.4003 | -44.8674
133 | -3.375 | 0 | -3.3011 | 0 | -3.5828 | 0 | -3.2019 | 0 | -59.0972 | -166.6557 | -49.512 | 31.4658 | -61.5401 | -122.6442 | -53.0527 | 123.3533 | -55.2887 | 161.4603 | -62.2148 | 45.2564 | -59.3536 | -117.1965 | -50.0695 | 111.8888 | -71.5124 | -69.2663 | -53.8335 | 119.761 | -56.3074 | -2.4134 | -56.4697 | 30.9723 | -19.7189 | 68.4009 | -21.293 | 58.0865 | -16.8725 | 43.1356 | -24.4535 | 94.9803 | -20.1109 | 86.8091 | -20.6866 | 38.5065 | -17.6054 | 35.9016 | -24.4604 | 95.434 | -47.3666 | -50.7421 | -52.8468 | -52.1401 | -55.5737 | -72.9217 | -47.2777 | -55.7937 | -53.2305 | -54.9808 | -55.5785 | -63.3523 | -47.441 | 133 | -48.8201 | -50.3899 | -47.7621 | -53.705 | -49.5576 | -51.1706 | -47.8962 | -53.3113 | 133 | -52.4187 | -49.8555 | -48.7651 | -52.2726 | -69.6206 | -43.6949 | -52.4926 | -49.6477 | -48.9382 | -51.9909 | -69.7198 | -44.0758 | -47.3671 | -49.4718 | -51.6058 | -52.2774 | -60.0512 | -43.8582 | -47.441 | -49.264 | -51.7789 | -51.9957 | -60.1504 | -44.2391
134 | -3.4191 | 0 | -3.3062 | 0 | -3.5553 | 0 | -3.2207 | 0 | -63.7425 | -138.8503 | -48.4222 | 9.0591 | -64.4251 | -104.8623 | -51.6196 | 119.7358 | -56.6846 | 151.6226 | -66.34 | 68.2066 | -59.8588 | -85.6676 | -50.2933 | 87.8286 | -62.4672 | 1.5961 | -52.105 | 83.0865 | -58.6017 | -24.6093 | -56.1177 | 42.6506 | -17.3395 | 58.0508 | -22.9307 | 38.189 | -17.7366 | 30.2885 | -24.4063 | 82.4972 | -17.24 | 71.8237 | -22.2938 | 24.0476 | -19.1534 | 13.4035 | -23.984 | 83.2678 | -47.4772 | -52.1248 | -53.0237 | -52.5593 | -55.4265 | -73.4451 | -47.3531 | -55.6022 | -53.2394 | -54.5992 | -55.7164 | -62.7272 | -47.1796 | 134 | -48.1918 | -50.2433 | -46.6756 | -55.6244 | -49.6072 | -50.6693 | -47.4592 | -53.5742 | 134 | -52.1831 | -49.8203 | -49.1402 | -52.1203 | -70.1389 | -43.7978 | -52.296 | -49.6841 | -49.3386 | -51.8712 | -70.2244 | -44.1324 | -48.7057 | -49.6046 | -51.1801 | -52.4102 | -59.421 | -43.6243 | -48.8186 | -49.4684 | -51.3785 | -52.1611 | -59.5065 | -43.9589
135 | -3.481 | 0 | -3.2865 | 0 | -3.5247 | 0 | -3.2397 | 0 | -59.8105 | -105.1675 | -48.7707 | -11.7989 | -62.0041 | -80.0465 | -50.6107 | 110.4018 | -58.3909 | 150.1827 | -62.2321 | 104.2007 | -55.9186 | -77.594 | -51.7075 | 65.4396 | -56.8296 | -9.4488 | -51.4513 | 49.378 | -63.1103 | -46.0746 | -53.9675 | 43.9947 | -15.994 | 42.1272 | -26.1882 | 22.5504 | -19.449 | 21.3356 | -25.4923 | 70.7084 | -15.8185 | 53.2227 | -25.4845 | 15.7976 | -22.8492 | -7.5028 | -24.4488 | 73.4501 | -47.5747 | -53.0824 | -53.1794 | -52.7974 | -55.2075 | -72.4848 | -47.5834 | -56.2395 | -53.2779 | -54.0951 | -55.7435 | -63.2825 | -47.1493 | 135 | -48.2545 | -49.5151 | -46.467 | -55.7236 | -49.4372 | -49.9109 | -47.4668 | -51.8212 | 135 | -52.7585 | -49.7969 | -49.3164 | -51.921 | -69.1983 | -44.0587 | -52.953 | -49.7532 | -49.5577 | -51.6828 | -69.2451 | -44.3437 | -49.6014 | -49.6984 | -50.6141 | -52.457 | -59.996 | -43.6246 | -49.7959 | -49.6547 | -50.8554 | -52.2188 | -60.0428 | -43.9096
136 | -3.5325 | 0 | -3.2791 | 0 | -3.4978 | 0 | -3.2659 | 0 | -55.5023 | -109.7138 | -50.2636 | -29.0924 | -58.8926 | -82.1986 | -50.2556 | 99.2534 | -59.1856 | 156.694 | -57.3565 | 95.9152 | -53.0871 | -88.8612 | -54.6423 | 45.7436 | -54.1039 | -29.4718 | -51.7666 | 15.9425 | -79.5298 | -63.8928 | -52.168 | 35.467 | -15.5851 | 24.2172 | -31.896 | 26.4005 | -21.7408 | 22.8292 | -27.8083 | 62.8334 | -15.4999 | 33.5102 | -30.3365 | 30.9488 | -32.4857 | -16.8891 | -25.5524 | 68.6029 | -47.5791 | -52.8798 | -53.3481 | -52.7901 | -55.083 | -71.0361 | -47.7752 | -57.3298 | -53.3801 | -53.8651 | -55.6893 | -64.7986 | -47.3103 | 136 | -48.6907 | -48.7123 | -46.845 | -53.6304 | -49.1246 | -49.3624 | -47.9151 | -50.0138 | 136 | -53.7973 | -49.8476 | -49.2576 | -51.8039 | -67.757 | -44.2774 | -54.0507 | -49.8823 | -49.5242 | -51.5852 | -67.7702 | -44.5093 | -49.3473 | -49.8156 | -50.3326 | -52.4102 | -61.5195 | -43.8125 | -49.6007 | -49.8503 | -50.5992 | -52.1915 | -61.5327 | -44.0444
137 | -3.5399 | 0 | -3.2864 | 0 | -3.4977 | 0 | -3.2616 | 0 | -52.9698 | -124.7474 | -52.9872 | -40.4275 | -57.3442 | -95.8193 | -50.5664 | 88.1925 | -58.2813 | 162.3511 | -54.6436 | 78.6075 | -51.5105 | -106.1218 | -60.9425 | 35.7988 | -52.9309 | -49.9276 | -53.0994 | -19.9257 | -65.9936 | 82.6059 | -50.931 | 22.0083 | -16.1503 | 6.068 | -32.0663 | 79.0351 | -22.4971 | 37.555 | -31.3373 | 75.0261 | -16.1402 | 14.0809 | -28.7165 | 71.4648 | -29.9579 | 96.5037 | -26.4769 | 71.9501 | -47.5865 | -51.9813 | -53.4884 | -52.5982 | -55.067 | -69.6923 | -47.9114 | -58.5992 | -53.4695 | -54.0013 | -55.5794 | -67.3844 | -47.4276 | 137 | -49.2384 | -48.1504 | -47.6355 | -51.6996 | -48.8741 | -49.132 | -48.6094 | -48.7243 | 137 | -55.0593 | -49.9296 | -49.0583 | -51.7806 | -66.4059 | -44.4137 | -55.3128 | -49.9718 | -49.3366 | -51.5693 | -66.4307 | -44.6498 | -48.4414 | -49.9485 | -50.4614 | -52.293 | -64.098 | -43.9299 | -48.6949 | -49.9907 | -50.7397 | -52.0817 | -64.1228 | -44.166
138 | -3.5003 | 0 | -3.3005 | 0 | -3.5355 | 0 | -3.2709 | 0 | -51.6601 | -142.8905 | -57.1052 | -35.7369 | -56.6538 | -113.3393 | -51.5489 | 79.4137 | -56.8799 | 159.0442 | -53.4629 | 55.7826 | -50.94 | -125.3053 | -65.4146 | 118.2283 | -52.9024 | -69.035 | -55.5067 | -63.5297 | -59.538 | 59.8868 | -50.4981 | 7.2611 | -17.75 | -10.9843 | -26.4072 | 82.022 | -20.5724 | 45.2196 | -30.5252 | 109.8979 | -17.9542 | -3.6877 | -24.1525 | 74.7046 | -22.2353 | 83.2096 | -26.0034 | 80.5144 | -47.5265 | -51.1169 | -53.5543 | -52.421 | -55.171 | -68.5075 | -47.949 | -59.6839 | -53.5823 | -54.4529 | -55.4607 | -71.0199 | -47.278 | 138 | -49.6132 | -47.993 | -48.7119 | -50.5962 | -48.7073 | -49.2154 | -49.2017 | -48.1946 | 138 | -56.1836 | -50.082 | -48.9207 | -51.8705 | -65.207 | -44.4135 | -56.3834 | -50.0468 | -49.1501 | -51.6355 | -65.2366 | -44.6781 | -47.6166 | -50.054 | -50.9526 | -52.1602 | -67.7194 | -43.7425 | -47.8164 | -50.0188 | -51.182 | -51.9252 | -67.749 | -44.0071
139 | -3.458 | 0 | -3.3273 | 0 | -3.5826 | 0 | -3.3091 | 0 | -51.296 | -162.0517 | -57.8914 | 3.1524 | -57.3198 | -131.121 | -53.0437 | 76.7545 | -55.8186 | 148.9126 | -53.5247 | 33.6604 | -51.2703 | -145.3989 | -55.6134 | 126.1524 | -53.9557 | -86.5753 | -57.8578 | -125.166 | -56.5993 | 36.6955 | -50.7066 | -10.961 | -20.8482 | -23.5162 | -23.3092 | 65.0834 | -18.5947 | 38.4993 | -25.9926 | 117.0714 | -21.4335 | -15.1096 | -21.4496 | 62.7365 | -19.1566 | 60.8466 | -24.0951 | 83.3507 | -47.4244 | -50.5742 | -53.5433 | -52.4361 | -55.3384 | -67.6484 | -47.9172 | -59.9068 | -53.6924 | -55.218 | -55.3937 | -72.7037 | -46.8446 | 139 | -49.6263 | -48.2389 | -49.5749 | -50.4992 | -48.4675 | -49.4732 | -48.9002 | -48.3243 | 139 | -56.4488 | -50.2344 | -48.9781 | -52.0111 | -64.3211 | -44.3346 | -56.5795 | -50.1098 | -49.127 | -51.7558 | -64.3393 | -44.6081 | -47.1162 | -50.0853 | -51.76 | -52.0664 | -69.3764 | -43.262 | -47.2469 | -49.9607 | -51.9089 | -51.8111 | -69.3946 | -43.5355
140 | -3.4441 | 0 | -3.3614 | 0 | -3.6366 | 0 | -3.3345 | 0 | -51.8756 | 178.8132 | -52.8803 | 14.8722 | -59.1861 | -144.753 | -53.9691 | 84.7476 | -55.527 | 136.0191 | -54.5656 | 13.1537 | -52.6527 | -165.3866 | -51.1961 | 105.3741 | -55.8255 | -99.0224 | -56.5754 | 165.3155 | -55.2558 | 13.6769 | -51.8474 | -28.3131 | -25.6006 | -16.3302 | -21.8867 | 43.2511 | -17.6466 | 25.6379 | -22.7482 | 105.9468 | -26.4869 | -0.8992 | -20.2144 | 46.7754 | -18.0946 | 37.2245 | -22.0871 | 76.5134 | -47.4936 | -50.6048 | -53.5412 | -52.8452 | -55.5952 | -67.1165 | -47.963 | -58.7616 | -53.7957 | -56.2872 | -55.5255 | -69.5936 | -46.3946 | 140 | -48.9106 | -48.7604 | -48.9769 | -51.2482 | -48.0586 | -49.7426 | -47.8707 | -49.1609 | 140 | -55.3175 | -50.3516 | -49.4011 | -52.2338 | -63.7551 | -44.3264 | -55.4002 | -50.1591 | -49.5107 | -51.9586 | -63.782 | -44.6285 | -47.1607 | -50.0971 | -52.8431 | -52.1641 | -66.2322 | -42.758 | -47.2434 | -49.9046 | -52.9527 | -51.8889 | -66.2591 | -43.0601
141 | -3.4622 | 0 | -3.3893 | 0 | -3.6647 | 0 | -3.3591 | 0 | -53.4887 | 162.6483 | -49.4025 | 2.5285 | -62.3719 | -151.9411 | -52.6812 | 92.8003 | -55.9841 | 122.6791 | -56.734 | -4.9162 | -55.5064 | 176.7913 | -49.1007 | 80.3371 | -58.827 | -97.0999 | -53.6335 | 114.3533 | -55.0359 | -8.9804 | -54.5323 | -43.8198 | -25.85 | 22.6723 | -21.8118 | 19.0212 | -17.8204 | 10.8734 | -20.8364 | 89.5715 | -24.9302 | 39.8638 | -20.0863 | 29.8201 | -18.5321 | 13.5255 | -20.6957 | 64.3813 | -47.631 | -51.3166 | -53.5359 | -53.6974 | -55.8263 | -67.2033 | -48.0846 | -56.9929 | -53.802 | -57.3268 | -55.7409 | -66.7507 | -45.9733 | 141 | -47.8166 | -49.0682 | -47.2148 | -52.822 | -47.8449 | -49.8792 | -46.9564 | -50.9864 | 141 | -53.5307 | -50.3398 | -50.2352 | -52.437 | -63.814 | -44.4199 | -53.6036 | -50.1373 | -50.3383 | -52.1616 | -63.8442 | -44.7255 | -47.8544 | -50.0737 | -53.8646 | -52.3516 | -63.3614 | -42.3086 | -47.9273 | -49.8712 | -53.9677 | -52.0762 | -63.3916 | -42.6142
142 | -3.4836 | 0 | -3.4041 | 0 | -3.6323 | 0 | -3.3758 | 0 | -56.2547 | 152.6861 | -47.7648 | -15.93 | -66.0416 | -133.0577 | -50.7662 | 88.6847 | -57.4533 | 111.6331 | -60.7098 | -15.6406 | -60.9273 | 170.1526 | -48.457 | 55.2399 | -59.4163 | -78.4925 | -51.6739 | 75.9146 | -55.8979 | -31.4106 | -59.483 | -47.9998 | -21.1729 | 29.215 | -22.7899 | -6.2877 | -18.8926 | -2.2039 | -19.7792 | 70.4968 | -20.5772 | 40.2463 | -21.0442 | 14.0941 | -20.5554 | -9.3735 | -19.9901 | 48.7891 | -47.8451 | -52.4248 | -53.5574 | -54.7826 | -55.9818 | -68.1592 | -48.2635 | -55.5854 | -53.8234 | -57.6228 | -56.0135 | -65.1909 | -45.5891 | 142 | -47.1335 | -49.0139 | -45.8565 | -55.3827 | -47.9002 | -49.9221 | -46.5377 | -53.1498 | 142 | -52.1018 | -50.3398 | -51.299 | -52.5777 | -64.7551 | -44.6312 | -52.1813 | -50.1911 | -51.4068 | -52.3495 | -64.7834 | -44.8877 | -48.9412 | -50.0738 | -54.1392 | -52.6094 | -61.7868 | -41.9568 | -49.0207 | -49.9251 | -54.247 | -52.3812 | -61.8151 | -42.2133
143 | -3.5251 | 0 | -3.3842 | 0 | -3.611 | 0 | -3.3827 | 0 | -59.5569 | 160.8089 | -47.3972 | -33.6253 | -63.8415 | -103.864 | -49.656 | 77.6685 | -59.5658 | 109.1938 | -66.5506 | 13.4726 | -65.3937 | -136.5941 | -48.8985 | 30.8415 | -57.1572 | -72.6901 | -50.8303 | 42.6479 | -58.2172 | -54.5841 | -62.9137 | -14.7589 | -18.5379 | 16.0758 | -25.4815 | -34.7936 | -21.2737 | -10.8947 | -19.6894 | 50.7657 | -18.075 | 25.795 | -23.0545 | 2.4348 | -25.1344 | -29.8414 | -20.0212 | 31.5471 | -48.001 | -53.1926 | -53.5755 | -55.5166 | -55.9268 | -69.7239 | -48.4897 | -54.8922 | -53.8649 | -57.2866 | -56.2045 | -64.3102 | -45.2628 | 143 | -47.0489 | -48.8483 | -45.3381 | -57.5962 | -48.2102 | -49.9757 | -46.6438 | -54.0416 | 143 | -51.3671 | -50.3398 | -51.9915 | -52.5426 | -66.3397 | -44.8787 | -51.508 | -50.2539 | -52.1339 | -52.3158 | -66.3412 | -45.107 | -49.6675 | -50.0504 | -53.7615 | -52.8203 | -60.926 | -41.6518 | -49.8084 | -49.9645 | -53.9039 | -52.5935 | -60.9275 | -41.8801
144 | -3.5691 | 0 | -3.3864 | 0 | -3.5949 | 0 | -3.3917 | 0 | -59.1949 | -174.3725 | -47.9939 | -50.0906 | -59.9867 | -103.0288 | -49.4119 | 65.4425 | -61.1828 | 119.8344 | -61.8581 | 55.3012 | -58.3441 | -116.093 | -50.4915 | 7.1911 | -55.0033 | -76.5813 | -51.0484 | 11.2026 | -63.2051 | -78.1912 | -58.839 | 9.1798 | -17.3915 | -2.4452 | -30.7927 | -70.9782 | -24.2613 | -4.8671 | -20.334 | 30.4578 | -17.1473 | 7.6119 | -26.2026 | 1.0461 | -38.312 | -18.7597 | -20.8286 | 13.3028 | -48.0852 | -52.9383 | -53.5609 | -55.6477 | -55.7532 | -70.9656 | -48.6364 | -54.712 | -54.1199 | -56.8786 | -56.2653 | -63.7433 | -45.0198 | 144 | -47.4285 | -48.724 | -45.5326 | -56.168 | -48.6793 | -50.0889 | -47.4252 | -53.0589 | 144 | -51.1429 | -50.5508 | -52.0786 | -52.3668 | -67.5792 | -45.0415 | -51.3256 | -50.525 | -52.256 | -52.1583 | -67.5739 | -45.2447 | -49.3692 | -49.9918 | -53.3095 | -52.8789 | -60.3569 | -41.4249 | -49.5519 | -49.966 | -53.4869 | -52.6704 | -60.3516 | -41.6281
145 | -3.5898 | 0 | -3.3885 | 0 | -3.5965 | 0 | -3.4067 | 0 | -55.7988 | -169.3763 | -49.5395 | -63.1908 | -57.3136 | -113.85 | -49.9126 | 53.7464 | -59.6528 | 134.2583 | -56.624 | 50.6243 | -54.3068 | -130.5142 | -53.8499 | -15.4184 | -53.4929 | -87.2998 | -52.4062 | -20.0198 | -83.3309 | -112.0882 | -55.0673 | 5.1089 | -17.5082 | -22.0742 | -38.5974 | -170.7077 | -24.4859 | 17.2266 | -21.882 | 10.1897 | -17.3886 | -10.8864 | -28.1934 | 20.0918 | -28.3354 | 78.1057 | -22.4323 | -4.5606 | -48.0288 | -52.0141 | -53.5113 | -55.4038 | -55.521 | -71.1782 | -48.662 | -54.8894 | -54.496 | -56.7518 | -56.1502 | -63.284 | -44.7514 | 145 | -48.0671 | -48.5644 | -46.2898 | -52.9114 | -49.0993 | -50.2409 | -48.8669 | -51.1962 | 145 | -51.2996 | -50.9062 | -51.814 | -52.1325 | -67.7897 | -45.0655 | -51.5009 | -50.8995 | -51.9971 | -51.9245 | -67.7715 | -45.2553 | -48.4243 | -49.9215 | -53.162 | -52.7617 | -59.8955 | -41.1549 | -48.6256 | -49.9148 | -53.3451 | -52.5537 | -59.8773 | -41.3447
146 | -3.5709 | 0 | -3.4006 | 0 | -3.6151 | 0 | -3.4016 | 0 | -53.1432 | 179.8518 | -52.289 | -68.0333 | -56.069 | -130.3156 | -51.1028 | 45.5194 | -56.6964 | 130.7265 | -53.5106 | 33.099 | -52.2373 | -150.881 | -62.0524 | -29.4327 | -53.1218 | -103.2819 | -55.37 | -54.7177 | -64.6275 | 61.232 | -53.0226 | -10.1941 | -18.9008 | -41.8053 | -30.6283 | 104.6711 | -21.8739 | 23.3903 | -24.5798 | -9.0545 | -18.8659 | -28.4033 | -26.4063 | 35.9142 | -22.6163 | 60.7863 | -25.3779 | -23.1808 | -47.8535 | -51.0679 | -53.3519 | -55.1425 | -55.3652 | -70.3882 | -48.4983 | -55.1893 | -54.7819 | -56.8811 | -55.9163 | -62.7518 | -44.4766 | 146 | -48.7861 | -48.3131 | -47.4192 | -50.4249 | -49.4041 | -50.3514 | -50.699 | -49.9124 | 146 | -51.6184 | -51.211 | -51.5716 | -51.9646 | -66.9876 | -44.8832 | -51.7887 | -51.1668 | -51.7409 | -51.7501 | -66.9866 | -45.0967 | -47.497 | -49.781 | -53.3102 | -52.5157 | -59.3512 | -40.8615 | -47.6673 | -49.7368 | -53.4795 | -52.3012 | -59.3502 | -41.075
147 | -3.5393 | 0 | -3.4424 | 0 | -3.6454 | 0 | -3.3966 | 0 | -51.6073 | 163.045 | -54.9324 | -50.1705 | -55.9834 | -148.9195 | -52.7872 | 43.6479 | -54.9259 | 117.1345 | -51.8958 | 12.9698 | -51.3778 | -173.5674 | -62.9018 | 87.1951 | -53.5671 | -117.1738 | -60.8672 | -105.2809 | -58.4197 | 37.7143 | -52.0844 | -27.9431 | -22.0107 | -59.2777 | -26.4222 | 68.5105 | -19.9198 | 14.1706 | -29.0175 | -25.8687 | -21.7764 | -39.7511 | -24.048 | 33.0159 | -20.3099 | 38.1131 | -30.5447 | -40.6198 | -47.6258 | -50.5514 | -53.168 | -55.0906 | -55.3367 | -69.6608 | -48.2081 | -55.3368 | -54.8089 | -57.2393 | -55.7706 | -62.2001 | -44.1744 | 147 | -48.9825 | -48.1285 | -48.257 | -49.136 | -49.1391 | -50.2048 | -51.2379 | -49.199 | 147 | -51.7975 | -51.2696 | -51.5513 | -51.8943 | -66.2184 | -44.5627 | -51.8944 | -51.1635 | -51.694 | -51.6913 | -66.2642 | -44.8115 | -47.0121 | -49.6287 | -53.7 | -52.3282 | -58.7577 | -40.529 | -47.109 | -49.5226 | -53.8427 | -52.1252 | -58.8035 | -40.7778
148 | -3.5215 | 0 | -3.4693 | 0 | -3.6848 | 0 | -3.4076 | 0 | -51.0033 | 143.8889 | -52.3116 | -26.7803 | -56.8752 | -167.1308 | -53.8031 | 53.2778 | -54.0984 | 98.4768 | -50.8699 | -6.8036 | -51.4968 | 163.1623 | -53.5821 | 74.1277 | -54.6063 | -129.0792 | -62.4203 | 149.5692 | -55.4321 | 15.1142 | -51.533 | -48.8619 | -28.2115 | -64.1377 | -24.8371 | 38.5774 | -19.3479 | -0.773 | -37.2786 | -31.7225 | -26.005 | -34.1813 | -23.0182 | 21.3576 | -19.9656 | 14.7979 | -43.6417 | -58.1808 | -47.4652 | -50.5674 | -53.0056 | -55.4144 | -55.4847 | -69.3604 | -47.9068 | -54.9973 | -54.4746 | -57.8326 | -55.8092 | -61.8059 | -43.9087 | 148 | -47.996 | -47.9602 | -47.3937 | -48.4985 | -48.2593 | -49.7797 | -49.2148 | -48.7449 | 148 | -51.4758 | -50.9531 | -51.8929 | -52.0154 | -65.8911 | -44.222 | -51.528 | -50.7898 | -52.0068 | -51.7999 | -65.9528 | -44.4992 | -47.0459 | -49.4841 | -54.3111 | -52.3399 | -58.3366 | -40.2239 | -47.0981 | -49.3208 | -54.425 | -52.1244 | -58.3983 | -40.5011
149 | -3.5407 | 0 | -3.4953 | 0 | -3.7034 | 0 | -3.4457 | 0 | -51.2209 | 124.9202 | -48.6341 | -30.4104 | -58.9577 | -177.3375 | -52.4469 | 63.2734 | -54.384 | 77.7627 | -50.8309 | -29.4094 | -52.541 | 139.5731 | -49.6958 | 50.699 | -56.4656 | -131.7439 | -56.1655 | 89.1177 | -53.828 | -7.0392 | -52.0388 | -69.9234 | -31.6037 | 4.2225 | -24.9275 | 10.4013 | -19.994 | -15.965 | -41.8735 | 61.7372 | -26.5349 | -1.395 | -23.175 | 8.426 | -21.2432 | -7.5531 | -37.0207 | 100.027 | -47.3857 | -51.1289 | -52.978 | -56.1318 | -55.6513 | -69.3789 | -47.6399 | -54.3362 | -53.904 | -58.5617 | -56.0227 | -61.5901 | -43.5713 | 149 | -46.475 | -47.7247 | -45.5835 | -48.8028 | -47.3159 | -49.1612 | -47.1227 | -48.9784 | 149 | -50.7955 | -50.3633 | -52.5911 | -52.156 | -65.8836 | -43.9365 | -50.8409 | -50.2006 | -52.6861 | -51.9479 | -65.9332 | -44.1942 | -47.5882 | -49.4373 | -55.021 | -52.5274 | -58.0948 | -39.8679 | -47.6336 | -49.2746 | -55.116 | -52.3193 | -58.1444 | -40.1256
150 | -3.5753 | 0 | -3.4964 | 0 | -3.7045 | 0 | -3.4517 | 0 | -52.2312 | 106.4035 | -46.4535 | -44.8475 | -62.6157 | 179.2885 | -50.2739 | 60.3983 | -55.7371 | 55.9565 | -51.9355 | -53.4625 | -54.7016 | 115.7907 | -47.7518 | 26.0987 | -57.8227 | -125.6409 | -52.6972 | 52.9282 | -53.2251 | -29.1786 | -53.3867 | -90.1041 | -24.297 | 15.2047 | -26.8034 | -20.2976 | -21.9711 | -29.1331 | -34.8368 | 68.8199 | -22.9585 | 4.3431 | -24.5845 | -3.6672 | -24.6353 | -29.756 | -31.269 | 86.5024 | -47.3868 | -51.966 | -53.1688 | -56.9102 | -55.711 | -69.3449 | -47.4417 | -54.0053 | -53.3761 | -59.2698 | -56.2464 | -61.228 | -43.1852 | 150 | -45.3524 | -47.4377 | -44.1543 | -50.1682 | -46.6116 | -48.6903 | -45.7284 | -49.5882 | 150 | -50.43 | -49.8008 | -53.3349 | -52.2146 | -65.8485 | -43.7372 | -50.5089 | -49.6716 | -53.4585 | -52.0065 | -65.8932 | -43.99 | -48.3907 | -49.5935 | -55.6945 | -52.75 | -57.7316 | -39.4807 | -48.4696 | -49.4643 | -55.8181 | -52.5419 | -57.7763 | -39.7335
151 | -3.6151 | 0 | -3.4735 | 0 | -3.6875 | 0 | -3.4602 | 0 | -54.1426 | 90.4376 | -45.4305 | -61.4751 | -63.7786 | -152.5295 | -48.8365 | 49.615 | -58.7776 | 34.904 | -54.3235 | -73.8019 | -58.6238 | 92.0453 | -46.9665 | 1.149 | -57.8086 | -116.1458 | -51.0777 | 22.9176 | -53.5731 | -51.9983 | -56.3501 | -111.308 | -20.8152 | -0.4525 | -31.2306 | -55.5302 | -25.3802 | -31.8944 | -33.8407 | 58.9618 | -20.5969 | -6.9221 | -27.146 | -6.5033 | -32.5001 | -39.5166 | -29.1143 | 75.2725 | -47.4107 | -52.5349 | -53.4196 | -57.2154 | -55.3326 | -69.4099 | -47.3367 | -54.1679 | -53.0526 | -59.7039 | -56.1063 | -60.5039 | -42.7575 | 151 | -44.8267 | -47.3874 | -43.4289 | -52.6446 | -46.3571 | -48.675 | -45.1961 | -50.7749 | 151 | -50.5528 | -49.4375 | -53.6003 | -51.8591 | -65.9364 | -43.6492 | -50.6944 | -49.3651 | -53.7552 | -51.6451 | -65.9497 | -43.8765 | -48.9198 | -49.8045 | -56.0888 | -52.6328 | -57.0304 | -39.07 | -49.0614 | -49.7321 | -56.2437 | -52.4188 | -57.0437 | -39.2973
152 | -3.6641 | 0 | -3.4722 | 0 | -3.6844 | 0 | -3.4753 | 0 | -57.1537 | 80.8625 | -45.2835 | -78.4737 | -60.7837 | -137.3974 | -48.2665 | 36.1683 | -66.4135 | 19.5513 | -58.729 | -91.6124 | -67.2622 | 72.4541 | -47.1703 | -23.2177 | -56.1637 | -116.0896 | -50.738 | -5.0799 | -55.03 | -75.0232 | -60.7869 | -126.0936 | -19.4634 | -20.777 | -38.4827 | -142.5888 | -28.3228 | -11.838 | -35.9843 | 57.5935 | -19.7495 | -24.4603 | -29.2272 | 6.8903 | -35.2628 | 59.6584 | -28.4349 | 67.4992 | -47.4563 | -52.4731 | -53.5818 | -57.0735 | -54.511 | -69.3598 | -47.3355 | -54.7156 | -53.1211 | -60.0581 | -55.4019 | -59.8758 | -42.3516 | 152 | -44.8965 | -47.6802 | -43.3847 | -56.192 | -46.617 | -49.2939 | -45.4581 | -51.9424 | 152 | -51.0515 | -49.457 | -53.4094 | -51.0388 | -65.8876 | -43.6511 | -51.2434 | -49.4367 | -53.5982 | -50.8266 | -65.8845 | -43.8602 | -48.809 | -49.9177 | -56.394 | -51.9297 | -56.4036 | -38.6672 | -49.0009 | -49.8974 | -56.5828 | -51.7175 | -56.4005 | -38.8763
153 | -3.676 | 0 | -3.5046 | 0 | -3.6997 | 0 | -3.5058 | 0 | -60.5636 | 89.6298 | -46.0079 | -94.681 | -57.4902 | -144.6634 | -48.5025 | 23.0564 | -69.817 | 128.0518 | -68.2791 | -83.7132 | -70.819 | -151.9876 | -48.4979 | -47.9018 | -54.8148 | -118.8786 | -51.5371 | -31.5575 | -58.5089 | -96.5729 | -68.0161 | -116.5843 | -19.4852 | -41.3587 | -31.8484 | 121.9918 | -26.1784 | 9.1484 | -37.6666 | 89.9896 | -20.2038 | -43.5356 | -27.6416 | 23.6338 | -26.5781 | 55.8301 | -27.9888 | 64.9155 | -47.4184 | -51.9025 | -53.5233 | -56.766 | -53.6605 | -68.5744 | -47.3327 | -55.4849 | -53.4846 | -60.4187 | -54.3757 | -59.5395 | -42.0267 | 153 | -45.5699 | -48.2103 | -44.0518 | -56.9139 | -47.5659 | -50.6998 | -46.7143 | -53.1269 | 153 | -51.8089 | -49.8086 | -53.09 | -50.1559 | -65.0698 | -43.633 | -51.9803 | -49.7849 | -53.2602 | -49.9608 | -65.0686 | -43.8269 | -48.2265 | -49.8473 | -56.7427 | -50.8711 | -56.0349 | -38.327 | -48.3979 | -49.8236 | -56.9129 | -50.676 | -56.0337 | -38.5209
154 | -3.6673 | 0 | -3.5343 | 0 | -3.7255 | 0 | -3.514 | 0 | -60.1004 | 112.5915 | -47.8061 | -107.716 | -55.6615 | -160.9483 | -49.4219 | 12.2209 | -60.3927 | 121.025 | -63.7625 | 8.2632 | -60.9158 | -168.002 | -51.3991 | -72.1749 | -53.4412 | -128.8178 | -53.741 | -57.4316 | -66.3816 | -110.4532 | -67.4001 | -68.4827 | -20.741 | -61.4295 | -27.099 | 83.2062 | -23.6061 | 5.1754 | -32.9866 | 114.4704 | -21.964 | -63.0449 | -25.282 | 21.898 | -23.8075 | 36.2504 | -27.367 | 65.7795 | -47.319 | -51.2329 | -53.327 | -56.5026 | -53.2097 | -67.3774 | -47.2804 | -56.2958 | -54.0501 | -60.8116 | -53.6046 | -59.5653 | -41.8646 | 154 | -46.9325 | -48.7568 | -45.4642 | -53.926 | -49.002 | -52.7855 | -49.3354 | -53.063 | 154 | -52.6285 | -50.3828 | -52.8353 | -49.6754 | -63.8431 | -43.5549 | -52.7615 | -50.3246 | -52.9886 | -49.4842 | -63.8634 | -43.7664 | -47.5656 | -49.6597 | -57.1443 | -50.0703 | -56.031 | -38.1391 | -47.6986 | -49.6015 | -57.2976 | -49.8791 | -56.0513 | -38.3506
155 | -3.6489 | 0 | -3.5671 | 0 | -3.7536 | 0 | -3.5296 | 0 | -56.958 | 114.9796 | -50.8165 | -110.4183 | -54.843 | 178.1388 | -50.9412 | 5.62 | -56.9428 | 99.7297 | -57.2283 | -0.2396 | -57.1828 | 168.9345 | -57.8606 | -90.9927 | -53.2627 | -141.3583 | -58.4347 | -82.4451 | -69.4608 | -7.942 | -62.6487 | -61.0422 | -23.5691 | -78.3552 | -24.8403 | 53.3508 | -22.6886 | -6.9946 | -28.3308 | 109.7123 | -25.5569 | -78.6246 | -23.905 | 9.5806 | -23.409 | 14.7504 | -26.2675 | 63.0574 | -47.1916 | -50.8098 | -53.0976 | -56.4143 | -53.3614 | -66.4462 | -47.1354 | -56.9195 | -54.4282 | -61.1315 | -53.3639 | -59.8296 | -41.7224 | 155 | -48.6712 | -49.1765 | -47.392 | -51.4306 | -50.8264 | -54.609 | -54.4202 | -52.6968 | 155 | -53.2706 | -50.7793 | -52.7654 | -49.7943 | -62.8791 | -43.3818 | -53.3524 | -50.6746 | -52.8847 | -49.6078 | -62.9166 | -43.6058 | -47.1609 | -49.4487 | -57.4826 | -49.7968 | -56.2625 | -37.9688 | -47.2427 | -49.344 | -57.6019 | -49.6103 | -56.3 | -38.1928
156 | -3.6455 | 0 | -3.5836 | 0 | -3.7633 | 0 | -3.5348 | 0 | -54.5944 | 102.6034 | -52.8765 | -90.0531 | -55.3405 | 156.1545 | -52.6482 | 7.4046 | -55.2584 | 78.1039 | -54.0304 | -18.7695 | -55.2931 | 144.8731 | -65.9769 | 4.6707 | -54.1143 | -153.6657 | -74.1578 | -86.2888 | -60.4221 | -5.7543 | -59.6573 | -76.462 | -28.5451 | -84.0126 | -24.2393 | 25.1066 | -23.2499 | -20.4083 | -25.5708 | 94.5318 | -32.3904 | -78.8394 | -23.7087 | -5.6005 | -25.0201 | -5.0448 | -25.1661 | 55.5013 | -47.0616 | -50.6281 | -52.8734 | -56.5771 | -54.0451 | -66.3564 | -46.9703 | -57.0934 | -54.4247 | -61.2301 | -53.679 | -60.3566 | -41.4347 | 156 | -49.3734 | -49.2496 | -48.373 | -50.0627 | -51.4959 | -54.0875 | -58.6232 | -52.3157 | 156 | -53.4479 | -50.7792 | -52.9316 | -50.4615 | -62.7728 | -43.207 | -53.5098 | -50.6614 | -53.0423 | -50.2818 | -62.8216 | -43.4355 | -46.9826 | -49.2279 | -57.5846 | -50.0954 | -56.773 | -37.6714 | -47.0445 | -49.1101 | -57.6953 | -49.9157 | -56.8218 | -37.8999
157 | -3.6393 | 0 | -3.5863 | 0 | -3.7582 | 0 | -3.5363 | 0 | -53.2759 | 84.0469 | -50.1236 | -71.9484 | -57.1607 | 132.957 | -53.0311 | 18.6069 | -54.4815 | 54.7215 | -52.5162 | -40.5825 | -54.379 | 120.7435 | -53.8925 | 13.6361 | -55.546 | -159.7825 | -61.5378 | 42.123 | -56.5461 | -21.9643 | -58.2456 | -103.8395 | -33.0725 | -46.6435 | -25.0391 | -2.5518 | -25.3112 | -29.5264 | -24.1356 | 77.4187 | -35.2192 | -15.3175 | -24.8624 | -22.5801 | -29.6344 | -18.5463 | -24.695 | 44.6054 | -47.0232 | -50.6404 | -52.6505 | -56.949 | -55.1482 | -67.1873 | -46.8206 | -56.8246 | -54.1042 | -61.0511 | -54.5589 | -61.2465 | -41.0017 | 157 | -47.866 | -48.7802 | -46.9255 | -49.5513 | -49.7807 | -51.8275 | -52.0201 | -51.8698 | 157 | -53.1853 | -50.4649 | -53.3097 | -51.5619 | -63.601 | -43.0624 | -53.2383 | -50.346 | -53.4127 | -51.39 | -63.651 | -43.2843 | -47.0011 | -49.0112 | -57.4118 | -50.9726 | -57.6602 | -37.2435 | -47.0541 | -48.8923 | -57.5148 | -50.8007 | -57.7102 | -37.4654
158 | -3.6281 | 0 | -3.5814 | 0 | -3.7732 | 0 | -3.5535 | 0 | -52.8821 | 62.9833 | -46.9087 | -76.6781 | -62.5024 | 105.3445 | -51.2488 | 25.0339 | -54.3105 | 28.8954 | -52.2473 | -60.1822 | -54.1738 | 95.3998 | -49.3019 | -9.1443 | -57.07 | -152.3183 | -55.1979 | 18.4266 | -54.355 | -40.0422 | -57.1702 | -135.7349 | -28.7093 | -21.791 | -27.5962 | -30.1926 | -28.2388 | -22.6255 | -23.7933 | 60.7064 | -29.1586 | -4.8689 | -27.5004 | -37.4706 | -38.0508 | 22.6677 | -25.3633 | 30.177 | -46.9832 | -50.4562 | -52.6158 | -57.1199 | -56.284 | -68.1085 | -46.8158 | -56.5701 | -53.6594 | -60.726 | -56.1518 | -61.7654 | -40.5009 | 158 | -45.8355 | -47.8629 | -44.706 | -49.9018 | -47.5617 | -49.7819 | -47.777 | -51.2202 | 158 | -52.942 | -50.0313 | -53.4918 | -52.7026 | -64.5271 | -43.0426 | -52.9887 | -49.8862 | -53.5664 | -52.5108 | -64.555 | -43.2623 | -46.8281 | -48.9877 | -57.0979 | -52.5704 | -58.184 | -36.7277 | -46.8748 | -48.8426 | -57.1725 | -52.3786 | -58.2119 | -36.9474
159 | -3.6548 | 0 | -3.5839 | 0 | -3.7836 | 0 | -3.5715 | 0 | -53.2897 | 40.9445 | -44.7975 | -90.1188 | -83.9741 | 177.1382 | -49.2437 | 18.9645 | -55.2356 | -4.717 | -52.7936 | -81.8124 | -54.4879 | 68.7246 | -46.9303 | -34.3196 | -55.9273 | -142.9296 | -52.4084 | -5.8383 | -52.7045 | -61.3546 | -57.5253 | -170.6963 | -25.8304 | -31.9997 | -33.1111 | -63.0021 | -28.2928 | -1.5006 | -24.5581 | 45.6668 | -26.7415 | -17.9588 | -32.3786 | -41.0571 | -29.8145 | 67.4795 | -27.3249 | 16.266 | -47.0793 | -49.9626 | -53.0565 | -56.7238 | -56.2629 | -68.2009 | -46.9237 | -56.6742 | -52.9947 | -60.5995 | -58.5292 | -60.8578 | -39.9916 | 159 | -44.2223 | -47.0805 | -42.9852 | -50.8328 | -45.786 | -48.3369 | -45.5616 | -50.1381 | 159 | -53.0194 | -49.3399 | -53.069 | -52.679 | -64.617 | -43.1401 | -53.0903 | -49.2111 | -53.1523 | -52.4793 | -64.6294 | -43.3522 | -46.3078 | -49.4017 | -56.9447 | -54.9453 | -57.2739 | -36.208 | -46.3787 | -49.2729 | -57.028 | -54.7456 | -57.2863 | -36.4201
160 | -3.6775 | 0 | -3.5855 | 0 | -3.8207 | 0 | -3.6084 | 0 | -54.8072 | 16.9395 | -43.7185 | -107.3107 | -62.4667 | -147.7432 | -48.0189 | 6.8316 | -57.7345 | -55.9607 | -54.2043 | -105.0242 | -55.4642 | 39.9281 | -45.8355 | -60.4065 | -53.3344 | -146.7964 | -51.2866 | -29.8224 | -51.9414 | -89.6617 | -57.8084 | 152.1135 | -25.2387 | -48.1857 | -46.7426 | -170.3638 | -25.6423 | 3.6042 | -25.7964 | 37.0501 | -26.8571 | -32.9023 | -35.7148 | 7.3497 | -25.0874 | 54.6082 | -31.5768 | 10.9376 | -47.2606 | -49.2927 | -54.0049 | -55.9247 | -53.7723 | -68.6481 | -47.2457 | -57.1449 | -52.2048 | -61.1324 | -58.273 | -59.4379 | -39.6301 | 160 | -43.3396 | -46.8255 | -42.0722 | -52.1827 | -44.7404 | -47.7799 | -44.5369 | -48.9647 | 160 | -53.4674 | -48.5273 | -52.2472 | -50.1868 | -65.0626 | -43.425 | -53.5594 | -48.3841 | -52.3163 | -49.9516 | -65.0397 | -43.6373 | -45.6152 | -50.3274 | -57.4549 | -54.6875 | -55.8524 | -35.8094 | -45.7072 | -50.1842 | -57.524 | -54.4523 | -55.8295 | -36.0217
161 | -3.6775 | 0 | -3.6097 | 0 | -3.842 | 0 | -3.6246 | 0 | -57.9213 | -2.1464 | -43.6397 | -126.135 | -59.26 | -163.9535 | -47.7753 | -7.1956 | -62.4153 | -142.1725 | -58.1346 | -126.3748 | -57.4085 | 10.2893 | -45.7234 | -87.2005 | -52.0152 | -160.0377 | -51.4077 | -52.9067 | -53.3812 | -125.4509 | -57.7283 | 117.227 | -26.454 | -64.7037 | -33.6681 | 90.3793 | -24.0023 | -6.7294 | -27.1563 | 35.3059 | -28.9422 | -47.894 | -31.1987 | 23.2403 | -23.6155 | 35.5702 | -39.063 | 49.8722 | -47.6246 | -48.6225 | -54.4306 | -55.1246 | -51.1285 | -68.6225 | -47.8675 | -57.9084 | -51.7556 | -62.6839 | -53.9573 | -58.4592 | -39.5459 | 161 | -43.3673 | -47.2405 | -42.1126 | -54.8205 | -44.5749 | -48.6524 | -44.4746 | -49.0082 | 161 | -54.2309 | -48.0781 | -51.4471 | -47.5188 | -65.0128 | -44.0255 | -54.2987 | -47.9136 | -51.5 | -47.2865 | -64.9979 | -44.2429 | -44.945 | -50.7531 | -59.0064 | -50.3476 | -54.8495 | -35.7039 | -45.0128 | -50.5886 | -59.0593 | -50.1153 | -54.8346 | -35.9213
162 | -3.6755 | 0 | -3.6301 | 0 | -3.8575 | 0 | -3.6464 | 0 | -62.0897 | -10.1665 | -44.7105 | -144.7624 | -57.2561 | -178.2611 | -48.2216 | -19.6567 | -61.3834 | 128.4954 | -68.9783 | -149.2083 | -60.2597 | -16.4612 | -46.7314 | -114.7823 | -51.8244 | -173.1585 | -52.7493 | -74.1207 | -58.1841 | -159.9203 | -57.4826 | 86.2198 | -29.7109 | -74.4339 | -29.0682 | 59.2639 | -24.0077 | -22.3926 | -27.6391 | 39.6876 | -33.4844 | -47.1269 | -28.3284 | 13.5568 | -23.9994 | 17.227 | -32.1237 | 105.2476 | -47.8911 | -48.0833 | -53.9912 | -54.5122 | -50.4536 | -66.3567 | -48.3489 | -58.5684 | -51.9685 | -64.8098 | -51.9582 | -57.9239 | -39.7019 | 162 | -44.4007 | -47.85 | -43.099 | -55.6308 | -45.4155 | -51.0954 | -45.479 | -50.0549 | 162 | -54.8929 | -48.293 | -50.8367 | -46.8235 | -62.7266 | -44.4914 | -54.9383 | -48.111 | -50.8658 | -46.5961 | -62.7103 | -44.7025 | -44.4078 | -50.3157 | -61.1343 | -48.3281 | -54.2938 | -35.8444 | -44.4532 | -50.1337 | -61.1634 | -48.1007 | -54.2775 | -36.0555
163 | -3.6871 | 0 | -3.6333 | 0 | -3.8734 | 0 | -3.6289 | 0 | -66.3353 | 1.9334 | -47.2362 | -158.6511 | -55.7911 | 159.5466 | -49.1922 | -30.5849 | -59.6731 | 86.8728 | -65.7079 | 9.0423 | -63.8741 | -40.4345 | -49.1114 | -143.211 | -52.0678 | 173.3464 | -55.4329 | -90.6059 | -68.2762 | 170.8326 | -57.0447 | 55.7777 | -34.6031 | -58.1146 | -27.6369 | 32.478 | -26.0664 | -38.0796 | -26.7466 | 40.5448 | -35.5521 | -0.3642 | -27.5161 | -2.3735 | -26.4818 | 5.1148 | -26.4831 | 98.8197 | -47.9411 | -47.8063 | -53.6981 | -54.3044 | -50.9294 | -64.9039 | -48.563 | -58.0219 | -52.2496 | -67.2817 | -51.6059 | -58.1273 | -40.0108 | 163 | -46.6225 | -48.7436 | -45.0572 | -53.9984 | -47.2372 | -54.6587 | -47.6681 | -50.7907 | 163 | -54.3348 | -48.5625 | -50.6173 | -47.2961 | -61.2706 | -44.6896 | -54.3886 | -48.3762 | -50.6755 | -47.056 | -61.275 | -44.9341 | -44.1192 | -50.011 | -63.5946 | -47.9726 | -54.494 | -36.1374 | -44.173 | -49.8247 | -63.6528 | -47.7325 | -54.4984 | -36.3819
164 | -3.6995 | 0 | -3.628 | 0 | -3.8652 | 0 | -3.6518 | 0 | -65.6388 | 32.8451 | -51.2252 | -157.2094 | -55.2418 | 134.392 | -50.9194 | -38.391 | -58.6385 | 63.5649 | -57.2953 | -18.0188 | -69.7181 | -59.3732 | -54.1585 | -172.7276 | -53.04 | 160.992 | -59.7397 | -95.8021 | -71.727 | -6.1644 | -57.8445 | 29.5505 | -32.6144 | -17.7494 | -28.0883 | 6.6006 | -31.2241 | -40.3647 | -25.3164 | 32.4152 | -30.6523 | 16.4648 | -28.5927 | -19.1579 | -30.6555 | 19.9777 | -23.508 | 85.4097 | -47.9475 | -47.8097 | -53.4526 | -54.7913 | -51.9241 | -64.423 | -48.5577 | -55.6621 | -52.3088 | -68.3468 | -51.8975 | -59.7636 | -40.1783 | 164 | -49.6634 | -50.1174 | -47.5701 | -52.0598 | -50.5007 | -59.081 | -51.8423 | -51.755 | 164 | -51.9626 | -48.6093 | -51.0918 | -48.2961 | -60.795 | -44.6925 | -52.0341 | -48.4436 | -51.1395 | -48.0589 | -60.7712 | -44.9059 | -44.1102 | -49.7531 | -64.6473 | -48.2695 | -56.1356 | -36.3131 | -44.1817 | -49.5874 | -64.695 | -48.0323 | -56.1118 | -36.5265
165 | -3.7138 | 0 | -3.6499 | 0 | -3.8915 | 0 | -3.6564 | 0 | -61.9856 | 31.6475 | -52.3545 | -127.6526 | -56.0385 | 102.774 | -53.1485 | -34.7613 | -57.6462 | 41.213 | -54.5591 | -44.3603 | -79.1417 | -11.5057 | -72.0724 | 138.5247 | -54.8691 | 151.2507 | -64.3133 | -68.049 | -62.6459 | -29.4138 | -60.5927 | 7.3927 | -28.8611 | -19.8146 | -31.1287 | -19.4263 | -34.0843 | 18.792 | -24.9206 | 16.2994 | -28.0268 | 5.0753 | -31.8036 | -33.1145 | -28.6044 | 55.8749 | -22.2984 | 69.5919 | -47.9577 | -47.8829 | -52.9123 | -56.0944 | -53.2741 | -64.8517 | -48.4741 | -53.3134 | -52.2881 | -65.7593 | -52.6929 | -64.7665 | -40.0054 | 165 | -50.4877 | -51.4292 | -48.4898 | -51.1298 | -54.7713 | -60.3323 | -58.8443 | -53.302 | 165 | -49.5996 | -48.5743 | -52.3806 | -49.6242 | -61.2018 | -44.5826 | -49.6635 | -48.3966 | -52.438 | -49.3826 | -61.1953 | -44.8177 | -44.1691 | -49.1985 | -62.0455 | -49.043 | -61.1166 | -36.1139 | -44.233 | -49.0208 | -62.1029 | -48.8014 | -61.1101 | -36.349
166 | -3.7287 | 0 | -3.6554 | 0 | -3.9265 | 0 | -3.672 | 0 | -60.0573 | 15.3862 | -48.9298 | -114.9481 | -58.5402 | 60.4183 | -53.2296 | -18.8917 | -57.1398 | 14.92 | -53.8987 | -62.3632 | -69.2756 | 26.0753 | -56.4912 | -39.3834 | -57.5997 | 153.9512 | -60.5803 | -31.1487 | -58.6875 | -45.7923 | -67.8931 | 23.0842 | -27.3293 | -34.4744 | -39.9769 | -49.5681 | -26.6671 | 33.2253 | -25.5262 | -4.4206 | -27.45 | -6.9586 | -38.4699 | -18.9645 | -23.8178 | 55.266 | -21.846 | 55.7028 | -47.9631 | -47.5781 | -52.2123 | -57.5725 | -54.8421 | -65.9804 | -48.3975 | -52.032 | -52.174 | -62.6124 | -53.8741 | -80.4265 | -39.3608 | 166 | -48.187 | -51.1505 | -46.6508 | -51.3038 | -53.8729 | -56.2969 | -54.8404 | -54.8769 | 166 | -48.3033 | -48.4453 | -53.8438 | -51.1867 | -62.325 | -44.471 | -48.3766 | -48.2475 | -53.9005 | -50.9156 | -62.3084 | -44.7255 | -43.8494 | -48.4836 | -58.8837 | -50.2187 | -76.7711 | -35.4343 | -43.9227 | -48.2858 | -58.9404 | -49.9476 | -76.7545 | -35.6888
167 | -3.7605 | 0 | -3.6592 | 0 | -3.9715 | 0 | -3.6758 | 0 | -59.34 | -3.5007 | -45.8036 | -121.5558 | -62.1107 | -17.2401 | -50.9911 | -13.8709 | -57.1787 | -16.2746 | -53.4433 | -77.3848 | -63.8914 | 8.8944 | -50.2206 | -68.2274 | -58.4577 | 174.815 | -56.086 | -36.1232 | -56.1149 | -62.5612 | -61.0684 | 71.7269 | -28.0076 | -51.7375 | -38.9194 | 121.6091 | -22.9051 | 17.9882 | -27.682 | -30.5965 | -28.8724 | -15.4136 | -35.0486 | 41.7705 | -21.2139 | 39.4867 | -22.4443 | 44.3346 | -47.9552 | -46.8691 | -51.6659 | -57.5646 | -56.4005 | -67.4824 | -48.4014 | -51.9598 | -51.9128 | -60.5224 | -55.5381 | -62.9871 | -38.523 | 167 | -45.5191 | -49.5709 | -44.1155 | -51.5148 | -49.4541 | -52.7432 | -48.9451 | -53.3212 | 167 | -48.1993 | -48.1523 | -53.8041 | -52.7413 | -63.8232 | -44.4299 | -48.3006 | -47.9413 | -53.8888 | -52.429 | -63.8066 | -44.7256 | -43.1086 | -47.9054 | -56.7619 | -51.8789 | -59.3279 | -34.5515 | -43.2099 | -47.6944 | -56.8466 | -51.5666 | -59.3113 | -34.8472
168 | -3.7631 | 0 | -3.6808 | 0 | -4.0303 | 0 | -3.6792 | 0 | -59.1427 | -23.9849 | -43.7613 | -136.972 | -58.9585 | -93.7099 | -49.017 | -20.5554 | -57.3805 | -59.3126 | -53.2492 | -92.8999 | -60.3706 | -13.3951 | -47.0719 | -96.3138 | -55.2528 | -170.6607 | -53.9863 | -52.4694 | -54.249 | -81.9677 | -55.6723 | 55.8486 | -31.3053 | -63.1847 | -30.0026 | 90.459 | -21.1237 | -2.1441 | -32.3729 | -65.0959 | -31.78 | -8.6198 | -29.5362 | 36.4919 | -20.2346 | 19.6515 | -23.7777 | 38.6361 | -47.9182 | -45.9279 | -51.5162 | -56.0901 | -57.1839 | -68.7873 | -48.4347 | -52.9483 | -51.3725 | -59.0988 | -58.0753 | -57.7686 | -37.8748 | 168 | -43.5116 | -48.0726 | -42.2671 | -51.0617 | -46.2844 | -50.6193 | -45.7959 | -50.245 | 168 | -49.1852 | -47.6094 | -52.327 | -53.5031 | -65.1065 | -44.4044 | -49.2675 | -47.3422 | -52.4109 | -53.1536 | -65.1081 | -44.7555 | -42.1648 | -47.7531 | -55.3357 | -54.3945 | -54.0878 | -33.8445 | -42.2471 | -47.4859 | -55.4196 | -54.045 | -54.0894 | -34.1956
169 | -3.786 | 0 | -3.7351 | 0 | -4.0542 | 0 | -3.6917 | 0 | -59.6381 | -49.5968 | -42.7757 | -156.3522 | -55.4642 | -143.3945 | -47.6871 | -32.3397 | -56.7074 | -126.5841 | -53.3448 | -117.1122 | -57.5126 | -39.1255 | -45.4379 | -124.9527 | -51.7924 | 179.3548 | -53.7587 | -68.2715 | -52.5095 | -112.1438 | -54.0359 | 32.9795 | -37.1752 | -33.3806 | -26.6571 | 64.7343 | -20.9303 | -24.1852 | -40.6391 | -147.8589 | -31.0463 | 22.7339 | -26.9448 | 16.9844 | -20.6712 | -1.6347 | -24.7716 | 42.1813 | -47.8906 | -45.0495 | -52.0235 | -54.6054 | -54.0156 | -69.3893 | -48.5008 | -55.1597 | -50.454 | -57.9187 | -58.4695 | -55.0855 | -37.5473 | 169 | -42.4639 | -46.9349 | -41.2821 | -50.1749 | -44.3202 | -49.3581 | -44.3478 | -47.9108 | 169 | -51.3737 | -46.668 | -50.8194 | -50.2805 | -65.6542 | -44.4466 | -51.4246 | -46.3998 | -50.9137 | -49.9614 | -65.6976 | -44.8091 | -41.2635 | -48.2375 | -54.1327 | -54.7344 | -51.3504 | -33.4931 | -41.3144 | -47.9693 | -54.227 | -54.4153 | -51.3938 | -33.8556
170 | -3.8101 | 0 | -3.7606 | 0 | -4.0712 | 0 | -3.7129 | 0 | -62.9759 | -74.8412 | -42.9463 | -178.2776 | -54.9874 | -174.5054 | -47.1495 | -48.053 | -55.9964 | 145.9562 | -56.8641 | -151.0708 | -56.1329 | -70.9921 | -44.8322 | -154.2655 | -50.2386 | 157.5528 | -54.1065 | -76.9472 | -54.3838 | -161.7776 | -54.4328 | 20.3727 | -31.2407 | 12.2298 | -25.3953 | 41.6723 | -22.3777 | -45.7827 | -34.4206 | 117.7371 | -26.8964 | 28.9261 | -26.3811 | -8.3166 | -22.8872 | -23.9292 | -24.7959 | 47.4593 | -48.3418 | -44.4649 | -52.5163 | -53.0098 | -49.6348 | -69.2892 | -49.0184 | -59.8916 | -49.7515 | -57.2841 | -51.8895 | -54.3291 | -37.5995 | 170 | -42.6426 | -46.5178 | -41.4219 | -51.1103 | -43.4901 | -50.0152 | -43.9409 | -47.7694 | 170 | -56.0815 | -45.9414 | -49.1997 | -45.8742 | -65.5286 | -44.9472 | -56.131 | -45.6803 | -49.2969 | -45.5636 | -65.5763 | -45.3055 | -40.6548 | -48.7062 | -53.474 | -48.1289 | -50.5685 | -33.5283 | -40.7043 | -48.4451 | -53.5712 | -47.8183 | -50.6162 | -33.8866
171 | -3.8387 | 0 | -3.7714 | 0 | -4.0701 | 0 | -3.7127 | 0 | -66.5761 | -75.6459 | -44.7062 | 159.9408 | -53.378 | 163.2885 | -47.438 | -62.0353 | -57.7609 | 84.2668 | -69.3688 | 143.2369 | -56.2941 | -96.5568 | -45.2701 | 175.3847 | -50.3648 | 140.0082 | -54.5292 | -83.3926 | -63.5218 | 157.9735 | -53.418 | 19.4671 | -25.9705 | 4.5439 | -25.4337 | 21.3942 | -26.3301 | -62.6304 | -29.1482 | 82.738 | -23.8771 | 18.8011 | -27.319 | -34.0044 | -28.4438 | -42.1929 | -23.8498 | 51.5196 | -48.2901 | -44.3114 | -51.8066 | -51.5479 | -49.4542 | -64.2763 | -49.3573 | -70.6951 | -50.2019 | -58.3183 | -50.4394 | -54.2576 | -38.0008 | 171 | -44.1285 | -47.0043 | -42.8408 | -51.9488 | -43.8449 | -51.9954 | -44.226 | -48.4799 | 171 | -66.8564 | -46.3632 | -47.7092 | -45.6828 | -60.5049 | -45.2872 | -66.9237 | -46.1318 | -47.8352 | -45.3841 | -60.5636 | -45.6446 | -40.4727 | -47.9679 | -54.4796 | -46.668 | -50.4862 | -33.9307 | -40.54 | -47.7365 | -54.6056 | -46.3693 | -50.5449 | -34.2881
172 | -3.8667 | 0 | -3.7596 | 0 | -4.0634 | 0 | -3.7504 | 0 | -68.7875 | -65.7789 | -48.4536 | 147.2019 | -52.9403 | 137.2878 | -48.2348 | -76.7572 | -59.1361 | 55.9416 | -59.8917 | -8.6009 | -56.7622 | -118.8441 | -47.068 | 144.4297 | -50.6879 | 123.8796 | -54.4845 | -87.2155 | -78.2952 | -36.1697 | -51.5557 | 8.6549 | -23.3788 | -14.1376 | -26.975 | 3.0006 | -34.2094 | -41.8323 | -27.2158 | 52.3345 | -22.4347 | 3.014 | -30.2004 | -64.8154 | -39.3159 | 46.8804 | -22.7451 | 48.8247 | -47.8447 | -44.6329 | -51.526 | -51.3135 | -50.3604 | -59.7071 | -48.994 | -60.7626 | -50.4643 | -60.8495 | -50.6776 | -54.6962 | -38.7092 | 172 | -47.1018 | -47.8603 | -45.1831 | -51.351 | -45.1877 | -52.4541 | -45.201 | -48.0857 | 172 | -56.8959 | -46.5976 | -47.4468 | -46.6008 | -55.9475 | -44.9306 | -57.003 | -46.4009 | -47.5631 | -46.297 | -55.9567 | -45.2436 | -40.7662 | -47.6593 | -56.9828 | -46.918 | -50.9366 | -34.6458 | -40.8733 | -47.4626 | -57.0991 | -46.6142 | -50.9458 | -34.9588
173 | -3.871 | 0 | -3.761 | 0 | -4.058 | 0 | -3.7733 | 0 | -66.5994 | -50.8448 | -52.763 | 161.1661 | -53.188 | 105.2449 | -50.3971 | -89.3117 | -58.9188 | 34.446 | -54.6014 | -42.4255 | -58.0161 | -139.669 | -50.6157 | 115.9812 | -51.7298 | 106.5086 | -54.8304 | -95.5624 | -64.4884 | -54.0512 | -51.2148 | -7.5974 | -22.4605 | -34.7532 | -30.3885 | -5.9356 | -28.6241 | 14.1878 | -27.165 | 22.264 | -22.2195 | -13.9912 | -35.8421 | -113.8649 | -26.1493 | 64.4922 | -22.0549 | 42.4829 | -47.4711 | -45.4283 | -51.3193 | -52.5141 | -51.4789 | -56.6588 | -48.3509 | -55.5268 | -50.6014 | -66.6009 | -51.3001 | -56.3276 | -39.4226 | 173 | -49.8669 | -49.7356 | -47.475 | -50.2007 | -47.7027 | -52.8208 | -47.0938 | -48.3475 | 173 | -51.6558 | -46.7304 | -48.6431 | -47.7179 | -52.8978 | -44.2929 | -51.7658 | -46.5434 | -48.7408 | -47.4209 | -52.8855 | -44.5776 | -41.5573 | -47.4483 | -62.7299 | -47.5391 | -52.5666 | -35.3646 | -41.6673 | -47.2613 | -62.8276 | -47.2421 | -52.5543 | -35.6493
174 | -3.8722 | 0 | -3.7611 | 0 | -4.0787 | 0 | -3.7871 | 0 | -63.307 | -63.8071 | -51.9961 | -171.4814 | -55.3037 | 68.6735 | -53.5625 | -84.6372 | -58.774 | 7.9053 | -52.8035 | -65.0139 | -60.1702 | -154.6535 | -57.6482 | 88.0021 | -54.0265 | 90.2991 | -56.5625 | -96.0356 | -60.13 | -67.1101 | -52.0914 | -16.3042 | -22.9382 | -55.4083 | -34.2974 | 16.1281 | -23.2413 | 2.617 | -28.8045 | -13.1688 | -23.4073 | -29.3365 | -36.8412 | 142.3783 | -21.6991 | 44.764 | -22.04 | 36.441 | -47.3071 | -46.1443 | -50.8752 | -55.3384 | -52.7837 | -54.8083 | -47.7962 | -53.5826 | -50.7081 | -82.1908 | -52.1947 | -58.567 | -39.7012 | 174 | -50.1185 | -52.0788 | -47.9691 | -50.2142 | -51.7803 | -53.8312 | -49.9553 | -49.5446 | 174 | -49.7104 | -46.8359 | -51.4662 | -49.0226 | -51.0472 | -43.7175 | -49.8215 | -46.6294 | -51.5513 | -48.705 | -51.0212 | -44.0091 | -42.2721 | -47.003 | -78.3186 | -48.4336 | -54.8059 | -35.6225 | -42.3832 | -46.7965 | -78.4037 | -48.116 | -54.7799 | -35.9141
175 | -3.8707 | 0 | -3.7841 | 0 | -4.1177 | 0 | -3.7998 | 0 | -61.9792 | -87.2132 | -48.8896 | -165.1213 | -59.0164 | 15.06 | -53.4337 | -65.1662 | -59.1678 | -23.5722 | -51.8584 | -77.5176 | -63.1696 | -160.4648 | -67.0441 | -108.0784 | -57.8264 | 84.2037 | -56.3078 | -80.4612 | -57.5626 | -81.1139 | -51.9896 | -10.7713 | -25.2712 | -71.984 | -30.6332 | 45.2494 | -20.6681 | -18.8338 | -32.7965 | -61.436 | -26.4934 | -37.2737 | -30.6567 | 85.4524 | -19.8101 | 23.2637 | -22.4155 | 32.961 | -47.2716 | -45.9919 | -50.3659 | -58.8419 | -54.0567 | -53.8122 | -47.5146 | -52.9771 | -50.7301 | -66.4091 | -53.2295 | -58.1373 | -38.9865 | 175 | -48.2969 | -51.9513 | -46.2038 | -50.4653 | -56.3282 | -53.3962 | -50.5246 | -50.1202 | 175 | -49.1064 | -46.8594 | -54.9712 | -50.2726 | -50.0281 | -43.3969 | -49.193 | -46.6124 | -55.0421 | -49.939 | -50.0124 | -43.7148 | -42.1212 | -46.4952 | -62.5384 | -49.4454 | -54.3532 | -34.8688 | -42.2078 | -46.2482 | -62.6093 | -49.1118 | -54.3375 | -35.1867
176 | -3.8836 | 0 | -3.7821 | 0 | -4.1976 | 0 | -3.8077 | 0 | -62.2 | -109.3283 | -46.085 | -173.4234 | -60.3545 | -67.7641 | -51.1315 | -63.1022 | -60.1334 | -60.6022 | -50.4139 | -89.2327 | -66.2789 | -146.5229 | -52.782 | -142.978 | -62.5849 | 105.8771 | -53.607 | -78.9434 | -55.8933 | -95.1035 | -49.3685 | -12.1868 | -30.3708 | -72.9071 | -26.5537 | 39.316 | -19.7486 | -43.5279 | -33.9017 | -154.5345 | -30.2784 | -18.871 | -27.5352 | 50.7536 | -19.4241 | 1.0533 | -22.6462 | 34.2975 | -47.3516 | -45.0053 | -50.0858 | -58.2266 | -55.2071 | -53.3295 | -47.4423 | -52.6546 | -50.6492 | -61.5517 | -54.2743 | -55.514 | -37.8556 | 176 | -45.8243 | -50.3251 | -43.8269 | -49.5931 | -52.1775 | -51.446 | -46.7381 | -48.3295 | 176 | -48.771 | -46.7656 | -54.343 | -51.425 | -49.5474 | -43.2447 | -48.8725 | -46.4516 | -54.4189 | -51.0095 | -49.5218 | -43.6346 | -41.1217 | -46.2022 | -57.6681 | -50.4922 | -51.7319 | -33.658 | -41.2232 | -45.8882 | -57.744 | -50.0767 | -51.7063 | -34.0479
177 | -3.8991 | 0 | -3.8065 | 0 | -4.2535 | 0 | -3.8219 | 0 | -63.1678 | -122.1025 | -44.2073 | 168.3587 | -56.5726 | -130.7457 | -49.6563 | -70.4788 | -59.7911 | -103.7432 | -49.118 | -107.0811 | -64.8256 | -117.934 | -47.6966 | -173.6049 | -59.4552 | 143.2296 | -51.9066 | -89.0291 | -54.8417 | -110.0782 | -47.587 | -27.445 | -31.7096 | -21.6601 | -24.5339 | 22.8285 | -20.1415 | -71.0728 | -27.9682 | 142.8485 | -27.5605 | 16.1776 | -26.2628 | 19.5102 | -20.3266 | -21.0031 | -22.0007 | 36.9583 | -47.458 | -43.7331 | -49.949 | -54.4775 | -56.1103 | -53.2448 | -47.5604 | -52.0191 | -50.5202 | -59.1424 | -55.5682 | -53.2652 | -36.8569 | 177 | -43.9106 | -49.0816 | -42.1445 | -48.0959 | -47.338 | -49.9759 | -43.8857 | -46.6068 | 177 | -48.12 | -46.6211 | -50.5784 | -52.3038 | -49.4383 | -43.3069 | -48.2126 | -46.2667 | -50.6556 | -51.8568 | -49.4229 | -43.7385 | -39.834 | -46.0499 | -55.2433 | -51.7617 | -49.4587 | -32.6034 | -39.9266 | -45.6955 | -55.3205 | -51.3147 | -49.4433 | -33.035
178 | -3.9359 | 0 | -3.8072 | 0 | -4.3196 | 0 | -3.8641 | 0 | -63.084 | -126.8416 | -43.7132 | 144.2236 | -54.2104 | -171.7701 | -48.7258 | -78.2502 | -57.8346 | -152.0751 | -48.9092 | -132.2407 | -60.5055 | -113.4016 | -44.9641 | 154.2991 | -54.7384 | 137.6077 | -51.3912 | -98.8933 | -53.7295 | -126.9201 | -46.8586 | -47.1251 | -25.3073 | -11.7159 | -23.7953 | 3.9088 | -21.9919 | -101.8128 | -24.0374 | 105.303 | -23.2579 | 15.5297 | -26.4849 | -10.6589 | -23.138 | -41.1212 | -20.5482 | 36.6481 | -47.5173 | -42.5493 | -49.9272 | -51.4079 | -56.0759 | -53.7211 | -47.772 | -51.0501 | -50.3461 | -58.1431 | -57.8619 | -51.7806 | -36.2161 | 178 | -43.2963 | -48.0833 | -41.6245 | -47.3768 | -44.4208 | -49.0707 | -42.2361 | -45.4962 | 178 | -47.1142 | -46.4102 | -47.472 | -52.2687 | -49.9139 | -43.4524 | -47.2429 | -46.0265 | -47.5438 | -51.7563 | -49.857 | -43.9079 | -38.6134 | -45.9913 | -54.2072 | -54.0547 | -47.9734 | -31.8965 | -38.7421 | -45.6076 | -54.279 | -53.5423 | -47.9165 | -32.352
179 | -3.9736 | 0 | -3.8284 | 0 | -4.369 | 0 | -3.9112 | 0 | -61.7112 | -139.3434 | -45.1424 | 116.6526 | -52.8458 | 154.1476 | -47.3436 | -88.242 | -53.9453 | 151.611 | -50.2618 | -163.3732 | -57.0001 | -125.8527 | -43.8176 | 121.2595 | -52.5817 | 120.2478 | -50.7661 | -102.5976 | -52.926 | -159.7804 | -48.1701 | -64.7234 | -21.6587 | -26.8852 | -24.3579 | -15.1731 | -26.3409 | -140.8702 | -21.6968 | 73.6927 | -20.6608 | 2.1149 | -27.9032 | -44.6926 | -29.647 | -51.3951 | -19.1115 | 28.8269 | -47.4096 | -41.8134 | -50.129 | -49.3589 | -52.3706 | -55.9463 | -47.9925 | -50.2401 | -49.9033 | -58.5042 | -58.8714 | -51.1815 | -35.9959 | 179 | -44.3806 | -46.3562 | -42.332 | -47.2956 | -43.0952 | -48.1034 | -41.8614 | -45.8743 | 179 | -46.2665 | -45.9297 | -45.3853 | -48.5422 | -52.1179 | -43.6235 | -46.4117 | -45.5343 | -45.4477 | -48.0016 | -52.0351 | -44.0813 | -37.8398 | -46.1554 | -54.5306 | -55.043 | -47.3531 | -31.6269 | -37.985 | -45.76 | -54.593 | -54.5024 | -47.2703 | -32.0847
180 | -4.0076 | 0 | -3.8287 | 0 | -4.3742 | 0 | -3.9325 | 0 | -62.555 | -155.1751 | -49.6177 | 93.8693 | -53.165 | 129.6242 | -46.4858 | -109.9994 | -53.6042 | 82.3564 | -56.2061 | 154.425 | -55.152 | -147.5979 | -44.1906 | 88.734 | -51.8524 | 97.9753 | -49.1837 | -111.6669 | -59.8271 | 143.6008 | -50.7574 | -64.5588 | -19.8314 | -47.3769 | -26.2272 | -30.5327 | -33.7804 | 133.5491 | -20.7579 | 44.4942 | -19.4746 | -14.6197 | -30.6398 | -89.028 | -32.9213 | 32.6773 | -18.3591 | 16.5557 | -47.3513 | -41.8656 | -50.2099 | -48.281 | -48.8904 | -61.7601 | -48.2779 | -50.1984 | -49.4295 | -58.7428 | -51.4498 | -51.9524 | -36.4582 | 180 | -47.878 | -45.6262 | -44.4641 | -49.3624 | -43.2164 | -47.9151 | -42.3233 | -47.9675 | 180 | -46.1908 | -45.4219 | -44.2734 | -45.0617 | -57.9314 | -43.9037 | -46.3697 | -45.0553 | -44.3485 | -44.5162 | -57.8276 | -44.3454 | -37.858 | -46.2023 | -54.7352 | -47.6211 | -48.1237 | -32.084 | -38.0369 | -45.8357 | -54.8103 | -47.0756 | -48.0199 | -32.5257
181 | -4.004 | 0 | -3.8043 | 0 | -4.317 | 0 | -3.9117 | 0 | -62.8315 | -154.7621 | -57.9454 | 111.0802 | -53.4055 | 103.5273 | -47.9224 | -132.8552 | -57.7023 | 43.6168 | -71.599 | -53.6013 | -54.9931 | -166.5656 | -45.8771 | 60.2391 | -52.399 | 77.9773 | -48.5759 | -128.2354 | -67.0078 | -101.923 | -49.7362 | -54.2198 | -19.3892 | -69.0237 | -29.1497 | -35.7201 | -27.4424 | 34.7904 | -20.4062 | 16.7304 | -19.4907 | -31.0993 | -33.2191 | -155.217 | -24.1235 | 35.1516 | -18.1494 | 3.7782 | -47.1628 | -42.7615 | -50.2063 | -48.573 | -49.7839 | -82.1052 | -48.0855 | -51.0006 | -49.5118 | -62.1754 | -50.7925 | -54.0084 | -37.8815 | 181 | -51.7451 | -47.3629 | -47.4937 | -51.9848 | -44.5888 | -47.6328 | -42.9803 | -47.8039 | 181 | -46.9966 | -45.5078 | -44.569 | -45.9796 | -78.3009 | -43.7685 | -47.1963 | -45.1948 | -44.6613 | -45.4669 | -78.1935 | -44.1738 | -38.7575 | -46.2023 | -58.1714 | -46.9882 | -50.2041 | -33.5645 | -38.9572 | -45.8893 | -58.2637 | -46.4755 | -50.0967 | -33.9698
182 | -3.9946 | 0 | -3.8196 | 0 | -4.2637 | 0 | -3.9228 | 0 | -60.9569 | -156.0492 | -54.8377 | 158.0269 | -55.0272 | 70.3802 | -51.5387 | -148.4057 | -60.8196 | 24.5079 | -57.0291 | -78.2563 | -55.3177 | 178.4457 | -48.5278 | 37.635 | -53.7029 | 60.3022 | -49.5678 | -143.6101 | -60.0174 | -116.1867 | -48.3233 | -58.8212 | -20.1719 | -90.1396 | -31.4522 | -22.0595 | -22.7235 | -6.8421 | -20.721 | -12.3808 | -20.5852 | -45.9818 | -31.3938 | 141.2166 | -20.6763 | 13.6128 | -18.4462 | -10.4629 | -47.0922 | -43.9778 | -50.4548 | -50.2563 | -50.9516 | -60.1575 | -47.8782 | -52.0645 | -49.6079 | -73.2766 | -51.4641 | -57.3067 | -39.6759 | 182 | -51.4101 | -50.6314 | -49.1076 | -52.253 | -46.729 | -48.2444 | -44.0019 | -46.996 | 182 | -48.0699 | -45.6133 | -46.2617 | -47.132 | -56.3379 | -43.6145 | -48.2449 | -45.3442 | -46.3335 | -46.6879 | -56.2347 | -43.9554 | -39.9832 | -46.4602 | -69.282 | -47.6445 | -53.4871 | -35.4122 | -40.1582 | -46.1911 | -69.3538 | -47.2004 | -53.3839 | -35.7531
183 | -3.9941 | 0 | -3.8399 | 0 | -4.2411 | 0 | -3.9109 | 0 | -58.6627 | -169.2576 | -51.7713 | 158.145 | -58.9591 | 22.6379 | -56.5573 | -132.8828 | -64.1403 | 2.4422 | -52.8944 | -91.7232 | -55.9159 | 165.7972 | -52.5406 | 18.2775 | -56.5172 | 43.1356 | -51.5175 | -147.6594 | -57.8348 | -127.3154 | -47.6495 | -64.4813 | -22.7125 | -108.792 | -29.7193 | -7.0893 | -20.4348 | -38.8707 | -21.9135 | -41.8727 | -22.9388 | -54.0557 | -28.8984 | 97.979 | -19.2567 | -9.179 | -19.4238 | -24.8152 | -47.1868 | -44.8341 | -50.5597 | -53.0423 | -51.9251 | -53.5724 | -47.8751 | -52.3817 | -49.6894 | -67.3946 | -52.1798 | -56.9208 | -40.911 | 183 | -50.3235 | -54.0281 | -48.5402 | -51.6803 | -49.8456 | -49.4853 | -45.2574 | -46.766 | 183 | -48.3876 | -45.6953 | -49.0482 | -48.0852 | -49.7325 | -43.634 | -48.5418 | -45.4483 | -49.1314 | -47.684 | -49.6615 | -43.9642 | -40.84 | -46.5656 | -63.4005 | -48.3399 | -53.0809 | -36.6699 | -40.9942 | -46.3186 | -63.4837 | -47.9387 | -53.0099 | -37.0001
184 | -3.9783 | 0 | -3.8518 | 0 | -4.2747 | 0 | -3.9131 | 0 | -57.541 | 170.0733 | -49.5995 | 154.736 | -61.5226 | -65.1117 | -54.1989 | -101.0433 | -71.1304 | -28.8436 | -49.6262 | -106.0807 | -57.0049 | 154.0716 | -62.73 | 16.2573 | -61.9123 | 32.8934 | -51.9555 | -139.1199 | -57.1039 | -139.7497 | -46.3876 | -65.5588 | -27.9185 | -114.3802 | -27.1366 | -13.3609 | -19.381 | -69.8545 | -23.7082 | -72.9321 | -25.9822 | -43.3763 | -27.5726 | 65.4822 | -19.0361 | -31.8913 | -21.2623 | -37.7314 | -47.3979 | -44.7739 | -50.4501 | -56.5112 | -52.7924 | -50.0434 | -48.051 | -51.8176 | -49.7087 | -60.6096 | -52.7893 | -52.7668 | -40.5227 | 184 | -48.7186 | -52.486 | -45.9061 | -49.3255 | -54.9892 | -49.865 | -45.2459 | -45.9234 | 184 | -47.8393 | -45.7304 | -52.5329 | -48.9406 | -46.1916 | -43.7763 | -47.9658 | -45.434 | -52.5981 | -48.5177 | -46.1303 | -44.1379 | -40.7956 | -46.4718 | -56.6313 | -48.9375 | -48.915 | -36.248 | -40.9221 | -46.1754 | -56.6965 | -48.5146 | -48.8537 | -36.6096
185 | -3.9848 | 0 | -3.8671 | 0 | -4.3579 | 0 | -3.9087 | 0 | -57.89 | 148.7724 | -47.216 | 143.607 | -57.0399 | -136.9854 | -50.838 | -105.9955 | -75.4584 | 172.6323 | -46.9373 | -127.7827 | -59.0715 | 145.7362 | -55.892 | 122.904 | -66.9072 | 87.0519 | -50.3833 | -137.6777 | -57.1043 | -149.3891 | -44.232 | -74.6915 | -30.7543 | -56.96 | -25.6429 | -29.1613 | -19.4376 | -100.1905 | -26.7147 | -105.2304 | -25.0403 | -16.2178 | -27.5767 | 38.5194 | -19.8411 | -55.2131 | -24.3423 | -46.7448 | -47.7062 | -43.7165 | -50.1755 | -57.2179 | -53.6554 | -47.7048 | -48.3749 | -50.9478 | -49.8091 | -57.1562 | -53.3476 | -49.3696 | -39.1723 | 185 | -46.4614 | -50.044 | -43.2356 | -46.527 | -53.9606 | -49.0863 | -43.0566 | -43.9912 | 185 | -46.963 | -45.8243 | -53.2331 | -49.7883 | -43.8377 | -44.017 | -47.0807 | -45.4512 | -53.3092 | -49.2975 | -43.7961 | -44.4662 | -39.7317 | -46.1907 | -53.1714 | -49.4805 | -45.5025 | -34.8144 | -39.8494 | -45.8176 | -53.2475 | -48.9897 | -45.4609 | -35.2636
186 | -4.0042 | 0 | -3.8672 | 0 | -4.4939 | 0 | -3.907 | 0 | -59.9365 | 133.7076 | -45.7223 | 120.7422 | -53.8471 | -178.5111 | -49.3342 | -117.4989 | -65.0425 | 135.8281 | -45.2776 | -156.1994 | -61.961 | 153.4773 | -47.7719 | 100.6063 | -59.9318 | 112.9575 | -49.2193 | -145.8333 | -57.2849 | -157.2866 | -42.5865 | -93.2614 | -23.5438 | -44.4331 | -25.5254 | -50.0412 | -20.4112 | -132.6055 | -31.1068 | -138.8952 | -21.258 | -13.2088 | -29.0522 | 12.8775 | -21.644 | -80.8354 | -28.4536 | -42.8293 | -48.0227 | -42.1026 | -49.7026 | -53.5383 | -54.6438 | -46.0323 | -48.8086 | -50.2596 | -49.9807 | -55.0742 | -53.9219 | -46.8963 | -37.7888 | 186 | -44.9599 | -48.8657 | -41.6686 | -44.6723 | -47.3622 | -48.3939 | -40.7677 | -42.365 | 186 | -46.2554 | -45.9765 | -49.5341 | -50.7766 | -42.1651 | -44.3147 | -46.3924 | -45.4868 | -49.6313 | -50.1499 | -42.1253 | -44.9016 | -38.0984 | -45.6984 | -51.07 | -50.0547 | -43.0291 | -33.2949 | -38.2354 | -45.2087 | -51.1672 | -49.428 | -42.9893 | -33.8818
187 | -4.0391 | 0 | -3.8748 | 0 | -4.622 | 0 | -3.9073 | 0 | -62.5503 | 139.0125 | -46.2811 | 89.7346 | -52.3526 | 150.8747 | -48.2932 | -128.0249 | -60.4893 | 117.7838 | -45.0581 | 169.253 | -61.3237 | -179.9804 | -43.9644 | 68.7481 | -55.8008 | 97.1891 | -48.907 | -153.1972 | -56.9103 | -159.5278 | -42.2556 | -117.6065 | -19.4532 | -60.6493 | -26.5799 | -74.0049 | -22.8812 | -168.8529 | -39.3596 | -177.4599 | -18.6386 | -23.188 | -32.5335 | -8.1903 | -25.6511 | -112.3 | -31.1726 | -12.4864 | -48.1592 | -40.7228 | -48.925 | -50.171 | -55.6045 | -44.9454 | -49.4178 | -49.8798 | -50.086 | -54.203 | -54.7655 | -45.2001 | -36.6902 | 187 | -45.2407 | -47.8878 | -41.5763 | -44.2121 | -43.6146 | -48.0588 | -39.4889 | -41.9276 | 187 | -45.8407 | -46.0469 | -46.1319 | -51.7297 | -41.0706 | -44.7958 | -46.005 | -45.464 | -46.2637 | -50.9825 | -41.0381 | -45.5105 | -36.6837 | -44.8859 | -50.1639 | -50.8907 | -41.3253 | -32.0682 | -36.848 | -44.303 | -50.2957 | -50.1435 | -41.2928 | -32.7829
188 | -4.1014 | 0 | -3.8765 | 0 | -4.6639 | 0 | -3.9084 | 0 | -61.4515 | 153.8878 | -50.4088 | 56.3786 | -52.3969 | 124.3191 | -46.9675 | -142.3249 | -56.7857 | 105.1938 | -46.7646 | 131.545 | -57.5935 | -175.3541 | -42.6631 | 34.9424 | -54.2017 | 75.2386 | -48.1781 | -157.17 | -56.1159 | -168.5536 | -44.1073 | -141.8983 | -17.2779 | -81.7087 | -29.2397 | -99.3072 | -28.0103 | 146.7371 | -45.0522 | -31.753 | -17.0767 | -38.3737 | -40.3646 | -7.0814 | -35.239 | -168.911 | -28.6993 | 11.5192 | -47.9031 | -40.1397 | -48.1748 | -48.3641 | -55.7117 | -44.917 | -49.9234 | -49.4998 | -49.9021 | -54.7672 | -56.2125 | -44.5936 | -36.2282 | 188 | -48.0754 | -46.3989 | -42.9871 | -45.3882 | -42.2401 | -47.1224 | -39.6572 | -43.4596 | 188 | -45.3984 | -45.8007 | -44.2627 | -51.8352 | -41.0405 | -45.2595 | -45.6233 | -45.2382 | -44.4557 | -51.0478 | -41.0086 | -46.015 | -36.0383 | -44.0734 | -50.6658 | -52.336 | -40.7171 | -31.5643 | -36.2632 | -43.5109 | -50.8588 | -51.5486 | -40.6852 | -32.3198
189 | -4.1339 | 0 | -3.8868 | 0 | -4.5667 | 0 | -3.9034 | 0 | -59.4861 | 153.586 | -63.6595 | 60.1757 | -53.4119 | 104.261 | -46.4347 | -165.2351 | -52.602 | 83.8206 | -51.0824 | 95.5225 | -54.8401 | 176.3578 | -43.3074 | 5.521 | -54.1941 | 55.0484 | -46.9571 | -166.6216 | -56.0135 | 162.9547 | -48.0568 | -152.2533 | -16.365 | -103.6647 | -35.2332 | -127.6407 | -36.5523 | 45.0018 | -33.7899 | -69.5793 | -16.4777 | -54.5779 | -39.9712 | 69.6795 | -31.938 | 46.5216 | -26.2312 | 13.1547 | -47.4212 | -40.5074 | -47.8441 | -48.2063 | -53.3001 | -46.4566 | -50.1563 | -48.8519 | -49.5245 | -57.2462 | -58.5274 | -45.3949 | -37.0764 | 189 | -52.1363 | -45.3247 | -45.0933 | -47.4848 | -42.6936 | -45.861 | -40.8361 | -46.5848 | 189 | -44.718 | -45.3906 | -44.0724 | -49.4133 | -42.5698 | -45.5896 | -44.9651 | -44.9578 | -44.3029 | -48.7334 | -42.5532 | -46.2529 | -36.3735 | -43.7102 | -53.1123 | -54.6406 | -41.5081 | -32.5097 | -36.6206 | -43.2774 | -53.3428 | -53.9607 | -41.4915 | -33.173
190 | -4.1465 | 0 | -3.9122 | 0 | -4.432 | 0 | -3.9137 | 0 | -57.5815 | 156.2302 | -55.7787 | 137.21 | -54.5059 | 85.7184 | -47.5999 | 166.682 | -50.9877 | 38.9656 | -57.8736 | 57.632 | -52.6797 | 161.8545 | -45.1097 | -15.3072 | -54.1634 | 33.5288 | -46.3268 | 177.752 | -72.7649 | 151.5349 | -50.9616 | -134.8981 | -16.4436 | -125.6778 | -50.2755 | 74.8446 | -28.6731 | -52.0025 | -29.1363 | -108.5414 | -16.5981 | -70.8111 | -32.9442 | 65.1066 | -25.9991 | 5.7158 | -24.9426 | 9.154 | -47.1146 | -41.3804 | -47.552 | -49.4232 | -49.3958 | -50.0132 | -50.2286 | -48.2484 | -48.9122 | -60.8224 | -53.006 | -48.0687 | -39.1135 | 190 | -51.0063 | -45.672 | -46.6448 | -48.8138 | -43.9725 | -45.4142 | -42.0659 | -49.2442 | 190 | -44.1019 | -44.7657 | -45.2767 | -45.4836 | -46.101 | -45.7966 | -44.3362 | -44.4802 | -45.5095 | -44.9638 | -46.0995 | -46.3149 | -37.2339 | -43.4055 | -56.6759 | -49.0938 | -44.1565 | -34.6815 | -37.4682 | -43.12 | -56.9087 | -48.574 | -44.155 | -35.1998
191 | -4.1235 | 0 | -3.9238 | 0 | -4.3435 | 0 | -3.9088 | 0 | -54.3895 | 147.4449 | -52.4899 | 114.0416 | -58.0444 | 62.1484 | -51.4247 | 140.8948 | -54.0487 | 9.1808 | -67.4518 | -41.7823 | -51.6717 | 144.4308 | -47.0969 | -25.9531 | -55.8329 | 12.1049 | -47.3207 | 161.6701 | -57.6115 | -137.9311 | -49.6886 | -118.8648 | -17.5688 | -146.8023 | -33.5564 | 12.7171 | -24.2155 | -91.4547 | -26.6084 | -144.7217 | -17.6566 | -85.8024 | -29.8315 | 45.6942 | -23.9381 | -19.9401 | -24.0069 | 7.0737 | -47.1027 | -42.3623 | -47.5876 | -51.2551 | -49.5754 | -56.0849 | -49.6191 | -47.9216 | -48.5727 | -66.0215 | -51.3808 | -53.2146 | -40.9899 | 191 | -49.6478 | -48.3034 | -48.854 | -52.4525 | -45.3868 | -45.675 | -43.1169 | -48.214 | 191 | -43.7981 | -44.4492 | -47.1316 | -45.6516 | -52.1611 | -45.2756 | -43.9978 | -44.2292 | -47.3463 | -45.2319 | -52.1761 | -45.7103 | -38.2388 | -43.4641 | -61.898 | -47.457 | -49.2908 | -36.6464 | -38.4385 | -43.2441 | -62.1127 | -47.0373 | -49.3058 | -37.0811
192 | -4.1029 | 0 | -3.9261 | 0 | -4.3109 | 0 | -3.9384 | 0 | -52.3141 | 130.3059 | -53.7092 | 94.2539 | -69.9707 | 42.474 | -59.5229 | 133.1501 | -57.4183 | -1.5203 | -58.0642 | -105.9588 | -51.2348 | 127.481 | -48.6015 | -31.2637 | -59.0772 | -8.5582 | -49.1802 | 155.6628 | -55.3279 | -163.4232 | -48.0284 | -113.8545 | -20.0432 | -164.9608 | -28.9298 | -16.6705 | -21.8868 | -122.7158 | -24.9355 | 179.9806 | -19.5181 | -96.2954 | -28.927 | 21.9928 | -23.1037 | -42.9914 | -23.1664 | 3.1568 | -47.0348 | -43.1656 | -47.942 | -54.2223 | -50.2808 | -58.7946 | -49.0316 | -47.9594 | -48.3646 | -66.4457 | -51.559 | -69.5492 | -41.4535 | 192 | -49.9026 | -50.5564 | -51.5898 | -54.5912 | -46.4664 | -46.4714 | -43.8067 | -47.0083 | 192 | -43.8565 | -44.2617 | -50.1194 | -46.3547 | -54.8685 | -44.7207 | -44.0333 | -44.0537 | -50.2839 | -45.9699 | -54.8562 | -45.0932 | -39.0627 | -43.8391 | -62.3428 | -47.6329 | -65.6231 | -37.1426 | -39.2395 | -43.6311 | -62.5073 | -47.2481 | -65.6108 | -37.5151
193 | -4.0843 | 0 | -3.9342 | 0 | -4.3351 | 0 | -3.961 | 0 | -51.2316 | 110.5345 | -56.6133 | 97.903 | -61.0438 | -179.2397 | -61.0392 | -153.0433 | -61.38 | 0.4817 | -51.7876 | -137.3337 | -51.3502 | 109.7392 | -50.0641 | -31.7561 | -64.2627 | -29.8355 | -49.9924 | 162.0911 | -54.9632 | 178.1974 | -45.2636 | -114.4493 | -24.4409 | -172.4746 | -26.9433 | -43.529 | -20.6316 | -152.4772 | -23.8924 | 146.0049 | -22.0973 | -97.3051 | -29.4862 | -2.3747 | -22.9498 | -65.7506 | -22.3895 | -1.4721 | -47.0311 | -43.5648 | -48.4663 | -58.5663 | -50.8319 | -50.9281 | -48.5358 | -48.5734 | -48.1429 | -60.528 | -51.778 | -55.6046 | -41.548 | 193 | -49.7888 | -50.4356 | -50.18 | -50.8938 | -47.5557 | -46.8751 | -43.0424 | -44.7724 | 193 | -44.4891 | -44.0586 | -54.482 | -46.8977 | -46.9939 | -44.2007 | -44.6392 | -43.8078 | -54.6053 | -46.4968 | -46.9671 | -44.5748 | -39.4805 | -44.382 | -56.4437 | -47.8438 | -51.6704 | -37.2129 | -39.6306 | -44.1312 | -56.567 | -47.4429 | -51.6436 | -37.587
194 | -4.0659 | 0 | -3.9411 | 0 | -4.4455 | 0 | -3.9993 | 0 | -51.224 | 90.0787 | -54.6805 | 107.808 | -54.1959 | 157.1702 | -55.6939 | -155.6591 | -62.0399 | 28.806 | -47.4309 | -170.2602 | -52.346 | 91.1341 | -50.4839 | -19.3417 | -78.4642 | 4.6341 | -48.5947 | 164.0892 | -55.4193 | 165.3536 | -42.0101 | -127.9139 | -28.1684 | -137.3178 | -26.1743 | -70.5413 | -20.1063 | 179.3601 | -23.5815 | 111.8342 | -23.4453 | -83.0022 | -31.0644 | -29.6912 | -23.3078 | -91.9828 | -21.6089 | -7.3259 | -47.1434 | -43.2 | -48.9927 | -57.8462 | -51.4944 | -45.9668 | -48.0875 | -50.1947 | -48.0776 | -56.1321 | -51.9294 | -48.3004 | -40.6863 | 194 | -48.3112 | -49.6399 | -46.1678 | -46.4784 | -48.3014 | -46.4746 | -40.6694 | -41.8155 | 194 | -46.1288 | -44.0117 | -53.7803 | -47.5533 | -42.0257 | -43.642 | -46.2536 | -43.6321 | -53.8469 | -47.0489 | -41.9675 | -44.0882 | -39.1341 | -44.9268 | -52.0662 | -47.9883 | -44.3593 | -36.2408 | -39.2589 | -44.5472 | -52.1328 | -47.4839 | -44.3011 | -36.687
195 | -4.108 | 0 | -3.9422 | 0 | -4.6456 | 0 | -4.0363 | 0 | -52.4922 | 72.7993 | -53.2977 | 81.0156 | -51.3115 | 129.1595 | -54.9219 | -165.1328 | -58.8378 | 38.5654 | -44.6667 | 149.237 | -54.6967 | 74.0478 | -47.0498 | -12.2611 | -65.493 | 81.4755 | -47.2922 | 153.7695 | -56.4065 | 156.0805 | -39.9601 | -153.9233 | -23.1748 | -113.9957 | -26.4612 | -96.3025 | -20.444 | 149.2028 | -23.7227 | 75.8554 | -21.6528 | -70.1848 | -33.6533 | -60.4375 | -24.6816 | -123.6856 | -20.7467 | -15.0099 | -47.3125 | -42.0301 | -48.9938 | -52.0386 | -52.5764 | -42.654 | -47.8367 | -53.1713 | -48.2017 | -53.0578 | -52.1823 | -44.2074 | -39.2986 | 195 | -47.5186 | -49.9311 | -43.7629 | -43.6809 | -46.3081 | -46.1381 | -38.5604 | -39.8509 | 195 | -49.0633 | -44.0937 | -47.9306 | -48.6342 | -38.7118 | -43.1911 | -49.2291 | -43.5561 | -48.0023 | -47.9308 | -38.6177 | -43.8004 | -37.9221 | -44.8858 | -48.9498 | -48.2401 | -40.2652 | -34.653 | -38.0879 | -44.3482 | -49.0215 | -47.5367 | -40.1711 | -35.2623
196 | -4.1694 | 0 | -3.9472 | 0 | -4.8101 | 0 | -4.0588 | 0 | -54.7747 | 66.2317 | -57.7503 | 24.768 | -50.7011 | 103.7679 | -53.5025 | -163.2179 | -56.5543 | 30.0557 | -43.606 | 106.2321 | -59.4517 | 67.0553 | -43.5987 | -29.9959 | -61.7229 | 49.5241 | -47.2532 | 140.7593 | -57.6476 | 153.5767 | -39.9796 | 172.5897 | -19.1826 | -124.117 | -27.6449 | -120.2032 | -22.258 | 117.8404 | -24.2098 | 36.2001 | -19.1771 | -72.593 | -36.9685 | -98.1973 | -28.2069 | -161.1156 | -20.2067 | -24.0822 | -47.3644 | -40.9226 | -48.0554 | -48.4347 | -54.0519 | -40.6882 | -47.8534 | -54.2671 | -48.2866 | -51.3222 | -52.6737 | -41.8726 | -38.0938 | 196 | -48.6907 | -49.9975 | -43.0334 | -42.6511 | -43.4226 | -46.6402 | -37.8792 | -39.8774 | 196 | -50.0977 | -44.1172 | -44.2653 | -50.1047 | -36.741 | -43.0433 | -50.3199 | -43.4765 | -44.3759 | -49.2418 | -36.6294 | -43.7946 | -36.7532 | -43.886 | -47.1528 | -48.7265 | -37.9254 | -33.2837 | -36.9754 | -43.2453 | -47.2634 | -47.8636 | -37.8138 | -34.035
197 | -4.2021 | 0 | -3.9355 | 0 | -4.7802 | 0 | -4.0616 | 0 | -55.9283 | 75.2602 | -58.6597 | -123.3551 | -51.123 | 84.2734 | -50.6614 | -178.4807 | -55.8432 | 21.2317 | -44.3745 | 62.5269 | -64.1451 | 109.8202 | -42.3742 | -57.2715 | -61.5428 | 14.9454 | -47.8287 | 133.6671 | -57.7131 | 157.1919 | -42.7081 | 138.8901 | -17.04 | -142.4353 | -29.9108 | -140.8335 | -26.7998 | 89.3567 | -24.593 | -8.2974 | -17.3694 | -83.9309 | -39.3184 | -150.1948 | -35.2677 | 155.7226 | -19.9215 | -35.5511 | -47.1613 | -40.6818 | -47.0528 | -46.9738 | -54.9816 | -40.2677 | -48.0644 | -51.4248 | -48.1435 | -50.9355 | -53.416 | -41.1006 | -37.5797 | 197 | -49.3417 | -48.6185 | -43.3282 | -43.2932 | -42.2935 | -47.3131 | -38.9287 | -42.5183 | 197 | -47.2227 | -43.9414 | -42.7717 | -51.0461 | -36.3322 | -43.2842 | -47.4893 | -43.3633 | -42.9122 | -50.2014 | -36.2061 | -44.0028 | -36.4797 | -42.8507 | -46.7334 | -49.4805 | -37.1651 | -32.7995 | -36.7463 | -42.2726 | -46.8739 | -48.6358 | -37.039 | -33.5181
198 | -4.2366 | 0 | -3.9618 | 0 | -4.6369 | 0 | -4.0661 | 0 | -54.7133 | 82.8953 | -51.3757 | 173.0977 | -52.2058 | 71.6349 | -49.7765 | 152.1594 | -54.8957 | 16.189 | -46.2609 | 25.8197 | -58.2158 | 139.1844 | -43.0889 | -83.5127 | -64.4715 | -20.8566 | -47.7937 | 127.7242 | -56.1866 | 155.0475 | -49.2868 | 116.6251 | -16.1203 | -162.5887 | -33.0913 | -149.5986 | -38.7341 | 84.5895 | -24.4081 | -52.9832 | -16.4408 | -99.2038 | -38.6338 | 167.0174 | -48.9466 | 56.0428 | -19.8868 | -48.2819 | -46.8946 | -41.14 | -46.6069 | -46.9884 | -54.8907 | -41.0814 | -48.3251 | -49.6057 | -48.0256 | -51.3837 | -54.5009 | -41.5002 | -38.6045 | 198 | -47.7779 | -47.6585 | -43.8229 | -44.8266 | -42.927 | -46.8752 | -41.1065 | -48.3719 | 198 | -45.3691 | -43.789 | -42.7518 | -50.9289 | -37.1196 | -43.6882 | -45.6439 | -43.3887 | -42.9223 | -50.2538 | -37.0153 | -44.259 | -36.9034 | -42.3703 | -47.1471 | -50.5391 | -37.5384 | -33.9676 | -37.1782 | -41.97 | -47.3176 | -49.864 | -37.4341 | -34.5384
199 | -4.2624 | 0 | -3.967 | 0 | -4.496 | 0 | -4.041 | 0 | -52.8927 | 81.8926 | -49.5175 | 133.7707 | -53.9481 | 60.1267 | -50.952 | 117.3622 | -53.0588 | 4.2389 | -48.5 | -5.8717 | -53.8959 | 131.898 | -45.2414 | -102.8772 | -72.1414 | -66.9141 | -47.8403 | 118.7134 | -55.6051 | 136.2081 | -58.0816 | 165.0967 | -16.1624 | 178.1256 | -34.7592 | -136.1956 | -33.4515 | -168.6774 | -23.6005 | -93.366 | -16.262 | -115.2266 | -37.5478 | 142.2535 | -39.818 | -45.6538 | -20.3565 | -61.6323 | -46.6303 | -41.9639 | -46.5741 | -47.8998 | -53.7084 | -42.835 | -48.5452 | -48.8866 | -48.0163 | -51.9436 | -56.1389 | -42.5936 | -40.6629 | 199 | -46.9162 | -47.42 | -44.7714 | -46.3641 | -44.6786 | -46.3318 | -43.1956 | -53.5977 | 199 | -44.6242 | -43.7539 | -43.6374 | -49.7414 | -38.868 | -44.0492 | -44.9196 | -43.5203 | -43.8588 | -49.2124 | -38.794 | -44.5042 | -37.7015 | -42.3117 | -47.6812 | -52.1719 | -38.6266 | -36.1669 | -37.9969 | -42.0781 | -47.9026 | -51.6429 | -38.5526 | -36.6219
200 | -4.2444 | 0 | -3.9707 | 0 | -4.3941 | 0 | -4.0546 | 0 | -50.8333 | 76.9457 | -50.7744 | 101.7604 | -55.6839 | 49.2379 | -54.1853 | 72.7502 | -52.8392 | -24.6734 | -50.3021 | -36.5916 | -50.9157 | 118.0015 | -48.2971 | -110.3183 | -80.8834 | 161.6395 | -48.1289 | 111.5741 | -60.1259 | 133.4816 | -52.7231 | -162.5857 | -17.0582 | 159.3375 | -32.5353 | -128.1659 | -27.4061 | 177.7186 | -22.9849 | -128.2221 | -16.8434 | -131.2624 | -36.4092 | 125.4963 | -35.7312 | -72.5318 | -21.2579 | -74.8393 | -46.2823 | -42.7917 | -46.4389 | -49.5402 | -50.7863 | -45.5417 | -48.5488 | -48.7378 | -47.7991 | -52.1347 | -53.9668 | -44.5269 | -42.3698 | 200 | -47.1394 | -47.6271 | -46.6737 | -47.637 | -46.4001 | -46.1162 | -44.4943 | -51.9919 | 200 | -44.4934 | -43.5547 | -45.2958 | -46.8156 | -41.571 | -44.1547 | -44.7671 | -43.405 | -45.4856 | -46.3922 | -41.4871 | -44.4942 | -38.5473 | -42.1945 | -47.8903 | -49.9961 | -40.5562 | -37.9757 | -38.821 | -42.0448 | -48.0801 | -49.5727 | -40.4723 | -38.3152
201 | -4.1905 | 0 | -3.9948 | 0 | -4.3409 | 0 | -4.0403 | 0 | -49.028 | 62.4011 | -56.1761 | 80.6771 | -60.4466 | 58.1588 | -59.4168 | 1.0011 | -57.4934 | -38.0204 | -52.0773 | -71.3717 | -49.1911 | 97.6498 | -50.4537 | -100.9839 | -73.7715 | 156.4089 | -48.6232 | 101.2454 | -56.874 | 147.6666 | -49.3573 | -158.9784 | -18.9944 | 144.5783 | -29.4628 | -138.1706 | -24.9698 | 162.8196 | -22.8975 | -156.3724 | -18.1933 | -145.515 | -35.7437 | 113.4568 | -32.3995 | -96.8776 | -22.6563 | -87.7053 | -46.3182 | -43.5354 | -46.7834 | -50.6346 | -50.5252 | -49.0159 | -48.0651 | -49.0362 | -47.2725 | -53.03 | -52.2995 | -47.9659 | -43.0239 | 201 | -48.0072 | -48.1155 | -50.1081 | -50.5151 | -46.7577 | -45.5546 | -44.6428 | -48.6357 | 201 | -44.8457 | -43.082 | -46.4441 | -46.5304 | -45.0211 | -43.7242 | -45.0414 | -42.9316 | -46.5943 | -46.1843 | -44.9756 | -44.0248 | -39.3449 | -42.5929 | -48.8395 | -48.3047 | -43.9711 | -38.683 | -39.5406 | -42.4425 | -48.9897 | -47.9586 | -43.9256 | -38.9836
202 | -4.1536 | 0 | -3.9891 | 0 | -4.3553 | 0 | -4.0572 | 0 | -48.2861 | 45.7399 | -61.2502 | 149.0851 | -58.6472 | 101.5697 | -58.6703 | -81.091 | -60.7795 | -15.2821 | -53.528 | -119.8542 | -48.6967 | 76.2649 | -49.5579 | -90.2381 | -66.3409 | 143.6732 | -49.7284 | 96.8183 | -55.7768 | 130.2598 | -46.1758 | -165.241 | -22.0337 | 138.7345 | -27.421 | -157.0955 | -23.5383 | 149.3323 | -23.4566 | -178.5879 | -20.4846 | -154.2358 | -35.5286 | 99.7123 | -29.3551 | -126.3141 | -24.4394 | -99.6303 | -46.5 | -44.1865 | -47.5121 | -51.7422 | -51.0743 | -52.2178 | -47.8251 | -49.6287 | -47.0012 | -53.3056 | -52.3407 | -51.9451 | -42.5775 | 202 | -47.7073 | -47.6872 | -51.8401 | -51.7788 | -46.0548 | -45.7203 | -43.3876 | -45.6865 | 202 | -45.4751 | -42.8476 | -47.5886 | -47.0852 | -48.2287 | -43.4698 | -45.6396 | -42.6459 | -47.685 | -46.719 | -48.1606 | -43.7679 | -40.0329 | -43.3585 | -49.152 | -48.3516 | -47.956 | -38.2222 | -40.1974 | -43.1568 | -49.2484 | -47.9854 | -47.8879 | -38.5203
203 | -4.1516 | 0 | -3.9898 | 0 | -4.4506 | 0 | -4.0859 | 0 | -48.4443 | 28.6444 | -53.0957 | 152.3766 | -53.3436 | 100.315 | -56.56 | -118.7966 | -58.0067 | 8.389 | -53.3565 | 165.0229 | -49.2084 | 55.1667 | -47.9582 | -90.6719 | -61.778 | 123.7153 | -49.7132 | 96.0977 | -56.7046 | 116.7289 | -43.3626 | 179.0435 | -24.8027 | 155.6058 | -26.3408 | -176.607 | -22.7732 | 136.3833 | -24.8527 | 166.9192 | -23.1761 | -149.4852 | -36.6714 | 83.4675 | -26.9686 | -163.3643 | -27.3912 | -111.0052 | -46.8523 | -44.5396 | -48.4125 | -51.2038 | -51.7781 | -48.2427 | -47.7437 | -50.8998 | -47.0344 | -51.7867 | -52.4937 | -49.392 | -42.1691 | 203 | -46.2268 | -47.4237 | -49.3079 | -49.6537 | -45.4264 | -46.0524 | -41.3793 | -43.1066 | 203 | -46.7482 | -42.8828 | -47.0522 | -47.7883 | -44.2529 | -43.2931 | -46.91 | -42.5838 | -47.1179 | -47.3275 | -44.1568 | -43.6578 | -40.388 | -44.2609 | -47.6351 | -48.5039 | -45.4022 | -37.7185 | -40.5498 | -43.9619 | -47.7008 | -48.0431 | -45.3061 | -38.0832
204 | -4.1719 | 0 | -4.003 | 0 | -4.6124 | 0 | -4.0835 | 0 | -49.69 | 13.9064 | -51.6769 | 137.0597 | -51.2036 | 80.7943 | -54.3576 | -131.8416 | -54.5773 | 4.1324 | -49.6401 | 85.79 | -51.0237 | 34.8602 | -46.1135 | -95.1136 | -59.8733 | 96.8328 | -49.2201 | 85.945 | -58.3918 | 107.9934 | -41.7356 | 150.1999 | -22.7857 | 177.2864 | -26.064 | 164.7947 | -22.9335 | 121.9989 | -26.747 | 166.0987 | -23.2547 | -131.9269 | -41.4646 | 65.4148 | -25.5216 | 156.567 | -32.5361 | -117.7019 | -47.3264 | -43.9982 | -48.7765 | -48.4436 | -52.967 | -43.3732 | -47.8624 | -53.6709 | -47.375 | -49.2257 | -52.7999 | -44.253 | -41.542 | 204 | -46.0004 | -47.4735 | -46.7106 | -46.5898 | -44.7625 | -46.7131 | -39.8508 | -41.578 | 204 | -49.499 | -43.2031 | -44.2717 | -48.964 | -39.3702 | -43.25 | -49.6679 | -42.7626 | -44.3601 | -48.3546 | -39.2897 | -43.7789 | -39.8263 | -44.6046 | -45.0538 | -48.7969 | -40.25 | -36.9296 | -39.9952 | -44.1641 | -45.1422 | -48.1875 | -40.1695 | -37.4585
205 | -4.2106 | 0 | -4.0236 | 0 | -4.7105 | 0 | -4.0828 | 0 | -51.8643 | 8.6967 | -50.6374 | 142.5964 | -51.2754 | 61.3979 | -51.3928 | -151.9553 | -52.9164 | -9.2808 | -46.5603 | 24.0531 | -54.9883 | 21.2206 | -44.0308 | -108.1628 | -60.7788 | 72.0718 | -50.3396 | 72.0581 | -60.8831 | 112.9655 | -42.64 | 116.0128 | -19.567 | 175.5233 | -26.4995 | 150.1018 | -24.6224 | 116.2865 | -26.5868 | 179.2361 | -20.5093 | -125.5942 | -50.053 | -116.1432 | -25.8206 | 118.1676 | -38.3384 | -61.3228 | -47.722 | -43.0378 | -48.0262 | -46.2884 | -54.2728 | -40.8152 | -48.2697 | -59.0035 | -47.7887 | -47.4025 | -53.3635 | -41.5387 | -40.324 | 205 | -46.4589 | -47.241 | -44.2056 | -44.6038 | -43.6115 | -48.7829 | -39.862 | -42.5102 | 205 | -54.7929 | -43.5781 | -42.0778 | -50.2492 | -36.7916 | -43.5592 | -54.9799 | -43.0782 | -42.2056 | -49.5623 | -36.7324 | -44.1869 | -38.8272 | -43.8156 | -43.1919 | -49.3399 | -37.5151 | -35.6135 | -39.0142 | -43.3157 | -43.3197 | -48.653 | -37.4559 | -36.2412
206 | -4.2591 | 0 | -4.0409 | 0 | -4.6727 | 0 | -4.0744 | 0 | -53.1793 | 18.2175 | -46.9896 | 135.5656 | -52.1314 | 49.7514 | -50.414 | 178.1532 | -52.3576 | -21.1457 | -45.3799 | -24.084 | -61.8825 | 44.4259 | -43.0321 | -129.8666 | -64.9963 | 65.2652 | -52.6159 | 70.3139 | -60.6316 | 134.0802 | -46.616 | 84.4702 | -17.4633 | 163.8116 | -27.1432 | 140.3408 | -25.042 | 126.0316 | -23.7785 | -175.4983 | -18.1308 | -134.8631 | -34.6038 | -147.4713 | -27.0719 | 81.1232 | -30.9633 | -27.5772 | -47.915 | -42.621 | -47.1567 | -45.376 | -54.8642 | -40.1171 | -48.9471 | -64.9032 | -47.9544 | -46.6776 | -53.8963 | -40.6805 | -39.384 | 206 | -45.096 | -47.053 | -42.3608 | -43.8821 | -42.9487 | -51.5563 | -41.1338 | -46.3868 | 206 | -60.6441 | -43.6953 | -41.1169 | -50.8233 | -36.0762 | -44.2744 | -60.8623 | -43.2817 | -41.3016 | -50.1915 | -36.0427 | -44.8727 | -38.3619 | -42.8976 | -42.4185 | -49.8554 | -36.6396 | -34.7113 | -38.5801 | -42.484 | -42.6032 | -49.2236 | -36.6061 | -35.3096
207 | -4.3084 | 0 | -4.0488 | 0 | -4.611 | 0 | -4.0872 | 0 | -51.8829 | 28.5574 | -44.9669 | 113.2312 | -52.89 | 44.9546 | -51.9994 | 147.2555 | -52.015 | -30.0463 | -45.6525 | -60.8445 | -56.9421 | 96.3022 | -43.5179 | -152.9708 | -66.9496 | 101.3242 | -52.8316 | 79.2517 | -57.3186 | 135.6549 | -55.5019 | 67.2545 | -16.3418 | 149.0469 | -27.3484 | 136.3991 | -23.1977 | 129.8533 | -21.0365 | 176.2714 | -16.7209 | -150.8634 | -28.7129 | -170.2308 | -28.9186 | 44.0835 | -26.2279 | -36.9044 | -47.9112 | -42.6999 | -46.6552 | -45.1964 | -54.8722 | -40.3484 | -49.6387 | -60.818 | -47.9803 | -46.5683 | -54.2598 | -40.8063 | -39.3694 | 207 | -43.6164 | -47.1942 | -41.8451 | -44.1297 | -43.306 | -50.4162 | -42.7974 | -53.1219 | 207 | -56.5096 | -43.6719 | -40.888 | -50.8234 | -36.2996 | -45.0277 | -56.7692 | -43.3693 | -41.1092 | -50.2612 | -36.2612 | -45.5515 | -38.3915 | -42.3468 | -42.2599 | -50.211 | -36.7575 | -34.7584 | -38.6511 | -42.0442 | -42.4811 | -49.6488 | -36.7191 | -35.2822
208 | -4.2961 | 0 | -4.0786 | 0 | -4.5231 | 0 | -4.1361 | 0 | -49.7015 | 27.3481 | -44.987 | 88.5502 | -53.0979 | 42.539 | -57.3414 | 117.0706 | -51.8463 | -38.4814 | -46.718 | -88.9683 | -51.487 | 90.2031 | -45.5271 | -173.6165 | -61.9224 | 119.7317 | -51.36 | 76.5338 | -54.9191 | 120.5121 | -59.6902 | 162.9634 | -16.0812 | 133.871 | -26.7126 | 132.8509 | -21.7075 | 123.8309 | -19.2644 | 162.6931 | -16.2476 | -169.0367 | -25.527 | 168.9996 | -30.773 | -7.727 | -23.1923 | -53.8321 | -47.8707 | -43.0027 | -46.3968 | -45.3668 | -54.7848 | -41.0847 | -50.2779 | -56.5817 | -47.8976 | -46.8208 | -54.7114 | -41.4215 | -40.1724 | 208 | -43.2487 | -47.1913 | -42.608 | -44.8508 | -44.4671 | -47.5365 | -44.3897 | -53.0645 | 208 | -52.2856 | -43.6015 | -41.0707 | -50.7062 | -37.0061 | -45.7548 | -52.5031 | -43.3745 | -41.2307 | -50.2617 | -36.9486 | -46.1418 | -38.7066 | -42.1007 | -42.5247 | -50.6328 | -37.3429 | -35.6493 | -38.9241 | -41.8737 | -42.6847 | -50.1883 | -37.2854 | -36.0363
209 | -4.2921 | 0 | -4.1019 | 0 | -4.4649 | 0 | -4.1904 | 0 | -47.9948 | 18.3876 | -47.1487 | 66.1426 | -52.8355 | 41.3302 | -76.2569 | -69.4198 | -51.7204 | -46.3306 | -48.0299 | -109.4686 | -48.531 | 73.1538 | -49.5567 | 176.1013 | -57.5679 | 110.2798 | -50.6063 | 62.8434 | -54.2997 | 97.4407 | -52.385 | 162.2792 | -16.4677 | 120.0357 | -25.5901 | 124.1788 | -20.9185 | 116.0776 | -18.136 | 147.4381 | -16.6903 | 172.5608 | -23.5455 | 148.0616 | -30.3133 | -71.8055 | -21.3565 | -72.8163 | -47.7651 | -43.2609 | -46.2756 | -45.6714 | -54.4448 | -42.1672 | -50.891 | -53.5001 | -47.8116 | -47.2894 | -55.2855 | -42.3634 | -41.0793 | 209 | -43.9411 | -46.4549 | -44.5538 | -45.5792 | -45.7105 | -45.7778 | -45.9268 | -49.4921 | 209 | -49.208 | -43.5195 | -41.3793 | -50.3429 | -38.0653 | -46.4261 | -49.3982 | -43.3467 | -41.481 | -49.9799 | -37.9768 | -46.7006 | -38.9688 | -41.9835 | -42.9973 | -51.1836 | -38.2615 | -36.6144 | -39.159 | -41.8107 | -43.099 | -50.8206 | -38.173 | -36.8889
210 | -4.2755 | 0 | -4.1444 | 0 | -4.4377 | 0 | -4.2139 | 0 | -46.7681 | 7.4021 | -52.5328 | 57.1963 | -52.274 | 35.6904 | -55.6204 | -113.1825 | -51.9705 | -57.0013 | -49.241 | -126.0891 | -46.7517 | 55.9247 | -53.3267 | -155.9471 | -55.6491 | 90.0128 | -51.2221 | 47.1598 | -56.8267 | 75.8167 | -50.8118 | 147.9611 | -17.5441 | 109.2636 | -24.968 | 110.7993 | -20.5381 | 110.5122 | -17.742 | 132.4099 | -18.1091 | 154.3532 | -22.7568 | 128.2506 | -26.9669 | -127.304 | -20.3912 | -95.4925 | -47.538 | -43.4564 | -45.9855 | -46.3505 | -52.7919 | -43.6087 | -51.4256 | -50.969 | -47.7012 | -47.992 | -54.8006 | -43.5471 | -41.7711 | 210 | -44.8742 | -45.2084 | -46.9396 | -46.1644 | -45.4518 | -45.1215 | -46.8844 | -48.829 | 210 | -46.6935 | -43.4257 | -42.075 | -48.6475 | -39.4643 | -46.9879 | -46.8246 | -43.2635 | -42.1366 | -48.3542 | -39.3948 | -47.2117 | -39.1809 | -41.71 | -43.7165 | -50.6562 | -39.4027 | -37.3334 | -39.312 | -41.5478 | -43.7781 | -50.3629 | -39.3332 | -37.5572
211 | -4.2799 | 0 | -4.154 | 0 | -4.409 | 0 | -4.2359 | 0 | -45.882 | -6.404 | -55.1589 | 113.4595 | -52.4793 | 30.7616 | -50.8526 | -136.8845 | -53.4754 | -58.7915 | -50.6534 | -141.948 | -45.616 | 35.1307 | -49.0155 | -136.458 | -56.7772 | 81.9048 | -52.1976 | 34.8566 | -58.5035 | 79.9277 | -50.7922 | 146.9207 | -19.1135 | 104.6159 | -25.2599 | 95.2621 | -19.9425 | 106.4155 | -17.9678 | 118.1588 | -20.9667 | 140.8569 | -23.0079 | 110.9699 | -23.6346 | -169.2837 | -20.041 | -118.2223 | -47.3328 | -43.7675 | -45.9431 | -47.239 | -51.4968 | -45.6152 | -51.0133 | -49.1512 | -47.3268 | -48.6501 | -53.0211 | -45.0965 | -41.9887 | 211 | -44.6206 | -44.1431 | -47.0182 | -47.271 | -43.7587 | -44.5741 | -45.7015 | -49.2649 | 211 | -44.8713 | -43.0469 | -42.9591 | -47.3428 | -41.4612 | -46.6043 | -44.9972 | -42.9178 | -43.0031 | -47.0878 | -41.3793 | -46.7774 | -39.4876 | -41.6632 | -44.3702 | -48.8671 | -40.9425 | -37.5797 | -39.6135 | -41.5341 | -44.4142 | -48.6121 | -40.8606 | -37.7528
212 | -4.2696 | 0 | -4.1438 | 0 | -4.4848 | 0 | -4.2272 | 0 | -45.8353 | -22.1848 | -48.6722 | 121.1893 | -51.7666 | 28.9331 | -48.4263 | -155.9287 | -52.8889 | -51.8225 | -53.719 | -157.1219 | -45.7011 | 12.2492 | -45.8923 | -148.3215 | -55.1501 | 86.3077 | -53.2322 | 20.7032 | -58.9506 | 66.5483 | -48.2011 | 142.6707 | -20.2933 | 109.2478 | -26.6667 | 79.889 | -19.1147 | 99.62 | -18.6468 | 106.0641 | -25.6673 | 146.438 | -24.3816 | 97.9854 | -21.5314 | 155.3896 | -20.2282 | -142.6096 | -47.6898 | -44.316 | -46.5695 | -47.5257 | -51.8734 | -47.2886 | -50.4133 | -48.641 | -47.1407 | -48.4993 | -52.6008 | -46.395 | -41.8773 | 212 | -43.3419 | -43.4105 | -44.9227 | -47.9461 | -42.5404 | -44.8237 | -43.4073 | -47.1086 | 212 | -44.3714 | -42.8711 | -43.2561 | -47.7296 | -43.1448 | -45.9285 | -44.4972 | -42.6559 | -43.2985 | -47.3886 | -43.0614 | -46.1861 | -40.0464 | -42.2999 | -44.2297 | -48.457 | -42.2512 | -37.3925 | -40.1722 | -42.0847 | -44.2721 | -48.116 | -42.1678 | -37.6501
213 | -4.2821 | 0 | -4.134 | 0 | -4.5881 | 0 | -4.2339 | 0 | -46.7063 | -35.9823 | -45.8649 | 108.3165 | -50.9469 | 19.1773 | -46.7208 | -173.862 | -51.2031 | -55.3259 | -58.6412 | -131.0021 | -47.0117 | -9.5353 | -44.4416 | -162.9363 | -53.0992 | 73.8884 | -54.7258 | -1.2874 | -62.1507 | 51.7854 | -46.8284 | 118.4063 | -19.8136 | 118.1828 | -29.9907 | 70.3469 | -18.7402 | 90.0306 | -19.7621 | 96.8549 | -25.6999 | -170.7454 | -26.8264 | 94.4796 | -20.8312 | 121.8499 | -21.2707 | -166.5979 | -48.055 | -44.4193 | -47.2383 | -46.9613 | -52.6527 | -45.4427 | -49.9817 | -49.7795 | -47.4149 | -47.3098 | -52.5559 | -45.6155 | -42.0394 | 213 | -42.5726 | -42.9924 | -43.1374 | -47.6984 | -42.1639 | -46.2202 | -42.2122 | -45.8062 | 213 | -45.4974 | -43.1328 | -42.6792 | -48.5187 | -41.3087 | -45.3936 | -45.6455 | -42.8268 | -42.7274 | -48.0646 | -41.2088 | -45.7478 | -40.1372 | -42.9562 | -43.0277 | -48.4219 | -41.4815 | -37.4513 | -40.2853 | -42.6502 | -43.0759 | -47.9678 | -41.3816 | -37.8055
214 | -4.3452 | 0 | -4.1518 | 0 | -4.6593 | 0 | -4.2209 | 0 | -48.2425 | -43.9454 | -44.1259 | 97.0926 | -51.2312 | 6.0935 | -45.7749 | 164.873 | -50.0226 | -64.7139 | -52.9138 | -106.6912 | -49.9826 | -28.0804 | -43.3832 | -178.3086 | -53.0937 | 57.9418 | -58.4086 | -38.7432 | -71.0115 | 68.5988 | -48.8825 | 89.5031 | -18.0008 | 119.9147 | -35.1655 | 93.1912 | -18.9274 | 81.6757 | -21.0658 | 92.3923 | -20.532 | -165.9683 | -28.342 | 111.2205 | -21.4026 | 90.7973 | -23.3104 | 168.9959 | -48.2603 | -43.9475 | -47.149 | -46.2486 | -53.2603 | -43.092 | -49.7416 | -52.589 | -47.7475 | -46.0463 | -52.4682 | -44.089 | -41.6266 | 214 | -42.133 | -42.8911 | -41.5341 | -46.4605 | -42.1587 | -49.3697 | -42.1995 | -47.467 | 214 | -48.2438 | -43.4023 | -41.9034 | -49.1085 | -38.9402 | -45.0823 | -48.4372 | -43.0882 | -42.0277 | -48.601 | -38.8711 | -45.5207 | -39.6023 | -42.8038 | -41.7011 | -48.3164 | -39.9372 | -36.9673 | -39.7957 | -42.4897 | -41.8254 | -47.8089 | -39.8681 | -37.4057
215 | -4.3964 | 0 | -4.1712 | 0 | -4.67 | 0 | -4.2011 | 0 | -49.7526 | -43.4444 | -42.6497 | 81.9529 | -52.1696 | -0.0711 | -46.086 | 143.8282 | -49.4137 | -77.1397 | -49.1228 | -124.9377 | -55.6712 | -32.4052 | -42.8193 | 162.3227 | -54.033 | 51.0216 | -64.3837 | -120.6422 | -65.3285 | 146.1157 | -56.7112 | 69.7786 | -16.2394 | 112.9412 | -31.2609 | 137.6453 | -19.3996 | 75.25 | -22.238 | 92.071 | -17.2168 | 179.1195 | -25.8924 | 127.3345 | -23.6042 | 61.6537 | -26.2339 | 147.4324 | -48.1977 | -43.5363 | -46.6026 | -45.8579 | -53.4438 | -41.8801 | -49.6869 | -56.9981 | -47.8456 | -45.2337 | -52.265 | -43.1817 | -40.9931 | 215 | -41.4885 | -43.3107 | -40.4004 | -45.2649 | -42.2982 | -54.7275 | -42.6166 | -51.9541 | 215 | -52.6017 | -43.4492 | -41.4615 | -49.2726 | -37.7089 | -45.0169 | -52.8269 | -43.1756 | -41.6568 | -48.7738 | -37.679 | -45.4858 | -39.1399 | -42.2062 | -40.8373 | -48.0938 | -39.0105 | -36.3231 | -39.3651 | -41.9326 | -41.0326 | -47.595 | -38.9806 | -36.792
216 | -4.4708 | 0 | -4.2025 | 0 | -4.6438 | 0 | -4.2093 | 0 | -50.0419 | -35.8494 | -42.1072 | 62.7215 | -52.6909 | -0.2315 | -47.7086 | 125.0125 | -49.3997 | -89.6124 | -47.8317 | -147.0518 | -58.8249 | 24.9394 | -43.2755 | 139.7268 | -53.9637 | 55.3949 | -59.7348 | 146.4607 | -58.5417 | 132.0887 | -59.3155 | 168.5314 | -15.045 | 101.6039 | -26.0612 | 133.5912 | -20.0973 | 71.5156 | -22.8655 | 94.5781 | -15.4918 | 159.9336 | -22.9764 | 123.5949 | -28.6726 | 28.7954 | -32.1831 | 129.9179 | -47.9477 | -43.3226 | -46.1106 | -45.6313 | -53.4516 | -41.3929 | -49.8158 | -64.0032 | -47.7208 | -44.7806 | -52.097 | -42.7532 | -40.6976 | 216 | -41.144 | -44.164 | -40.2236 | -44.7705 | -42.8097 | -54.2334 | -43.074 | -51.8149 | 216 | -59.5324 | -43.25 | -41.1605 | -49.2491 | -37.1904 | -45.172 | -59.8007 | -43.077 | -41.422 | -48.8078 | -37.1836 | -45.6065 | -38.8518 | -41.6398 | -40.3098 | -47.8945 | -38.5507 | -36.0538 | -39.1201 | -41.4668 | -40.5713 | -47.4532 | -38.5439 | -36.4883
217 | -4.5299 | 0 | -4.2436 | 0 | -4.6098 | 0 | -4.2268 | 0 | -48.8595 | -31.3768 | -42.8905 | 42.181 | -52.2723 | -1.5892 | -50.9065 | 115.8784 | -49.9141 | -101.0084 | -47.9079 | -166.638 | -52.0241 | 40.4386 | -45.2896 | 115.8966 | -52.6054 | 52.0454 | -55.939 | 101.976 | -55.5792 | 108.1024 | -50.6167 | 163.1844 | -14.4817 | 88.0159 | -23.2322 | 117.3723 | -20.8132 | 71.8743 | -22.9379 | 96.5261 | -14.8102 | 139.2654 | -21.1562 | 111.4519 | -43.2288 | -76.523 | -43.1253 | -167.2792 | -47.7193 | -43.1715 | -45.736 | -45.4615 | -53.5045 | -41.2652 | -50.0796 | -63.7934 | -47.4752 | -44.5991 | -52.1968 | -42.5786 | -40.7693 | 217 | -41.5287 | -45.0419 | -41.2089 | -44.906 | -43.8357 | -49.3593 | -43.8927 | -47.7129 | 217 | -59.2635 | -42.9453 | -40.9316 | -49.2609 | -37.0216 | -45.4698 | -59.5498 | -42.8654 | -41.2347 | -48.8947 | -37.0384 | -45.8528 | -38.6416 | -41.2061 | -40.0692 | -47.9532 | -38.335 | -36.1595 | -38.9279 | -41.1262 | -40.3723 | -47.587 | -38.3518 | -36.5425
218 | -4.5364 | 0 | -4.2684 | 0 | -4.5718 | 0 | -4.2357 | 0 | -47.2044 | -34.2444 | -45.5545 | 24.3627 | -51.7102 | -8.265 | -54.2682 | 130.2648 | -50.8163 | -109.4355 | -48.6741 | 179.5763 | -48.1803 | 27.9353 | -50.3343 | 95.2492 | -51.3921 | 44.113 | -54.861 | 66.0559 | -54.3191 | 81.3794 | -47.5424 | 141.057 | -14.5498 | 74.1823 | -21.9783 | 98.8927 | -20.8525 | 77.1422 | -22.7904 | 97.6406 | -15.0721 | 118.1164 | -20.5619 | 95.8165 | -28.4068 | 176.3232 | -31.6807 | -131.5808 | -47.4824 | -42.9421 | -45.4496 | -45.4511 | -53.5878 | -41.3093 | -50.4324 | -57.0875 | -47.2551 | -44.577 | -52.6199 | -42.6109 | -41.0714 | 218 | -42.7073 | -45.0774 | -43.4539 | -45.4361 | -44.9865 | -46.5426 | -45.2094 | -45.4414 | 218 | -52.5511 | -42.7187 | -40.9147 | -49.3194 | -37.0409 | -45.8606 | -52.8191 | -42.6833 | -41.2154 | -49.016 | -37.0736 | -46.1967 | -38.4057 | -40.9132 | -40.0406 | -48.3515 | -38.3425 | -36.4996 | -38.6737 | -40.8778 | -40.3413 | -48.0481 | -38.3752 | -36.8357
219 | -4.5093 | 0 | -4.277 | 0 | -4.5318 | 0 | -4.2421 | 0 | -45.7582 | -42.542 | -51.528 | 26.5034 | -51.7047 | -18.0193 | -52.6697 | 155.5116 | -51.888 | -113.6368 | -49.2235 | 173.0655 | -45.9929 | 11.1496 | -62.6432 | 153.6608 | -50.7499 | 30.258 | -55.7108 | 30.9868 | -55.1609 | 50.1898 | -47.1628 | 120.8597 | -15.3107 | 60.8787 | -22.0369 | 80.2676 | -19.7599 | 80.6133 | -22.6196 | 96.6486 | -16.2785 | 98.3651 | -21.1601 | 81.3537 | -22.6189 | 145.2794 | -26.9023 | -149.958 | -47.2918 | -42.7966 | -45.1842 | -45.659 | -53.4442 | -41.6091 | -50.8747 | -53.3092 | -47.0522 | -44.82 | -53.3004 | -42.8443 | -41.5472 | 219 | -43.9422 | -44.1522 | -46.1262 | -45.9885 | -44.6701 | -45.1015 | -46.4883 | -45.1315 | 219 | -48.7999 | -42.5429 | -41.1497 | -49.1672 | -37.3321 | -46.3429 | -49.0322 | -42.5204 | -41.4169 | -48.9124 | -37.367 | -46.6326 | -38.2873 | -40.6749 | -40.3107 | -49.0234 | -38.5673 | -37.0154 | -38.5196 | -40.6524 | -40.5779 | -48.7686 | -38.6022 | -37.3051
220 | -4.4734 | 0 | -4.2806 | 0 | -4.5372 | 0 | -4.2376 | 0 | -44.7 | -54.5192 | -50.8004 | 82.6889 | -52.2647 | -25.6411 | -49.3569 | 157.3679 | -52.5941 | -112.5741 | -48.6946 | 167.0916 | -44.7495 | -7.832 | -49.4443 | -168.5441 | -51.693 | 20.2429 | -58.0933 | -7.7769 | -58.1479 | 20.3466 | -48.0069 | 106.7605 | -16.8488 | 50.5531 | -23.4302 | 64.6166 | -18.1637 | 77.0054 | -22.5466 | 95.1416 | -18.8625 | 81.3854 | -23.201 | 70.5691 | -19.988 | 118.2909 | -24.7761 | -171.751 | -47.2251 | -43.1692 | -45.0663 | -46.0962 | -52.858 | -42.4153 | -50.808 | -51.4434 | -46.8757 | -45.2494 | -53.5736 | -43.4591 | -42.1425 | 220 | -43.1751 | -42.9257 | -44.76 | -46.03 | -42.8704 | -44.3672 | -45.4151 | -46.1749 | 220 | -46.97 | -42.4023 | -41.6228 | -48.5774 | -38.1347 | -46.2708 | -47.1628 | -42.3385 | -41.8586 | -48.3208 | -38.1777 | -46.5704 | -38.6958 | -40.5929 | -40.776 | -49.293 | -39.1785 | -37.6053 | -38.8886 | -40.5291 | -41.0118 | -49.0364 | -39.2215 | -37.9049
221 | -4.438 | 0 | -4.2759 | 0 | -4.5526 | 0 | -4.2405 | 0 | -44.3584 | -69.2455 | -45.0519 | 81.663 | -52.7064 | -30.3958 | -46.8805 | 148.1041 | -52.3229 | -108.7333 | -48.156 | 154.9858 | -44.4816 | -29.026 | -44.8099 | 170.0922 | -52.5557 | 17.7434 | -60.38 | -61.6535 | -62.9022 | -15.8989 | -48.7726 | 103.1939 | -19.0699 | 48.1265 | -26.4121 | 58.7534 | -17.0067 | 67.2778 | -22.7246 | 93.4778 | -23.4312 | 77.2405 | -26.6923 | 75.9579 | -18.9217 | 91.7315 | -24.1639 | 166.8649 | -47.5017 | -44.087 | -45.4099 | -46.4002 | -52.3611 | -43.712 | -50.1353 | -51.1776 | -46.7701 | -45.608 | -53.1548 | -44.451 | -42.6383 | 221 | -41.3509 | -42.0049 | -41.7363 | -45.766 | -41.2947 | -44.3109 | -43.2587 | -47.1376 | 221 | -46.7396 | -42.3321 | -41.9622 | -48.0852 | -39.4361 | -45.5827 | -46.9017 | -42.2175 | -42.1597 | -47.8085 | -39.4715 | -45.8948 | -39.649 | -40.9719 | -41.17 | -48.8789 | -40.1751 | -38.0857 | -39.8111 | -40.8573 | -41.3675 | -48.6022 | -40.2105 | -38.3978
222 | -4.4219 | 0 | -4.2947 | 0 | -4.6208 | 0 | -4.2569 | 0 | -44.9329 | -83.8791 | -42.3098 | 67.1553 | -53.3295 | -35.5017 | -45.2398 | 133.4532 | -50.8936 | -110.2549 | -48.2418 | 143.198 | -45.4528 | -49.8858 | -42.8348 | 148.5063 | -52.894 | 19.4342 | -58.5427 | -125.1336 | -68.4616 | -96.8081 | -48.8331 | 96.35 | -20.6785 | 59.0868 | -29.1194 | 79.9769 | -16.7267 | 53.9758 | -23.0512 | 93.3754 | -26.37 | 114.4894 | -27.1086 | 109.0493 | -19.198 | 64.8474 | -25.1102 | 147.5278 | -47.9815 | -44.956 | -46.0501 | -46.6182 | -52.1807 | -44.5342 | -49.6463 | -52.3278 | -47.0352 | -45.4979 | -52.5643 | -45.4958 | -42.9918 | 222 | -40.1994 | -41.5379 | -39.8436 | -45.5632 | -40.6707 | -45.224 | -41.769 | -47.3611 | 222 | -47.9059 | -42.6133 | -42.1963 | -47.886 | -40.2395 | -45.0255 | -48.0331 | -42.4144 | -42.3613 | -47.5599 | -40.2773 | -45.3894 | -40.5341 | -41.6282 | -41.076 | -48.2696 | -41.2011 | -38.371 | -40.6613 | -41.4293 | -41.241 | -47.9435 | -41.2389 | -38.7349
223 | -4.4488 | 0 | -4.3247 | 0 | -4.6589 | 0 | -4.2892 | 0 | -46.3399 | -94.6198 | -40.8483 | 50.6233 | -54.438 | -34.355 | -44.5497 | 116.1547 | -49.5427 | -119.9433 | -48.1568 | 133.6499 | -47.8837 | -67.5596 | -41.9001 | 127.7379 | -52.7633 | 18.484 | -54.6946 | -171.9464 | -61.3865 | -168.3054 | -50.3105 | 88.9509 | -19.406 | 73.3123 | -25.6868 | 103.1336 | -17.3042 | 42.5116 | -23.3276 | 97.7025 | -21.2966 | 132.7393 | -22.7719 | 121.3876 | -21.0895 | 38.1902 | -27.7918 | 136.9584 | -48.3748 | -45.2051 | -46.4051 | -46.6248 | -52.078 | -44.2441 | -49.5474 | -54.3425 | -47.4605 | -44.9029 | -51.9224 | -45.9675 | -42.8618 | 223 | -39.6224 | -41.5854 | -38.7739 | -45.2293 | -40.6482 | -46.904 | -41.1201 | -48.1448 | 223 | -49.8937 | -43.0117 | -42.176 | -47.7533 | -39.9194 | -44.8885 | -50.0178 | -42.8016 | -42.3356 | -47.4191 | -39.9549 | -45.2582 | -40.7563 | -41.9563 | -40.4541 | -47.5977 | -41.6428 | -38.2029 | -40.8804 | -41.7462 | -40.6137 | -47.2635 | -41.6783 | -38.5726
224 | -4.5161 | 0 | -4.3614 | 0 | -4.6763 | 0 | -4.3265 | 0 | -48.3115 | -97.2557 | -40.1632 | 33.2888 | -54.1754 | -29.7062 | -44.7692 | 98.5259 | -48.874 | -133.2427 | -47.9573 | 122.6268 | -52.2201 | -72.8246 | -41.7164 | 106.0957 | -52.5331 | 26.1152 | -51.8829 | 151.5485 | -56.3784 | 153.6463 | -51.9915 | 97.0688 | -16.9856 | 72.595 | -21.8235 | 96.9211 | -18.6276 | 33.8851 | -22.9306 | 104.5078 | -17.7075 | 120.7658 | -19.5183 | 112.8453 | -25.4173 | 12.5933 | -31.0964 | 153.9069 | -48.5873 | -44.8944 | -46.3553 | -46.3529 | -52.1029 | -43.4023 | -49.8575 | -56.981 | -47.8715 | -44.1426 | -51.3731 | -45.7505 | -42.3401 | 224 | -39.3973 | -42.1424 | -38.3664 | -44.8427 | -41.0275 | -48.3026 | -40.9606 | -48.4756 | 224 | -52.4649 | -43.3554 | -41.8368 | -47.7415 | -39.0409 | -45.1812 | -52.6196 | -43.1952 | -42.0264 | -47.4266 | -39.0758 | -45.531 | -40.3783 | -41.8392 | -39.6265 | -47.0117 | -41.3891 | -37.6638 | -40.533 | -41.679 | -39.8161 | -46.6968 | -41.424 | -38.0136
225 | -4.5817 | 0 | -4.4002 | 0 | -4.6773 | 0 | -4.3357 | 0 | -49.5737 | -88.3093 | -40.3836 | 13.9658 | -52.993 | -26.8014 | -45.9762 | 82.6753 | -48.8351 | -149.4898 | -47.6373 | 108.782 | -55.8136 | -37.9236 | -42.565 | 83.2373 | -50.6425 | 28.5304 | -50.5941 | 118.8338 | -53.7082 | 124.705 | -50.5849 | 110.7095 | -15.2187 | 62.5394 | -19.5125 | 80.5898 | -20.272 | 33.0509 | -21.5894 | 109.2101 | -15.8391 | 101.6344 | -17.6806 | 98.2029 | -38.5948 | -1.341 | -27.9019 | -177.1622 | -48.6262 | -44.2392 | -45.9874 | -45.7355 | -52.3097 | -42.4033 | -50.4705 | -60.4273 | -48.1364 | -43.3572 | -51.0838 | -45.0249 | -41.9307 | 225 | -39.682 | -43.0658 | -38.7279 | -44.5191 | -41.7623 | -48.0684 | -41.3751 | -46.6509 | 225 | -55.8456 | -43.5547 | -41.1538 | -47.9095 | -38.0031 | -45.7932 | -56.0271 | -43.4591 | -41.3998 | -47.6324 | -38.0676 | -46.1348 | -39.6575 | -41.4057 | -38.7755 | -46.6836 | -40.6247 | -37.2534 | -39.839 | -41.3101 | -39.0215 | -46.4065 | -40.6892 | -37.595
226 | -4.6449 | 0 | -4.444 | 0 | -4.6819 | 0 | -4.356 | 0 | -48.4181 | -76.8004 | -41.969 | -4.5285 | -51.5184 | -35.1129 | -48.2092 | 71.7956 | -49.6768 | -164.5518 | -48.373 | 92.5988 | -50.8939 | -13.0205 | -45.0658 | 60.7533 | -48.9013 | 21.4036 | -50.8633 | 87.3377 | -52.4176 | 98.9766 | -47.9499 | 106.4741 | -14.3317 | 48.5713 | -18.4648 | 60.9176 | -21.2087 | 40.2065 | -19.7501 | 109.7369 | -15.184 | 81.2562 | -16.9823 | 82.574 | -29.6233 | 133.8503 | -22.8446 | 179.9538 | -48.674 | -43.4431 | -45.4413 | -44.9826 | -52.8459 | -41.5017 | -51.2682 | -65.7483 | -48.1528 | -42.7214 | -51.2097 | -43.9123 | -41.8648 | 226 | -40.7062 | -43.9501 | -40.306 | -44.899 | -42.8262 | -46.5623 | -42.5667 | -44.6039 | 226 | -61.1034 | -43.5079 | -40.3377 | -48.4019 | -37.0577 | -46.5863 | -61.3043 | -43.4709 | -40.6266 | -48.164 | -37.1457 | -46.9122 | -38.7982 | -40.7964 | -38.0765 | -46.7657 | -39.4683 | -37.1829 | -38.9991 | -40.7594 | -38.3654 | -46.5278 | -39.5563 | -37.5088
227 | -4.6647 | 0 | -4.4411 | 0 | -4.6976 | 0 | -4.3929 | 0 | -46.009 | -76.872 | -45.8121 | -16.7861 | -50.8804 | -45.5249 | -51.3385 | 72.7528 | -51.3433 | -178.0142 | -50.1143 | 78.7967 | -46.7619 | -21.5287 | -51.3889 | 44.4895 | -47.5344 | 8.4804 | -53.0997 | 57.9343 | -52.641 | 72.4476 | -47.1758 | 91.3137 | -14.2704 | 33.4584 | -18.5159 | 39.815 | -20.5079 | 47.414 | -17.9922 | 103.9575 | -15.5355 | 60.2605 | -17.2442 | 67.349 | -23.2589 | 110.4695 | -19.6954 | 163.69 | -48.8352 | -42.873 | -44.883 | -44.343 | -53.5735 | -40.8964 | -52.1599 | -66.6898 | -47.8444 | -42.3747 | -51.8161 | -42.9633 | -42.3022 | 227 | -42.2576 | -44.0062 | -43.6334 | -45.9783 | -43.3741 | -45.0281 | -45.0415 | -43.742 | 227 | -62.0251 | -43.1797 | -39.6783 | -49.1324 | -36.4553 | -47.4623 | -62.2487 | -43.1468 | -39.9501 | -48.8759 | -36.5035 | -47.767 | -38.2083 | -40.2183 | -37.71 | -47.375 | -38.5222 | -37.6046 | -38.4319 | -40.1854 | -37.9818 | -47.1185 | -38.5704 | -37.9093
228 | -4.643 | 0 | -4.4487 | 0 | -4.6807 | 0 | -4.4355 | 0 | -43.9668 | -87.0713 | -50.9983 | 10.6406 | -50.6541 | -56.2891 | -52.6925 | 93.3343 | -53.909 | 174.7043 | -52.7694 | 82.9517 | -44.3149 | -38.7014 | -56.9498 | 131.2524 | -47.2768 | -0.2523 | -58.4757 | 32.4479 | -54.101 | 49.9245 | -47.9281 | 80.7822 | -15.0528 | 18.7797 | -19.7855 | 18.5036 | -19.0489 | 46.5362 | -16.5991 | 94.1261 | -16.9337 | 40.146 | -18.43 | 55.0002 | -20.7066 | 86.544 | -17.7149 | 143.5501 | -49.1357 | -42.8326 | -44.6152 | -44.0225 | -54.3467 | -40.8912 | -53.0385 | -59.3252 | -47.4125 | -42.4526 | -52.7533 | -42.4971 | -43.1093 | 228 | -42.4669 | -43.0486 | -47.3023 | -47.4588 | -42.3833 | -43.7329 | -47.088 | -44.1202 | 228 | -54.6822 | -42.7695 | -39.3795 | -49.898 | -36.4425 | -48.3578 | -54.8765 | -42.7318 | -39.587 | -49.666 | -36.4557 | -48.603 | -38.1896 | -39.9722 | -37.8096 | -48.3046 | -38.0484 | -38.4286 | -38.3839 | -39.9345 | -38.0171 | -48.0726 | -38.0616 | -38.6738
229 | -4.6008 | 0 | -4.4414 | 0 | -4.6658 | 0 | -4.4351 | 0 | -42.7415 | -102.293 | -46.4979 | 44.0927 | -51.1105 | -65.5666 | -50.4581 | 107.0074 | -56.992 | -179.7571 | -51.1847 | 95.246 | -43.0372 | -59.0765 | -47.0679 | 135.9934 | -47.3641 | -9.3173 | -82.0106 | 29.6377 | -57.3259 | 32.6455 | -48.6547 | 83.8895 | -16.8253 | 7.1001 | -22.7728 | -1.1323 | -17.9971 | 37.8804 | -15.7543 | 81.9381 | -19.9336 | 22.7416 | -20.6991 | 49.4334 | -20.0209 | 62.83 | -16.6812 | 122.3691 | -49.5035 | -43.4271 | -44.6902 | -44.0504 | -54.8433 | -41.4974 | -53.8164 | -55.1463 | -47.1789 | -42.9179 | -53.6875 | -42.6228 | -44.0943 | 229 | -40.7918 | -41.9253 | -44.0883 | -47.6057 | -40.5709 | -42.8778 | -44.7781 | -44.707 | 229 | -50.5455 | -42.5781 | -39.4496 | -50.4019 | -37.056 | -49.1506 | -50.7049 | -42.5131 | -39.6153 | -50.1775 | -37.0623 | -49.3813 | -38.8263 | -40.0894 | -38.3171 | -49.2461 | -38.1814 | -39.4285 | -38.9857 | -40.0244 | -38.4828 | -49.0217 | -38.1877 | -39.6592
230 | -4.5542 | 0 | -4.433 | 0 | -4.6603 | 0 | -4.459 | 0 | -42.3555 | -119.0396 | -42.5122 | 37.3425 | -51.0447 | -70.8087 | -47.9239 | 104.1961 | -57.5388 | -156.0218 | -48.943 | 85.3274 | -42.7212 | -80.4366 | -43.1902 | 116.676 | -46.9194 | -16.7522 | -59.4678 | 169.0578 | -62.8095 | 26.3191 | -47.7382 | 83.7331 | -19.5449 | 4.4531 | -29.3674 | -9.884 | -17.8713 | 25.8016 | -15.4705 | 68.1809 | -25.4712 | 20.9189 | -22.7151 | 59.8884 | -20.7129 | 38.9307 | -16.4499 | 100.8131 | -49.7452 | -44.3396 | -44.9484 | -44.3702 | -54.8936 | -42.3279 | -54.3158 | -53.0392 | -47.273 | -43.4252 | -54.1361 | -43.172 | -44.698 | 230 | -39.1337 | -41.1903 | -40.7078 | -46.5014 | -39.1457 | -42.5888 | -41.8088 | -44.2385 | 230 | -48.485 | -42.7188 | -39.816 | -50.4606 | -37.8949 | -49.6555 | -48.6062 | -42.6127 | -39.9112 | -50.2333 | -37.8689 | -49.8568 | -39.7854 | -40.3942 | -38.871 | -49.7031 | -38.739 | -40.0377 | -39.9066 | -40.2881 | -38.9662 | -49.4758 | -38.713 | -40.239
231 | -4.5305 | 0 | -4.4695 | 0 | -4.6532 | 0 | -4.4821 | 0 | -42.8386 | -136.1993 | -40.3489 | 23.2768 | -51.1667 | -81.9993 | -46.112 | 94.6309 | -54.1961 | -145.2574 | -48.216 | 70.1797 | -43.3841 | -101.7619 | -41.2735 | 96.0599 | -46.7944 | -23.5444 | -52.7945 | 148.7613 | -68.1417 | 77.9569 | -46.5124 | 75.7523 | -21.4269 | 19.7641 | -33.2328 | 71.8142 | -18.7941 | 14.7238 | -15.7918 | 54.6729 | -27.8046 | 71.2693 | -21.8547 | 76.4404 | -23.2757 | 15.5102 | -17.0562 | 78.9773 | -49.6645 | -45.0279 | -45.163 | -44.7934 | -54.4613 | -42.9458 | -54.4929 | -52.2079 | -47.5578 | -43.6374 | -53.8796 | -43.8485 | -44.5736 | 231 | -38.1832 | -40.9528 | -38.7995 | -45.7627 | -38.4961 | -42.9001 | -39.9071 | -43.6254 | 231 | -47.6774 | -43.0273 | -40.2629 | -49.9918 | -38.4763 | -49.8397 | -47.7384 | -42.9046 | -40.3113 | -49.8081 | -38.4637 | -50.0108 | -40.4974 | -40.6325 | -39.1069 | -49.4101 | -39.379 | -39.9204 | -40.5584 | -40.5098 | -39.1553 | -49.2264 | -39.3664 | -40.0915
232 | -4.5776 | 0 | -4.4923 | 0 | -4.6515 | 0 | -4.4805 | 0 | -44.2387 | -151.0762 | -39.2131 | 7.3752 | -51.8993 | -88.5206 | -45.0009 | 80.5097 | -51.3921 | -155.2186 | -48.0368 | 54.614 | -45.1737 | -122.0675 | -40.441 | 75.5502 | -46.9052 | -30.4509 | -49.1169 | 125.6565 | -60.5943 | 112.5706 | -46.2775 | 68.6585 | -19.665 | 34.902 | -24.4277 | 78.4118 | -20.5914 | 9.1039 | -16.7849 | 42.0535 | -21.7824 | 83.3017 | -19.3639 | 79.2078 | -29.8116 | -1.2038 | -18.6601 | 58.7566 | -49.3904 | -45.2489 | -45.0813 | -44.9842 | -53.742 | -43.1551 | -54.3282 | -52.2882 | -47.7808 | -43.3204 | -53.0469 | -44.5148 | -44.0796 | 232 | -37.8515 | -41.1602 | -37.7677 | -45.312 | -38.5041 | -43.6141 | -38.9907 | -43.4844 | 232 | -47.7106 | -43.2032 | -40.4066 | -49.2497 | -38.6628 | -49.6767 | -47.7959 | -43.1293 | -40.5037 | -49.0905 | -38.6746 | -49.8477 | -40.6713 | -40.5037 | -38.7428 | -48.5546 | -40.0225 | -39.4281 | -40.7566 | -40.4298 | -38.8399 | -48.3954 | -40.0343 | -39.5991
233 | -4.6264 | 0 | -4.5489 | 0 | -4.6584 | 0 | -4.4743 | 0 | -46.6493 | -160.4512 | -39.0436 | -10.0755 | -52.4097 | -97.1443 | -44.8005 | 64.5747 | -49.878 | -172.4802 | -48.4 | 41.1374 | -48.6207 | -137.0106 | -40.6419 | 54.2939 | -46.8064 | -37.0818 | -47.2314 | 100.0458 | -55.9269 | 104.0406 | -46.3548 | 63.2462 | -17.1628 | 31.6413 | -20.5339 | 59.7378 | -22.2949 | 14.8418 | -18.5127 | 33.3428 | -18.5806 | 68.5275 | -17.6077 | 70.8473 | -37.5397 | 93.2054 | -21.8821 | 41.2523 | -49.019 | -44.86 | -44.7622 | -44.543 | -53.0398 | -42.8859 | -53.9171 | -53.2987 | -47.7767 | -42.5574 | -52.1662 | -44.957 | -43.7447 | 233 | -38.1814 | -41.8692 | -37.6397 | -45.1597 | -39.1772 | -44.5333 | -38.9169 | -43.3194 | 233 | -48.6723 | -43.1503 | -39.9166 | -48.4909 | -38.337 | -49.2587 | -48.7498 | -43.1183 | -40.0687 | -48.3814 | -38.4116 | -49.4428 | -40.2336 | -40.1358 | -37.931 | -47.6173 | -40.4081 | -39.0863 | -40.3111 | -40.1038 | -38.0831 | -47.5078 | -40.4827 | -39.2704
234 | -4.6801 | 0 | -4.5782 | 0 | -4.6911 | 0 | -4.4536 | 0 | -49.5244 | -155.7246 | -39.988 | -26.7817 | -53.157 | -103.0934 | -45.474 | 49.6726 | -49.5066 | 167.7008 | -48.8018 | 27.1466 | -54.0806 | -130.3062 | -42.0362 | 33.9726 | -46.7025 | -42.701 | -46.8246 | 74.6394 | -53.1163 | 84.907 | -45.4028 | 57.7807 | -15.5542 | 20.0118 | -18.8449 | 36.7197 | -22.2017 | 25.1014 | -20.7764 | 31.812 | -16.9251 | 49.3429 | -16.6376 | 59.1532 | -26.4268 | 99.1886 | -27.7178 | 35.5796 | -48.7908 | -44.1695 | -44.2826 | -43.6958 | -52.699 | -42.2279 | -53.3544 | -55.1296 | -47.4724 | -41.6282 | -51.6717 | -44.8486 | -43.861 | 234 | -39.3454 | -42.9488 | -38.483 | -45.3441 | -40.5627 | -45.2926 | -39.5013 | -42.591 | 234 | -50.4495 | -42.7923 | -39.0157 | -48.1208 | -37.6497 | -48.6633 | -50.5514 | -42.7813 | -39.2422 | -48.0079 | -37.7743 | -48.9008 | -39.4894 | -39.6025 | -36.9481 | -47.0935 | -40.2704 | -39.1699 | -39.5913 | -39.5915 | -37.1746 | -46.9806 | -40.395 | -39.4074
235 | -4.7291 | 0 | -4.5841 | 0 | -4.7343 | 0 | -4.4321 | 0 | -50.14 | -135.958 | -42.3583 | -39.0738 | -53.7429 | -108.1253 | -46.9476 | 38.5421 | -50.2645 | 147.1719 | -50.3077 | 9.4088 | -54.4244 | -83.8602 | -45.2552 | 18.2862 | -46.7478 | -52.3747 | -47.8008 | 51.1574 | -51.9611 | 63.4639 | -44.9069 | 46.9168 | -14.9043 | 4.5605 | -18.5131 | 11.87 | -20.869 | 27.7721 | -22.4652 | 41.1707 | -16.53 | 28.4052 | -16.5815 | 46.9157 | -22.5202 | 81.153 | -32.5876 | 97.4395 | -48.7089 | -43.5779 | -43.7993 | -42.7948 | -52.8105 | -41.5349 | -52.8536 | -56.4882 | -46.9206 | -40.9317 | -51.7481 | -44.1991 | -44.4319 | 235 | -41.4263 | -44.0575 | -40.5745 | -46.3924 | -42.6301 | -45.7562 | -41.0392 | -42.2315 | 235 | -51.7591 | -42.1915 | -38.0657 | -48.2264 | -36.9508 | -48.1193 | -51.9041 | -42.1863 | -38.3627 | -48.0762 | -37.1028 | -48.4215 | -38.8488 | -39.0702 | -36.2026 | -47.164 | -39.615 | -39.6976 | -38.9938 | -39.065 | -36.4996 | -47.0138 | -39.767 | -39.9998
236 | -4.728 | 0 | -4.5758 | 0 | -4.7519 | 0 | -4.4306 | 0 | -47.4481 | -127.0468 | -45.8104 | -32.8761 | -56.0945 | -110.4909 | -48.7036 | 33.7047 | -51.8723 | 129.2591 | -54.5705 | 4.991 | -49.1622 | -78.7178 | -51.0007 | 29.3797 | -47.2065 | -58.1767 | -50.0921 | 33.6272 | -52.2002 | 42.4991 | -45.1248 | 32.1451 | -15.2004 | -11.6114 | -19.3637 | -14.2496 | -19.6381 | 21.3338 | -21.709 | 52.8821 | -17.229 | 7.5158 | -17.2409 | 36.4411 | -21.1246 | 58.67 | -25.0047 | 115.9494 | -48.7006 | -43.4549 | -43.5364 | -42.1733 | -53.2397 | -41.2674 | -52.6695 | -55.1035 | -46.3217 | -40.7008 | -52.4117 | -43.5566 | -45.0276 | 236 | -43.3074 | -44.2053 | -43.6442 | -49.0495 | -44.0787 | -45.5372 | -43.1462 | -42.5353 | 236 | -50.3755 | -41.5937 | -37.4453 | -48.6639 | -36.6916 | -47.9176 | -50.5277 | -41.5698 | -37.7427 | -48.4878 | -36.8368 | -48.2389 | -38.7269 | -38.8084 | -35.9728 | -47.8359 | -38.9808 | -40.2757 | -38.8791 | -38.7845 | -36.2702 | -47.6598 | -39.126 | -40.597
237 | -4.6971 | 0 | -4.5468 | 0 | -4.7475 | 0 | -4.4461 | 0 | -44.9033 | -134.3151 | -45.7202 | -5.6141 | -56.6426 | -101.3931 | -50.3118 | 33.7221 | -55.0977 | 114.957 | -56.8629 | 44.8141 | -46.0186 | -93.6549 | -49.0393 | 77.2564 | -47.8189 | -59.7928 | -53.5486 | 25.0788 | -53.6008 | 25.0782 | -46.0244 | 24.5524 | -16.4697 | -26.7614 | -21.6912 | -42.8602 | -19.2069 | 10.1579 | -20.087 | 53.3529 | -19.0862 | -11.8845 | -18.3933 | 30.7138 | -21.144 | 36.5865 | -21.1398 | 102.9403 | -48.5779 | -43.8138 | -43.4822 | -41.8982 | -53.6326 | -41.5091 | -52.7343 | -53.2319 | -45.9471 | -40.8358 | -53.289 | -43.2944 | -45.1052 | 237 | -42.126 | -43.4936 | -44.1843 | -51.3563 | -42.6752 | -44.7117 | -43.7809 | -43.3851 | 237 | -48.5348 | -41.25 | -37.2011 | -49.0858 | -36.9623 | -47.9868 | -48.6851 | -41.1996 | -37.4521 | -48.8851 | -37.063 | -48.2882 | -39.1167 | -38.7851 | -36.1387 | -48.7422 | -38.7476 | -40.3577 | -39.267 | -38.7347 | -36.3897 | -48.5415 | -38.8483 | -40.6591
238 | -4.6576 | 0 | -4.5389 | 0 | -4.7144 | 0 | -4.4697 | 0 | -43.4049 | -148.4053 | -42.3065 | 2.0348 | -54.6928 | -89.7292 | -51.7066 | 39.4558 | -60.2355 | 110.4533 | -51.0375 | 51.8809 | -44.4129 | -113.4587 | -43.7226 | 77.4045 | -47.8902 | -59.732 | -58.3039 | 36.8585 | -56.3689 | 13.0661 | -46.5382 | 22.002 | -18.8406 | -38.2612 | -26.3735 | -78.945 | -19.7747 | -2.6689 | -19.0162 | 44.8662 | -22.6058 | -29.1429 | -19.6566 | 30.8677 | -22.9495 | 14.4528 | -19.6058 | 85.3496 | -48.2966 | -44.4291 | -43.5246 | -41.9841 | -53.8005 | -42.019 | -52.8787 | -52.1988 | -45.8724 | -41.2498 | -54.0428 | -43.3316 | -44.6346 | 238 | -39.6719 | -42.7282 | -41.3417 | -49.1306 | -40.2277 | -43.981 | -41.7976 | -43.8984 | 238 | -47.5412 | -41.2148 | -37.3265 | -49.2616 | -37.4801 | -48.1643 | -47.6599 | -41.158 | -37.5144 | -49.0861 | -37.5493 | -48.409 | -39.7715 | -38.867 | -36.5922 | -49.5039 | -38.7927 | -39.9202 | -39.8902 | -38.8102 | -36.7801 | -49.3284 | -38.8619 | -40.1649
239 | -4.635 | 0 | -4.545 | 0 | -4.686 | 0 | -4.5079 | 0 | -42.8511 | -164.8105 | -39.586 | -5.8319 | -52.9431 | -96.9437 | -51.6563 | 52.2034 | -62.7238 | 159.9461 | -47.9818 | 37.8456 | -43.9829 | -135.916 | -40.5994 | 62.9288 | -47.2776 | -63.8128 | -57.2223 | 81.8363 | -60.7411 | 14.8049 | -46.516 | 16.3072 | -22.0245 | -36.4551 | -33.6534 | -163.1191 | -21.516 | -12.2125 | -18.9415 | 33.3605 | -28.8605 | -27.8082 | -19.7694 | 35.7512 | -26.8317 | -3.0481 | -19.508 | 67.6506 | -47.8625 | -45.0987 | -43.5021 | -42.2243 | -53.5187 | -42.5231 | -52.7967 | -51.9301 | -46.0254 | -41.6637 | -54.252 | -43.549 | -44.0542 | 239 | -37.7742 | -42.2746 | -38.7698 | -46.6701 | -38.3626 | -43.695 | -39.5347 | -43.7815 | 239 | -47.2951 | -41.3904 | -37.5893 | -48.9737 | -37.9781 | -48.1107 | -47.3851 | -41.3394 | -37.7164 | -48.8327 | -38.0152 | -48.2888 | -40.4637 | -38.8671 | -37.0287 | -49.707 | -39.004 | -39.3682 | -40.5537 | -38.8161 | -37.1558 | -49.566 | -39.0411 | -39.5463
240 | -4.611 | 0 | -4.5588 | 0 | -4.6674 | 0 | -4.5097 | 0 | -43.1249 | 178.8196 | -37.8958 | -19.7059 | -51.7034 | -109.882 | -49.8646 | 58.3566 | -57.2047 | 177.448 | -46.6479 | 17.5621 | -44.5209 | -158.6418 | -38.8525 | 44.3244 | -46.5816 | -69.3462 | -51.8302 | 88.6856 | -62.7597 | 54.4018 | -46.4279 | 3.9037 | -23.5476 | -18.1185 | -27.7087 | 104.0786 | -24.0073 | -13.4738 | -19.9699 | 21.5716 | -30.6091 | 29.6533 | -19.0015 | 37.1584 | -35.1989 | 2.6864 | -20.5255 | 52.1689 | -47.4372 | -45.581 | -43.3784 | -42.4025 | -52.9381 | -42.9248 | -52.3522 | -52.1278 | -46.1637 | -41.8655 | -53.8503 | -43.8894 | -43.5458 | 240 | -36.6196 | -42.1525 | -37.1154 | -45.1861 | -37.2695 | -43.7262 | -37.9706 | -43.4426 | 240 | -47.5168 | -41.5527 | -37.7915 | -48.3793 | -38.366 | -47.6848 | -47.569 | -41.4963 | -37.8928 | -48.2707 | -38.4151 | -47.8425 | -40.97 | -38.7674 | -37.2545 | -49.2915 | -39.3306 | -38.8784 | -41.0222 | -38.711 | -37.3558 | -49.1829 | -39.3797 | -39.0361
241 | -4.621 | 0 | -4.5968 | 0 | -4.6678 | 0 | -4.5151 | 0 | -44.1544 | 163.7024 | -37.1215 | -35.3787 | -51.616 | -126.116 | -48.0507 | 53.6006 | -53.5834 | 163.3809 | -46.2924 | -0.5737 | -46.1324 | 178.1895 | -38.1395 | 24.0938 | -46.3049 | -77.3499 | -48.4196 | 73.7638 | -57.4627 | 76.5356 | -46.9331 | -8.7711 | -21.6556 | -6.03 | -23.2556 | 64.3216 | -25.881 | -1.0586 | -22.2954 | 13.8011 | -25.0561 | 37.7144 | -18.227 | 31.91 | -33.841 | 86.6404 | -23.0015 | 42.0578 | -47.1788 | -45.7927 | -43.1952 | -42.2999 | -52.3897 | -43.2068 | -51.6437 | -52.6443 | -46.2031 | -41.7218 | -53.1866 | -44.3553 | -43.2363 | 241 | -36.2099 | -42.3309 | -36.3233 | -44.5894 | -36.9624 | -43.9204 | -37.2554 | -43.4226 | 241 | -48.0233 | -41.5821 | -37.6789 | -47.7929 | -38.61 | -46.9759 | -48.0475 | -41.5353 | -37.7848 | -47.7219 | -38.6917 | -47.1286 | -41.1717 | -38.5742 | -37.1008 | -48.5898 | -39.7585 | -38.5685 | -41.1959 | -38.5274 | -37.2067 | -48.5188 | -39.8402 | -38.7212
242 | -4.6489 | 0 | -4.6115 | 0 | -4.6974 | 0 | -4.5024 | 0 | -45.8794 | 153.3659 | -37.3357 | -51.6182 | -52.1585 | -142.6014 | -46.9819 | 44.1588 | -51.9708 | 143.5084 | -47.1652 | -17.6099 | -49.2617 | 156.701 | -38.4563 | 4.5792 | -46.4886 | -86.3743 | -46.7862 | 54.7545 | -53.5161 | 65.9567 | -48.4649 | -19.1512 | -19.5721 | -11.8812 | -21.3135 | 33.7643 | -24.9543 | 9.6484 | -25.7261 | 22.9925 | -22.1087 | 23.4647 | -17.8634 | 23.85 | -27.4004 | 79.22 | -25.9953 | 53.1202 | -47.1701 | -45.6701 | -43.0474 | -41.881 | -52.2404 | -43.3888 | -50.967 | -53.2755 | -46.0044 | -41.2756 | -52.6584 | -44.9005 | -43.1604 | 242 | -36.6435 | -42.8221 | -36.4989 | -44.9972 | -37.5207 | -44.2872 | -37.4987 | -43.8577 | 242 | -48.6266 | -41.3555 | -37.2321 | -47.6289 | -38.7773 | -46.2696 | -48.664 | -41.307 | -37.3786 | -47.543 | -38.8864 | -46.4646 | -41.0212 | -38.3985 | -36.6267 | -48.0469 | -40.289 | -38.463 | -41.0586 | -38.35 | -36.7732 | -47.961 | -40.3981 | -38.658
243 | -4.7014 | 0 | -4.6109 | 0 | -4.7238 | 0 | -4.4987 | 0 | -48.1387 | 151.0002 | -38.4973 | -64.6843 | -53.8408 | -157.4714 | -46.3532 | 34.2292 | -51.6391 | 122.3253 | -48.7278 | -32.2139 | -55.1474 | 137.8383 | -39.8685 | -12.7176 | -47.0854 | -94.8153 | -46.2375 | 35.6662 | -51.5658 | 48.8831 | -51.1407 | -27.4188 | -18.6347 | -25.1402 | -21.0144 | 4.9798 | -23.7299 | 7.8402 | -25.6479 | 54.4102 | -21.0722 | 5.3606 | -18.1947 | 15.2147 | -25.3084 | 61.888 | -24.8365 | 78.2225 | -47.4547 | -45.6261 | -43.0647 | -41.3961 | -52.5094 | -43.6144 | -50.6344 | -53.5128 | -45.6818 | -40.9 | -52.564 | -45.3761 | -43.1163 | 243 | -37.9365 | -43.4329 | -37.4982 | -46.128 | -39.0068 | -44.7093 | -38.7113 | -44.6563 | 243 | -48.8114 | -40.9804 | -36.6947 | -47.8985 | -39.0035 | -45.9106 | -48.9019 | -40.958 | -36.8974 | -47.7856 | -39.1157 | -46.1357 | -40.9247 | -38.3633 | -36.1986 | -47.9531 | -40.7652 | -38.3925 | -41.0152 | -38.3409 | -36.4013 | -47.8402 | -40.8774 | -38.6176
244 | -4.6999 | 0 | -4.5969 | 0 | -4.7276 | 0 | -4.5139 | 0 | -49.601 | 160.1849 | -40.4149 | -71.2958 | -58.1418 | -171.1049 | -45.9894 | 21.902 | -51.913 | 99.5519 | -51.2872 | -34.5609 | -71.2875 | -157.4969 | -42.5697 | -23.9828 | -48.1689 | -99.4973 | -46.4565 | 17.2096 | -50.9621 | 30.8722 | -54.7697 | -17.2608 | -18.8235 | -40.8705 | -22.1725 | -24.2442 | -23.5677 | -1.5954 | -21.7243 | 64.0079 | -21.4265 | -14.0112 | -19.1956 | 8.6817 | -25.6387 | 44.5307 | -21.285 | 81.0828 | -47.9563 | -45.7589 | -43.2859 | -41.0305 | -53.179 | -44.0558 | -50.7024 | -53.3878 | -45.3874 | -40.7219 | -52.9602 | -45.8135 | -42.9561 | 244 | -39.8554 | -43.708 | -39.0832 | -48.123 | -41.5084 | -45.1286 | -40.8998 | -45.7525 | 244 | -48.6879 | -40.6875 | -36.3306 | -48.5821 | -39.4589 | -45.9748 | -48.7909 | -40.6598 | -36.5166 | -48.4514 | -39.5419 | -46.1885 | -41.059 | -38.586 | -36.022 | -48.3633 | -41.2166 | -38.2285 | -41.162 | -38.5583 | -36.208 | -48.2326 | -41.2996 | -38.4422
245 | -4.6676 | 0 | -4.5964 | 0 | -4.7271 | 0 | -4.557 | 0 | -48.4379 | 170.4558 | -42.2434 | -65.5926 | -67.364 | -151.0385 | -46.3567 | 6.7931 | -53.1933 | 76.4915 | -52.7681 | -17.0187 | -55.3617 | -106.0325 | -46.1247 | -16.3592 | -48.99 | -98.1578 | -47.4803 | -0.9909 | -51.204 | 15.8378 | -54.5363 | 12.9477 | -20.1285 | -56.5787 | -25.1773 | -57.3085 | -24.8483 | -11.134 | -18.8855 | 55.8362 | -22.8817 | -32.3177 | -20.4927 | 7.8786 | -27.9325 | 34.0533 | -18.8775 | 69.0378 | -48.5222 | -45.8639 | -43.5935 | -40.9011 | -54.2019 | -44.5943 | -51.1276 | -53.1763 | -45.3551 | -40.7565 | -53.8425 | -46.2271 | -42.6859 | 245 | -41.2978 | -43.7406 | -40.5511 | -49.8869 | -43.9864 | -45.4742 | -43.3923 | -46.2496 | 245 | -48.5087 | -40.6875 | -36.2335 | -49.6055 | -39.9979 | -46.4005 | -48.5799 | -40.628 | -36.3441 | -49.4748 | -40.0373 | -46.5706 | -41.1963 | -38.9259 | -36.0889 | -49.2461 | -41.6307 | -37.9588 | -41.2675 | -38.8664 | -36.1995 | -49.1154 | -41.6701 | -38.1289
246 | -4.6621 | 0 | -4.5874 | 0 | -4.7223 | 0 | -4.6056 | 0 | -46.2419 | 166.5957 | -41.8412 | -52.1603 | -59.4933 | -78.3274 | -47.9706 | -8.3734 | -55.3636 | 48.2478 | -50.319 | -5.6994 | -50.1905 | -126.1518 | -45.7927 | 12.4587 | -49.0015 | -95.7784 | -49.8544 | -19.2666 | -51.909 | 2.484 | -50.6067 | 19.7908 | -22.6675 | -69.0556 | -31.3061 | -107.1366 | -27.8053 | -12.4242 | -17.2914 | 42.1389 | -25.7619 | -47.2553 | -21.2332 | 13.3583 | -31.5406 | 47.0428 | -17.604 | 52.6677 | -48.8883 | -45.7185 | -43.7052 | -40.986 | -55.2477 | -45.0037 | -51.896 | -53.1012 | -45.7597 | -40.9585 | -55.0679 | -46.5504 | -42.4194 | 246 | -40.4418 | -43.7036 | -40.4242 | -48.7537 | -43.1423 | -45.7914 | -43.431 | -45.5714 | 246 | -48.4391 | -41.0976 | -36.3239 | -50.6603 | -40.4163 | -47.1737 | -48.5138 | -41.0374 | -36.3804 | -50.5254 | -40.3981 | -47.2904 | -41.0564 | -39.0431 | -36.2964 | -50.4805 | -41.963 | -37.6971 | -41.1311 | -38.9829 | -36.3529 | -50.3456 | -41.9448 | -37.8138
247 | -4.6623 | 0 | -4.6181 | 0 | -4.7149 | 0 | -4.6578 | 0 | -44.7094 | 152.8958 | -39.6038 | -48.8657 | -53.3651 | -86.2507 | -51.5045 | -16.2628 | -59.0174 | 11.3839 | -47.4193 | -12.3121 | -47.7967 | -149.2488 | -41.9206 | 18.475 | -48.4329 | -94.1497 | -54.8074 | -29.7221 | -53.3401 | -10.8823 | -47.7082 | 6.6877 | -26.574 | -71.69 | -32.745 | 140.3581 | -30.2906 | 11.4537 | -16.7386 | 26.8402 | -30.2647 | -55.6863 | -20.7442 | 18.0536 | -30.0724 | 81.2785 | -17.4804 | 33.975 | -48.6964 | -45.2776 | -43.5413 | -41.2393 | -55.2315 | -45.1135 | -52.911 | -52.961 | -46.4787 | -41.2939 | -56.2157 | -46.8008 | -42.3064 | 247 | -38.2982 | -43.7533 | -38.705 | -46.2019 | -40.213 | -46.0997 | -40.7306 | -44.4454 | 247 | -48.2987 | -41.8164 | -36.577 | -50.6134 | -40.4954 | -48.1961 | -48.3429 | -41.7638 | -36.5815 | -50.5166 | -40.4557 | -48.2532 | -40.6153 | -38.879 | -36.6316 | -51.5976 | -42.1827 | -37.5915 | -40.6595 | -38.8264 | -36.6361 | -51.5008 | -42.143 | -37.6486
248 | -4.6781 | 0 | -4.636 | 0 | -4.743 | 0 | -4.6536 | 0 | -44.2552 | 134.9177 | -37.5838 | -56.9951 | -50.0912 | -106.8209 | -55.8831 | 6.7322 | -64.4867 | -64.5765 | -45.3953 | -25.9655 | -46.9504 | -174.3381 | -39.0753 | 6.9721 | -47.0821 | -95.8324 | -61.2102 | 17.6499 | -56.3763 | -20.6583 | -46.1843 | -13.2352 | -30.0396 | -50.7497 | -26.3219 | 83.7025 | -27.5829 | 34.2704 | -17.0521 | 12.1881 | -35.9917 | -36.1403 | -19.6297 | 16.7027 | -26.0029 | 83.2946 | -18.433 | 15.5473 | -47.9253 | -44.6925 | -43.0884 | -41.5034 | -53.5698 | -45.0362 | -53.8704 | -52.661 | -47.1507 | -41.6321 | -56.0579 | -47.0868 | -42.4165 | 248 | -36.5412 | -43.9281 | -36.8638 | -44.0872 | -37.8651 | -46.3373 | -38.281 | -43.3764 | 248 | -47.9829 | -42.4726 | -36.8253 | -48.9338 | -40.4002 | -49.1274 | -48.025 | -42.4077 | -36.8498 | -48.8268 | -40.3826 | -49.2168 | -40.0144 | -38.4103 | -36.954 | -51.4219 | -42.4508 | -37.6735 | -40.0565 | -38.3454 | -36.9785 | -51.3149 | -42.4332 | -37.7629
249 | -4.6722 | 0 | -4.6667 | 0 | -4.7813 | 0 | -4.6565 | 0 | -44.8749 | 115.7527 | -36.4113 | -69.6407 | -48.2093 | -130.4412 | -52.6887 | 39.706 | -61.0393 | -157.8894 | -44.5007 | -44.7592 | -47.349 | 161.3101 | -37.5145 | -9.3272 | -45.6292 | -105.2377 | -53.8968 | 49.9295 | -61.1103 | 1.8154 | -45.7841 | -36.3628 | -28.7142 | -28.7252 | -23.1754 | 49.5751 | -24.6649 | 31.0683 | -18.2435 | -0.4166 | -35.0906 | 2.7375 | -18.8765 | 9.7374 | -23.8753 | 70.8469 | -20.7441 | -1.4664 | -47.2139 | -44.2737 | -42.61 | -41.5811 | -51.7998 | -45.0745 | -54.1941 | -51.9141 | -47.0394 | -41.78 | -54.4675 | -47.4922 | -42.56 | 249 | -35.5887 | -44.1208 | -35.6968 | -42.8932 | -36.5169 | -46.3333 | -36.8254 | -42.6335 | 249 | -47.2419 | -42.3672 | -36.9089 | -47.1331 | -40.4078 | -49.4128 | -47.2474 | -42.2581 | -36.9246 | -47.0185 | -40.418 | -49.5376 | -39.6015 | -37.9378 | -37.1078 | -49.8008 | -42.8255 | -37.7787 | -39.607 | -37.8287 | -37.1235 | -49.6862 | -42.8357 | -37.9035
250 | -4.7 | 0 | -4.6749 | 0 | -4.8116 | 0 | -4.6184 | 0 | -46.568 | 98.7902 | -36.1004 | -84.3935 | -47.7966 | -155.5791 | -48.6855 | 37.1259 | -57.6177 | 151.2254 | -44.4665 | -64.3935 | -48.7361 | 139.0445 | -36.9985 | -27.6495 | -45.0015 | -120.9306 | -49.5817 | 38.1017 | -57.0512 | 36.2874 | -46.3704 | -62.0994 | -26.8787 | -28.6255 | -21.9416 | 19.8956 | -23.4283 | 18.3919 | -20.1362 | -7.1935 | -33.0327 | 6.5251 | -18.7832 | 0.0224 | -23.4944 | 55.5741 | -25.4454 | -13.3319 | -47.0111 | -44.1049 | -42.3917 | -41.4486 | -50.9291 | -45.4682 | -53.8975 | -50.7687 | -46.0906 | -41.7178 | -52.9796 | -48.1319 | -42.4027 | 250 | -35.4653 | -44.2823 | -35.3056 | -42.6684 | -36.1157 | -45.7904 | -36.3139 | -42.4681 | 250 | -46.0687 | -41.3906 | -36.7486 | -46.2542 | -40.7933 | -49.0859 | -46.0938 | -41.279 | -36.8302 | -46.1175 | -40.8498 | -49.2791 | -39.4049 | -37.6917 | -37.0178 | -48.3047 | -43.457 | -37.5911 | -39.43 | -37.5801 | -37.0994 | -48.168 | -43.5135 | -37.7843
251 | -4.7031 | 0 | -4.6594 | 0 | -4.824 | 0 | -4.6145 | 0 | -49.1805 | 85.7653 | -36.6012 | -98.5401 | -48.6577 | 179.2488 | -46.2895 | 24.1596 | -56.7188 | 112.7516 | -45.6021 | -82.0868 | -51.0116 | 118.622 | -37.4048 | -45.4106 | -45.6583 | -138.5143 | -47.3434 | 20.9152 | -53.047 | 26.7651 | -48.1492 | -91.6102 | -26.666 | -35.9651 | -22.0893 | -8.9931 | -23.9542 | 5.804 | -21.9517 | -1.6137 | -33.2539 | 1.3182 | -19.3523 | -9.4401 | -24.7216 | 43.6419 | -34.0757 | 23.6599 | -47.3355 | -44.211 | -42.5238 | -41.2339 | -50.9371 | -46.2579 | -53.4719 | -49.5076 | -45.0625 | -41.6203 | -52.2961 | -49.0037 | -41.958 | 251 | -36.1187 | -44.2361 | -35.6905 | -43.6372 | -36.6381 | -45.0424 | -36.6652 | -43.2379 | 251 | -44.8045 | -40.3594 | -36.5308 | -46.2777 | -41.5985 | -48.6479 | -44.8482 | -40.2385 | -36.6194 | -46.1131 | -41.6434 | -48.8574 | -39.5079 | -37.8207 | -36.9172 | -47.6367 | -44.3443 | -37.134 | -39.5516 | -37.6998 | -37.0058 | -47.4721 | -44.3892 | -37.3435
252 | -4.7222 | 0 | -4.6422 | 0 | -4.8339 | 0 | -4.6098 | 0 | -52.9391 | 81.3328 | -37.9515 | -109.1751 | -50.9904 | 154.8553 | -45.0228 | 7.1726 | -57.6035 | 78.6065 | -47.8599 | -95.108 | -54.5 | 101.5353 | -38.8075 | -60.1587 | -47.7468 | -152.0521 | -46.3256 | 0.4321 | -51.3384 | 11.915 | -51.2276 | -126.5066 | -27.8443 | -41.8375 | -23.5743 | -39.11 | -26.3505 | -1.7686 | -21.5792 | 8.7225 | -35.0857 | 6.4922 | -20.4712 | -16.2267 | -27.4857 | 44.1183 | -26.3927 | 77.4236 | -47.9785 | -44.3498 | -42.9335 | -41.1113 | -51.4941 | -47.2991 | -53.0758 | -48.5917 | -44.4566 | -41.5758 | -52.2789 | -49.955 | -41.3545 | 252 | -37.6117 | -44.1707 | -36.8174 | -45.8393 | -38.1831 | -44.6597 | -37.8931 | -44.9913 | 252 | -43.8695 | -39.7344 | -36.3891 | -46.8519 | -42.6569 | -48.2419 | -43.9495 | -39.6227 | -36.5015 | -46.6602 | -42.6893 | -48.466 | -39.6276 | -38.2113 | -36.8536 | -47.6367 | -45.3128 | -36.5206 | -39.7076 | -38.0996 | -36.966 | -47.445 | -45.3452 | -36.7447
253 | -4.7159 | 0 | -4.6339 | 0 | -4.8448 | 0 | -4.6339 | 0 | -56.7636 | 100.5623 | -40.02 | -111.6901 | -55.6777 | 130.2507 | -44.8068 | -11.6395 | -59.8103 | 44.7218 | -51.0808 | -97.9688 | -60.5408 | 95.7121 | -41.3881 | -67.9548 | -50.6394 | -154.9665 | -46.3909 | -20.386 | -50.8491 | -2.7146 | -55.1822 | -176.5182 | -29.8742 | -37.8956 | -26.7091 | -74.2878 | -29.7947 | 15.0164 | -19.6918 | 9.099 | -35.6799 | 31.6732 | -21.8401 | -17.6022 | -28.1496 | 70.3794 | -20.9489 | 69.1184 | -48.7358 | -44.3491 | -43.4663 | -41.103 | -52.4038 | -48.2983 | -52.587 | -48.1885 | -44.2862 | -41.63 | -52.6807 | -50.7901 | -40.7677 | 253 | -39.815 | -44.4114 | -38.5264 | -49.3753 | -40.8536 | -44.9399 | -40.0598 | -47.0142 | 253 | -43.4726 | -39.5703 | -36.3871 | -47.7699 | -43.6644 | -47.7422 | -43.5546 | -39.4414 | -36.4691 | -47.559 | -43.6644 | -47.9531 | -39.6332 | -38.7504 | -36.9141 | -48.0468 | -46.1562 | -35.9229 | -39.7152 | -38.6215 | -36.9961 | -47.8359 | -46.1562 | -36.1338
254 | -4.7288 | 0 | -4.6461 | 0 | -4.8932 | 0 | -4.7026 | 0 | -55.0933 | 129.8242 | -41.2272 | -99.8503 | -70.7027 | 103.6616 | -45.6815 | -30.3587 | -62.0694 | 6.7007 | -53.2894 | -80.4428 | -64.7262 | 155.4828 | -44.0944 | -57.0023 | -52.8284 | -144.2546 | -47.6579 | -40.0318 | -51.0846 | -15.7248 | -55.7091 | 107.6321 | -30.5222 | -23.4156 | -31.8649 | -126.495 | -27.3676 | 47.8739 | -18.0444 | -0.931 | -33.2332 | 46.4489 | -22.6653 | -14.3849 | -24.4143 | 82.5534 | -18.4041 | 51.7274 | -49.2754 | -43.9248 | -43.9519 | -41.2441 | -53.6738 | -48.8545 | -51.9781 | -48.3424 | -44.6156 | -41.7476 | -53.4586 | -51.3072 | -40.4136 | 254 | -41.0477 | -45.1221 | -39.702 | -52.6802 | -43.5159 | -45.9731 | -42.3071 | -48.0438 | 254 | -43.6136 | -39.8868 | -36.5153 | -49.0277 | -44.2084 | -47.0849 | -43.6963 | -39.7224 | -36.5415 | -48.7806 | -44.1519 | -47.2755 | -39.196 | -39.2231 | -37.0188 | -48.8125 | -46.6611 | -35.5204 | -39.2787 | -39.0587 | -37.045 | -48.5654 | -46.6046 | -35.711
255 | -4.738 | 0 | -4.646 | 0 | -4.9367 | 0 | -4.7614 | 0 | -51.4472 | 130.4135 | -39.513 | -88.8866 | -59.4276 | -91.0667 | -47.9481 | -48.3748 | -61.2148 | -45.3978 | -51.2541 | -58.9399 | -56.9181 | 170.229 | -42.6996 | -35.8417 | -53.0891 | -126.6523 | -50.2883 | -55.7194 | -51.329 | -22.6247 | -52.2098 | 53.1061 | -29.3921 | -16.0405 | -33.3405 | 142.8962 | -23.1679 | 48.1141 | -17.2077 | -17.0013 | -31.4048 | 46.367 | -22.592 | -11.759 | -21.4134 | 73.7807 | -17.1974 | 33.7546 | -49.1699 | -43.109 | -44.1486 | -41.5254 | -55.3183 | -48.6363 | -51.3179 | -49.0538 | -45.4958 | -41.8882 | -54.8452 | -51.3585 | -40.2656 | 255 | -39.2019 | -46.2049 | -38.6839 | -50.2739 | -42.1716 | -47.2689 | -41.6066 | -47.3788 | 255 | -44.3158 | -40.7578 | -36.7874 | -50.6723 | -43.9903 | -46.3812 | -44.4078 | -40.5591 | -36.764 | -50.3816 | -43.8749 | -46.5565 | -38.371 | -39.4106 | -37.1502 | -50.1992 | -46.7125 | -35.3289 | -38.463 | -39.2119 | -37.1268 | -49.9085 | -46.5971 | -35.5042
256 | -4.7555 | 0 | -4.6453 | 0 | -4.9874 | 0 | -4.8245 | 0 | -49.0314 | 115.9504 | -37.0997 | -93.0911 | -51.9174 | -113.0469 | -52.7656 | -59.3276 | -56.3651 | -99.2621 | -47.4033 | -58.7456 | -52.3388 | 148.4544 | -39.4095 | -36.1546 | -50.806 | -111.0175 | -54.5308 | -59.5893 | -51.0197 | -33.4556 | -49.3997 | 15.2272 | -28.7656 | -19.8621 | -29.319 | 83.757 | -20.7425 | 35.2174 | -17.1507 | -35.8572 | -30.8322 | 46.3389 | -22.1773 | -14.2529 | -19.8246 | 58.2324 | -16.9022 | 16.4386 | -47.9582 | -42.1831 | -43.7755 | -41.8567 | -55.5559 | -47.6285 | -50.907 | -50.2217 | -46.8063 | -42.0515 | -57.8796 | -50.8819 | -40.41 | 256 | -36.6973 | -46.9685 | -36.6061 | -45.6987 | -38.904 | -47.628 | -38.875 | -45.5759 | 256 | -45.4662 | -42.0508 | -37.1012 | -50.9106 | -42.9832 | -45.9196 | -45.5764 | -41.8189 | -37.0322 | -50.5685 | -42.804 | -46.0825 | -37.4276 | -39.02 | -37.296 | -53.2343 | -46.2366 | -35.4226 | -37.5378 | -38.7881 | -37.227 | -52.8922 | -46.0574 | -35.5855
257 | -4.763 | 0 | -4.6576 | 0 | -5.0013 | 0 | -4.8568 | 0 | -48.3575 | 93.265 | -35.5974 | -105.3881 | -47.4737 | -140.2068 | -59.1881 | -11.5649 | -51.8277 | -152.373 | -44.169 | -76.0201 | -50.0598 | 116.307 | -37.2429 | -48.4457 | -46.6216 | -114.1297 | -57.649 | -31.3118 | -52.1018 | -53.7678 | -47.5166 | -20.9486 | -30.117 | -24.9345 | -27.4261 | 46.5958 | -19.836 | 19.2126 | -17.8599 | -56.133 | -30.8165 | 53.6845 | -22.1852 | -21.2978 | -19.6433 | 41.2339 | -17.2957 | 0.0276 | -46.4432 | -41.6307 | -42.5839 | -42.162 | -51.7909 | -46.6307 | -51.1654 | -50.9896 | -46.3568 | -42.3451 | -58.0443 | -50.5873 | -41.1309 | 257 | -35.1134 | -46.5039 | -35.0157 | -42.0241 | -36.5697 | -47.5093 | -36.8171 | -43.4058 | 257 | -46.2266 | -41.5938 | -37.399 | -47.1333 | -41.9731 | -46.1641 | -46.332 | -41.3555 | -37.3052 | -46.7896 | -41.7739 | -46.3086 | -36.8677 | -37.8209 | -37.5821 | -53.3867 | -45.9297 | -36.1296 | -36.9731 | -37.5826 | -37.4883 | -53.043 | -45.7305 | -36.2741
258 | -4.7896 | 0 | -4.6718 | 0 | -5.0038 | 0 | -4.8712 | 0 | -49.705 | 73.6326 | -35.0436 | -119.0749 | -45.4014 | -175.3854 | -52.2622 | 18.7561 | -50.3281 | 155.5257 | -42.8277 | -103.2154 | -49.7432 | 83.5707 | -36.0843 | -64.5387 | -44.0085 | -137.1032 | -54.5677 | -10.9782 | -57.0659 | -58.3491 | -46.7122 | -59.5471 | -33.7916 | -15.8221 | -27.6755 | 14.8207 | -20.2372 | 3.8267 | -19.161 | -78.4756 | -29.0749 | 67.0646 | -22.9872 | -29.7035 | -20.8131 | 25.9465 | -18.2016 | -15.3189 | -46.1255 | -41.8012 | -41.5167 | -42.3052 | -49.02 | -47.0902 | -51.8007 | -50.0858 | -43.899 | -42.6289 | -52.9179 | -51.6952 | -42.0864 | 258 | -34.5271 | -45.8645 | -34.3044 | -40.4455 | -35.2768 | -47.9405 | -35.6675 | -42.0054 | 258 | -45.2962 | -39.1094 | -37.5156 | -44.3482 | -42.4184 | -46.7969 | -45.414 | -38.8952 | -37.434 | -44.0162 | -42.219 | -46.9295 | -37.0116 | -36.7271 | -37.8393 | -48.2461 | -47.0234 | -37.0826 | -37.1294 | -36.5129 | -37.7577 | -47.9141 | -46.824 | -37.2152
259 | -4.8096 | 0 | -4.6739 | 0 | -5.0011 | 0 | -4.8566 | 0 | -51.3817 | 64.1362 | -35.0679 | -133.1311 | -45.5336 | 149.8279 | -48.3898 | 10.858 | -51.5999 | 112.7057 | -43.0761 | -130.4141 | -50.078 | 55.8885 | -35.7604 | -81.4352 | -43.8224 | -162.8735 | -51.6813 | -14.931 | -56.866 | -21.5577 | -46.976 | -101.3348 | -33.19 | 37.382 | -30.03 | -17.804 | -21.972 | -7.0484 | -21.4435 | -104.3363 | -25.874 | 71.8066 | -24.6491 | -34.077 | -23.6015 | 18.3385 | -19.722 | -28.6133 | -46.8464 | -42.3962 | -41.3844 | -42.4245 | -48.5143 | -49.0641 | -51.6505 | -48.4815 | -42.6261 | -42.8458 | -50.8028 | -54.044 | -41.3766 | 259 | -34.6022 | -45.4239 | -34.259 | -40.7503 | -34.9931 | -47.2886 | -35.3419 | -41.9659 | 259 | -43.6719 | -37.8165 | -37.6149 | -43.8404 | -44.3902 | -46.6494 | -43.8076 | -37.625 | -37.5679 | -43.5132 | -44.2075 | -46.7939 | -37.5866 | -36.5748 | -38.0362 | -46.1289 | -49.3701 | -36.3755 | -37.7223 | -36.3833 | -37.9892 | -45.8017 | -49.1874 | -36.52
260 | -4.8231 | 0 | -4.6791 | 0 | -5.002 | 0 | -4.8235 | 0 | -52.3692 | 56.1203 | -35.8278 | -146.4225 | -47.1332 | 118.303 | -46.1354 | -2.2312 | -54.5389 | 80.7426 | -44.3598 | -155.8329 | -50.2467 | 29.9178 | -36.2864 | -99.268 | -45.171 | 175.5325 | -49.9835 | -28.1865 | -53.2655 | -24.4328 | -47.41 | -144.5335 | -26.5765 | 48.4676 | -35.7896 | -67.2816 | -24.8191 | -3.1824 | -24.9621 | -135.8357 | -22.8877 | 65.7847 | -26.5322 | -28.7295 | -27.0519 | 34.4746 | -21.6606 | -38.781 | -47.6055 | -42.9753 | -41.812 | -42.6406 | -48.9453 | -50.6276 | -51.1635 | -47.4278 | -42.37 | -43.1088 | -50.2455 | -54.5293 | -39.6978 | 260 | -35.4288 | -44.7289 | -34.9168 | -42.254 | -35.6066 | -46.1618 | -35.7946 | -42.735 | 260 | -42.6047 | -37.5469 | -37.8175 | -44.2662 | -45.9485 | -46.1615 | -42.7487 | -37.368 | -37.8171 | -43.9433 | -45.8041 | -46.34 | -38.1522 | -36.9889 | -38.2857 | -45.5664 | -49.8502 | -34.6958 | -38.2962 | -36.81 | -38.2853 | -45.2435 | -49.7058 | -34.8743
261 | -4.8453 | 0 | -4.6812 | 0 | -5.0719 | 0 | -4.7984 | 0 | -53.1999 | 44.8789 | -37.5392 | -156.4041 | -49.8229 | 86.9876 | -44.8211 | -16.7542 | -58.8758 | 58.4537 | -46.1776 | 176.4494 | -50.3713 | 3.3652 | -37.9312 | -114.1115 | -47.5103 | 160.1395 | -49.6583 | -44.6927 | -51.6073 | -39.6224 | -47.1309 | 173.4367 | -22.5348 | 37.0481 | -36.1031 | -177.3895 | -24.9024 | 20.7165 | -29.2367 | 179.3372 | -20.8092 | 52.6635 | -26.4474 | -17.6428 | -24.7578 | 63.8811 | -23.7465 | -45.8003 | -48.2053 | -43.3029 | -42.3733 | -42.9748 | -49.6858 | -49.51 | -50.6226 | -47.107 | -42.5562 | -43.3219 | -50.1422 | -52.0367 | -38.1894 | 261 | -37.1798 | -44.0855 | -36.3209 | -44.4583 | -37.2598 | -45.7015 | -37.1851 | -43.5647 | 261 | -42.2617 | -37.7109 | -38.1295 | -45.0046 | -44.8288 | -45.5507 | -42.4258 | -37.4843 | -38.1764 | -44.6139 | -44.7116 | -45.8242 | -38.4576 | -37.528 | -38.4766 | -45.461 | -47.3555 | -33.1175 | -38.6217 | -37.3014 | -38.5235 | -45.0703 | -47.2383 | -33.391
262 | -4.8771 | 0 | -4.7073 | 0 | -5.156 | 0 | -4.7806 | 0 | -54.5525 | 29.201 | -39.8053 | -154.2119 | -53.8513 | 51.3646 | -44.1612 | -31.4598 | -65.3339 | 51.7816 | -48.4949 | 141.5919 | -50.5774 | -23.1159 | -40.8728 | -120.2184 | -50.4253 | 149.3479 | -50.5312 | -58.425 | -51.5527 | -58.3413 | -46.0528 | 133.5385 | -20.2779 | 20.505 | -29.3758 | 131.4748 | -21.4716 | 27.7515 | -31.7263 | 117.5552 | -19.7669 | 38.0187 | -24.9276 | -15.1319 | -20.687 | 63.1894 | -25.723 | -52.5354 | -48.6806 | -43.059 | -42.8661 | -43.3173 | -50.4189 | -47.0434 | -50.0628 | -47.2732 | -42.9553 | -43.3831 | -50.1331 | -49.2732 | -37.1719 | 262 | -39.4997 | -43.7512 | -38.0386 | -47.3155 | -40.0167 | -46.091 | -39.3758 | -43.8853 | 262 | -42.3961 | -38.0782 | -38.4402 | -45.7116 | -42.3361 | -44.9068 | -42.5659 | -37.7993 | -38.5367 | -45.2629 | -42.2628 | -45.2822 | -38.1819 | -37.989 | -38.506 | -45.4258 | -44.5659 | -32.0159 | -38.3517 | -37.7101 | -38.6025 | -44.9771 | -44.4926 | -32.3913
263 | -4.906 | 0 | -4.7217 | 0 | -5.2779 | 0 | -4.7922 | 0 | -57.0363 | 10.0694 | -39.939 | -138.478 | -58.6337 | -5.2176 | -43.9109 | -47.2798 | -70.2794 | 94.7651 | -50.6822 | 86.9371 | -51.0552 | -50.5391 | -43.3535 | -103.8278 | -54.0338 | 149.6054 | -51.886 | -64.9298 | -52.9113 | -73.2331 | -44.746 | 96.8122 | -19.4167 | 3.697 | -25.9085 | 103.9291 | -18.8887 | 17.456 | -30.3035 | 70.3591 | -19.7049 | 20.9201 | -23.5003 | -25.7582 | -18.3648 | 47.7413 | -27.9152 | -62.6516 | -49.1169 | -42.1575 | -43.1762 | -43.531 | -51.0115 | -44.8138 | -49.4053 | -47.9381 | -43.406 | -43.128 | -50.042 | -47.0553 | -36.704 | 263 | -39.7979 | -43.6949 | -38.2218 | -49.9957 | -42.3662 | -47.114 | -40.6446 | -43.7066 | 263 | -43.0321 | -38.5 | -38.625 | -46.2898 | -40.0921 | -44.1274 | -43.2164 | -38.1281 | -38.7388 | -45.7336 | -40.0216 | -44.6131 | -37.2515 | -38.2702 | -38.222 | -45.3203 | -42.3336 | -31.4261 | -37.4358 | -37.8983 | -38.3358 | -44.7641 | -42.2631 | -31.9118
264 | -4.9111 | 0 | -4.7362 | 0 | -5.3516 | 0 | -4.7659 | 0 | -62.1828 | -11.2137 | -37.4516 | -134.3425 | -57.8554 | -82.6572 | -44.1626 | -64.5822 | -67.7274 | 111.2511 | -49.4568 | 19.827 | -52.1907 | -79.1831 | -40.9967 | -85.4486 | -57.1508 | 165.8212 | -52.2284 | -66.5287 | -55.5441 | -80.6815 | -43.4759 | 60.8193 | -19.7682 | -11.0968 | -24.393 | 83.5259 | -17.6837 | 1.4414 | -29.343 | 45.7659 | -20.8556 | 6.667 | -23.2753 | -43.1036 | -17.3712 | 29.7941 | -31.8436 | -80.5678 | -49.4947 | -40.9733 | -43.2165 | -43.4869 | -51.5533 | -43.0554 | -48.7401 | -49.2109 | -43.915 | -42.5409 | -50.0917 | -45.2851 | -36.9299 | 264 | -37.3978 | -44.0758 | -36.3922 | -48.8142 | -40.582 | -48.2931 | -38.8473 | -43.0422 | 264 | -44.2998 | -39.0039 | -38.5758 | -46.8171 | -38.3192 | -43.3885 | -44.4747 | -38.5634 | -38.721 | -46.2017 | -38.2895 | -43.9742 | -36.0622 | -38.3054 | -37.6298 | -45.3555 | -40.5489 | -31.5783 | -36.2371 | -37.8649 | -37.775 | -44.7401 | -40.5192 | -32.164
265 | -4.9157 | 0 | -4.7517 | 0 | -5.3767 | 0 | -4.7634 | 0 | -77.1735 | 27.9221 | -35.318 | -144.4444 | -53.8522 | -130.7673 | -45.416 | -85.5693 | -70.8588 | 131.3274 | -46.26 | -35.8651 | -54.8944 | -111.5907 | -37.9566 | -90.8884 | -56.6547 | -160.4224 | -51.7597 | -77.5915 | -56.6743 | -64.7761 | -42.8195 | 23.4312 | -21.248 | -20.755 | -24.0221 | 68.2264 | -17.7441 | -15.6327 | -29.1265 | 33.7323 | -23.4755 | 0.1164 | -24.1546 | -65.9269 | -17.7054 | 10.5862 | -40.8127 | -129.0896 | -49.475 | -39.9867 | -42.9047 | -43.2211 | -52.6157 | -41.9516 | -48.2126 | -51.9157 | -44.3571 | -41.9118 | -50.8845 | -44.1931 | -38.0136 | 265 | -35.2573 | -45.4007 | -34.6056 | -45.5502 | -37.8125 | -49.1868 | -36.5957 | -42.4752 | 265 | -47 | -39.4414 | -38.3054 | -47.864 | -37.1999 | -42.8359 | -47.164 | -38.9804 | -38.4577 | -47.239 | -37.1882 | -43.4492 | -35.071 | -37.989 | -36.9961 | -46.1328 | -39.4414 | -32.6369 | -35.235 | -37.528 | -37.1484 | -45.5078 | -39.4297 | -33.2502
266 | -4.9411 | 0 | -4.7562 | 0 | -5.3395 | 0 | -4.78 | 0 | -63.6243 | 74.7778 | -34.4005 | -159.86 | -51.0421 | -163.9107 | -48.9369 | -108.6221 | -61.3086 | 175.5983 | -44.2373 | -81.443 | -63.2663 | -159.0272 | -36.2587 | -104.9693 | -52.4743 | -151.5871 | -52.5665 | -101.0504 | -53.9488 | -73.8782 | -43.3873 | -19.6733 | -23.3358 | -15.6126 | -24.2978 | 60.7769 | -19.0442 | -30.0076 | -28.4015 | 30.7746 | -26.646 | 17.8052 | -26.4938 | -96.7481 | -19.5354 | -6.3318 | -35.1304 | 112.4099 | -48.4913 | -39.6566 | -42.2582 | -43.0968 | -54.4679 | -42.0316 | -48.2523 | -57.5348 | -44.57 | -41.5961 | -53.6625 | -44.1793 | -39.7068 | 266 | -34.3023 | -48.5551 | -33.8352 | -43.3442 | -36.1477 | -49.9837 | -35.4054 | -42.5549 | 266 | -52.5937 | -39.6289 | -38.1557 | -49.7117 | -37.2754 | -42.9128 | -52.7786 | -39.2305 | -38.3168 | -49.1284 | -37.2516 | -43.4723 | -34.7155 | -37.3171 | -36.655 | -48.9063 | -39.4231 | -34.3673 | -34.9004 | -36.9187 | -36.8161 | -48.323 | -39.3993 | -34.9268
267 | -4.9642 | 0 | -4.7991 | 0 | -5.2432 | 0 | -4.8118 | 0 | -61.8097 | 28.1401 | -34.3702 | -174.9475 | -48.957 | 160.1688 | -60.246 | -126.7902 | -53.9986 | 131.9449 | -43.7942 | -122.4957 | -60.5495 | 13.8754 | -35.5757 | -120.7334 | -48.2348 | -167.6104 | -56.6929 | -135.1479 | -55.6407 | -114.2529 | -45.2216 | -73.3535 | -22.85 | 3.8422 | -24.2438 | 61.5488 | -21.4661 | -36.8798 | -27.0693 | 28.5813 | -24.1903 | 47.0582 | -29.9619 | -145.3422 | -23.1638 | -13.5023 | -28.8631 | 79.9753 | -47.1241 | -39.9588 | -41.1876 | -43.6553 | -51.6631 | -43.4392 | -50.0022 | -55.2978 | -43.5697 | -42.0296 | -55.7053 | -45.8682 | -41.0675 | 267 | -34.2142 | -52.5286 | -33.8906 | -42.3329 | -35.3333 | -52.4025 | -35.0982 | -43.2064 | 267 | -50.3336 | -38.6055 | -38.6911 | -46.864 | -38.6401 | -44.759 | -50.4987 | -38.3265 | -38.8435 | -46.4199 | -38.6274 | -45.1904 | -34.9946 | -36.2234 | -37.0654 | -50.9062 | -41.0691 | -35.8243 | -35.1597 | -35.9444 | -37.2178 | -50.4621 | -41.0564 | -36.2557
268 | -5.0191 | 0 | -4.839 | 0 | -5.2264 | 0 | -4.8261 | 0 | -68.284 | 23.4797 | -34.9787 | 170.577 | -49.8967 | 111.3721 | -54.7574 | 9.7254 | -54.4109 | 75.3361 | -44.2829 | -162.976 | -54.7305 | -29.2239 | -35.3697 | -136.3555 | -47.3168 | 154.9705 | -65.2133 | 155.8465 | -75.159 | -61.026 | -47.0834 | -141.5934 | -19.6032 | 9.619 | -22.7707 | 62.0734 | -23.7367 | -25.9184 | -25.6899 | 19.8098 | -20.0356 | 48.0749 | -29.7953 | 140.2769 | -26.9973 | 10.9899 | -26.0682 | 60.4629 | -47.6132 | -40.7662 | -40.7855 | -44.5663 | -48.7538 | -45.4225 | -52.6515 | -49.2498 | -42.0035 | -42.9757 | -50.7804 | -49.2967 | -41.4492 | 268 | -34.839 | -51.4788 | -34.456 | -42.9105 | -35.0538 | -54.3223 | -35.0822 | -44.1848 | 268 | -44.2307 | -36.9844 | -39.5472 | -43.9148 | -40.5835 | -47.4251 | -44.4108 | -36.7771 | -39.7402 | -43.5274 | -40.5964 | -47.8254 | -35.7471 | -35.7664 | -37.9566 | -45.9414 | -44.4577 | -36.2228 | -35.9272 | -35.5591 | -38.1496 | -45.554 | -44.4706 | -36.6231
269 | -5.0797 | 0 | -4.8688 | 0 | -5.3063 | 0 | -4.8219 | 0 | -62.6024 | 27.2927 | -36.3075 | 158.0467 | -54.4062 | 64.2386 | -47.2749 | -6.9131 | -59.8236 | 35.9422 | -45.1164 | 153.6182 | -52.6261 | -45.2557 | -35.7904 | -152.3282 | -50.2662 | 127.8597 | -58.4217 | 56.6991 | -57.6432 | -31.6629 | -45.531 | 156.256 | -16.8825 | 0.7015 | -20.9968 | 56.1381 | -22.3519 | -7.0468 | -24.7369 | 9.273 | -17.2186 | 37.0751 | -25.9651 | 88.394 | -23.6078 | 40.0575 | -24.5832 | 44.9592 | -48.5571 | -41.5727 | -41.6665 | -45.1235 | -48.9008 | -45.4321 | -53.2203 | -46.318 | -42.0641 | -43.3688 | -49.6344 | -48.5055 | -39.1307 | 269 | -36.2307 | -46.9209 | -35.474 | -44.5034 | -35.5521 | -50.6443 | -35.3309 | -44.0772 | 269 | -41.2383 | -36.9844 | -40.0438 | -44.032 | -40.5633 | -47.914 | -41.4492 | -36.7578 | -40.3016 | -43.5945 | -40.6102 | -48.3984 | -36.493 | -36.5868 | -38.2891 | -44.7656 | -43.6367 | -33.8244 | -36.7039 | -36.3602 | -38.5469 | -44.3281 | -43.6836 | -34.3088
270 | -5.142 | 0 | -4.9027 | 0 | -5.4583 | 0 | -4.8333 | 0 | -58.3602 | -12.5245 | -38.7438 | 150.8863 | -60.2455 | -2.8615 | -43.3201 | -26.5057 | -73.0348 | 2.4013 | -44.673 | 103.4988 | -50.3309 | -57.898 | -37.3048 | -167.0665 | -54.8618 | 111.3397 | -51.9346 | 23.9826 | -54.9252 | -56.7549 | -42.412 | 113.9318 | -15.2339 | -14.131 | -19.651 | 44.506 | -19.206 | -8.6195 | -24.4248 | -5.9119 | -15.6537 | 21.7462 | -23.4261 | 55.5255 | -19.6156 | 35.3398 | -24.3496 | 29.9427 | -49.0871 | -41.7481 | -42.6428 | -44.7472 | -49.4972 | -42.7013 | -53.1136 | -44.7786 | -42.6381 | -42.6605 | -49.305 | -44.4622 | -36.8257 | 270 | -38.6663 | -43.1816 | -36.6919 | -44.5481 | -37.0217 | -47.2379 | -36.0242 | -41.9472 | 270 | -39.6366 | -37.4961 | -39.6052 | -44.5945 | -37.7986 | -47.6553 | -39.8759 | -37.1798 | -39.9139 | -44.0389 | -37.868 | -48.2803 | -36.6061 | -37.5008 | -37.5185 | -44.4023 | -39.5595 | -31.3674 | -36.8454 | -37.1845 | -37.8272 | -43.8467 | -39.6289 | -31.9924
271 | -5.193 | 0 | -4.9157 | 0 | -5.6609 | 0 | -4.8694 | 0 | -55.1231 | -55.402 | -41.0712 | 162.2901 | -58.2539 | -84.1896 | -40.8816 | -50.2761 | -67.2783 | 160.737 | -42.5123 | 52.5842 | -48.3197 | -74.5253 | -39.9122 | -173.6241 | -61.9439 | 108.6834 | -47.9272 | -2.9799 | -55.1634 | -79.6268 | -39.6471 | 82.5048 | -14.584 | -31.0258 | -19.056 | 30.4147 | -17.1999 | -23.1574 | -25.6469 | -22.0539 | -15.0293 | 4.8452 | -22.2675 | 26.3791 | -17.3049 | 18.724 | -24.9767 | 17.9544 | -49.5806 | -41.0602 | -43.3423 | -43.4204 | -49.9477 | -39.7906 | -52.4704 | -44.0906 | -43.2672 | -41.275 | -48.861 | -41.243 | -35.4776 | 271 | -40.8244 | -40.7115 | -36.6586 | -42.3839 | -39.3031 | -44.6997 | -36.4469 | -39.502 | 271 | -38.8976 | -38.0742 | -38.2274 | -45.032 | -34.8749 | -46.8095 | -39.1749 | -37.6063 | -38.551 | -44.2868 | -34.9212 | -47.601 | -35.8672 | -38.1493 | -36.082 | -43.9453 | -36.3273 | -29.8167 | -36.1445 | -37.6814 | -36.4056 | -43.2001 | -36.3736 | -30.6082
272 | -5.1764 | 0 | -4.9001 | 0 | -5.8334 | 0 | -4.9002 | 0 | -52.4489 | -95.1609 | -39.3902 | 177.9727 | -53.7151 | -123.6574 | -39.6224 | -77.0303 | -62.1068 | 130.5482 | -39.6452 | 6.4181 | -46.9348 | -93.5149 | -41.5658 | -161.6298 | -68.2494 | -172.8301 | -45.5628 | -31.6158 | -58.1121 | -94.8039 | -37.3557 | 53.1609 | -15.0254 | -47.4952 | -19.2727 | 16.4131 | -16.5504 | -42.4395 | -27.8797 | -35.9118 | -15.4325 | -10.4622 | -22.5664 | 0.7032 | -16.3807 | -1.7698 | -26.2582 | 15.3744 | -50.1014 | -39.7731 | -43.6245 | -41.7907 | -50.1956 | -37.4305 | -51.3435 | -44.2073 | -43.7483 | -39.8967 | -48.3369 | -38.8115 | -35.2631 | 272 | -39.0304 | -39.3783 | -34.7799 | -39.4547 | -40.4511 | -43.0471 | -35.5076 | -37.3159 | 272 | -39.0309 | -38.5719 | -36.6143 | -45.2955 | -32.5304 | -45.5101 | -39.3072 | -37.9149 | -36.8905 | -44.3622 | -32.5303 | -46.4433 | -34.5967 | -38.4481 | -34.7203 | -43.4368 | -33.9114 | -29.4297 | -34.873 | -37.7911 | -34.9965 | -42.5035 | -33.9113 | -30.3629
273 | -5.1341 | 0 | -4.9036 | 0 | -5.9055 | 0 | -4.9329 | 0 | -50.6671 | -131.3705 | -36.7652 | 172.6182 | -50.5139 | -152.9773 | -39.5837 | -106.528 | -62.5246 | 111.794 | -37.396 | -37.0029 | -46.367 | -114.2039 | -39.9193 | -152.2326 | -58.2023 | -136.5753 | -44.5798 | -62.6794 | -62.0035 | -70.7679 | -35.8429 | 21.491 | -16.4279 | -61.3831 | -20.3329 | 4.6669 | -17.1273 | -61.8938 | -32.3655 | -40.3039 | -16.7983 | -22.242 | -24.3625 | -23.6624 | -16.6685 | -22.8396 | -26.9216 | 21.5567 | -50.2871 | -38.5962 | -43.248 | -40.5182 | -50.7066 | -35.7855 | -50.0757 | -45.5204 | -43.8546 | -38.9627 | -48.1828 | -37.1082 | -36.1104 | 273 | -36.4193 | -39.2374 | -32.986 | -37.1765 | -38.9801 | -42.3248 | -34.0104 | -35.8073 | 273 | -40.3863 | -38.7205 | -35.3841 | -45.803 | -30.8819 | -44.1702 | -40.6168 | -37.9491 | -35.5853 | -44.8011 | -30.8526 | -45.1428 | -33.4621 | -38.1139 | -33.8286 | -43.2792 | -32.2046 | -30.2049 | -33.6926 | -37.3425 | -34.0298 | -42.2773 | -32.1753 | -31.1775
274 | -5.0945 | 0 | -4.8966 | 0 | -5.8438 | 0 | -4.9676 | 0 | -49.8927 | -163.3555 | -35.5428 | 157.1228 | -48.6959 | 177.0294 | -40.9654 | -137.6345 | -64.3248 | 129.1875 | -36.3055 | -79.4544 | -46.7847 | -134.851 | -37.8911 | -159.3523 | -53.0232 | -156.502 | -45.102 | -97.4953 | -57.2634 | -52.4141 | -35.5034 | -13.8538 | -19.0355 | -67.9579 | -22.1173 | -0.833 | -18.837 | -79.3302 | -37.9705 | -0.9523 | -19.0448 | -26.2749 | -28.4812 | -49.3299 | -18.259 | -43.979 | -25.995 | 26.5264 | -49.6553 | -37.9736 | -42.3297 | -39.9678 | -52.0537 | -35.083 | -49.0645 | -49.1993 | -43.3718 | -38.6817 | -48.8536 | -36.3243 | -37.9303 | 274 | -35.1881 | -40.4245 | -32.2675 | -36.0555 | -37.2477 | -42.6976 | -33.2329 | -35.3988 | 274 | -44.1048 | -38.2773 | -34.8733 | -47.1571 | -30.1864 | -43.2207 | -44.3027 | -37.528 | -35.0002 | -46.2099 | -30.1154 | -44.0969 | -32.8791 | -37.2352 | -33.5872 | -43.957 | -31.4277 | -32.0865 | -33.077 | -36.4859 | -33.7141 | -43.0098 | -31.3567 | -32.9627
275 | -5.1087 | 0 | -4.9144 | 0 | -5.6713 | 0 | -4.9761 | 0 | -50.1567 | 169.3988 | -35.7094 | 142.3875 | -48.7745 | 145.9747 | -44.338 | -172.6952 | -58.9606 | 145.6547 | -36.7725 | -120.5702 | -48.3173 | -152.1204 | -36.9816 | -172.0282 | -51.4154 | 179.705 | -47.7459 | -138.0095 | -54.9358 | -73.7574 | -36.95 | -50.8933 | -21.6688 | -52.9963 | -23.6627 | 5.9984 | -21.8563 | -87.9629 | -32.3301 | 38.9789 | -20.8203 | -12.563 | -43.1885 | -93.3555 | -21.8232 | -59.8438 | -24.8473 | 24.7859 | -48.4152 | -38.2346 | -41.5549 | -40.3254 | -54.4113 | -35.6956 | -48.5628 | -61.0189 | -42.7025 | -39.2151 | -50.5745 | -36.8197 | -40.25 | 275 | -35.354 | -43.2106 | -32.8764 | -36.4823 | -36.5301 | -44.591 | -33.7777 | -36.7312 | 275 | -55.9102 | -37.5938 | -35.2167 | -49.4969 | -30.7812 | -42.8915 | -56.1045 | -37.0312 | -35.3493 | -48.74 | -30.7195 | -43.5867 | -33.1259 | -36.4462 | -34.1064 | -45.6601 | -31.9053 | -34.5787 | -33.3202 | -35.8836 | -34.239 | -44.9032 | -31.8436 | -35.2739
276 | -5.1637 | 0 | -4.9387 | 0 | -5.5315 | 0 | -4.9584 | 0 | -51.4061 | 146.4178 | -36.302 | 130.8603 | -50.9096 | 121.452 | -50.6865 | 135.3888 | -54.6777 | 128.461 | -38.6962 | -158.2445 | -50.7942 | -161.4824 | -36.5041 | 175.8828 | -52.548 | 161.7481 | -52.3554 | 156.5845 | -55.5177 | -100.9394 | -40.9108 | -91.0401 | -19.6063 | -30.8699 | -22.8209 | 17.5842 | -24.9702 | -77.5817 | -27.7784 | 30.5867 | -19.0565 | 3.9029 | -31.8878 | 92.4008 | -27.5406 | -53.6838 | -24.0072 | 17.4975 | -47.1935 | -39.1534 | -41.4185 | -41.4903 | -57.377 | -37.4854 | -48.6809 | -54.801 | -42.5309 | -40.2512 | -53.2668 | -38.7502 | -40.9814 | 276 | -36.0265 | -47.172 | -34.2266 | -38.3407 | -36.2424 | -47.7084 | -35.0786 | -40.4842 | 276 | -49.6373 | -37.3672 | -36.3266 | -52.4383 | -32.5467 | -43.1494 | -49.8623 | -36.9994 | -36.5319 | -51.8455 | -32.527 | -43.7225 | -33.9897 | -36.2548 | -35.0875 | -48.3281 | -33.8115 | -35.4499 | -34.2147 | -35.887 | -35.2928 | -47.7353 | -33.7918 | -36.023
277 | -5.2585 | 0 | -4.9851 | 0 | -5.5124 | 0 | -4.9617 | 0 | -53.9963 | 131.9418 | -37.0875 | 119.2497 | -53.3869 | 106.4196 | -50.328 | 25.6169 | -51.8799 | 98.7808 | -41.508 | 164.4109 | -53.3912 | -154.4464 | -36.1602 | 161.1926 | -53.0127 | 157.8812 | -49.9143 | 63.45 | -61.8927 | -138.8217 | -48.035 | -152.1715 | -16.1532 | -32.3545 | -20.6728 | 17.6383 | -24.0496 | -54.8915 | -25.9384 | 14.6782 | -16.1054 | 2.4049 | -25.3697 | 66.6012 | -27.9213 | -6.5876 | -23.7685 | 5.9815 | -46.0993 | -40.2985 | -41.4547 | -42.6422 | -57.5289 | -39.7477 | -49.6452 | -48.1257 | -42.696 | -40.8992 | -55.7624 | -41.4343 | -39.3844 | 277 | -36.9012 | -47.0458 | -35.599 | -40.8759 | -35.9917 | -48.1174 | -35.7184 | -46.7028 | 277 | -42.8672 | -37.4375 | -37.3837 | -52.5438 | -34.7626 | -44.1328 | -43.1406 | -37.1836 | -37.6805 | -52.0165 | -34.786 | -44.6835 | -35.04 | -36.1962 | -35.6407 | -50.7773 | -36.4492 | -33.872 | -35.3134 | -35.9423 | -35.9375 | -50.25 | -36.4726 | -34.4227
278 | -5.3639 | 0 | -5.0347 | 0 | -5.643 | 0 | -4.971 | 0 | -56.4411 | 125.7896 | -38.9751 | 107.9513 | -59.7031 | 69.9958 | -43.2731 | -28.0493 | -53.0605 | 53.5833 | -44.4195 | 112.5368 | -53.0486 | -142.9057 | -36.495 | 144.4825 | -53.9163 | 138.4916 | -44.3942 | 12.2645 | -61.1241 | -3.2158 | -45.6203 | 98.7144 | -13.9191 | -45.1366 | -18.9966 | 8.0256 | -20.6062 | -55.3197 | -26.2382 | 0.9027 | -14.1029 | -8.4813 | -22.4866 | 44.5141 | -22.9567 | -1.4742 | -25.454 | -6.3316 | -45.8403 | -41.3236 | -41.1851 | -42.3012 | -51.4262 | -40.4525 | -51.9488 | -45.272 | -42.1217 | -39.98 | -51.0191 | -42.3071 | -37.9057 | 278 | -38.862 | -42.6539 | -36.7814 | -43.7512 | -36.3237 | -43.7588 | -35.4076 | -44.9155 | 278 | -39.9081 | -36.7578 | -36.9373 | -46.3915 | -35.4178 | -46.3058 | -40.2373 | -36.4787 | -37.3302 | -45.7832 | -35.4815 | -46.9778 | -35.9597 | -35.8212 | -34.6161 | -45.9844 | -37.2724 | -32.2627 | -36.2889 | -35.5421 | -35.009 | -45.3761 | -37.3361 | -32.9347
279 | -5.4386 | 0 | -5.052 | 0 | -5.8965 | 0 | -4.963 | 0 | -64.7725 | 153.7131 | -42.1691 | 110.3256 | -62.935 | -142.9683 | -39.2186 | -65.0015 | -59.9323 | 32.4804 | -43.8396 | 36.745 | -52.4125 | -133.4343 | -37.8298 | 128.1516 | -59.2006 | 143.0235 | -40.8452 | -23.4068 | -55.1175 | -42.7425 | -38.9739 | 52.6202 | -12.7677 | -61.7096 | -18.1747 | -6.5304 | -18.2528 | -72.2523 | -27.676 | -6.131 | -13.0109 | -22.9264 | -21.2525 | 22.326 | -19.9291 | -17.9825 | -28.5988 | -6.9309 | -46.2677 | -41.7646 | -42.0019 | -40.0724 | -50.0216 | -38.4873 | -52.3098 | -43.9239 | -42.1143 | -38.0676 | -48.8176 | -39.8106 | -36.175 | 279 | -42.1093 | -39.1699 | -36.5422 | -43.6822 | -37.6507 | -40.4033 | -34.2737 | -38.8296 | 279 | -38.4853 | -36.6757 | -34.6338 | -44.9696 | -33.4353 | -46.4133 | -38.8719 | -36.2178 | -35.1094 | -44.1251 | -33.5243 | -47.3468 | -36.326 | -36.5633 | -32.629 | -43.7656 | -34.7586 | -30.2785 | -36.7126 | -36.1054 | -33.1046 | -42.9211 | -34.8476 | -31.212
280 | -5.4461 | 0 | -5.0465 | 0 | -6.1615 | 0 | -4.999 | 0 | -54.7498 | -154.0937 | -41.9349 | 134.7213 | -54.1044 | -165.2162 | -37.055 | -99.3461 | -66.3083 | 58.621 | -39.4182 | -24.7322 | -49.5957 | -128.9601 | -40.1976 | 118.7432 | -58.3 | 178.0472 | -38.7228 | -56.2038 | -54.2761 | -57.7226 | -35.0942 | 20.4528 | -12.5535 | -78.7777 | -18.3915 | -22.3615 | -17.4344 | -95.5151 | -29.5734 | 0.3089 | -12.8028 | -38.1885 | -21.4564 | 2.4069 | -18.753 | -40.5627 | -31.5547 | 23.2452 | -46.5669 | -41.1389 | -42.7478 | -37.9028 | -49.9926 | -35.8225 | -50.7496 | -43.7435 | -42.45 | -36.3472 | -48.0933 | -36.642 | -35.2525 | 280 | -41.47 | -36.9767 | -34.2551 | -39.2644 | -39.6655 | -38.271 | -32.6826 | -35.0216 | 280 | -38.2974 | -37.0039 | -32.4567 | -44.9461 | -30.776 | -44.5881 | -38.697 | -36.2885 | -32.9038 | -43.8311 | -30.8235 | -45.7506 | -35.6928 | -37.3017 | -30.9011 | -43.0468 | -31.5955 | -29.091 | -36.0924 | -36.5863 | -31.3482 | -41.9318 | -31.643 | -30.2535
281 | -5.3751 | 0 | -5.0353 | 0 | -6.3126 | 0 | -5.0431 | 0 | -49.0095 | -173.8115 | -38.4507 | 133.2366 | -50.2771 | 174.7868 | -36.4591 | -133.8235 | -67.3426 | 120.89 | -35.9282 | -71.267 | -46.9743 | -139.2468 | -42.2067 | 122.7156 | -54.6928 | -174.2673 | -37.8606 | -88.6713 | -53.2869 | -65.108 | -32.7645 | -11.1715 | -13.2412 | -95.4869 | -19.6721 | -37.2662 | -18.1367 | -121.0825 | -29.1874 | 22.414 | -13.2825 | -52.9762 | -22.6494 | -16.0798 | -18.7945 | -66.1557 | -27.381 | 45.0778 | -46.6768 | -39.876 | -42.7354 | -36.5401 | -50.4736 | -33.8408 | -48.6212 | -44.6915 | -42.4962 | -35.3361 | -47.8946 | -34.4025 | -35.3061 | 281 | -37.8302 | -36.2208 | -32.0465 | -35.7685 | -40.7765 | -37.2487 | -31.2324 | -32.6986 | 281 | -39.3164 | -37.1211 | -31.165 | -45.4383 | -28.8055 | -42.3086 | -39.6562 | -36.1836 | -31.497 | -44.161 | -28.7977 | -43.5781 | -34.5009 | -37.3603 | -29.961 | -42.8593 | -29.3672 | -28.9935 | -34.8407 | -36.4228 | -30.293 | -41.582 | -29.3594 | -30.263
282 | -5.2836 | 0 | -5.0285 | 0 | -6.2174 | 0 | -5.0952 | 0 | -46.2723 | 163.5712 | -36.8342 | 115.5397 | -48.0946 | 150.4267 | -37.2848 | -167.2381 | -58.2544 | 139.7631 | -34.1888 | -112.4388 | -45.5444 | -154.6636 | -41.7707 | 128.8157 | -51.8345 | 174.2293 | -38.1808 | -119.7666 | -51.6976 | -77.405 | -31.8589 | -42.2482 | -14.9555 | -108.8255 | -22.2286 | -46.4142 | -20.5554 | -144.0665 | -25.776 | 29.811 | -14.7113 | -64.6513 | -25.5426 | -27.0339 | -20.4383 | -92.2874 | -23.5405 | 42.6694 | -46.3614 | -38.937 | -41.9876 | -36.0607 | -51.5841 | -32.8941 | -46.8996 | -46.858 | -42.0649 | -35.0949 | -48.3215 | -33.2877 | -36.1916 | 282 | -36.0838 | -36.7377 | -31.1052 | -33.9993 | -39.9581 | -37.2888 | -30.6031 | -31.771 | 282 | -41.5744 | -36.7813 | -30.7771 | -46.5556 | -27.8656 | -40.6822 | -41.8295 | -35.8475 | -30.9655 | -45.3667 | -27.7989 | -41.8044 | -33.6534 | -36.704 | -29.8113 | -43.293 | -28.2592 | -29.9742 | -33.9085 | -35.7702 | -29.9997 | -42.1041 | -28.1925 | -31.0964
283 | -5.2139 | 0 | -5.0121 | 0 | -6.0222 | 0 | -5.1197 | 0 | -44.8799 | 141.6292 | -37.1617 | 96.5137 | -48.0244 | 122.0838 | -39.4384 | 160.3134 | -52.9943 | 119.6716 | -34.116 | -150.6636 | -45.0771 | -171.1745 | -40.737 | 124.7925 | -50.6561 | 157.6032 | -39.6378 | -150.3227 | -51.2824 | -93.5462 | -32.327 | -72.4182 | -17.7257 | -113.2063 | -25.7174 | -39.1556 | -24.9956 | -158.9327 | -22.7266 | 22.9012 | -16.9534 | -69.1102 | -29.3335 | -17.5872 | -23.5929 | -118.0947 | -21.1359 | 29.6193 | -45.763 | -38.7887 | -41.1054 | -36.4036 | -53.1927 | -32.9215 | -45.9223 | -49.741 | -41.4756 | -35.5512 | -49.2973 | -33.2331 | -37.7348 | 283 | -36.1888 | -38.2007 | -31.5886 | -33.8892 | -39.0638 | -38.3207 | -31.0886 | -32.2096 | 283 | -44.5271 | -36.2617 | -31.1897 | -48.1806 | -27.9094 | -39.9001 | -44.7289 | -35.4534 | -31.2839 | -47.1705 | -27.8018 | -40.8026 | -33.5748 | -35.8915 | -30.3373 | -44.2852 | -28.221 | -31.7126 | -33.7766 | -35.0832 | -30.4315 | -43.2751 | -28.1134 | -32.6151
284 | -5.2131 | 0 | -5.0529 | 0 | -5.8058 | 0 | -5.1139 | 0 | -44.2241 | 121.0118 | -38.5147 | 84.2119 | -50.818 | 96.3066 | -42.999 | 125.2474 | -50.6121 | 95.3762 | -35.3783 | 174.6733 | -45.3697 | 173.3831 | -40.0438 | 116.7854 | -51.4807 | 141.5942 | -42.4312 | 177.6479 | -52.2737 | -108.7643 | -34.1063 | -99.9649 | -19.8889 | -98.6961 | -25.8034 | -9.4301 | -31.4199 | -141.2203 | -20.5574 | 10.5382 | -18.858 | -58.3904 | -28.512 | 14.318 | -29.3206 | -141.9202 | -19.8482 | 13.8208 | -45.0694 | -39.3692 | -40.6593 | -37.4522 | -55.0069 | -33.7364 | -45.7013 | -50.9933 | -41.0803 | -36.506 | -50.5099 | -34.0871 | -39.4326 | 284 | -37.2846 | -40.1491 | -33.1808 | -35.1312 | -38.6918 | -40.3575 | -32.6391 | -33.963 | 284 | -45.7802 | -35.8672 | -32.2391 | -49.954 | -28.6835 | -39.8955 | -45.9404 | -35.2745 | -32.3383 | -49.2011 | -28.6225 | -40.5874 | -34.1561 | -35.4462 | -31.2929 | -45.457 | -29.0342 | -33.6268 | -34.3163 | -34.8535 | -31.3921 | -44.7041 | -28.9732 | -34.3187
285 | -5.2689 | 0 | -5.0932 | 0 | -5.6635 | 0 | -5.1127 | 0 | -44.1895 | 99.7893 | -39.4692 | 78.4044 | -57.9794 | 92.9215 | -48.1109 | 67.9172 | -49.7684 | 72.7517 | -37.7547 | 142.7302 | -46.4265 | 159.6549 | -39.2044 | 106.8189 | -53.3615 | 139.2093 | -47.4271 | 133.705 | -53.8248 | -114.8328 | -37.3117 | -122.6685 | -18.0089 | -81.5396 | -22.0952 | -1.2351 | -28.33 | -94.6068 | -19.3309 | -4.9393 | -17.7348 | -42.6712 | -24.4139 | 17.8403 | -47.5629 | 171.1283 | -19.2603 | -4.0678 | -44.5706 | -40.6722 | -40.594 | -38.9495 | -57.2464 | -35.1604 | -46.1635 | -49.1478 | -41.0619 | -37.5814 | -51.5619 | -35.7416 | -40.5482 | 285 | -38.1615 | -41.9309 | -35.2849 | -37.4512 | -38.3125 | -43.4681 | -34.8959 | -37.1116 | 285 | -43.8789 | -35.793 | -33.6806 | -52.1532 | -30.0672 | -40.5 | -44.0546 | -35.3984 | -33.8368 | -51.5829 | -30.0477 | -41.0508 | -35.4033 | -35.3251 | -32.3125 | -46.4687 | -30.6484 | -34.8847 | -35.579 | -34.9305 | -32.4687 | -45.8984 | -30.6289 | -35.4355
286 | -5.3683 | 0 | -5.1352 | 0 | -5.6879 | 0 | -5.0869 | 0 | -45.2005 | 76.9725 | -39.9689 | 68.1358 | -56.608 | 157.2908 | -46.4398 | -27.2232 | -49.8061 | 53.2199 | -41.2333 | 110.4114 | -48.5623 | 149.399 | -38.3132 | 92.4507 | -53.2823 | 150.0345 | -50.4165 | 29.2437 | -54.4879 | -113.1856 | -42.8927 | -141.4878 | -15.159 | -83.7635 | -19.4163 | -10.3736 | -23.0365 | -98.537 | -18.7549 | -20.4025 | -15.2232 | -42.1041 | -21.7687 | 5.1321 | -31.6926 | -1.7224 | -19.7754 | -23.1483 | -44.222 | -42.6615 | -40.7403 | -39.8041 | -60.1673 | -36.9701 | -47.2758 | -46.7153 | -41.384 | -37.811 | -52.1665 | -38.1528 | -40.5729 | 286 | -38.7583 | -41.9824 | -37.0181 | -40.5592 | -37.7968 | -45.7565 | -36.821 | -42.2456 | 286 | -41.347 | -36.0157 | -34.4358 | -55.0321 | -31.8349 | -41.5879 | -41.5801 | -35.6961 | -34.7172 | -54.4794 | -31.8832 | -42.1889 | -37.2932 | -35.372 | -32.4427 | -47.0313 | -33.0176 | -34.885 | -37.5263 | -35.0524 | -32.7241 | -46.4786 | -33.0659 | -35.486
287 | -5.4676 | 0 | -5.188 | 0 | -5.8774 | 0 | -5.0858 | 0 | -48.264 | 53.2221 | -41.7863 | 52.7184 | -50.9291 | 148.1681 | -40.4769 | -83.7846 | -50.0703 | 34.6859 | -46.427 | 58.107 | -52.0185 | 156.6562 | -38.111 | 71.8681 | -50.4134 | 148.7185 | -42.7831 | -43.1369 | -55.2981 | -115.278 | -64.922 | -81.6404 | -13.2863 | -96.772 | -17.9933 | -24.9702 | -19.8034 | -119.2548 | -19.1214 | -35.2674 | -13.3783 | -51.8999 | -20.4205 | -13.1714 | -25.8061 | -33.076 | -21.4621 | -44.2118 | -44.181 | -45.2728 | -40.8787 | -38.4076 | -60.3607 | -38.2299 | -48.977 | -44.8813 | -41.9168 | -36.4887 | -52.6098 | -40.2719 | -38.9891 | 287 | -40.4931 | -39.4175 | -37.4801 | -43.9062 | -37.699 | -42.0816 | -36.8299 | -49.0775 | 287 | -39.4137 | -36.4492 | -32.94 | -55.1727 | -33.0419 | -43.0996 | -39.6933 | -36.0394 | -33.3218 | -54.4833 | -33.1441 | -43.8912 | -39.8052 | -35.4111 | -31.0211 | -47.4218 | -35.0839 | -33.1117 | -40.0848 | -35.0013 | -31.4029 | -46.7324 | -35.1861 | -33.9033
288 | -5.5138 | 0 | -5.1927 | 0 | -6.1738 | 0 | -5.0933 | 0 | -55.8253 | 43.5211 | -46.1931 | 50.0903 | -50.0357 | 128.8036 | -37.0141 | -126.0092 | -50.6892 | 6.7591 | -46.5825 | -43.9261 | -50.7315 | -172.8119 | -39.2305 | 49.1574 | -48.7448 | 129.2515 | -38.404 | -86.796 | -56.2896 | -92.5521 | -41.1656 | -15.4435 | -12.4608 | -112.5927 | -17.5429 | -39.9002 | -18.3261 | -145.8286 | -19.9796 | -45.2198 | -12.3884 | -65.2615 | -20.086 | -33.2788 | -23.0485 | -67.2332 | -25.0119 | -66.6688 | -44.4827 | -46.3817 | -40.7335 | -36.0374 | -55.6624 | -37.0224 | -50.6732 | -44.0722 | -42.3068 | -34.7631 | -52.9662 | -39.0996 | -37.8637 | 288 | -44.37 | -36.7772 | -36.1106 | -43.9344 | -38.5021 | -38.0908 | -34.6819 | -40.3545 | 288 | -38.5584 | -36.793 | -30.5236 | -50.4697 | -31.8297 | -44.4994 | -38.8795 | -36.133 | -30.9441 | -49.4886 | -31.9291 | -45.5799 | -40.8679 | -35.2197 | -29.2493 | -47.7735 | -33.9069 | -31.6899 | -41.189 | -34.5597 | -29.6698 | -46.7924 | -34.0063 | -32.7704
289 | -5.4908 | 0 | -5.1744 | 0 | -6.3697 | 0 | -5.0884 | 0 | -58.7767 | 138.3975 | -46.6622 | 79.4051 | -49.1744 | 127.0456 | -35.6726 | -165.0705 | -56.1696 | -34.3402 | -40.3036 | -107.1738 | -46.9177 | -173.2287 | -41.5871 | 33.7459 | -49.7569 | 112.4727 | -36.6042 | -123.7147 | -50.7705 | -97.3668 | -34.8307 | -44.3497 | -12.48 | -128.9144 | -17.9103 | -53.6247 | -18.3181 | -174.308 | -20.7962 | -47.9218 | -12.255 | -79.894 | -20.4915 | -52.9902 | -22.5013 | -101.2881 | -34.0301 | -87.1866 | -45.2729 | -43.9878 | -40.9018 | -34.4096 | -53.0112 | -34.8276 | -49.9009 | -44.608 | -42.0025 | -33.7915 | -50.2212 | -36.4595 | -37.4114 | 289 | -44.5611 | -35.613 | -34.1378 | -39.6755 | -39.987 | -36.0682 | -32.0989 | -34.5873 | 289 | -39.1172 | -36.5117 | -28.9188 | -47.8368 | -29.6532 | -43.5312 | -39.4336 | -35.6328 | -29.3212 | -46.6415 | -29.7392 | -44.8125 | -38.497 | -35.411 | -28.3007 | -45.0468 | -31.2851 | -31.0417 | -38.8134 | -34.5321 | -28.7031 | -43.8515 | -31.3711 | -32.323
290 | -5.4308 | 0 | -5.1594 | 0 | -6.3201 | 0 | -5.1098 | 0 | -49.6458 | 140.7758 | -43.7386 | 73.5345 | -47.4679 | 112.0497 | -35.92 | 160.1489 | -70.8283 | -173.875 | -36.963 | -150.8224 | -44.4286 | 175.5753 | -43.786 | 30.7512 | -50.6572 | 103.4895 | -36.4177 | -157.2204 | -49.1567 | -118.4826 | -32.1321 | -75.3911 | -13.372 | -144.1862 | -18.8703 | -64.7108 | -19.8803 | 160.0617 | -20.6929 | -48.6617 | -12.932 | -94.0714 | -21.9121 | -74.4848 | -23.6775 | -133.6832 | -35.0739 | 70.8659 | -45.965 | -41.6921 | -41.2052 | -33.8283 | -53.1955 | -33.5436 | -48.1711 | -46.7693 | -41.9894 | -33.6008 | -49.675 | -34.7497 | -37.4205 | 290 | -41.4847 | -35.7383 | -33.0158 | -36.591 | -40.6305 | -35.5851 | -30.5452 | -31.9874 | 290 | -41.3385 | -36.5586 | -28.3975 | -48.0361 | -28.3842 | -41.851 | -41.6099 | -35.6693 | -28.7185 | -46.8754 | -28.4338 | -43.0613 | -36.2613 | -35.7744 | -28.17 | -44.5156 | -29.5903 | -31.1004 | -36.5327 | -34.8851 | -28.491 | -43.3549 | -29.6399 | -32.3107
291 | -5.3645 | 0 | -5.1233 | 0 | -6.1416 | 0 | -5.1648 | 0 | -45.6195 | 124.3846 | -43.8303 | 52.4078 | -47.2873 | 91.8217 | -37.1937 | 129.2429 | -55.5181 | 107.559 | -35.8451 | 172.4165 | -42.8761 | 160.7948 | -44.0317 | 31.4601 | -51.1954 | 91.6892 | -37.3686 | 173.6566 | -48.8228 | -136.8758 | -31.2815 | -104.4083 | -15.1616 | -155.6152 | -20.1881 | -69.9951 | -22.8383 | 141.0051 | -19.7405 | -51.236 | -14.4922 | -105.3205 | -24.4705 | -97.2572 | -25.4224 | -162.8359 | -26.3691 | 60.0158 | -46.175 | -40.4003 | -41.1388 | -33.8977 | -53.5383 | -33.1229 | -47.1936 | -50.9658 | -41.8605 | -33.8968 | -50.0061 | -34.2002 | -37.9961 | 291 | -40.5803 | -36.5551 | -33.0757 | -35.5007 | -40.0575 | -36.056 | -30.1444 | -31.1624 | 291 | -45.6013 | -36.496 | -28.5332 | -48.415 | -27.9996 | -41.052 | -45.8425 | -35.7189 | -28.7329 | -47.3967 | -27.9581 | -42.0288 | -35.0358 | -35.7743 | -28.5323 | -44.8828 | -29.0769 | -31.8545 | -35.277 | -34.9972 | -28.732 | -43.8645 | -29.0354 | -32.8313
292 | -5.2943 | 0 | -5.0948 | 0 | -5.9374 | 0 | -5.2057 | 0 | -43.314 | 106.1479 | -46.9412 | 33.3612 | -49.0297 | 73.171 | -39.1686 | 100.8365 | -50.8227 | 78.058 | -36.2102 | 139.8447 | -42.0364 | 144.2046 | -43.5635 | 24.4291 | -52.7246 | 74.7886 | -39.1879 | 147.6082 | -49.3537 | -155.1973 | -31.7219 | -131.1331 | -17.6172 | -157.2158 | -21.0978 | -69.333 | -26.9287 | 136.4 | -18.4721 | -58.8262 | -16.841 | -108.6576 | -29.1056 | -118.4639 | -27.4775 | 175.468 | -22.0869 | 39.0458 | -46.0761 | -39.9618 | -41.014 | -34.4004 | -53.7324 | -33.3055 | -46.7666 | -60.5234 | -41.5795 | -34.5244 | -50.4463 | -34.371 | -39.0617 | 292 | -41.0045 | -37.545 | -34.1948 | -35.8486 | -39.5106 | -37.1055 | -30.7714 | -31.6139 | 292 | -55.2291 | -36.2852 | -29.1061 | -48.6376 | -28.2107 | -40.8292 | -55.4286 | -35.6421 | -29.1947 | -47.795 | -28.0998 | -41.5609 | -34.6675 | -35.7197 | -29.2301 | -45.3515 | -29.2762 | -33.1243 | -34.867 | -35.0766 | -29.3187 | -44.5089 | -29.1653 | -33.856
293 | -5.2789 | 0 | -5.1031 | 0 | -5.7672 | 0 | -5.2554 | 0 | -42.0035 | 86.463 | -52.9678 | 41.9387 | -53.2733 | 63.0937 | -41.6751 | 69.3261 | -48.8527 | 51.1494 | -37.7003 | 110.1598 | -41.8342 | 127.2102 | -43.4489 | 14.4554 | -56.7959 | 59.7689 | -41.9494 | 122.3344 | -50.9994 | -172.7454 | -33.2714 | -154.7848 | -18.978 | -143.036 | -20.9149 | -65.6948 | -29.5448 | 157.249 | -17.4611 | -71.2952 | -18.6544 | -95.092 | -43.6862 | -125.8485 | -29.3213 | 157.3086 | -20.0245 | 21.2096 | -45.7446 | -40.1196 | -41.0103 | -35.2564 | -54.186 | -33.8618 | -46.6695 | -56.9312 | -41.3883 | -35.439 | -50.9586 | -35.0328 | -40.3487 | 293 | -41.3787 | -38.4144 | -36.1465 | -37.269 | -39.4754 | -38.6223 | -32.3668 | -33.1798 | 293 | -51.6523 | -36.1094 | -29.9775 | -49.0829 | -28.7587 | -40.9023 | -51.8281 | -35.6211 | -30.001 | -48.4188 | -28.6064 | -41.4141 | -34.8407 | -35.7314 | -30.1601 | -45.8555 | -29.9297 | -34.5815 | -35.0165 | -35.2431 | -30.1836 | -45.1914 | -29.7774 | -35.0933
294 | -5.3534 | 0 | -5.1204 | 0 | -5.6557 | 0 | -5.2589 | 0 | -41.5341 | 65.7768 | -51.3781 | 76.1641 | -57.4091 | 105.5449 | -44.5306 | 28.4999 | -48.5795 | 25.4618 | -40.2832 | 84.8499 | -42.2999 | 109.5716 | -43.2933 | 7.0827 | -69.3916 | 77.3017 | -46.406 | 91.4417 | -54.1655 | 177.8784 | -35.9123 | -174.2061 | -17.0454 | -132.0709 | -19.8316 | -67.6399 | -27.3116 | 175.4261 | -16.8915 | -86.4247 | -17.1777 | -80.1468 | -33.8035 | 9.4355 | -30.9517 | 137.3704 | -18.7745 | 3.8186 | -45.219 | -40.7465 | -41.1317 | -36.4729 | -55.6018 | -34.6684 | -47.0149 | -48.8354 | -41.3222 | -36.6087 | -51.8001 | -36.0502 | -41.1906 | 294 | -41.0052 | -39.2321 | -38.6582 | -39.6109 | -39.7532 | -40.6755 | -34.8674 | -35.8459 | 294 | -43.482 | -35.9688 | -31.1195 | -50.4814 | -29.548 | -41.3592 | -43.715 | -35.6665 | -31.214 | -49.9461 | -29.4095 | -41.756 | -35.3931 | -35.7783 | -31.2553 | -46.6797 | -30.9298 | -35.5349 | -35.6261 | -35.476 | -31.3498 | -46.1444 | -30.7913 | -35.9317
295 | -5.4518 | 0 | -5.1566 | 0 | -5.6544 | 0 | -5.2509 | 0 | -42.1197 | 43.98 | -49.1073 | 56.9564 | -50.9058 | 126.9052 | -45.6941 | -37.2462 | -50.2141 | 2.2399 | -43.544 | 66.2051 | -43.7098 | 91.8662 | -41.9759 | -0.0755 | -58.534 | 171.9813 | -54.0557 | 7.895 | -56.9278 | -165.4178 | -39.8672 | 175.063 | -14.6112 | -136.9015 | -18.8247 | -76.323 | -24.2848 | 174.0685 | -16.875 | -104.3507 | -14.6529 | -82.5338 | -27.8858 | -12.3756 | -33.3694 | 121.7865 | -18.5186 | -13.2117 | -44.5989 | -41.9444 | -41.2652 | -37.6966 | -58.9778 | -35.7491 | -47.8636 | -44.2365 | -41.2799 | -37.5277 | -53.2347 | -37.4982 | -41.131 | 295 | -40.8735 | -40.0943 | -40.7856 | -42.0863 | -39.6895 | -43.1407 | -37.6832 | -39.7251 | 295 | -38.7847 | -35.8281 | -32.2448 | -53.8212 | -30.5925 | -42.2092 | -39.0799 | -35.6255 | -32.4457 | -53.3234 | -30.4982 | -42.6127 | -36.4926 | -35.8134 | -32.0759 | -48.0781 | -32.3416 | -35.4766 | -36.7878 | -35.6108 | -32.2768 | -47.5803 | -32.2473 | -35.8801
296 | -5.5629 | 0 | -5.187 | 0 | -5.8008 | 0 | -5.2037 | 0 | -44.3279 | 23.2865 | -52.8803 | 10.3741 | -46.6956 | 109.5978 | -42.4264 | -105.8325 | -53.5062 | -7.0649 | -46.7742 | 48.9633 | -46.896 | 77.5116 | -39.9352 | -16.5543 | -51.9601 | 155.5691 | -45.4287 | -97.5228 | -54.6408 | -154.5421 | -44.7886 | -175.0147 | -12.9983 | -149.4196 | -18.3553 | -87.8198 | -21.6079 | 163.4313 | -17.5821 | -122.1678 | -12.8803 | -93.1026 | -25.0869 | -35.7768 | -39.3132 | 140.1017 | -18.8707 | -29.0613 | -44.1684 | -44.3955 | -41.224 | -37.5121 | -62.7231 | -37.1885 | -49.4331 | -41.1719 | -41.1215 | -36.8042 | -54.8081 | -39.7618 | -40.6877 | 296 | -41.9744 | -40.0625 | -40.7902 | -43.2902 | -38.9175 | -42.7966 | -37.8687 | -43.665 | 296 | -35.609 | -35.5586 | -31.9492 | -57.5361 | -32.0015 | -43.6323 | -35.9849 | -35.3207 | -32.3084 | -56.9223 | -31.9848 | -44.2294 | -38.8326 | -35.6611 | -31.2413 | -49.6211 | -34.5748 | -34.8869 | -39.2085 | -35.4232 | -31.6005 | -49.0073 | -34.5581 | -35.484
297 | -5.6176 | 0 | -5.184 | 0 | -6.0708 | 0 | -5.1684 | 0 | -49.4484 | 15.1283 | -56.136 | -140.453 | -45.0017 | 84.7905 | -39.1107 | -159.6064 | -55.8829 | 2.4832 | -52.0984 | 4.3882 | -52.9803 | 88.1964 | -38.8511 | -43.2708 | -48.9857 | 131.9604 | -39.7686 | -143.483 | -53.7048 | -163.8574 | -45.7538 | -133.9298 | -12.076 | -164.6769 | -18.3751 | -100.4587 | -19.7552 | 144.4035 | -18.8792 | -140.3167 | -11.9164 | -108.3651 | -23.8784 | -61.6636 | -31.5135 | 173.0992 | -19.9161 | -43.522 | -44.2358 | -50.0404 | -41.0912 | -35.6772 | -58.9936 | -38.9428 | -51.0903 | -39.6801 | -40.977 | -34.9536 | -55.1684 | -41.9731 | -40.0907 | 297 | -43.4295 | -38.6436 | -38.8165 | -43.9406 | -38.2989 | -39.4018 | -35.8113 | -43.6175 | 297 | -34.0625 | -35.3594 | -30.0596 | -53.8096 | -33.7588 | -45.0195 | -34.4961 | -34.9062 | -30.5088 | -52.9228 | -33.7744 | -45.9219 | -44.4228 | -35.4736 | -29.336 | -49.9844 | -36.7891 | -34.0199 | -44.8564 | -35.0204 | -29.7852 | -49.0976 | -36.8047 | -34.9223
298 | -5.6209 | 0 | -5.1702 | 0 | -6.2494 | 0 | -5.1419 | 0 | -52.897 | 60.049 | -47.9104 | 153.9611 | -45.4786 | 61.4599 | -37.717 | 155.8426 | -56.7472 | 13.8327 | -51.763 | -134.3169 | -50.7029 | 139.1344 | -39.5212 | -70.8897 | -47.9371 | 107.4904 | -37.6209 | 178.0267 | -54.3888 | -162.7263 | -40.5479 | -118.134 | -12.0331 | 178.9851 | -19.0549 | -110.9461 | -19.7394 | 119.759 | -21.5994 | -154.8516 | -11.7914 | -124.6537 | -23.4155 | -85.6029 | -26.8017 | 150.129 | -21.5806 | -53.8575 | -44.718 | -52.7855 | -40.9265 | -34.2648 | -55.382 | -39.5199 | -50.8616 | -39.8236 | -41.156 | -33.7405 | -56.2483 | -40.3978 | -39.2696 | 298 | -43.0422 | -37.5348 | -37.1669 | -44.3061 | -38.6569 | -37.3261 | -34.2858 | -39.6711 | 298 | -34.2027 | -35.5351 | -28.6439 | -50.2118 | -34.3497 | -44.6122 | -34.6534 | -34.9066 | -29.1229 | -49.1326 | -34.378 | -45.7197 | -47.1646 | -35.3056 | -28.1196 | -51.0781 | -35.2276 | -33.0202 | -47.6153 | -34.6771 | -28.5986 | -49.9989 | -35.2559 | -34.1277
299 | -5.5688 | 0 | -5.1701 | 0 | -6.2247 | 0 | -5.1307 | 0 | -47.4758 | 78.8403 | -46.4127 | 121.0386 | -46.971 | 46.5277 | -37.742 | 118.13 | -55.1493 | 40.5758 | -44.783 | 163.4935 | -45.5302 | 136.4885 | -41.6332 | -90.0125 | -48.9734 | 85.6415 | -37.5274 | 144.4256 | -51.3576 | -161.4112 | -36.4599 | -131.5267 | -12.5907 | 164.1141 | -19.705 | -118.9324 | -21.6555 | 99.9673 | -25.5148 | -157.9428 | -12.3836 | -141.2512 | -23.5189 | -112.2015 | -25.002 | 127.9569 | -23.4666 | -57.8805 | -45.175 | -46.3272 | -40.9565 | -33.7101 | -53.3117 | -38.0264 | -49.3342 | -41.0918 | -41.3032 | -33.4592 | -56.0607 | -38.4668 | -38.9638 | 299 | -42.1602 | -37.2325 | -36.4922 | -42.4884 | -39.6133 | -36.7364 | -33.2669 | -36.0919 | 299 | -35.523 | -35.7344 | -28.1413 | -48.1416 | -32.8563 | -43.1095 | -35.9217 | -35.0785 | -28.5794 | -47.087 | -32.8957 | -44.2035 | -40.7584 | -35.3877 | -27.8904 | -50.8906 | -33.2967 | -32.7391 | -41.1571 | -34.7318 | -28.3285 | -49.836 | -33.3361 | -33.8331
300 | -5.48 | 0 | -5.1702 | 0 | -6.0936 | 0 | -5.1335 | 0 | -43.7135 | 70.2795 | -48.4231 | 106.2588 | -48.6673 | 32.5853 | -38.6898 | 84.1487 | -50.5019 | 38.0907 | -41.9061 | 124.8677 | -42.8118 | 122.2331 | -43.7333 | -95.3438 | -50.828 | 73.2687 | -38.6977 | 116.3061 | -49.9713 | 177.5914 | -34.6483 | -154.1605 | -13.85 | 150.9564 | -20.1848 | -124.6934 | -25.2695 | 95.8418 | -28.5293 | -134.9382 | -13.8156 | -156.1642 | -23.877 | -140.2245 | -24.3509 | 113.1664 | -24.5807 | -58.8453 | -45.5032 | -43.2938 | -41.3051 | -33.6868 | -52.9719 | -36.8407 | -47.6272 | -43.1952 | -41.3432 | -33.7405 | -54.3655 | -37.5272 | -39.2081 | 300 | -41.5184 | -37.2898 | -36.6945 | -40.6061 | -39.8744 | -37.0471 | -32.8383 | -34.4221 | 300 | -37.7152 | -35.8632 | -28.2068 | -47.8017 | -31.6705 | -41.5336 | -38.025 | -35.2496 | -28.5533 | -46.8783 | -31.7072 | -42.4937 | -37.8138 | -35.8251 | -28.2605 | -49.1953 | -32.357 | -33.1145 | -38.1236 | -35.2115 | -28.607 | -48.2719 | -32.3937 | -34.0746
301 | -5.3938 | 0 | -5.1594 | 0 | -5.9406 | 0 | -5.1438 | 0 | -41.464 | 55.1614 | -49.7645 | 123.9346 | -51.9341 | 21.2079 | -40.228 | 50.6062 | -47.7855 | 21.936 | -40.8563 | 90.5804 | -41.2663 | 104.893 | -43.9635 | -93.5991 | -53.1922 | 66.0192 | -40.633 | 92.166 | -50.2199 | 157.2199 | -34.4111 | -176.5374 | -15.7785 | 142.3306 | -20.4568 | -129.7893 | -26.8168 | 117.3932 | -26.4484 | -111.6148 | -16.5078 | -166.9171 | -25.2441 | -170.2859 | -23.5659 | 98.9303 | -24.8389 | -52.8852 | -45.6096 | -41.9533 | -41.4182 | -33.9689 | -52.9728 | -36.3205 | -46.382 | -45.9914 | -41.4094 | -34.2492 | -53.6047 | -37.1828 | -39.7975 | 301 | -40.5381 | -37.3774 | -37.2689 | -39.7814 | -39.2209 | -37.6789 | -33.1093 | -34.2429 | 301 | -40.5976 | -36.0156 | -28.5751 | -47.8134 | -31.1611 | -40.4414 | -40.832 | -35.4688 | -28.8251 | -47.0322 | -31.1767 | -41.2382 | -36.5595 | -36.0244 | -28.8554 | -48.4453 | -32.0234 | -33.8569 | -36.7939 | -35.4776 | -29.1054 | -47.6641 | -32.039 | -34.6537
302 | -5.3252 | 0 | -5.1666 | 0 | -5.8364 | 0 | -5.1656 | 0 | -40.1234 | 38.6562 | -46.1438 | 132.6307 | -57.8675 | 30.5623 | -42.0254 | 15.4177 | -46.2407 | 1.2512 | -41.2081 | 58.2845 | -40.5877 | 87.2269 | -43.0973 | -97.7187 | -56.2977 | 70.4438 | -43.2624 | 71.0061 | -51.841 | 137.7896 | -35.2284 | 163.3607 | -17.7447 | 144.1756 | -20.2594 | -136.0777 | -23.8099 | 129.0159 | -23.253 | -114.4881 | -19.8273 | -163.1898 | -26.7876 | 158.2457 | -22.6299 | 87.4154 | -24.485 | -55.3634 | -45.4762 | -41.5912 | -41.4433 | -34.5191 | -53.5543 | -36.2397 | -45.5924 | -49.0864 | -41.3877 | -34.9596 | -53.315 | -37.2543 | -40.6076 | 302 | -39.0962 | -37.3591 | -37.8849 | -39.9518 | -38.5793 | -38.5057 | -34.0207 | -35.1016 | 302 | -43.7612 | -36.0625 | -29.1939 | -48.3877 | -31.0731 | -39.756 | -43.9198 | -35.5513 | -29.3535 | -47.7179 | -31.0741 | -40.4268 | -36.266 | -36.1181 | -29.6344 | -48.1484 | -32.0877 | -34.7712 | -36.4246 | -35.6069 | -29.794 | -47.4786 | -32.0887 | -35.442
303 | -5.3317 | 0 | -5.1796 | 0 | -5.7568 | 0 | -5.1508 | 0 | -39.5515 | 18.8078 | -43.7732 | 119.644 | -56.6408 | 93.5677 | -43.4519 | -27.2614 | -46.0222 | -20.8921 | -42.6702 | 27.5774 | -40.737 | 68.6686 | -42.5259 | -104.6297 | -58.2864 | 101.3035 | -46.8591 | 45.569 | -55.2729 | 126.784 | -36.9849 | 146.7355 | -18.2152 | 153.4516 | -20.1564 | -144.5555 | -21.287 | 120.3835 | -21.6891 | -124.5311 | -20.7028 | -139.7553 | -29.3951 | 123.3534 | -22.004 | 70.1577 | -23.9494 | -63.4484 | -45.161 | -42.0507 | -41.3795 | -35.4266 | -55.5673 | -36.4179 | -45.2616 | -49.7568 | -41.3122 | -35.9491 | -53.7655 | -37.5302 | -41.4814 | 303 | -38.0969 | -37.4224 | -38.5022 | -40.9028 | -38.484 | -39.6669 | -35.5794 | -36.8894 | 303 | -44.4251 | -35.9805 | -30.0949 | -50.3877 | -31.2383 | -39.5048 | -44.5772 | -35.5554 | -30.2758 | -49.8105 | -31.2671 | -40.1108 | -36.719 | -36.0478 | -30.6174 | -48.5859 | -32.3506 | -35.7246 | -36.8711 | -35.6227 | -30.7983 | -48.0087 | -32.3794 | -36.3306
304 | -5.3647 | 0 | -5.2137 | 0 | -5.7131 | 0 | -5.1522 | 0 | -39.8717 | -0.914 | -44.0793 | 105.0086 | -49.9236 | 96.2348 | -43.5345 | -79.2862 | -47.4117 | -41.9186 | -44.9534 | 2.2126 | -41.8949 | 50.8615 | -41.8387 | -108.5436 | -53.4101 | 125.3527 | -53.7808 | -6.6711 | -57.9017 | 145.367 | -39.3393 | 136.8102 | -16.7571 | 158.8671 | -19.9299 | -154.0663 | -20.1398 | 107.7882 | -20.7709 | -137.4425 | -17.8285 | -131.1528 | -33.3561 | 79.8378 | -22.3519 | 50.6034 | -23.8813 | -75.1641 | -44.7381 | -43.5617 | -41.0336 | -36.5779 | -61.2576 | -36.8117 | -45.6512 | -45.9865 | -41.0405 | -36.866 | -55.1981 | -38.1076 | -42.1098 | 304 | -38.174 | -37.813 | -39.3791 | -42.1976 | -38.7068 | -41.5212 | -37.3025 | -39.1146 | 304 | -40.6218 | -35.6758 | -31.2132 | -56.0439 | -31.598 | -39.9381 | -40.7728 | -35.3274 | -31.4257 | -55.5445 | -31.6595 | -40.499 | -38.197 | -35.6689 | -31.5013 | -49.9844 | -32.8939 | -36.3967 | -38.348 | -35.3205 | -31.7138 | -49.485 | -32.9554 | -36.9576
305 | -5.4393 | 0 | -5.2284 | 0 | -5.787 | 0 | -5.1307 | 0 | -41.5585 | -20.3791 | -45.2727 | 112.7126 | -46.1492 | 75.7969 | -42.3187 | -135.375 | -50.1316 | -52.1477 | -46.7174 | -16.9217 | -44.4281 | 37.8345 | -39.9652 | -115.6541 | -48.7376 | 115.4432 | -50.8615 | -137.8608 | -55.4928 | 148.8061 | -41.5172 | 131.1032 | -15.0696 | 153.9319 | -20.2253 | -164.9362 | -19.778 | 95.0501 | -20.9294 | -148.7432 | -15.517 | -140.1788 | -37.0983 | 5.222 | -24.3645 | 33.517 | -24.6205 | -89.1618 | -44.5419 | -47.2684 | -40.3583 | -36.995 | -76.3739 | -37.8739 | -46.7948 | -42.3221 | -40.5253 | -36.705 | -56.1776 | -39.451 | -41.9457 | 305 | -39.0722 | -38.5955 | -39.601 | -42.5754 | -38.2318 | -43.27 | -37.4589 | -40.6193 | 305 | -36.8828 | -35.086 | -31.5557 | -71.1455 | -32.6455 | -41.0078 | -37.0937 | -34.7383 | -31.8643 | -70.5869 | -32.7432 | -41.6641 | -41.8291 | -34.919 | -31.2657 | -50.9492 | -34.2226 | -36.1587 | -42.04 | -34.5713 | -31.5743 | -50.3906 | -34.3203 | -36.815
306 | -5.5142 | 0 | -5.2355 | 0 | -5.9064 | 0 | -5.1173 | 0 | -45.0297 | -30.7221 | -42.5226 | 117.2853 | -44.8543 | 49.8723 | -41.5143 | 174.2677 | -52.2992 | -48.6889 | -47.4435 | -46.543 | -47.7727 | 42.1328 | -38.5703 | -133.7643 | -46.2934 | 92.6504 | -44.3634 | 167.5552 | -55.2836 | 134.9828 | -45.4248 | 126.4985 | -13.8918 | 143.3217 | -20.6827 | -173.9815 | -20.0705 | 81.6025 | -21.7123 | -156.2372 | -14.2958 | -155.9996 | -33.2396 | -76.4096 | -27.8881 | 32.7233 | -26.4451 | -105.4245 | -44.8927 | -54.6652 | -39.8433 | -36.049 | -60.5412 | -39.9933 | -47.5402 | -40.5939 | -40.1782 | -35.7121 | -55.7511 | -41.7228 | -41.6201 | 306 | -39.2063 | -39.6715 | -38.4007 | -42.4713 | -37.4675 | -42.4966 | -36.8978 | -42.5872 | 306 | -35.0797 | -34.664 | -30.5348 | -55.3057 | -34.7578 | -41.6338 | -35.3584 | -34.2718 | -30.9317 | -54.6348 | -34.876 | -42.4229 | -49.151 | -34.3291 | -30.1979 | -50.5156 | -36.4873 | -35.7137 | -49.4297 | -33.9369 | -30.5948 | -49.8447 | -36.6055 | -36.5028
307 | -5.5502 | 0 | -5.2182 | 0 | -5.9659 | 0 | -5.119 | 0 | -48.8048 | -16.8406 | -40.9881 | 104.2072 | -45.5311 | 26.6898 | -42.0122 | 130.8065 | -53.332 | -39.2054 | -49.8895 | -91.2211 | -48.117 | 62.6313 | -38.9034 | -152.65 | -45.851 | 70.1923 | -42.2999 | 130.9635 | -56.4725 | 127.2479 | -48.985 | 171.9409 | -13.3993 | 130.8764 | -21.1463 | 179.8732 | -21.659 | 69.3103 | -22.2124 | -155.9503 | -14.0166 | -174.3447 | -27.942 | -121.003 | -29.0259 | 52.5252 | -30.0709 | -119.1956 | -45.3793 | -49.8106 | -39.8207 | -35.0903 | -56.7739 | -42.0372 | -46.9369 | -40.5362 | -40.2494 | -35.0971 | -55.9447 | -42.9346 | -41.3635 | 307 | -39.1793 | -40.9297 | -38.158 | -43.6771 | -37.6917 | -41.1596 | -36.9844 | -43.8847 | 307 | -34.986 | -34.6992 | -29.5401 | -51.5557 | -36.819 | -40.971 | -35.318 | -34.2835 | -29.9713 | -50.808 | -36.9182 | -41.8179 | -44.2604 | -34.2705 | -29.5469 | -50.7265 | -37.7164 | -35.3976 | -44.5924 | -33.8548 | -29.9781 | -49.9788 | -37.8156 | -36.2445
308 | -5.5601 | 0 | -5.2378 | 0 | -5.9718 | 0 | -5.1583 | 0 | -47.7807 | 9.9496 | -41.4787 | 94.9128 | -47.6467 | 9.6251 | -43.7177 | 93.6365 | -52.2291 | -26.7686 | -55.1764 | -146.8995 | -45.7446 | 70.7576 | -40.2617 | -162.0191 | -46.51 | 50.2687 | -42.18 | 102.7101 | -58.0712 | 125.8477 | -42.6347 | -171.4357 | -13.5146 | 117.7407 | -21.2056 | 174.6686 | -24.4675 | 71.246 | -22.1706 | -151.413 | -14.7669 | 166.7282 | -24.5949 | -151.6178 | -27.0624 | 64.478 | -37.3734 | -108.9215 | -45.7505 | -45.2541 | -40.0689 | -34.6763 | -54.7818 | -42.5041 | -46.2495 | -41.2491 | -40.5992 | -35.0347 | -57.1519 | -42.4835 | -40.4752 | 308 | -39.7879 | -41.8615 | -39.3306 | -45.8147 | -38.4427 | -40.5191 | -36.7943 | -41.0562 | 308 | -35.689 | -35.0391 | -29.1162 | -49.544 | -37.2663 | -40.2777 | -36.0113 | -34.6274 | -29.518 | -48.81 | -37.3458 | -41.0912 | -39.694 | -34.5088 | -29.4746 | -51.9141 | -37.2457 | -34.5034 | -40.0163 | -34.0971 | -29.8764 | -51.1801 | -37.3252 | -35.3169
309 | -5.5434 | 0 | -5.2387 | 0 | -5.9379 | 0 | -5.2152 | 0 | -44.5393 | 14.7412 | -41.8837 | 97.9357 | -50.9072 | 4.6781 | -46.8132 | 57.5992 | -49.6413 | -26.3071 | -62.5922 | 87.3979 | -43.3842 | 65.6662 | -40.8882 | -160.0013 | -48.1093 | 30.9088 | -43.0013 | 79.5099 | -58.9498 | 140.7451 | -39.2028 | 172.8632 | -14.1529 | 106.7328 | -20.8633 | 168.0391 | -25.08 | 92.0271 | -20.5444 | -149.2853 | -16.7851 | 147.3049 | -22.8355 | -179.4514 | -24.2363 | 58.485 | -34.1098 | -32.5702 | -46.1069 | -43.1147 | -40.3452 | -34.56 | -53.7866 | -41.9155 | -45.7934 | -42.2035 | -41.1254 | -35.1645 | -58.891 | -41.8715 | -39.9142 | 309 | -39.6624 | -41.7488 | -40.6455 | -47.0938 | -38.4517 | -40.121 | -35.9902 | -38.6367 | 309 | -36.6601 | -35.582 | -29.0166 | -48.5479 | -36.6768 | -39.8555 | -36.9648 | -35.1875 | -29.3448 | -47.8487 | -36.7003 | -40.5782 | -37.5713 | -34.8018 | -29.6211 | -53.6523 | -36.6328 | -33.9763 | -37.876 | -34.4073 | -29.9493 | -52.9531 | -36.6563 | -34.699
310 | -5.5024 | 0 | -5.2541 | 0 | -5.9293 | 0 | -5.2544 | 0 | -42.0643 | 6.2977 | -40.3653 | 103.0131 | -53.5199 | 12.0464 | -51.7973 | 16.7471 | -47.6286 | -37.7675 | -55.0588 | -13.117 | -41.6498 | 52.9975 | -39.7547 | -158.8862 | -51.9465 | 13.6934 | -44.349 | 59.4552 | -55.8932 | 140.1799 | -37.8551 | 152.8675 | -15.1953 | 98.9795 | -20.5575 | 158.1685 | -22.4555 | 101.1357 | -18.8116 | -153.9364 | -20.5514 | 131.0345 | -21.7346 | 155.3211 | -22.4669 | 45.5704 | -27.345 | -37.4968 | -46.5208 | -41.9772 | -40.8668 | -34.6106 | -53.2942 | -40.7663 | -45.4924 | -43.3473 | -41.354 | -35.4846 | -57.2502 | -41.5465 | -39.8474 | 310 | -37.9984 | -40.6528 | -39.9283 | -46.0502 | -37.433 | -39.6776 | -35.1369 | -37.6238 | 310 | -37.8449 | -35.8516 | -29.1082 | -48.0401 | -35.5122 | -39.5631 | -38.0932 | -35.4247 | -29.3562 | -47.3649 | -35.5119 | -40.238 | -36.4748 | -35.3644 | -29.9822 | -51.9961 | -36.2924 | -33.9181 | -36.7231 | -34.9375 | -30.2302 | -51.3209 | -36.2921 | -34.593
311 | -5.4522 | 0 | -5.2524 | 0 | -5.8831 | 0 | -5.2552 | 0 | -40.5263 | -6.8247 | -38.1648 | 97.4495 | -54.4243 | 35.8514 | -56.0099 | -52.8264 | -46.5366 | -52.4865 | -51.0354 | -58.4372 | -40.8852 | 37.6572 | -38.1989 | -166.5024 | -59.2486 | 26.4367 | -45.845 | 40.6836 | -55.3804 | 124.5517 | -37.8487 | 133.2738 | -16.0968 | 95.59 | -20.6286 | 145.3393 | -20.1879 | 93.0865 | -17.4957 | -163.776 | -27.676 | 137.7425 | -21.554 | 135.9607 | -21.9409 | 27.9185 | -23.7928 | -59.7471 | -46.6831 | -41.6264 | -41.4407 | -34.8312 | -53.0228 | -40.1551 | -45.2406 | -44.6915 | -41.2803 | -36.0166 | -55.711 | -41.3303 | -39.9889 | 311 | -36.1121 | -39.458 | -37.8788 | -44.7252 | -36.3052 | -39.5668 | -34.6657 | -37.7419 | 311 | -39.2393 | -35.8281 | -29.379 | -47.7704 | -34.9027 | -39.3575 | -39.4391 | -35.3972 | -29.576 | -47.1397 | -34.8999 | -39.9854 | -36.1742 | -35.9885 | -30.5644 | -50.4586 | -36.0779 | -34.1058 | -36.374 | -35.5576 | -30.7614 | -49.8279 | -36.0751 | -34.7337
312 | -5.4521 | 0 | -5.271 | 0 | -5.8431 | 0 | -5.2666 | 0 | -39.6838 | -21.5277 | -36.7546 | 83.7838 | -51.3496 | 54.401 | -52.179 | -116.9125 | -46.2457 | -71.0344 | -48.8768 | -95.6023 | -40.9027 | 21.2266 | -37.2457 | -178.6029 | -58.5362 | 99.6267 | -47.603 | 17.1429 | -56.1786 | 114.6556 | -38.8649 | 114.4439 | -16.4413 | 97.2338 | -21.2364 | 133.2442 | -19.2876 | 82.0424 | -16.5067 | -174.7985 | -26.3931 | -156.2224 | -22.4112 | 118.307 | -22.3956 | 6.7141 | -21.628 | -82.0125 | -46.5255 | -41.9307 | -41.8047 | -35.2903 | -54.0149 | -39.885 | -45.2943 | -46.4221 | -41.1512 | -36.7394 | -55.4193 | -41.2024 | -40.4577 | 312 | -34.8677 | -38.6219 | -36.3802 | -43.5637 | -35.6673 | -39.9564 | -34.7394 | -38.7393 | 312 | -40.97 | -35.6991 | -29.8382 | -48.7439 | -34.614 | -39.4512 | -41.1511 | -35.3081 | -30.0237 | -48.1718 | -34.6184 | -40.0277 | -36.4786 | -36.3526 | -31.2873 | -50.1483 | -35.9314 | -34.6146 | -36.6597 | -35.9616 | -31.4728 | -49.5762 | -35.9358 | -35.1911
313 | -5.4824 | 0 | -5.2597 | 0 | -5.7831 | 0 | -5.2558 | 0 | -39.5312 | -38.2089 | -36.6406 | 67.8276 | -47.4746 | 51.6533 | -46.9196 | -150.369 | -47.2841 | -90.7469 | -48.3307 | -130.2131 | -41.7565 | 5.232 | -37.0327 | 168.7995 | -51.0617 | 109.8745 | -50.1981 | -20.044 | -56.664 | 112.4668 | -40.9131 | 99.2644 | -15.8129 | 98.1009 | -22.5729 | 124.3733 | -19.459 | 72.6562 | -15.8028 | 173.8896 | -20.3357 | -157.1378 | -24.3036 | 105.5723 | -24.189 | -18.39 | -20.0791 | -106.4427 | -46.0031 | -42.9288 | -41.7609 | -36.0499 | -57.2023 | -39.6437 | -45.6738 | -47.9277 | -40.791 | -37.6074 | -55.7636 | -41.1542 | -41.3473 | 313 | -34.6089 | -38.2271 | -35.9903 | -42.9019 | -35.6448 | -41.0544 | -35.3967 | -40.4084 | 313 | -42.4453 | -35.3086 | -30.5675 | -51.9426 | -34.384 | -39.8907 | -42.668 | -35.0079 | -30.7941 | -51.4192 | -34.3879 | -40.418 | -37.4464 | -36.2785 | -32.125 | -50.5039 | -35.8945 | -35.5642 | -37.6691 | -35.9778 | -32.3516 | -49.9805 | -35.8984 | -36.0915
314 | -5.571 | 0 | -5.2866 | 0 | -5.7555 | 0 | -5.2674 | 0 | -40.3998 | -54.5444 | -37.8776 | 58.7824 | -44.6913 | 35.2515 | -42.8111 | 179.6901 | -50.1193 | -101.7421 | -50.3187 | -150.7345 | -43.7801 | -7.2155 | -37.2528 | 159.3002 | -46.3941 | 95.321 | -52.9755 | -88.1085 | -55.9154 | 104.0653 | -43.4564 | 90.4707 | -14.6182 | 94.196 | -24.323 | 122.4749 | -19.9475 | 69.5921 | -15.3917 | 162.6192 | -17.07 | -175.7599 | -27.0945 | 112.5057 | -29.0918 | -48.1731 | -19.2074 | -132.6277 | -45.5222 | -45.159 | -41.0723 | -36.9128 | -61.7683 | -39.6395 | -46.5952 | -46.2633 | -40.1531 | -38.3023 | -55.6694 | -41.6305 | -41.9059 | 314 | -35.4034 | -38.1451 | -36.4848 | -42.7594 | -35.9677 | -43.0557 | -36.2269 | -41.5107 | 314 | -40.6923 | -34.5821 | -31.3418 | -56.4817 | -34.3529 | -40.8397 | -40.9767 | -34.3976 | -31.6454 | -56.0128 | -34.3721 | -41.3278 | -39.588 | -35.5013 | -32.7313 | -50.3828 | -36.3439 | -36.1504 | -39.8724 | -35.3168 | -33.0349 | -49.9139 | -36.3631 | -36.6385
315 | -5.6657 | 0 | -5.3016 | 0 | -5.7982 | 0 | -5.2604 | 0 | -42.5768 | -65.2404 | -38.5323 | 60.5278 | -43.4241 | 12.8838 | -40.6003 | 147.7803 | -52.7432 | -94.237 | -50.1164 | -136.7597 | -46.841 | -8.3329 | -37.3565 | 151.7155 | -43.754 | 73.5306 | -51.1233 | -165.0481 | -56.5007 | 83.8058 | -46.731 | 78.3066 | -13.5927 | 86.0067 | -25.0903 | 133.9311 | -19.7457 | 70.858 | -15.2617 | 151.9446 | -15.5195 | 162.8041 | -26.6279 | 135.61 | -39.8848 | -159.2339 | -18.5824 | -158.7162 | -45.5255 | -49.233 | -40.124 | -37.0099 | -58.1505 | -40.7408 | -47.4657 | -43.1927 | -39.5759 | -38.118 | -54.8758 | -43.2982 | -42.0935 | 315 | -36.1814 | -38.3075 | -36.2519 | -42.1818 | -36.0796 | -45.1349 | -36.7213 | -41.8312 | 315 | -37.527 | -33.9102 | -31.3442 | -52.8489 | -35.4392 | -41.6675 | -37.8911 | -33.7777 | -31.7495 | -52.3523 | -35.4804 | -42.2053 | -43.5673 | -34.4583 | -32.4523 | -49.5742 | -37.9966 | -36.2953 | -43.9314 | -34.3258 | -32.8576 | -49.0776 | -38.0378 | -36.8331
316 | -5.7224 | 0 | -5.3295 | 0 | -5.8926 | 0 | -5.2726 | 0 | -45.0126 | -60.8231 | -37.9589 | 59.2826 | -43.8615 | -8.8802 | -40.3525 | 117.1828 | -52.7468 | -82.6299 | -45.6449 | -147.0984 | -48.2961 | 10.12 | -37.8272 | 144.0941 | -42.7367 | 50.6536 | -48.7074 | 149.3856 | -59.985 | 62.6525 | -58.5785 | 80.1702 | -12.9703 | 74.8659 | -23.1778 | 145.1698 | -19.0096 | 69.7957 | -15.298 | 142.6324 | -15.1133 | 139.3337 | -22.8936 | 142.1714 | -28.3885 | 104.2109 | -18.7034 | 173.6783 | -45.9441 | -49.3041 | -39.5792 | -36.3308 | -55.2058 | -43.3979 | -47.6733 | -41.545 | -39.3513 | -37.5483 | -54.8686 | -45.838 | -42.3759 | 316 | -36.3334 | -38.8925 | -35.5368 | -41.3269 | -36.3268 | -45.3351 | -37.4527 | -42.546 | 316 | -35.8226 | -33.6289 | -30.6084 | -49.8763 | -38.0684 | -41.7807 | -36.2155 | -33.4587 | -31.0582 | -49.3132 | -38.1253 | -42.4007 | -43.5817 | -33.8568 | -31.8259 | -49.5391 | -40.5085 | -36.4833 | -43.9746 | -33.6866 | -32.2757 | -48.976 | -40.5654 | -37.1033
317 | -5.746 | 0 | -5.3749 | 0 | -5.9921 | 0 | -5.2773 | 0 | -45.0097 | -45.921 | -37.8166 | 56.1069 | -45.5603 | -25.5129 | -41.4904 | 92.9755 | -51.5771 | -75.0989 | -43.4654 | -170.3853 | -46.2598 | 23.7319 | -38.4493 | 143.6302 | -42.8455 | 30.07 | -47.5876 | 121.2518 | -69.6088 | 58.4592 | -49.2394 | -171.2433 | -12.9012 | 62.372 | -20.4639 | 141.9777 | -18.2112 | 66.3101 | -15.4753 | 134.2196 | -15.6747 | 116.0406 | -19.93 | 132.6071 | -23.7337 | 71.9939 | -19.4445 | 147.0764 | -46.4115 | -45.4544 | -39.5208 | -35.7083 | -53.9583 | -46.9427 | -47.4218 | -41.0937 | -39.4687 | -37.2968 | -55.9257 | -47.6523 | -42.7101 | 317 | -36.4845 | -39.6075 | -35.5083 | -40.9813 | -36.6054 | -43.8513 | -37.6383 | -41.9411 | 317 | -35.3477 | -33.7227 | -29.9623 | -48.5834 | -41.5678 | -41.4297 | -35.7188 | -33.4766 | -30.431 | -47.9662 | -41.6654 | -42.1445 | -39.7084 | -33.7748 | -31.5508 | -50.5508 | -42.2774 | -36.718 | -40.0795 | -33.5287 | -32.0195 | -49.9336 | -42.375 | -37.4328
318 | -5.72 | 0 | -5.4177 | 0 | -6.0476 | 0 | -5.2892 | 0 | -42.9685 | -41.1707 | -37.5115 | 56.3296 | -47.8649 | -33.9497 | -43.4121 | 76.1551 | -49.3443 | -75.506 | -42.8614 | 168.3735 | -43.7399 | 21.836 | -37.8444 | 146.9332 | -43.7591 | 11.5991 | -47.0737 | 99.0897 | -65.9473 | 168.5272 | -42.8364 | 168.7988 | -13.2727 | 49.863 | -18.4687 | 129.783 | -17.2197 | 59.4393 | -15.7712 | 126.4193 | -17.2368 | 92.2884 | -18.1046 | 118.5055 | -21.6182 | 44.4644 | -21.0507 | 120.9559 | -46.8371 | -43.135 | -39.741 | -35.298 | -53.5129 | -49.4475 | -47.0779 | -41.2898 | -39.8215 | -37.2458 | -57.2849 | -47.9695 | -42.1918 | 318 | -36.1227 | -39.678 | -35.6117 | -40.9841 | -36.0446 | -42.0664 | -36.2722 | -40.2513 | 318 | -35.5698 | -34.1015 | -29.578 | -48.0952 | -44.0298 | -41.0303 | -35.8721 | -33.7739 | -30.0088 | -47.4653 | -44.1583 | -41.7887 | -37.415 | -34.021 | -31.5258 | -51.8672 | -42.5518 | -36.1442 | -37.7173 | -33.6934 | -31.9566 | -51.2373 | -42.6803 | -36.9026
319 | -5.6569 | 0 | -5.4615 | 0 | -6.0773 | 0 | -5.2811 | 0 | -40.9494 | -47.3563 | -36.3672 | 56.2419 | -50.1148 | -31.5483 | -45.6583 | 68.0183 | -47.3134 | -86.4005 | -42.5837 | 154.0717 | -41.7282 | 12.4191 | -36.1912 | 144.2735 | -45.8716 | -6.6146 | -47.0457 | 77.6603 | -58.3794 | 150.5019 | -40.3569 | 147.2083 | -14.3066 | 39.0331 | -17.396 | 114.3647 | -16.7333 | 50.212 | -16.1993 | 120.7199 | -20.0755 | 67.1096 | -17.1639 | 100.8297 | -20.6749 | 18.5747 | -23.7174 | 90.8138 | -47.3302 | -41.9968 | -40.2717 | -35.0998 | -53.7013 | -48.0163 | -46.6178 | -42.0031 | -40.2624 | -37.3639 | -56.8912 | -47.175 | -41.2805 | 319 | -34.9359 | -38.9928 | -35.0423 | -40.785 | -34.7702 | -40.5371 | -34.5318 | -39.2287 | 319 | -36.3462 | -34.6055 | -29.4429 | -48.2398 | -42.5548 | -40.5405 | -36.5416 | -34.1851 | -29.8187 | -47.624 | -42.7352 | -41.3367 | -36.3399 | -34.6148 | -31.707 | -51.4297 | -41.7135 | -35.2032 | -36.5353 | -34.1944 | -32.0828 | -50.8139 | -41.8939 | -35.9994
320 | -5.5905 | 0 | -5.4786 | 0 | -6.0504 | 0 | -5.2669 | 0 | -39.5353 | -58.5471 | -34.8503 | 50.2519 | -51.7027 | -17.3447 | -47.9977 | 63.9033 | -46.385 | -102.3943 | -41.8741 | 141.1054 | -40.5436 | -2.2297 | -34.7362 | 133.598 | -50.6169 | -13.9364 | -47.8084 | 53.2793 | -56.3198 | 129.0548 | -39.6353 | 126.0154 | -15.6447 | 32.3042 | -17.0342 | 97.7229 | -16.6064 | 39.4578 | -16.5267 | 115.0727 | -25.1603 | 43.2127 | -17.1767 | 83.7935 | -21.0315 | -6.8826 | -29.2516 | 58.854 | -47.488 | -41.4309 | -40.8382 | -35.1404 | -53.9216 | -45.5911 | -46.1505 | -43.4098 | -40.4069 | -37.674 | -55.4044 | -45.8434 | -40.879 | 320 | -33.5128 | -38.2351 | -33.892 | -40.2367 | -33.6357 | -39.7008 | -33.3596 | -39.2165 | 320 | -37.8193 | -34.8164 | -29.5499 | -48.443 | -40.1125 | -40.1001 | -37.9312 | -34.3565 | -29.8735 | -47.8712 | -40.3242 | -40.8836 | -35.8404 | -35.2477 | -32.0835 | -49.9258 | -40.3648 | -34.8286 | -35.9523 | -34.7878 | -32.4071 | -49.354 | -40.5765 | -35.6121
321 | -5.5445 | 0 | -5.4781 | 0 | -5.9781 | 0 | -5.275 | 0 | -38.7131 | -72.8318 | -33.8238 | 38.4956 | -49.4926 | -2.392 | -51.4845 | 73.8093 | -46.309 | -119.7899 | -41.1998 | 125.533 | -40.218 | -17.6349 | -34.0647 | 120.194 | -54.6584 | 27.4867 | -50.0033 | 21.9949 | -55.6125 | 112.2949 | -40.1037 | 108.9217 | -17.0583 | 32.4013 | -17.6888 | 83.2566 | -17.2708 | 29.0127 | -16.8725 | 113.2535 | -44.4139 | 49.9369 | -18.3505 | 68.9411 | -22.4423 | -33.5435 | -41.9466 | -71.6742 | -47.1477 | -41.5462 | -40.9798 | -35.5032 | -54.5188 | -44.0852 | -45.9156 | -46.2398 | -40.2086 | -38.0953 | -54.3922 | -44.525 | -40.9946 | 321 | -32.5156 | -37.8255 | -33.0316 | -39.5666 | -33.0914 | -39.6721 | -33.0116 | -39.8377 | 321 | -40.6953 | -34.6641 | -29.9587 | -49.0407 | -38.6071 | -39.9375 | -40.7617 | -34.2305 | -30.2282 | -48.5407 | -38.8102 | -40.6406 | -36.0017 | -35.4353 | -32.5508 | -48.9141 | -39.0469 | -35.0165 | -36.0681 | -35.0017 | -32.8203 | -48.4141 | -39.25 | -35.7196
322 | -5.5536 | 0 | -5.4633 | 0 | -5.8739 | 0 | -5.265 | 0 | -38.669 | -89.202 | -33.7242 | 24.8833 | -46.3581 | -7.1597 | -50.2695 | 112.165 | -47.1824 | -135.6614 | -41.1667 | 107.3284 | -40.6046 | -31.7031 | -34.1558 | 106.561 | -48.7027 | 52.1668 | -54.6633 | -30.5065 | -55.8915 | 95.1207 | -41.0493 | 96.2416 | -17.6942 | 37.5557 | -19.2478 | 72.28 | -18.6327 | 21.8132 | -16.937 | 112.1864 | -27.8023 | 161.4015 | -20.545 | 58.8144 | -25.0948 | -62.0459 | -27.8903 | -151.2911 | -46.6955 | -42.5709 | -40.5554 | -36.3127 | -54.9611 | -43.2389 | -45.725 | -51.4637 | -39.8075 | -38.5258 | -53.5453 | -43.6083 | -41.6409 | 322 | -32.3418 | -37.8412 | -32.9239 | -39.2553 | -33.1465 | -40.3153 | -33.3158 | -40.2414 | 322 | -45.9101 | -34.2539 | -30.7591 | -49.4978 | -37.7756 | -39.8511 | -46.0004 | -33.9336 | -31.0477 | -49.0872 | -37.9739 | -40.46 | -37.0173 | -35.0018 | -32.9722 | -48.082 | -38.145 | -35.767 | -37.1076 | -34.6815 | -33.2608 | -47.6714 | -38.3433 | -36.3759
323 | -5.5962 | 0 | -5.4501 | 0 | -5.7848 | 0 | -5.2938 | 0 | -39.5649 | -104.0523 | -34.3052 | 15.0701 | -44.5568 | -23.5742 | -44.9365 | 112.66 | -48.7433 | -146.7007 | -42.3334 | 90.5865 | -41.6012 | -43.3973 | -34.6908 | 96.3583 | -44.6521 | 40.5009 | -55.0314 | -131.1954 | -57.4994 | 79.4842 | -42.2291 | 83.1191 | -16.8283 | 41.0083 | -21.2838 | 71.1128 | -19.9258 | 22.3622 | -16.5995 | 109.8117 | -22.161 | 137.762 | -24.2459 | 65.7455 | -29.8585 | -100.8448 | -22.344 | -177.6868 | -46.3895 | -44.6656 | -39.7855 | -37.2527 | -54.6082 | -43.4546 | -45.5478 | -52.6911 | -39.3892 | -38.8564 | -52.9657 | -43.6364 | -42.4117 | 323 | -32.868 | -38.0693 | -33.3572 | -39.7139 | -33.5361 | -41.3029 | -33.9517 | -40.1822 | 323 | -47.0949 | -33.793 | -31.6565 | -49.1581 | -38.0045 | -39.763 | -47.241 | -33.6044 | -31.9589 | -48.8234 | -38.1608 | -40.254 | -39.0694 | -34.1893 | -33.2602 | -47.5156 | -38.1863 | -36.6269 | -39.2155 | -34.0007 | -33.5626 | -47.1809 | -38.3426 | -37.1179
324 | -5.6437 | 0 | -5.4738 | 0 | -5.7806 | 0 | -5.3205 | 0 | -41.2379 | -114.7459 | -35.1297 | 7.571 | -44.0152 | -41.5627 | -41.9782 | 95.7557 | -50.534 | -154.5149 | -44.3937 | 84.7834 | -42.9773 | -50.6714 | -35.5993 | 87.7907 | -42.66 | 22.0213 | -49.3465 | 171.3064 | -60.8914 | 71.7837 | -45.2 | 68.3186 | -15.6632 | 36.7907 | -21.7911 | 83.3113 | -20.38 | 26.254 | -16.1129 | 105.1652 | -19.7787 | 112.5009 | -24.3417 | 98.3491 | -37.9331 | 178.4931 | -19.8072 | 157.3723 | -46.0734 | -46.9661 | -39.1886 | -37.7335 | -54.1398 | -44.888 | -45.2277 | -48.3587 | -39.1203 | -39.0675 | -52.8722 | -44.5033 | -43.1228 | 324 | -33.749 | -38.3134 | -33.9073 | -40.7122 | -34.2016 | -42.019 | -34.9854 | -40.6949 | 324 | -42.715 | -33.4766 | -32.0898 | -48.666 | -39.4142 | -39.4471 | -42.8849 | -33.3397 | -32.413 | -48.3592 | -39.5675 | -39.9072 | -41.3224 | -33.5449 | -33.4238 | -47.3984 | -39.0295 | -37.3422 | -41.4923 | -33.408 | -33.747 | -47.0916 | -39.1828 | -37.8023
325 | -5.6942 | 0 | -5.5301 | 0 | -5.8035 | 0 | -5.366 | 0 | -43.2763 | -117.7804 | -36.1944 | 5.003 | -44.5149 | -58.5393 | -40.6576 | 77.0586 | -52.7794 | -153.4757 | -45.1078 | 93.1972 | -44.3603 | -52.0043 | -36.9113 | 84.3679 | -41.9554 | 3.551 | -46.0981 | 137.2523 | -65.6174 | 92.6693 | -52.338 | 78.2847 | -14.9061 | 27.4539 | -19.8488 | 91.6227 | -20.0538 | 28.0356 | -15.8075 | 99.0488 | -18.9581 | 86.316 | -20.3746 | 109.3986 | -34.7188 | 75.8083 | -18.7584 | 134.0591 | -45.7392 | -47.204 | -38.9071 | -37.6259 | -53.9931 | -47.3798 | -44.8035 | -46.0652 | -38.9949 | -39.2293 | -53.2215 | -45.702 | -43.9822 | 325 | -34.9136 | -38.5933 | -34.4734 | -41.4581 | -35.1708 | -42.1131 | -36.3071 | -41.5578 | 325 | -40.371 | -33.3007 | -31.9317 | -48.463 | -41.8497 | -39 | -40.5351 | -33.1914 | -32.2599 | -48.1896 | -42.0138 | -39.4375 | -41.5098 | -33.2129 | -33.5351 | -47.6914 | -40.1719 | -38.1787 | -41.6739 | -33.1036 | -33.8633 | -47.418 | -40.336 | -38.6162
326 | -5.7172 | 0 | -5.5946 | 0 | -5.836 | 0 | -5.3685 | 0 | -44.6666 | -110.4548 | -37.0162 | 8.7564 | -45.6158 | -72.3498 | -40.2198 | 58.9664 | -53.845 | -140.7589 | -43.3851 | 97.1068 | -44.9269 | -46.4355 | -37.6329 | 90.9003 | -42.2364 | -14.5055 | -44.548 | 110.2451 | -62.9301 | 136.3186 | -49.1756 | 143.2707 | -14.7072 | 16.0699 | -17.5657 | 86.016 | -19.7474 | 25.9352 | -15.8596 | 92.1235 | -18.9455 | 59.4441 | -17.25 | 100.9463 | -30.2909 | 24.9606 | -18.7405 | 111.9523 | -45.5108 | -45.6702 | -38.9303 | -37.1866 | -53.9405 | -50.7522 | -44.3993 | -45.1212 | -38.9594 | -39.3993 | -53.8642 | -46.9688 | -44.9683 | 326 | -35.8441 | -38.7505 | -34.6889 | -41.1107 | -35.7777 | -41.6903 | -36.5827 | -41.4055 | 326 | -39.404 | -33.2422 | -31.4694 | -48.3459 | -45.1576 | -38.5633 | -39.5266 | -33.1234 | -31.8181 | -48.1045 | -45.3837 | -39.0308 | -39.953 | -33.2131 | -33.6821 | -48.2696 | -41.3742 | -39.1323 | -40.0756 | -33.0943 | -34.0308 | -48.0282 | -41.6003 | -39.5998
327 | -5.7119 | 0 | -5.6815 | 0 | -5.8788 | 0 | -5.3785 | 0 | -44.1783 | -100.8443 | -36.4295 | 16.3695 | -47.5052 | -81.6721 | -40.4095 | 41.1828 | -51.9595 | -129.7707 | -41.3272 | 90.4723 | -43.9561 | -42.3666 | -36.4701 | 97.6062 | -43.4784 | -31.6587 | -44.1482 | 85.4752 | -57.4968 | 139.5206 | -43.2754 | 136.9218 | -15.252 | 3.5747 | -16.0176 | 72.6354 | -19.7482 | 21.5601 | -16.3287 | 85.9472 | -19.9816 | 32.4277 | -15.5014 | 87.4896 | -29.3564 | -17.3299 | -19.8582 | 92.2758 | -45.4337 | -44.3146 | -39.1751 | -36.7189 | -53.8634 | -53.6389 | -44.0721 | -45.0233 | -38.9658 | -39.5565 | -54.5487 | -48.2225 | -45.7303 | 327 | -35.4744 | -38.678 | -34.0649 | -40.0967 | -35.079 | -40.9437 | -35.0733 | -40.2821 | 327 | -39.3114 | -33.2539 | -31.007 | -48.1819 | -47.9574 | -38.1933 | -39.3418 | -33.087 | -31.3404 | -47.9846 | -48.2604 | -38.6936 | -38.6027 | -33.4632 | -33.8446 | -48.8672 | -42.541 | -39.8515 | -38.6331 | -33.2963 | -34.178 | -48.6699 | -42.844 | -40.3518
328 | -5.6793 | 0 | -5.6958 | 0 | -5.9026 | 0 | -5.3633 | 0 | -42.3859 | -98.6955 | -34.6749 | 17.7887 | -49.7411 | -84.0654 | -41.3474 | 23.709 | -49.6424 | -135.5612 | -39.7755 | 77.8212 | -42.3275 | -46.3424 | -34.4263 | 95.3102 | -46.1226 | -43.7348 | -44.7919 | 61.3996 | -53.9903 | 126.2021 | -40.6989 | 119.0721 | -16.4141 | -6.5873 | -15.3689 | 56.3839 | -19.8894 | 18.3308 | -16.9746 | 81.8578 | -22.155 | 5.8132 | -14.7193 | 73.2322 | -29.8947 | -65.1917 | -22.6894 | 80.4322 | -45.4248 | -43.573 | -39.5645 | -36.5107 | -53.8076 | -52.0417 | -43.9341 | -45.6839 | -39.0036 | -39.6294 | -54.8951 | -49.305 | -46.3875 | 328 | -33.8811 | -38.4797 | -32.8446 | -38.9696 | -33.5279 | -40.1919 | -33.1949 | -39.4483 | 328 | -40.0046 | -33.3243 | -30.8314 | -48.1118 | -46.3459 | -38.0315 | -39.9881 | -33.101 | -31.1474 | -47.905 | -46.6784 | -38.5708 | -37.8937 | -33.8852 | -33.9501 | -49.1993 | -43.6092 | -40.4849 | -37.8772 | -33.6619 | -34.2661 | -48.9925 | -43.9417 | -41.0242
329 | -5.6444 | 0 | -5.6912 | 0 | -5.9061 | 0 | -5.3748 | 0 | -40.6041 | -105.9334 | -32.993 | 10.1252 | -50.7962 | -73.0909 | -43.4514 | 8.5512 | -48.2549 | -150.1441 | -38.846 | 61.9589 | -41.2327 | -57.1742 | -32.8074 | 84.6927 | -50.4079 | -38.3378 | -46.6221 | 39.0042 | -52.0258 | 107.14 | -39.8371 | 101.7466 | -18.3144 | -14.3214 | -15.7563 | 38.9528 | -20.3834 | 15.4721 | -17.896 | 84.7033 | -26.1411 | -23.7645 | -14.9481 | 60.0256 | -28.9509 | -119.5144 | -27.5775 | 97.1275 | -45.3617 | -43.4242 | -39.9398 | -36.6469 | -53.6508 | -48.7992 | -44.0936 | -47.3905 | -39.1327 | -39.6014 | -54.5936 | -49.8241 | -47.6376 | 329 | -32.2378 | -38.323 | -31.6902 | -38.1331 | -32.1588 | -39.8578 | -31.8742 | -39.2373 | 329 | -41.7461 | -33.4883 | -31.0025 | -47.9596 | -43.108 | -38.1875 | -41.6993 | -33.2266 | -31.2721 | -47.7447 | -43.4244 | -38.7188 | -37.7798 | -34.2954 | -33.957 | -48.9024 | -44.1329 | -41.7315 | -37.733 | -34.0337 | -34.2266 | -48.6875 | -44.4493 | -42.2628
330 | -5.6169 | 0 | -5.6383 | 0 | -5.8727 | 0 | -5.4076 | 0 | -39.4962 | -118.3713 | -31.9693 | -1.1329 | -49.8477 | -65.842 | -47.1435 | 4.509 | -47.9454 | -166.6187 | -38.5532 | 44.932 | -40.8168 | -69.5662 | -31.9696 | 71.2494 | -50.5467 | -0.9591 | -50.6965 | 15.3486 | -51.4018 | 86.0512 | -39.7729 | 87.6229 | -20.5078 | -14.4311 | -17.2812 | 22.0924 | -20.821 | 14.5078 | -17.7355 | 91.9336 | -33.3134 | -62.1261 | -15.8567 | 49.2721 | -27.3633 | -162.6781 | -24.8405 | 136.9243 | -45.3792 | -43.8284 | -40.0765 | -37.1722 | -53.1995 | -46.719 | -44.2985 | -50.6266 | -39.3513 | -39.4547 | -53.8844 | -49.8844 | -49.089 | 330 | -31.2028 | -38.3076 | -31.0003 | -37.8005 | -31.3843 | -40.0606 | -31.2536 | -39.1569 | 330 | -45.0097 | -33.7344 | -31.5553 | -47.5612 | -41.0807 | -38.4258 | -44.9883 | -33.4786 | -31.7646 | -47.3268 | -41.3114 | -38.8909 | -38.2115 | -34.4596 | -33.8378 | -48.2461 | -44.2461 | -43.2163 | -38.1901 | -34.2038 | -34.0471 | -48.0117 | -44.4768 | -43.6814
331 | -5.5928 | 0 | -5.5857 | 0 | -5.8309 | 0 | -5.4492 | 0 | -39.1641 | -132.6249 | -31.6526 | -14.2054 | -48.2744 | -69.0863 | -49.6516 | 27.3207 | -48.4134 | 176.3741 | -39.0063 | 28.5674 | -40.964 | -82.4442 | -31.856 | 56.8709 | -46.0362 | 6.5982 | -64.8673 | -16.7851 | -52.1888 | 65.4967 | -39.9656 | 73.5332 | -21.8039 | -4.9009 | -20.4194 | 9.5248 | -20.9337 | 13.1823 | -16.3778 | 95.7508 | -41.0435 | 172.8614 | -17.2798 | 45.1303 | -26.058 | 163.7933 | -19.7517 | 134.4018 | -45.4908 | -44.7828 | -39.8416 | -38.0689 | -52.5572 | -46.0055 | -44.4607 | -56.2059 | -39.5733 | -39.3435 | -53.242 | -50.0418 | -49.3642 | 331 | -30.864 | -38.3425 | -30.8616 | -38.0967 | -31.2077 | -40.6318 | -31.23 | -38.8026 | 331 | -50.6131 | -33.9805 | -32.4761 | -46.9715 | -40.4198 | -38.6298 | -50.6202 | -33.7424 | -32.6197 | -46.7263 | -40.5563 | -39.0115 | -39.19 | -34.2488 | -33.7507 | -47.6563 | -44.4561 | -43.5333 | -39.1971 | -34.0107 | -33.8943 | -47.4111 | -44.5926 | -43.915
332 | -5.6077 | 0 | -5.5596 | 0 | -5.7825 | 0 | -5.5612 | 0 | -39.4559 | -146.3421 | -32.0383 | -26.4768 | -47.4086 | -78.1178 | -46.853 | 44.7743 | -49.8674 | 159.7665 | -40.2151 | 14.1353 | -41.6054 | -94.1171 | -32.4413 | 43.2659 | -43.1176 | -4.4319 | -53.1235 | 151.2614 | -54.4291 | 49.7425 | -40.7838 | 57.8531 | -21.3447 | 2.722 | -25.9903 | 16.4911 | -20.911 | 9.5844 | -14.6256 | 91.805 | -32.171 | 98.1896 | -18.5234 | 49.8695 | -25.546 | 136.5399 | -16.8803 | 119.8761 | -45.4999 | -45.8986 | -39.4933 | -39.0312 | -52.2851 | -46.4416 | -44.4424 | -59.0364 | -39.7639 | -39.3174 | -52.7822 | -50.3489 | -48.4452 | 332 | -31.2095 | -38.4074 | -31.3005 | -39.0785 | -31.6249 | -41.1028 | -31.8154 | -38.6687 | 332 | -53.4287 | -34.1562 | -33.4235 | -46.7255 | -40.882 | -38.6599 | -53.4768 | -33.9814 | -33.47 | -46.5026 | -40.8804 | -38.8812 | -40.2909 | -33.8856 | -33.7097 | -47.2226 | -44.7893 | -42.6627 | -40.339 | -33.7108 | -33.7562 | -46.9997 | -44.7877 | -42.884
333 | -5.6181 | 0 | -5.5751 | 0 | -5.7392 | 0 | -5.6767 | 0 | -40.2556 | -158.8108 | -33.2289 | -37.0792 | -46.9076 | -88.5089 | -43.9371 | 40.398 | -52.4939 | 145.2215 | -42.0079 | 6.3278 | -42.564 | -102.3742 | -33.8675 | 32.3978 | -41.5647 | -20.099 | -46.034 | 124.5983 | -57.9882 | 47.5587 | -43.0178 | 43.485 | -20.3214 | 1.9196 | -25.2935 | 68.8209 | -21.4729 | 3.4613 | -13.3939 | 83.6174 | -28.9016 | 63.811 | -17.9976 | 58.5552 | -26.1809 | 114.8561 | -15.1621 | 100.8125 | -45.1874 | -46.4218 | -39.2109 | -39.6952 | -52.6406 | -47.5859 | -44.2235 | -53.8915 | -39.8446 | -39.4267 | -52.6103 | -50.5868 | -47.5547 | 333 | -32.2906 | -38.5292 | -32.3745 | -40.5064 | -32.7116 | -40.8659 | -33.1401 | -39.1632 | 333 | -48.2734 | -34.2265 | -34.0771 | -47.0655 | -42.0108 | -38.4843 | -48.3164 | -34.1054 | -34.0185 | -46.9014 | -41.9092 | -38.5468 | -40.8037 | -33.5928 | -33.8086 | -47.0352 | -45.0117 | -41.8155 | -40.8467 | -33.4717 | -33.75 | -46.8711 | -44.9101 | -41.878
334 | -5.6471 | 0 | -5.6418 | 0 | -5.7338 | 0 | -5.7534 | 0 | -41.592 | -168.5505 | -35.0695 | -39.523 | -47.0952 | -100.6827 | -42.0173 | 27.9517 | -57.4303 | 143.1097 | -43.7137 | 7.2227 | -43.4344 | -107.743 | -36.0373 | 30.6828 | -40.9928 | -36.2547 | -42.7306 | 99.6831 | -60.0964 | 69.9974 | -47.2929 | 40.1694 | -19.7029 | -2.9384 | -20.0139 | 73.8514 | -22.7144 | 2.1066 | -12.5227 | 72.6254 | -28.0799 | 31.5463 | -16.3325 | 59.7337 | -28.1495 | 104.1532 | -14.6258 | 81.2491 | -44.5589 | -46.0845 | -39.0447 | -39.7972 | -53.6839 | -49.2955 | -44.009 | -50.3588 | -39.8151 | -39.6809 | -52.9113 | -50.9096 | -47.2451 | 334 | -33.979 | -38.7302 | -33.8031 | -41.9483 | -34.2718 | -40.0151 | -34.9347 | -40.0351 | 334 | -44.7117 | -34.168 | -34.1501 | -48.0421 | -43.6537 | -38.2752 | -44.717 | -34.0813 | -34.0438 | -47.9501 | -43.5421 | -38.2556 | -40.4374 | -33.3976 | -34.0338 | -47.2695 | -45.2678 | -41.5113 | -40.4427 | -33.3109 | -33.9275 | -47.1775 | -45.1562 | -41.4917
335 | -5.6647 | 0 | -5.7053 | 0 | -5.7469 | 0 | -5.7663 | 0 | -43.4111 | -171.0233 | -35.8367 | -29.2945 | -47.9383 | -111.2559 | -41.0426 | 11.4438 | -58.6452 | -178.2774 | -43.8078 | 14.7776 | -44.1963 | -112.3597 | -36.6712 | 43.9145 | -41.259 | -52.4409 | -41.1935 | 75.6047 | -57.6494 | 83.7575 | -49.0131 | 72.3278 | -20.0733 | -14.611 | -17.3642 | 58.4596 | -24.375 | 5.2863 | -12.6533 | 60.7907 | -29.2325 | -0.3057 | -15.0643 | 52.066 | -29.5597 | 116.4044 | -15.2254 | 62.0807 | -43.9248 | -45.2869 | -39.0565 | -39.5133 | -55.204 | -51.1055 | -44.1824 | -48.547 | -39.7388 | -40.026 | -53.6752 | -51.6723 | -47.8344 | 335 | -34.915 | -39.0096 | -34.1898 | -42.2875 | -34.8399 | -39.3651 | -35.175 | -40.501 | 335 | -42.8823 | -34.0741 | -33.8486 | -49.4987 | -45.4002 | -38.4355 | -42.8417 | -33.9919 | -33.747 | -49.4571 | -45.3392 | -38.4161 | -39.6222 | -33.3918 | -34.3613 | -47.9699 | -45.967 | -42.0875 | -39.5816 | -33.3096 | -34.2597 | -47.9283 | -45.906 | -42.0681
336 | -5.6679 | 0 | -5.7519 | 0 | -5.7784 | 0 | -5.7325 | 0 | -44.5034 | -165.2191 | -34.6351 | -20.3157 | -49.4242 | -118.3453 | -40.8828 | -7.1797 | -54.542 | -158.5636 | -42.6559 | 17.7713 | -44.8901 | -114.5074 | -34.9898 | 53.1844 | -42.3413 | -66.6872 | -40.643 | 52.011 | -55.3893 | 82.9281 | -45.8249 | 93.6439 | -21.081 | -23.3543 | -16.0341 | 41.895 | -24.9222 | 17.2697 | -13.0109 | 50.6706 | -30.784 | -37.4008 | -14.4004 | 41.7086 | -27.9535 | 132.1855 | -16.7997 | 43.5712 | -43.5434 | -44.617 | -39.1766 | -39.1933 | -56.3463 | -52.1425 | -44.6887 | -47.9562 | -39.6835 | -40.3215 | -54.5053 | -53.0072 | -49.3207 | 336 | -34.0803 | -39.1875 | -33.1894 | -41.6 | -33.8963 | -39.152 | -33.6718 | -40.5864 | 336 | -42.2883 | -34.0156 | -33.5254 | -50.5944 | -46.3906 | -38.9103 | -42.2043 | -33.9051 | -33.4608 | -50.5679 | -46.41 | -38.9562 | -38.9491 | -33.5087 | -34.6536 | -48.7534 | -47.2553 | -43.5423 | -38.8651 | -33.3982 | -34.589 | -48.7269 | -47.2747 | -43.5882
337 | -5.6819 | 0 | -5.7757 | 0 | -5.8108 | 0 | -5.678 | 0 | -43.8834 | -157.6079 | -32.4896 | -19.9302 | -51.2486 | -118.3194 | -41.6054 | -26.4541 | -51.0106 | -168.9915 | -41.1181 | 14.5174 | -45.2162 | -114.5386 | -32.5625 | 51.4472 | -44.4426 | -76.7223 | -40.9599 | 29.1006 | -53.8836 | 75.7123 | -42.3378 | 89.8582 | -22.6784 | -32.6954 | -15.5547 | 24.183 | -24.0042 | 25.074 | -13.8502 | 42.3932 | -30.9314 | -85.8593 | -14.2681 | 30.1549 | -25.1576 | 135.2292 | -19.9388 | 24.2324 | -43.4431 | -44.2205 | -39.4002 | -38.9861 | -56.1306 | -51.6619 | -45.4358 | -48.4593 | -39.7093 | -40.4983 | -55.1155 | -55.0101 | -52.1554 | 337 | -32.1319 | -39.2843 | -31.4869 | -40.3279 | -32.0737 | -39.4178 | -31.5936 | -40.0693 | 337 | -42.7774 | -34.0274 | -33.3042 | -50.3549 | -45.8862 | -39.625 | -42.6836 | -33.8985 | -33.3081 | -50.3198 | -45.9839 | -39.7578 | -38.5386 | -33.7183 | -34.8164 | -49.3398 | -49.2344 | -46.3446 | -38.4448 | -33.5894 | -34.8203 | -49.3047 | -49.3321 | -46.4774
338 | -5.6825 | 0 | -5.7212 | 0 | -5.8219 | 0 | -5.6305 | 0 | -42.2236 | -161.6538 | -30.6983 | -29.4843 | -52.0012 | -107.9209 | -43.5941 | -42.8185 | -49.3364 | 171.186 | -39.8587 | 4.9333 | -44.6877 | -115.9216 | -30.785 | 39.4092 | -47.168 | -72.1633 | -42.509 | 7.1974 | -53.1814 | 64.6538 | -40.3121 | 75.1467 | -25.3236 | -32.5193 | -16.4851 | 6.7089 | -22.4156 | 24.1191 | -14.8115 | 40.3319 | -30.7118 | -126.4509 | -15.0149 | 19.2514 | -23.3043 | 124.5374 | -27.7623 | 19.5624 | -43.5997 | -44.2785 | -39.5532 | -39.1544 | -54.2404 | -50.0988 | -46.1939 | -50.1031 | -39.7958 | -40.3736 | -55.065 | -57.7164 | -57.4051 | 338 | -30.373 | -39.382 | -30.0066 | -39.1626 | -30.5168 | -40.2271 | -30.0708 | -39.3156 | 338 | -44.4206 | -34.1133 | -33.4719 | -48.5192 | -44.3776 | -40.372 | -44.3819 | -33.9739 | -33.5239 | -48.4185 | -44.4683 | -40.5634 | -38.596 | -33.8707 | -34.6911 | -49.3438 | -51.9952 | -51.5832 | -38.5573 | -33.7313 | -34.7431 | -49.2431 | -52.0859 | -51.7746
339 | -5.6707 | 0 | -5.6696 | 0 | -5.8274 | 0 | -5.6556 | 0 | -41.1822 | -172.7531 | -29.628 | -43.1827 | -50.2695 | -102.2799 | -46.6597 | -52.3189 | -48.9409 | 149.7403 | -39.1103 | -7.5884 | -43.9811 | -122.9679 | -29.8485 | 24.2082 | -47.1866 | -53.601 | -45.6482 | -12.0714 | -53.172 | 52.936 | -39.3003 | 57.7315 | -28.1134 | -23.969 | -18.7848 | -7.9524 | -22.0877 | 14.7888 | -15.2377 | 43.1292 | -30.6199 | -160.1155 | -16.5109 | 12.3457 | -22.6117 | 114.1214 | -27.7743 | 116.7043 | -43.8294 | -44.624 | -39.6118 | -39.6107 | -52.556 | -48.7646 | -46.6657 | -51.4016 | -39.9481 | -40.1188 | -54.3844 | -60.8743 | -62.9696 | 339 | -29.2996 | -39.566 | -29.0877 | -38.3895 | -29.6075 | -41.4243 | -29.2804 | -38.4951 | 339 | -45.7309 | -34.2774 | -33.94 | -46.8864 | -43.095 | -40.8383 | -45.732 | -34.1207 | -33.9551 | -46.7286 | -43.109 | -41.0101 | -38.9533 | -33.9411 | -34.4481 | -48.7148 | -55.2047 | -57.1422 | -38.9544 | -33.7844 | -34.4632 | -48.557 | -55.2187 | -57.314
340 | -5.6731 | 0 | -5.6133 | 0 | -5.8182 | 0 | -5.7444 | 0 | -40.9338 | 173.6162 | -29.3057 | -58.14 | -48.6564 | -107.2357 | -50.3022 | -46.3852 | -49.7552 | 128.1022 | -38.9517 | -21.7436 | -43.7527 | -134.0704 | -29.7063 | 8.2104 | -44.5434 | -48.3843 | -52.0255 | -19.3373 | -53.7374 | 42.9907 | -39.2559 | 37.2741 | -29.7806 | -6.4401 | -22.7802 | -12.3702 | -23.2193 | 4.7787 | -14.4593 | 44.9268 | -30.0675 | 176.523 | -18.414 | 13.1572 | -22.5324 | 108.3585 | -19.4573 | 114.3802 | -44.074 | -45.193 | -39.5557 | -40.2732 | -51.6092 | -47.7789 | -46.7578 | -50.4354 | -40.1848 | -39.8984 | -53.4141 | -63.4744 | -58.7537 | 340 | -28.9701 | -39.9757 | -28.8273 | -38.1957 | -29.4035 | -42.7864 | -29.2266 | -38.0121 | 340 | -44.7623 | -34.5117 | -34.6001 | -45.9959 | -42.1656 | -40.9396 | -44.8221 | -34.3666 | -34.5288 | -45.791 | -42.0345 | -41.0134 | -39.5199 | -33.8826 | -34.2253 | -47.8008 | -57.8611 | -52.9355 | -39.5797 | -33.7375 | -34.154 | -47.5959 | -57.73 | -53.0093
341 | -5.6682 | 0 | -5.594 | 0 | -5.8088 | 0 | -5.8908 | 0 | -41.4412 | 160.0912 | -29.8001 | -73.0347 | -47.5701 | -118.738 | -51.4818 | -23.9619 | -51.6044 | 108.663 | -39.4527 | -35.0436 | -44.1098 | -145.2413 | -30.4149 | -7.2333 | -42.4558 | -57.7716 | -55.7974 | 54.239 | -55.2925 | 34.1372 | -40.31 | 16.5531 | -29.6031 | 11.5895 | -26.3476 | 14.1841 | -26.4661 | 1.4041 | -13.3073 | 39.9249 | -29.373 | 163.8598 | -19.3361 | 23.2263 | -22.5746 | 110.3082 | -15.7741 | 97.6669 | -44.2657 | -45.793 | -39.5274 | -41.0548 | -51.4727 | -47.2032 | -46.551 | -48.3752 | -40.4377 | -39.8479 | -52.6643 | -64.9416 | -55.3774 | 341 | -29.4448 | -40.6661 | -29.3269 | -38.6063 | -29.9804 | -43.5257 | -29.9799 | -38.1566 | 341 | -42.707 | -34.7695 | -35.3866 | -45.8787 | -41.6092 | -40.7422 | -42.7812 | -34.6289 | -35.164 | -45.6639 | -41.3124 | -40.6602 | -40.1248 | -33.8592 | -34.1797 | -47.0703 | -59.3476 | -49.5686 | -40.199 | -33.7186 | -33.9571 | -46.8555 | -59.0508 | -49.4866
342 | -5.6983 | 0 | -5.6094 | 0 | -5.8227 | 0 | -6.0271 | 0 | -42.609 | 150.0791 | -31.2299 | -84.8027 | -47.5706 | -130.9569 | -49.3075 | -10.1934 | -54.7004 | 94.8633 | -40.5591 | -44.9086 | -44.8194 | -154.9816 | -32.0806 | -19.6527 | -41.4812 | -71.3041 | -47.551 | 64.9434 | -58.1363 | 37.2859 | -42.8997 | -3.1122 | -27.5608 | 27.602 | -22.6047 | 41.7097 | -29.1456 | 37.1682 | -12.3651 | 30.2164 | -28.0494 | 157.3182 | -18.367 | 32.2619 | -21.3311 | 113.9588 | -13.8678 | 79.4621 | -44.3633 | -46.2914 | -39.5459 | -41.707 | -52.1601 | -47.0063 | -46.1094 | -46.7524 | -40.7257 | -39.9336 | -52.3516 | -67.0141 | -53.6612 | 342 | -30.8317 | -41.5517 | -30.6904 | -39.6335 | -31.4061 | -42.8336 | -31.6227 | -39.0683 | 342 | -41.0541 | -35.0274 | -36.0087 | -46.5507 | -41.3969 | -40.2867 | -41.143 | -34.903 | -35.6799 | -46.3374 | -40.9792 | -40.0823 | -40.5931 | -33.8476 | -34.2353 | -46.7422 | -61.4047 | -47.8385 | -40.682 | -33.7232 | -33.9065 | -46.5289 | -60.987 | -47.6341
343 | -5.7066 | 0 | -5.6334 | 0 | -5.8757 | 0 | -6.093 | 0 | -44.2002 | 144.0364 | -33.4992 | -88.8907 | -47.9931 | -141.767 | -46.9565 | -13.1661 | -58.9068 | 91.148 | -41.9749 | -50.1277 | -45.6812 | -164.3729 | -34.6741 | -23.448 | -41.2686 | -84.6191 | -43.612 | 47.9728 | -58.6504 | 62.7807 | -47.952 | -16.6469 | -25.8445 | 28.5919 | -19.3705 | 34.3824 | -24.7029 | 63.0805 | -12.0145 | 17.1897 | -26.5633 | 151.1464 | -17.0201 | 30.0087 | -19.5817 | 112.7796 | -13.1606 | 60.9712 | -44.1881 | -46.3093 | -39.5426 | -41.9186 | -53.9225 | -47.2585 | -45.8014 | -45.8562 | -40.8863 | -40.2193 | -52.6217 | -71.9812 | -53.1167 | 343 | -33.0046 | -42.258 | -32.7541 | -40.9355 | -33.5402 | -41.431 | -33.9748 | -40.3594 | 343 | -40.1496 | -35.1797 | -36.212 | -48.2891 | -41.6251 | -39.9257 | -40.2228 | -35.0106 | -35.8256 | -48.0468 | -41.1655 | -39.7084 | -40.6027 | -33.836 | -34.5127 | -46.9883 | -66.3478 | -47.241 | -40.6759 | -33.6669 | -34.1263 | -46.746 | -65.8882 | -47.0237
344 | -5.739 | 0 | -5.6625 | 0 | -5.9414 | 0 | -6.0783 | 0 | -45.4413 | 145.6244 | -35.2073 | -76.9581 | -49.3121 | -150.6787 | -45.3312 | -23.9407 | -62.4267 | 114.17 | -43.0345 | -48.2176 | -47.1477 | -172.7702 | -36.3973 | -7.4756 | -41.6372 | -97.2396 | -41.7415 | 27.3154 | -55.3808 | 73.791 | -57.0427 | 16.0019 | -24.3338 | 25.9015 | -17.7669 | 19.4488 | -20.6064 | 57.2465 | -12.3036 | 2.4682 | -25.4647 | 142.0239 | -16.0536 | 23.3403 | -17.9844 | 104.714 | -13.2311 | 43.297 | -43.8696 | -45.7853 | -39.5165 | -41.6626 | -57.3696 | -47.9728 | -45.8305 | -45.7305 | -40.8719 | -40.5844 | -53.225 | -70.8125 | -53.628 | 344 | -34.6626 | -42.3329 | -34.1963 | -42.0754 | -34.9879 | -40.4989 | -35.2554 | -41.3392 | 344 | -39.9915 | -35.1329 | -35.9236 | -51.7071 | -42.3103 | -39.8891 | -40.068 | -34.9305 | -35.5843 | -51.4282 | -41.8945 | -39.7522 | -40.0463 | -33.7775 | -34.8454 | -47.5625 | -65.15 | -47.6866 | -40.1228 | -33.5751 | -34.5061 | -47.2836 | -64.7342 | -47.5497
345 | -5.7605 | 0 | -5.6668 | 0 | -5.9715 | 0 | -5.9949 | 0 | -45.306 | 149.9815 | -33.8021 | -63.0061 | -50.7293 | -152.1241 | -44.5815 | -38.5918 | -60.2799 | 132.4574 | -42.9859 | -43.7116 | -49.0402 | -175.0294 | -34.3932 | 7.3921 | -42.5499 | -108.3784 | -41.1695 | 6.2663 | -53.016 | 67.4923 | -50.3117 | 74.6937 | -23.5424 | 20.8317 | -17.5493 | 2.669 | -18.2638 | 43.4088 | -13.301 | -12.5888 | -25.1222 | 132.7266 | -15.9064 | 12.3651 | -17.2074 | 93.7907 | -14.1538 | 26.1146 | -43.5927 | -44.8857 | -39.4404 | -41.2998 | -63.6552 | -49.1318 | -46.034 | -46.2332 | -40.6473 | -40.9519 | -53.7098 | -63.0691 | -55.377 | 345 | -33.4238 | -41.8555 | -32.9949 | -42.2422 | -33.6481 | -40.2752 | -33.4742 | -41.5557 | 345 | -40.4727 | -34.8868 | -35.5393 | -57.9884 | -43.465 | -40.0625 | -40.5664 | -34.6758 | -35.3049 | -57.6837 | -43.1369 | -40.0391 | -39.1252 | -33.6799 | -35.1914 | -48.043 | -57.4023 | -49.4055 | -39.2189 | -33.4689 | -34.957 | -47.7383 | -57.0742 | -49.3821
346 | -5.7628 | 0 | -5.643 | 0 | -5.9683 | 0 | -5.881 | 0 | -44.2855 | 147.8551 | -31.2234 | -64.525 | -51.6943 | -144.4436 | -44.8369 | -54.8417 | -58.0947 | 126.439 | -41.939 | -42.0282 | -50.0732 | -169.6178 | -31.5323 | 3.9714 | -43.9787 | -115.1658 | -41.7094 | -14.4581 | -51.7563 | 57.3255 | -45.1708 | 67.2033 | -23.8374 | 13.6946 | -18.6203 | -15.5582 | -17.577 | 26.537 | -15.2019 | -26.7732 | -24.6868 | 121.6341 | -16.4462 | 5.3455 | -16.829 | 81.6037 | -15.8117 | 14.773 | -43.3034 | -43.9763 | -39.2904 | -41.069 | -64.5261 | -50.4216 | -46.143 | -47.0073 | -40.2863 | -41.2251 | -53.7016 | -58.4214 | -58.7255 | 346 | -30.977 | -41.4471 | -30.6991 | -41.4081 | -31.2347 | -40.7588 | -30.966 | -41.1304 | 346 | -41.2445 | -34.5235 | -35.3062 | -58.8831 | -44.7786 | -40.1747 | -41.3643 | -34.318 | -35.188 | -58.5578 | -44.5406 | -40.262 | -38.2135 | -33.5276 | -35.4623 | -48.0586 | -52.7784 | -52.7572 | -38.3333 | -33.3221 | -35.3441 | -47.7333 | -52.5404 | -52.8445
347 | -5.7764 | 0 | -5.6237 | 0 | -5.9636 | 0 | -5.7555 | 0 | -43.3191 | 139.0504 | -29.3245 | -74.4107 | -50.252 | -136.1342 | -46.2535 | -70.418 | -57.078 | 109.6572 | -40.5543 | -46.8232 | -49.4685 | -164.5513 | -29.573 | -8.7238 | -45.2402 | -113.4948 | -43.4228 | -33.3539 | -50.9496 | 49.3595 | -42.5555 | 50.8995 | -25.2445 | 12.8972 | -21.3264 | -30.8519 | -18.2577 | 10.3366 | -18.3371 | -36.6425 | -24.9246 | 120.8823 | -17.6778 | -1.4219 | -17.4488 | 72.5548 | -18.3684 | 6.049 | -43.0029 | -43.3624 | -39.1282 | -41.0849 | -58.6279 | -51.0889 | -45.9948 | -47.53 | -39.8975 | -41.2409 | -53.0729 | -55.5261 | -65.4202 | 347 | -29.1211 | -41.4133 | -28.9279 | -40.0255 | -29.4137 | -41.8838 | -29.1926 | -40.2929 | 347 | -41.7536 | -34.1211 | -35.3085 | -53.0042 | -45.4652 | -40.0312 | -41.9063 | -33.9339 | -35.3294 | -52.6643 | -45.3334 | -40.2393 | -37.586 | -33.3518 | -35.4645 | -47.4492 | -49.9024 | -59.4566 | -37.7387 | -33.1646 | -35.4854 | -47.1093 | -49.7706 | -59.6647
348 | -5.8035 | 0 | -5.6075 | 0 | -5.9389 | 0 | -5.6925 | 0 | -42.9005 | 125.1986 | -28.3344 | -89.6826 | -48.0738 | -141.7928 | -48.8199 | -78.8782 | -57.7117 | 82.892 | -39.3996 | -56.9189 | -48.3557 | -168.3209 | -28.6024 | -25.1537 | -45.1309 | -107.7492 | -46.695 | -46.956 | -50.4091 | 39.7528 | -41.3175 | 31.5275 | -27.1099 | 25.4134 | -26.2532 | -37.4945 | -20.5649 | -1.3758 | -22.6833 | -32.867 | -24.8167 | 129.9356 | -19.1179 | -2.1947 | -18.8451 | 70.1165 | -21.0006 | 7.1223 | -42.8305 | -43.2439 | -38.9914 | -41.3031 | -55.768 | -50.4861 | -45.7169 | -47.4233 | -39.6199 | -41.1427 | -52.2208 | -53.6303 | -76.8135 | 348 | -28.1409 | -41.7982 | -27.9713 | -38.7909 | -28.4621 | -43.4575 | -28.3125 | -39.4455 | 348 | -41.6198 | -33.8164 | -35.4996 | -50.1605 | -44.8786 | -39.778 | -41.8158 | -33.681 | -35.6106 | -49.8291 | -44.7936 | -40.0244 | -37.4404 | -33.1879 | -35.3392 | -46.6133 | -48.0228 | -70.8746 | -37.6364 | -33.0525 | -35.4502 | -46.2819 | -47.9378 | -71.121
349 | -5.83 | 0 | -5.5918 | 0 | -5.9472 | 0 | -5.6738 | 0 | -43.3254 | 108.9349 | -28.2271 | -105.3564 | -46.6866 | -154.9108 | -51.4444 | -75.1383 | -60.5236 | 48.553 | -38.7867 | -69.5251 | -47.4823 | -177.7529 | -28.568 | -42.7777 | -43.9203 | -109.5978 | -51.8254 | -38.631 | -50.6917 | 28.5137 | -41.1953 | 11.1088 | -25.4134 | 51.0887 | -31.2601 | 3.0579 | -24.4869 | 5.9689 | -24.3717 | -0.8236 | -22.5807 | 133.2321 | -19.9425 | 2.7295 | -19.478 | 77.9617 | -21.8116 | 23.6415 | -42.8148 | -43.7445 | -38.971 | -41.7132 | -54.846 | -49.307 | -45.4668 | -46.8652 | -39.4941 | -41.0332 | -51.709 | -52.5566 | -61.4665 | 349 | -28.0352 | -42.6314 | -27.8422 | -38.109 | -28.3893 | -44.8212 | -28.3177 | -39.0304 | 349 | -41.0352 | -33.6641 | -35.8832 | -49.2542 | -43.7152 | -39.5196 | -41.2734 | -33.5469 | -36.0394 | -48.8988 | -43.6332 | -39.793 | -37.9145 | -33.141 | -35.2032 | -46.1172 | -46.9648 | -55.5193 | -38.1527 | -33.0238 | -35.3594 | -45.7618 | -46.8828 | -55.7927
350 | -5.8813 | 0 | -5.6003 | 0 | -6.0164 | 0 | -5.6927 | 0 | -44.8433 | 93.5141 | -29.064 | -120.4316 | -46.4205 | -173.7776 | -52.6566 | -64.1324 | -64.9551 | -12.0404 | -38.8359 | -83.4018 | -47.1519 | 169.114 | -29.5498 | -59.4081 | -42.9659 | -120.097 | -51.128 | 1.6921 | -51.9951 | 23.5375 | -42.2721 | -9.6736 | -21.5127 | 56.6889 | -25.8312 | 36.6569 | -23.4613 | 44.269 | -21.2516 | 13.5195 | -19.8264 | 126.955 | -19.7305 | 9.3534 | -17.9763 | 86.1719 | -20.5114 | 30.3066 | -43.0028 | -44.8655 | -39.0926 | -42.2133 | -55.1515 | -48.4513 | -45.5337 | -46.224 | -39.5102 | -41.0299 | -51.6939 | -52.0864 | -56.1392 | 350 | -28.8736 | -44.1422 | -28.6117 | -38.1287 | -29.2848 | -44.7761 | -29.2952 | -39.3519 | 350 | -40.3427 | -33.6289 | -36.332 | -49.5512 | -42.851 | -39.5173 | -40.6237 | -33.4938 | -36.5206 | -49.1351 | -42.7586 | -39.841 | -38.9842 | -33.2113 | -35.1486 | -46.0936 | -46.4861 | -50.1228 | -39.2652 | -33.0762 | -35.3372 | -45.6775 | -46.3937 | -50.4465
351 | -5.9354 | 0 | -5.6161 | 0 | -6.1289 | 0 | -5.7144 | 0 | -47.291 | 84.5704 | -30.8639 | -131.6555 | -47.2876 | 167.3486 | -52.606 | -51.0168 | -64.2472 | -93.1411 | -39.3929 | -96.1768 | -47.3373 | 154.8929 | -31.5514 | -71.3343 | -42.8975 | -134.7465 | -46.7129 | 6.5617 | -52.6406 | 30.3508 | -44.5639 | -29.8261 | -18.6463 | 49.0732 | -22.5162 | 28.1519 | -18.8315 | 49.5483 | -19.0603 | 7.4486 | -17.9772 | 115.9926 | -19.1196 | 7.7341 | -15.9566 | 84.0799 | -19.5659 | 23.5019 | -43.4105 | -46.4112 | -39.3516 | -42.4993 | -56.1642 | -48.2309 | -45.8792 | -45.7182 | -39.617 | -41.1102 | -51.8836 | -51.959 | -53.0921 | 351 | -30.6705 | -46.1042 | -30.2682 | -38.7272 | -31.1385 | -43.4465 | -31.2154 | -40.3752 | 351 | -39.7828 | -33.6816 | -36.5639 | -50.5481 | -42.6148 | -39.7503 | -40.1021 | -33.4881 | -36.7849 | -50.0353 | -42.5165 | -40.1648 | -40.4758 | -33.4162 | -35.1748 | -46.2675 | -46.3429 | -46.9632 | -40.7951 | -33.2227 | -35.3958 | -45.7547 | -46.2446 | -47.3777
352 | -5.9868 | 0 | -5.6279 | 0 | -6.2364 | 0 | -5.7204 | 0 | -49.7046 | 85.9575 | -33.4761 | -132.5773 | -49.8906 | 152.369 | -50.7837 | -41.8301 | -60.3932 | -143.7961 | -40.3664 | -107.106 | -47.9632 | 140.9947 | -34.5089 | -73.2524 | -43.9693 | -149.439 | -44.0757 | -6.5147 | -51.2402 | 36.4717 | -48.5671 | -47.3603 | -16.8518 | 35.7779 | -21.3456 | 12.7921 | -15.8115 | 37.6041 | -18.2112 | -4.7616 | -16.6665 | 101.5888 | -18.8919 | 3.8683 | -14.1969 | 74.9962 | -19.6221 | 12.5806 | -44.0777 | -47.6589 | -39.6592 | -42.523 | -57.2574 | -48.7604 | -46.1865 | -45.5099 | -39.8384 | -41.2568 | -51.9365 | -51.9786 | -51.291 | 352 | -33.278 | -46.997 | -32.6011 | -39.8683 | -33.8704 | -42.0327 | -33.9028 | -42.11 | 352 | -39.5231 | -33.8516 | -36.5362 | -51.6295 | -43.1325 | -39.9501 | -39.882 | -33.602 | -36.8026 | -51.021 | -43.04 | -40.4661 | -41.6721 | -33.6724 | -35.27 | -46.3086 | -46.3507 | -45.0546 | -42.031 | -33.4228 | -35.5364 | -45.7001 | -46.2582 | -45.5706
353 | -5.982 | 0 | -5.6148 | 0 | -6.2867 | 0 | -5.7085 | 0 | -50.4603 | 91.0819 | -34.7004 | -116.2657 | -54.4764 | 153.3728 | -48.3708 | -45.8465 | -58.8043 | -174.2616 | -41.6875 | -116.4079 | -48.7645 | 129.0273 | -36.1836 | -55.0928 | -46.0961 | -159.0562 | -42.9261 | -23.367 | -49.2864 | 31.0362 | -56.8131 | -55.1645 | -16.0675 | 21.5109 | -21.9851 | -2.2837 | -14.2588 | 21.1967 | -18.6423 | -17.7676 | -16.4206 | 86.947 | -19.3034 | -0.8215 | -13.3495 | 62.5355 | -21.0862 | 0.9519 | -44.8263 | -47.1896 | -39.8068 | -42.4162 | -57.7247 | -50.1076 | -46.1499 | -45.4663 | -40.1382 | -41.5406 | -51.6499 | -51.6382 | -49.2592 | 353 | -34.5423 | -46.0444 | -33.7554 | -41.3854 | -35.5494 | -41.1887 | -35.3187 | -44.1524 | 353 | -39.4843 | -34.1562 | -36.4342 | -52.1099 | -44.4928 | -39.8632 | -39.8515 | -33.8515 | -36.7077 | -51.438 | -44.3991 | -40.4414 | -41.2076 | -33.8248 | -35.5586 | -46.0351 | -46.0234 | -42.9725 | -41.5748 | -33.5201 | -35.8321 | -45.3632 | -45.9297 | -43.5507
354 | -5.9666 | 0 | -5.5999 | 0 | -6.2564 | 0 | -5.7201 | 0 | -50.4636 | 90.014 | -32.5287 | -105.0259 | -54.6881 | -171.3504 | -46.9446 | -59.4588 | -59.1899 | 170.1457 | -43.2098 | -120.4025 | -49.2016 | 118.1272 | -33.9453 | -40.5841 | -48.3393 | -155.9526 | -42.7934 | -39.8517 | -48.1128 | 17.69 | -59.1548 | 56.9728 | -16.3958 | 7.5348 | -24.5908 | -14.2627 | -13.9072 | 3.0615 | -19.9987 | -28.6824 | -16.7874 | 73.8137 | -20.215 | -2.5756 | -13.2528 | 49.2899 | -24.0423 | -7.6833 | -45.2334 | -45.5383 | -39.6859 | -42.3427 | -57.3818 | -52.3586 | -45.7679 | -45.4127 | -40.408 | -41.9827 | -51.2718 | -50.6197 | -47.2172 | 354 | -32.4335 | -45.1711 | -32.0301 | -42.8102 | -33.667 | -40.9679 | -33.4015 | -45.0424 | 354 | -39.4461 | -34.4414 | -36.3761 | -51.7819 | -46.7587 | -39.5115 | -39.8128 | -34.1516 | -36.6226 | -51.1254 | -46.6385 | -40.0478 | -39.5717 | -33.7193 | -36.0161 | -45.6719 | -45.0198 | -40.9608 | -39.9384 | -33.4295 | -36.2626 | -45.0154 | -44.8996 | -41.4971
355 | -5.9408 | 0 | -5.6192 | 0 | -6.1941 | 0 | -5.7162 | 0 | -51.0061 | 86.6461 | -30.0168 | -110.3847 | -51.2605 | -171.2556 | -46.7048 | -75.4696 | -58.1501 | 165.8645 | -44.6785 | -118.3851 | -49.6417 | 101.6188 | -31.0747 | -43.8553 | -48.7042 | -145.0218 | -43.5078 | -54.6678 | -48.3175 | 2.8655 | -50.3611 | 52.8839 | -17.8678 | -1.9867 | -29.6057 | -6.1804 | -14.5798 | -14.2812 | -21.8944 | -31.1561 | -18.3423 | 64.7995 | -20.8287 | -1.6367 | -14.0631 | 36.4344 | -28.5182 | -2.2781 | -45.1823 | -43.8158 | -39.293 | -42.2565 | -54.8268 | -55.4799 | -45.5997 | -45.2332 | -40.2846 | -42.6856 | -51.7129 | -49.323 | -46.194 | 355 | -29.9501 | -45.1118 | -29.7817 | -43.6588 | -30.9414 | -41.5379 | -30.7854 | -44.2701 | 355 | -39.2924 | -34.3438 | -36.3157 | -49.2076 | -49.8607 | -39.4056 | -39.614 | -34.0905 | -36.5403 | -48.6327 | -49.7637 | -39.8835 | -37.875 | -33.3522 | -36.7448 | -46.0937 | -43.7038 | -39.9999 | -38.1966 | -33.0989 | -36.9694 | -45.5188 | -43.6068 | -40.4778
356 | -5.93 | 0 | -5.6425 | 0 | -6.1298 | 0 | -5.7401 | 0 | -50.974 | 85.1379 | -28.4973 | -123.0123 | -49.9119 | -179.0497 | -47.78 | -90.4082 | -57.1828 | 142.5396 | -44.7101 | -111.037 | -50.6105 | 85.4912 | -29.154 | -57.2344 | -47.6155 | -141.2293 | -44.8401 | -65.7598 | -49.6151 | -3.3421 | -47.0828 | 34.5549 | -20.2602 | -0.5181 | -29.5991 | 43.9453 | -16.4562 | -28.2594 | -23.1283 | -23.544 | -19.6187 | 68.9456 | -20.8172 | 6.6752 | -15.4142 | 29.7262 | -29.326 | 52.004 | -45.0885 | -42.5406 | -38.9892 | -42.1275 | -51.9439 | -56.1109 | -45.8456 | -45.0517 | -39.8636 | -43.5175 | -52.8417 | -48.3173 | -46.5281 | 356 | -28.4417 | -45.755 | -28.3449 | -43.3796 | -29.062 | -42.8047 | -28.9707 | -43.204 | 356 | -39.1217 | -33.9336 | -36.1975 | -46.3014 | -50.4684 | -39.7158 | -39.4092 | -33.7338 | -36.3874 | -45.8141 | -50.3708 | -40.1055 | -36.6106 | -33.0592 | -37.5875 | -47.1992 | -42.6748 | -40.3983 | -36.8981 | -32.8594 | -37.7774 | -46.7119 | -42.5772 | -40.788
357 | -5.9937 | 0 | -5.6969 | 0 | -6.0875 | 0 | -5.7437 | 0 | -50.2901 | 75.239 | -27.9403 | -137.8513 | -48.2686 | 171.761 | -49.7854 | -95.1905 | -61.614 | 114.5587 | -43.2994 | -111.6172 | -51.7444 | 71.3673 | -28.2522 | -74.1072 | -46.2499 | -146.5307 | -46.3349 | -71.6388 | -49.6795 | -2.5067 | -45.8454 | 12.5513 | -20.8984 | 21.2955 | -23.9292 | 57.0931 | -19.7595 | -31.6724 | -22.4743 | -16.9283 | -19.2982 | 82.0639 | -19.892 | 8.5018 | -17.1739 | 30.6305 | -24.7412 | 64.1538 | -45.0842 | -41.8499 | -39.0999 | -41.9944 | -50.8811 | -52.928 | -46.2555 | -45.1031 | -39.5758 | -44.314 | -52.8726 | -47.6187 | -48.2005 | 357 | -27.8752 | -46.8719 | -27.7882 | -42.0504 | -28.1648 | -43.9027 | -28.1114 | -42.1818 | 357 | -39.1094 | -33.5821 | -36.0007 | -45.1842 | -47.2311 | -40.168 | -39.4062 | -33.4883 | -36.2507 | -44.7936 | -47.1843 | -40.5118 | -35.8562 | -33.1062 | -38.3203 | -47.1757 | -41.9218 | -42.113 | -36.153 | -33.0124 | -38.5703 | -46.7851 | -41.875 | -42.4568
358 | -6.0979 | 0 | -5.7223 | 0 | -6.128 | 0 | -5.7772 | 0 | -50.9649 | 55.6514 | -28.1509 | -152.4509 | -47.1766 | 153.2972 | -50.1723 | -89.6119 | -68.5391 | -171.0988 | -42.4294 | -121.5016 | -52.4706 | 61.4143 | -28.3329 | -91.654 | -45.5502 | -159.3423 | -47.4308 | -72.0989 | -49.3509 | -8.9806 | -46.0546 | -9.9721 | -17.9114 | 31.8135 | -20.954 | 45.8239 | -22.0797 | -10.3404 | -20.8755 | -22.2775 | -16.8841 | 87.3005 | -19.112 | 3.1878 | -17.6326 | 41.4434 | -21.8324 | 58.4283 | -45.1878 | -41.7966 | -39.4385 | -41.9574 | -51.4808 | -50.4997 | -46.7926 | -45.6944 | -39.4221 | -44.9606 | -52.5544 | -47.378 | -50.9246 | 358 | -28.0745 | -47.5059 | -27.9655 | -41.166 | -28.2348 | -44.5171 | -28.2079 | -41.9194 | 358 | -39.5965 | -33.3242 | -35.8595 | -45.7585 | -44.7774 | -40.6646 | -39.9721 | -33.2941 | -36.1802 | -45.3528 | -44.7225 | -41.0154 | -35.6987 | -33.3406 | -38.8627 | -46.8321 | -41.6557 | -44.7966 | -36.0743 | -33.3105 | -39.1834 | -46.4264 | -41.6008 | -45.1474
359 | -6.2296 | 0 | -5.732 | 0 | -6.1936 | 0 | -5.7812 | 0 | -54.1607 | 34.8793 | -28.9538 | -165.1432 | -47.435 | 129.172 | -49.2436 | -97.9629 | -58.8348 | -166.9678 | -42.5165 | -132.6154 | -52.3405 | 51.2741 | -29.4071 | -108.7044 | -45.7387 | -176.7835 | -47.9403 | -72.3659 | -49.7817 | -16.6885 | -47.7987 | -35.7347 | -14.9791 | 27.0553 | -19.6588 | 33.767 | -19.4187 | 8.6015 | -20.1223 | -34.4894 | -14.4712 | 80.2541 | -19.0698 | -5.278 | -16.177 | 47.0499 | -20.4853 | 46.7351 | -45.3772 | -42.4522 | -39.9139 | -42.0725 | -53.0179 | -49.6592 | -47.5445 | -46.7718 | -39.3546 | -45.357 | -52.857 | -47.6311 | -52.1425 | 359 | -28.8797 | -47.6836 | -28.7279 | -41.2275 | -29.2856 | -44.8922 | -29.2851 | -42.6927 | 359 | -40.5422 | -33.125 | -35.8429 | -47.2859 | -43.9272 | -41.3509 | -41.0398 | -33.161 | -36.2913 | -46.8243 | -43.878 | -41.7633 | -36.2226 | -33.6843 | -39.1274 | -47.125 | -41.8991 | -45.9489 | -36.7202 | -33.7203 | -39.5758 | -46.6634 | -41.8499 | -46.3613
360 | -6.3259 | 0 | -5.7331 | 0 | -6.2578 | 0 | -5.7729 | 0 | -60.3332 | 38.6996 | -30.4261 | -175.2083 | -49.3467 | 102.9542 | -50.3081 | -116.7931 | -55.8492 | 174.0003 | -42.6518 | -140.5676 | -51.6368 | 39.8486 | -31.5392 | -121.2414 | -46.9905 | 163.6187 | -48.122 | -73.7384 | -50.555 | -21.1094 | -51.4719 | -67.4235 | -13.119 | 13.9553 | -19.62 | 20.8117 | -16.2413 | 2.5148 | -19.9563 | -51.7026 | -12.8047 | 68.52 | -20.1462 | -14.934 | -14.4541 | 43.8531 | -20.2794 | 36.422 | -45.7651 | -43.7038 | -40.2915 | -42.4487 | -54.3354 | -50.2663 | -48.3073 | -47.2227 | -39.3689 | -45.3698 | -53.6003 | -48.2578 | -49.3238 | 360 | -30.3664 | -48.9137 | -30.1315 | -41.6414 | -31.3761 | -45.0766 | -31.4019 | -44.4464 | 360 | -40.8968 | -33.043 | -36.1228 | -48.6023 | -44.5332 | -42.0495 | -41.4896 | -33.1111 | -36.6758 | -48.0776 | -44.4934 | -42.5344 | -37.3779 | -33.9656 | -39.0439 | -47.8672 | -42.5247 | -43.066 | -37.9707 | -34.0337 | -39.5969 | -47.3425 | -42.4849 | -43.5509
361 | -6.3689 | 0 | -5.7127 | 0 | -6.3103 | 0 | -5.7674 | 0 | -59.3138 | 76.3364 | -32.5691 | -177.7172 | -54.0875 | 73.8179 | -54.5854 | -128.243 | -54.6659 | 156.2876 | -42.3621 | -151.0848 | -50.7951 | 26.3493 | -34.6646 | -123.0482 | -49.9631 | 143.3271 | -48.3565 | -77.2521 | -51.4146 | -23.7661 | -56.0199 | -130.2124 | -12.2779 | -0.8103 | -20.5118 | 17.5291 | -14.5606 | -10.9149 | -20.9759 | -70.747 | -12.0458 | 54.51 | -22.3047 | -22.6894 | -13.5352 | 33.2398 | -20.9184 | 24.7566 | -46.4243 | -45.1783 | -40.4165 | -42.8892 | -54.2915 | -52.5064 | -48.6072 | -46.1736 | -39.4471 | -45.2088 | -54.451 | -48.9471 | -45.3685 | 361 | -32.5295 | -50.9338 | -32.1113 | -41.8465 | -34.4366 | -45.2076 | -34.4525 | -47.0321 | 361 | -39.8047 | -33.0782 | -36.5203 | -48.5788 | -46.7937 | -42.2969 | -40.4609 | -33.1368 | -37.1218 | -47.9812 | -46.739 | -42.8398 | -38.8094 | -34.0476 | -38.8399 | -48.7383 | -43.2344 | -39.0582 | -39.4656 | -34.1062 | -39.4414 | -48.1407 | -43.1797 | -39.6011
362 | -6.3448 | 0 | -5.7173 | 0 | -6.3179 | 0 | -5.7512 | 0 | -55.3608 | 64.9115 | -33.7257 | -166.6351 | -71.8677 | 32.7877 | -59.4072 | -98.0295 | -54.5069 | 137.0527 | -42.4113 | -168.1624 | -49.8387 | 13.7568 | -36.6659 | -104.0773 | -57.1807 | 127.1574 | -48.9086 | -80.0046 | -52.6058 | -22.3521 | -52.4509 | 153.4055 | -12.3156 | -17.2012 | -21.3696 | 18.6713 | -14.072 | -28.7608 | -22.7132 | -91.1631 | -12.16 | 40.3228 | -25.7461 | -17.3928 | -13.3357 | 21.5639 | -22.265 | 17.8963 | -47.3353 | -45.8225 | -40.3573 | -43.2103 | -53.2493 | -56.8498 | -48.2681 | -44.2866 | -39.7042 | -45.3306 | -54.7251 | -49.4116 | -42.083 | 362 | -33.6953 | -51.1925 | -33.1641 | -42.1466 | -36.425 | -45.4176 | -36.3074 | -48.8308 | 362 | -37.9418 | -33.3594 | -36.8655 | -47.532 | -51.1325 | -41.9502 | -38.5693 | -33.3863 | -37.4591 | -46.9314 | -51.0986 | -42.5169 | -39.4777 | -34.0125 | -38.9858 | -49.0078 | -43.6943 | -35.7651 | -40.1052 | -34.0394 | -39.5794 | -48.4072 | -43.6604 | -36.3318
363 | -6.2471 | 0 | -5.7171 | 0 | -6.315 | 0 | -5.7533 | 0 | -53.4254 | 35.9202 | -32.2436 | -158.116 | -57.7157 | -160.4643 | -56.2525 | -71.5089 | -56.5468 | 113.8806 | -43.6125 | 171.4311 | -48.5339 | 1.1364 | -34.3056 | -86.9918 | -62.0047 | -110.1422 | -49.2593 | -77.7584 | -52.9962 | -11.0983 | -47.3775 | 115.886 | -13.263 | -31.9865 | -20.9318 | 24.7751 | -14.6612 | -46.0427 | -24.9572 | -107.5486 | -12.9378 | 28.1472 | -26.947 | 14.7897 | -13.9495 | 9.916 | -24.3632 | 14.8207 | -48.2882 | -44.9485 | -40.1189 | -43.3624 | -52.2882 | -60.386 | -47.5999 | -42.6001 | -40.0869 | -46.0023 | -53.8304 | -49.608 | -40.1152 | 363 | -32.1984 | -50.3958 | -31.9217 | -43.2392 | -34.1375 | -45.1016 | -33.9663 | -46.2091 | 363 | -36.353 | -33.8398 | -37.1153 | -46.5711 | -54.6689 | -41.2849 | -36.883 | -33.7719 | -37.6091 | -45.9732 | -54.6327 | -41.8466 | -38.7014 | -33.8718 | -39.7552 | -48.1133 | -43.8909 | -33.8002 | -39.2314 | -33.8039 | -40.249 | -47.5154 | -43.8547 | -34.3619
364 | -6.1574 | 0 | -5.763 | 0 | -6.3189 | 0 | -5.7574 | 0 | -52.3267 | -1.7171 | -30.3378 | -163.3679 | -52.6727 | 169.6355 | -54.578 | -71.6868 | -65.3601 | 105.8978 | -46.3882 | 151.9729 | -46.9685 | -13.9873 | -31.3269 | -91.1807 | -51.5498 | -122.1784 | -48.2394 | -75.3481 | -51.493 | -5.0464 | -43.9961 | 89.6568 | -15.3831 | -40.7558 | -19.4074 | 27.806 | -16.2038 | -59.6855 | -28.3762 | -119.9351 | -14.4203 | 23.1044 | -23.1828 | 37.1675 | -15.3139 | 3.2769 | -27.1947 | 25.9691 | -48.8536 | -43.2611 | -39.6894 | -43.2794 | -52.0841 | -53.5814 | -46.9271 | -41.4048 | -40.5168 | -47.3294 | -52.8411 | -49.2369 | -39.5331 | 364 | -30.2853 | -50.1645 | -30.2154 | -45.4263 | -31.17 | -43.7481 | -31.0151 | -42.6812 | 364 | -35.2474 | -34.3594 | -37.122 | -46.3211 | -47.8184 | -40.6082 | -35.6418 | -34.1979 | -37.522 | -45.7652 | -47.824 | -41.1697 | -37.1037 | -33.532 | -41.172 | -47.0781 | -43.4739 | -33.2142 | -37.4981 | -33.3705 | -41.572 | -46.5222 | -43.4795 | -33.7757
365 | -6.1349 | 0 | -5.795 | 0 | -6.3693 | 0 | -5.7794 | 0 | -51.602 | -42.8412 | -29.3216 | -174.1357 | -51.814 | 142.8493 | -53.4677 | -63.6062 | -61.1053 | -166.7358 | -50.1178 | 142.1685 | -45.7464 | -32.3285 | -29.4489 | -105.082 | -48.0044 | -150.5852 | -46.6533 | -83.5066 | -50.5367 | -5.0552 | -41.903 | 65.1383 | -18.3684 | -32.4998 | -17.9389 | 21.7842 | -18.9029 | -64.3371 | -30.5684 | -122.0539 | -15.7093 | 28.2225 | -20.249 | 33.2893 | -16.9555 | 5.0676 | -28.782 | 53.2328 | -48.6122 | -41.7099 | -39.206 | -42.995 | -52.0224 | -48.9521 | -46.8536 | -40.9396 | -40.7404 | -49.006 | -53.6505 | -48.4044 | -40.3333 | 365 | -29.2717 | -49.1397 | -29.269 | -47.6717 | -29.2894 | -42.4353 | -29.1313 | -40.4968 | 365 | -34.8047 | -34.6055 | -36.8601 | -46.2274 | -43.1571 | -40.4843 | -35.1446 | -34.3711 | -37.2156 | -45.6531 | -43.1727 | -41.0742 | -35.575 | -33.0711 | -42.8711 | -47.8555 | -42.6094 | -33.964 | -35.9149 | -32.8367 | -43.2266 | -47.2812 | -42.625 | -34.5539
366 | -6.2193 | 0 | -5.8261 | 0 | -6.4482 | 0 | -5.7997 | 0 | -50.7099 | -76.7732 | -29.1316 | 173.5857 | -52.4578 | 125.7244 | -50.4832 | -65.1331 | -56.9989 | -174.6281 | -52.9091 | 134.1246 | -45.2376 | -51.0963 | -28.6479 | -121.8096 | -46.9412 | 178.5949 | -45.9906 | -100.6991 | -48.3881 | -1.5852 | -41.0876 | 41.798 | -17.8463 | -8.7931 | -17.2473 | 11.6587 | -20.7251 | -54.6594 | -29.6263 | -134.9438 | -15.2019 | 37.6535 | -18.8859 | 18.3399 | -17.4577 | 11.7008 | -27.8907 | 73.9335 | -47.8816 | -40.6482 | -39.2201 | -42.5652 | -50.573 | -46.4217 | -47.037 | -41.4053 | -40.6842 | -50.4238 | -55.8925 | -47.7217 | -42.4591 | 366 | -29.0815 | -47.1142 | -29.0819 | -48.9306 | -28.4912 | -41.5735 | -28.332 | -39.486 | 366 | -35.186 | -34.4649 | -36.3459 | -44.7469 | -40.5956 | -40.5888 | -35.5792 | -34.236 | -36.7655 | -44.1248 | -40.622 | -41.2373 | -34.4289 | -33.0008 | -44.2045 | -50.0664 | -41.8956 | -36.0109 | -34.8221 | -32.7719 | -44.6241 | -49.4443 | -41.922 | -36.6594
367 | -6.3831 | 0 | -5.8182 | 0 | -6.5118 | 0 | -5.8284 | 0 | -48.8935 | -105.8558 | -29.3288 | 163.4835 | -52.3857 | 104.8066 | -48.4951 | -80.9345 | -53.0954 | -171.1697 | -56.8568 | 108.8974 | -45.5265 | -67.8326 | -28.7953 | -139.1909 | -47.763 | 148.8563 | -46.9393 | -120.5803 | -45.9283 | -13.6843 | -41.9317 | 19.2051 | -14.5475 | -4.8129 | -17.3897 | 0.637 | -19.8932 | -43.5225 | -27.2613 | -154.9792 | -13.1524 | 39.442 | -18.8105 | 5.7819 | -16.5801 | 16.6831 | -23.3911 | 91.814 | -47.2838 | -40.161 | -40.0206 | -42.1471 | -50.3424 | -45.204 | -46.6542 | -43.1759 | -40.4925 | -49.6776 | -55.5917 | -47.7384 | -45.5929 | 367 | -29.2599 | -44.9558 | -29.2689 | -48.9488 | -28.6505 | -41.3204 | -28.5263 | -39.7318 | 367 | -36.7928 | -34.1094 | -35.764 | -44.5242 | -39.3858 | -40.1424 | -37.3577 | -33.9807 | -36.3187 | -43.8306 | -39.3756 | -40.8258 | -33.7779 | -33.6375 | -43.2945 | -49.7735 | -41.9202 | -39.0811 | -34.3428 | -33.5088 | -43.8492 | -49.0799 | -41.91 | -39.7645
368 | -6.562 | 0 | -5.7767 | 0 | -6.4828 | 0 | -5.8819 | 0 | -47.2476 | -135.3456 | -29.7088 | 153.2673 | -53.746 | 69.1663 | -48.6902 | -103.9161 | -49.2872 | 174.0466 | -64.3057 | 22.6666 | -46.2732 | -80.4168 | -29.7931 | -155.9554 | -49.7296 | 114.1261 | -49.3734 | -135.1529 | -45.0078 | -31.3913 | -44.596 | 4.3553 | -12.1152 | -14.3902 | -18.4701 | -7.0197 | -18.0707 | -43.5239 | -24.4908 | 174.7467 | -11.3246 | 31.724 | -19.879 | -5.1055 | -15.3854 | 14.1403 | -20.2192 | 87.9741 | -46.8556 | -40.2844 | -41.012 | -42.0587 | -51.7111 | -45.5617 | -46.0462 | -47.0375 | -40.437 | -47.5892 | -55.2064 | -49.2016 | -46.8099 | 368 | -29.6161 | -43.5506 | -29.6527 | -47.858 | -29.6536 | -41.7584 | -29.6057 | -41.1399 | 368 | -40.4755 | -33.875 | -35.4967 | -45.9344 | -39.785 | -39.5634 | -41.2608 | -33.9542 | -36.1768 | -45.2283 | -39.6798 | -40.1643 | -33.7224 | -34.45 | -41.0272 | -49.4297 | -43.4249 | -40.3271 | -34.5077 | -34.5292 | -41.7073 | -48.7236 | -43.3197 | -40.928
369 | -6.6861 | 0 | -5.7604 | 0 | -6.4283 | 0 | -5.9557 | 0 | -46.5081 | -164.46 | -30.6988 | 142.7628 | -56.365 | 13.0134 | -52.4755 | -125.42 | -47.1507 | 154.1263 | -57.4146 | -84.8444 | -47.3326 | -89.1274 | -31.6845 | -168.4441 | -51.7679 | 66.0902 | -52.5712 | -143.4891 | -45.1184 | -47.9701 | -48.2668 | 8.6459 | -10.7132 | -29.1342 | -20.0813 | -7.9642 | -16.2546 | -54.1907 | -22.2168 | 146.362 | -10.1583 | 20.5199 | -22.291 | -7.397 | -14.5071 | 8.335 | -17.8085 | 79.3933 | -46.5463 | -41.0072 | -41.5111 | -42.5111 | -53.8354 | -47.8744 | -45.3268 | -55.733 | -40.5533 | -46.2213 | -55.8619 | -52.5221 | -43.4506 | 369 | -30.5748 | -43.2539 | -30.6609 | -46.3087 | -31.5265 | -42.6133 | -31.5556 | -42.8123 | 369 | -49.0469 | -33.8672 | -35.825 | -48.075 | -42.114 | -38.8985 | -49.9726 | -34.125 | -36.5554 | -47.4071 | -41.9187 | -39.3711 | -34.3211 | -34.825 | -39.5352 | -50.1015 | -46.7617 | -37.0223 | -35.2468 | -35.0828 | -40.2656 | -49.4336 | -46.5664 | -37.4949
370 | -6.7118 | 0 | -5.7841 | 0 | -6.3934 | 0 | -6.0172 | 0 | -47.0317 | 169.0767 | -32.3645 | 138.5464 | -55.782 | -58.8931 | -63.0552 | -80.5329 | -45.9478 | 134.453 | -54.1337 | -140.9004 | -48.6434 | -90.5406 | -34.5009 | -173.504 | -51.7783 | 5.0931 | -57.0694 | -147.3869 | -46.0249 | -62.8573 | -49.6615 | 34.8067 | -10.2316 | -45.4016 | -20.909 | 2.2064 | -15.3667 | -70.5965 | -20.1556 | 118.6513 | -9.6636 | 6.7107 | -24.0301 | 4.3498 | -13.9488 | -1.9792 | -16.2719 | 66.8455 | -46.4723 | -42.2418 | -41.279 | -43.3473 | -55.6442 | -53.2223 | -44.702 | -58.8855 | -40.743 | -45.8661 | -57.1551 | -58.4363 | -40.0171 | 370 | -32.1996 | -43.3985 | -32.332 | -44.9588 | -34.2591 | -43.9142 | -34.3473 | -43.7237 | 370 | -52.1737 | -34.0312 | -36.6355 | -49.8601 | -47.4382 | -38.3086 | -53.1014 | -34.3496 | -37.3301 | -49.2508 | -47.2051 | -38.6848 | -35.53 | -34.5672 | -39.1543 | -51.371 | -52.6522 | -33.6237 | -36.4577 | -34.8856 | -39.8489 | -50.7617 | -52.4191 | -33.9999
371 | -6.6436 | 0 | -5.8247 | 0 | -6.3782 | 0 | -6.081 | 0 | -49.1518 | 147.2968 | -33.3479 | 143.9685 | -52.4686 | -111.4043 | -51.5741 | -31.9794 | -45.4372 | 114.1358 | -54.1046 | 151.9189 | -48.9664 | -81.2956 | -36.9735 | -161.2059 | -49.0552 | -47.838 | -66.9818 | -97.2283 | -47.7847 | -74.4623 | -47.028 | 58.7067 | -10.5644 | -61.0001 | -19.4952 | 11.7433 | -15.4597 | -88.7487 | -19.1048 | 92.7942 | -9.8675 | -6.017 | -22.7179 | 28.8875 | -14.049 | -11.8462 | -15.323 | 55.15 | -46.6927 | -43.8712 | -40.6209 | -44.388 | -55.72 | -84.2383 | -44.227 | -48.7805 | -41.0381 | -46.3911 | -57.8794 | -57.011 | -37.8611 | 371 | -33.1837 | -43.2138 | -33.2473 | -44.1856 | -36.4615 | -45.2956 | -36.5606 | -43.1061 | 371 | -42.1369 | -34.3945 | -37.7444 | -49.8953 | -78.4136 | -37.8488 | -42.9558 | -34.6599 | -38.307 | -49.3418 | -78.1573 | -38.146 | -37.2276 | -33.9773 | -39.7475 | -52.0547 | -51.1863 | -31.4829 | -38.0465 | -34.2427 | -40.3101 | -51.5012 | -50.93 | -31.7801
372 | -6.4929 | 0 | -5.8734 | 0 | -6.4501 | 0 | -6.1043 | 0 | -54.3215 | 136.4838 | -32.5801 | 147.706 | -50.3012 | -146.2658 | -46.2688 | -49.6827 | -45.8516 | 92.3094 | -51.5216 | 65.5412 | -46.913 | -74.051 | -35.7163 | -143.2851 | -46.5254 | -86.077 | -55.4624 | -42.8268 | -50.1348 | -77.7416 | -42.6987 | 64.2259 | -11.9699 | -75.6935 | -17.6373 | 11.9941 | -16.7714 | -106.6263 | -18.6143 | 70.2782 | -10.7248 | -17.338 | -19.6748 | 31.3514 | -14.5414 | -22.1361 | -15.1724 | 42.2716 | -47.128 | -45.4001 | -39.8608 | -45.4249 | -54.1476 | -52.5407 | -43.889 | -44.5009 | -41.321 | -48.014 | -56.9046 | -49.6845 | -36.8861 | 372 | -32.4788 | -42.7327 | -32.3454 | -43.7298 | -35.0758 | -44.8289 | -34.8851 | -40.6717 | 372 | -38.008 | -34.8281 | -38.932 | -48.2742 | -46.6673 | -37.4389 | -38.6275 | -34.8709 | -39.3206 | -47.6975 | -46.4364 | -37.7847 | -38.9072 | -33.3679 | -41.5211 | -51.0312 | -43.8111 | -30.436 | -39.5267 | -33.4107 | -41.9097 | -50.4545 | -43.5802 | -30.7818
373 | -6.3703 | 0 | -5.9133 | 0 | -6.5696 | 0 | -6.0774 | 0 | -57.8387 | -160.3972 | -31.5523 | 142.9214 | -49.5341 | -173.3425 | -43.9344 | -69.4661 | -47.8718 | 70.8072 | -46.8468 | 1.6327 | -44.2134 | -79.4671 | -32.9404 | -144.1425 | -45.3893 | -119.0874 | -49.8852 | -62.0766 | -51.7783 | -71.6704 | -38.7688 | 55.0125 | -14.3487 | -84.284 | -16.1186 | 1.8808 | -18.7333 | -118.9291 | -19.0555 | 47.7306 | -12.303 | -23.2057 | -17.7022 | 24.9671 | -15.8451 | -27.1604 | -15.8267 | 31.1984 | -47.6836 | -45.5469 | -39.2071 | -46.2617 | -52.5078 | -45.9219 | -43.7375 | -41.9641 | -41.4446 | -51.2297 | -55.5344 | -44.9602 | -37.0405 | 373 | -31.4737 | -42.337 | -31.1887 | -43.1763 | -32.4039 | -42.6114 | -31.8631 | -37.7384 | 373 | -35.5938 | -35.0743 | -39.8914 | -46.5945 | -40.0086 | -37.1679 | -36.0508 | -34.875 | -40.1843 | -45.9382 | -39.8445 | -37.6601 | -39.1766 | -32.8368 | -44.8594 | -49.6211 | -39.0469 | -30.4709 | -39.6336 | -32.6375 | -45.1523 | -48.9648 | -38.8828 | -30.9631
374 | -6.2893 | 0 | -5.9252 | 0 | -6.7561 | 0 | -6.0189 | 0 | -49.3302 | -146.8169 | -31.197 | 134.4794 | -49.8687 | 164.4702 | -42.8286 | -86.4043 | -52.631 | 59.1233 | -44.5504 | -44.2269 | -42.2721 | -92.7247 | -31.0622 | -155.733 | -45.3599 | -149.6505 | -47.8936 | -87.4418 | -51.8637 | -63.821 | -36.146 | 36.5066 | -17.4553 | -77.3401 | -15.6675 | -10.2664 | -20.6727 | -124.9576 | -20.4673 | 26.4644 | -13.5403 | -21.2382 | -16.716 | 11.74 | -16.5184 | -29.9061 | -17.2328 | 21.816 | -48.2151 | -43.9561 | -38.8096 | -46.3127 | -51.637 | -42.2999 | -43.726 | -40.4475 | -41.4338 | -55.0268 | -54.8041 | -42.1272 | -38.6762 | 374 | -31.0731 | -41.5952 | -30.7247 | -42.9384 | -30.5978 | -40.861 | -29.8207 | -35.5517 | 374 | -34.1582 | -35.1445 | -40.0234 | -45.7118 | -36.3747 | -36.9699 | -34.5223 | -34.6777 | -40.2938 | -44.8809 | -36.281 | -37.7071 | -37.6668 | -32.5203 | -48.7375 | -48.8789 | -36.202 | -31.9201 | -38.0309 | -32.0535 | -49.0079 | -48.048 | -36.1083 | -32.6573
375 | -6.3336 | 0 | -5.9226 | 0 | -6.9031 | 0 | -5.9946 | 0 | -44.7146 | -164.7836 | -31.117 | 127.4871 | -51.493 | 147.9791 | -42.1037 | -101.6757 | -56.5093 | 103.2958 | -44.8063 | -76.6744 | -41.2507 | -108.0711 | -30.2379 | -171.8509 | -46.7326 | -177.5888 | -48.1305 | -110.3344 | -51.383 | -61.879 | -34.9808 | 15.081 | -17.1748 | -55.4171 | -16.0464 | -22.5676 | -21.9583 | -127.8969 | -23.386 | 16.773 | -13.3288 | -13.1074 | -16.5114 | -1.9432 | -16.6001 | -31.7724 | -19.061 | 17.7818 | -48.4937 | -42.1539 | -38.7719 | -45.2984 | -51.7163 | -40.5055 | -43.6882 | -39.8875 | -41.5485 | -52.2742 | -54.6023 | -40.9813 | -42.0105 | 375 | -30.8933 | -40.105 | -30.6154 | -43.7274 | -29.8176 | -40.1042 | -28.9289 | -34.6077 | 375 | -33.5539 | -35.2149 | -38.9648 | -45.7937 | -34.5829 | -36.7851 | -33.9649 | -34.6454 | -39.3038 | -44.8132 | -34.5109 | -37.6936 | -35.8203 | -32.4383 | -45.9406 | -48.6797 | -35.0587 | -35.1074 | -36.2313 | -31.8688 | -46.2796 | -47.6992 | -34.9867 | -36.0159
376 | -6.457 | 0 | -5.9097 | 0 | -6.9249 | 0 | -6.0301 | 0 | -42.2861 | 174.2985 | -30.9013 | 119.5526 | -54.1593 | 145.216 | -42.0077 | -119.6469 | -50.6577 | 115.9487 | -45.9536 | -92.0484 | -40.9306 | -123.1717 | -30.3018 | 169.817 | -50.3775 | 150.0986 | -49.6075 | -129.0513 | -51.2695 | -63.1293 | -34.9269 | -5.9513 | -14.1531 | -51.3321 | -17.3183 | -32.3098 | -23.0081 | -130.7276 | -27.1326 | 27.9851 | -11.9762 | -10.2987 | -17.863 | -11.1727 | -17.1033 | -36.2986 | -21.4238 | 37.7513 | -48.0472 | -40.9647 | -39.1413 | -44.4144 | -51.9026 | -39.9647 | -43.6284 | -40.2257 | -41.9218 | -48.8042 | -55.6128 | -41.0499 | -45.7822 | 376 | -30.5774 | -38.8388 | -30.4529 | -44.2227 | -29.9023 | -40.0382 | -28.9777 | -34.7079 | 376 | -33.7687 | -35.4648 | -37.9574 | -45.9929 | -34.055 | -36.7035 | -34.316 | -34.9969 | -38.3843 | -44.9777 | -33.9346 | -37.5983 | -34.5077 | -32.6843 | -42.3472 | -49.7031 | -35.1402 | -38.8573 | -35.055 | -32.2164 | -42.7741 | -48.6879 | -35.0198 | -39.7521
377 | -6.6171 | 0 | -5.8789 | 0 | -6.8164 | 0 | -6.0898 | 0 | -41.1516 | 153.4344 | -30.7989 | 108.9642 | -56.0656 | 150.7311 | -43.0468 | -136.5219 | -47.9027 | 104.5933 | -46.7599 | -98.1446 | -41.2439 | -138.7143 | -31.1986 | 152.6211 | -59.6977 | 99.4376 | -52.3704 | -146.3309 | -50.6313 | -64.3254 | -36.2385 | -23.6342 | -11.8129 | -61.1363 | -19.2393 | -34.1036 | -23.2133 | -126.0209 | -25.1285 | 51.0532 | -10.4205 | -16.646 | -19.8612 | -14.2481 | -17.6747 | -36.3517 | -19.7146 | 57.5787 | -47.2038 | -40.4421 | -40.1726 | -43.9226 | -51.0007 | -40.6179 | -43.3398 | -41.5546 | -42.2578 | -46.7617 | -57.5078 | -41.6836 | -43.3336 | 377 | -30.4041 | -38.4619 | -30.4448 | -44.0046 | -30.7832 | -40.48 | -29.9897 | -36.0645 | 377 | -34.9375 | -35.6407 | -37.3055 | -45.1218 | -34.739 | -36.5234 | -35.6757 | -35.4414 | -37.8328 | -44.1843 | -34.5281 | -37.25 | -33.825 | -33.5555 | -40.1446 | -51.6289 | -35.8047 | -36.5172 | -34.5632 | -33.3562 | -40.6719 | -50.6914 | -35.5938 | -37.2438
378 | -6.7332 | 0 | -5.897 | 0 | -6.6465 | 0 | -6.1769 | 0 | -40.8017 | 132.5005 | -31.4751 | 95.656 | -56.7387 | -177.5692 | -45.8044 | -148.537 | -45.9549 | 89.8303 | -46.6013 | -103.0448 | -42.4324 | -152.1689 | -32.9562 | 138.5233 | -55.7317 | -49.5203 | -57.5971 | -165.9381 | -50.7943 | -71.55 | -38.5157 | -32.5242 | -10.7708 | -75.9814 | -20.7704 | -21.1614 | -22.1132 | -128.5934 | -21.2425 | 49.0281 | -9.498 | -26.4883 | -21.3244 | -6.5427 | -17.6916 | -40.3524 | -16.9203 | 58.2962 | -46.554 | -40.4832 | -41.1012 | -43.6829 | -50.679 | -43.034 | -42.9478 | -44.6739 | -42.6785 | -45.9712 | -57.1509 | -43.7325 | -39.6246 | 378 | -30.9839 | -38.7031 | -31.1909 | -43.0653 | -32.4714 | -41.7274 | -31.8792 | -38.1889 | 378 | -37.9407 | -35.9453 | -36.9497 | -44.782 | -37.137 | -36.3013 | -38.7769 | -36.032 | -37.506 | -44.0325 | -36.8571 | -36.7709 | -33.75 | -34.368 | -39.238 | -51.2539 | -37.8355 | -32.9781 | -34.5862 | -34.4547 | -39.7943 | -50.5044 | -37.5556 | -33.4477
379 | -6.7532 | 0 | -5.9333 | 0 | -6.5296 | 0 | -6.2779 | 0 | -41.5283 | 112.204 | -33.0055 | 85.9278 | -51.5194 | -166.264 | -50.2525 | -129.9277 | -45 | 69.4194 | -47.5852 | -109.9582 | -44.5855 | -158.1697 | -35.589 | 129.2717 | -48.3355 | -84.8646 | -66.9992 | 57.0216 | -52.1432 | -73.4729 | -40.7285 | -27.737 | -10.419 | -91.2408 | -19.2019 | -8.027 | -20.6858 | -137.5073 | -18.8194 | 29.9352 | -9.3111 | -38.6097 | -20.4396 | 11.8352 | -17.6267 | -45.3795 | -14.9284 | 52.3929 | -46.0474 | -41.1671 | -41.2032 | -43.9185 | -50.5982 | -47.7257 | -42.6912 | -51.4242 | -43.0891 | -46.3826 | -55.0115 | -48.0374 | -37.2146 | 379 | -32.3812 | -39.5314 | -32.7784 | -42.5098 | -34.8734 | -43.8622 | -34.4264 | -39.7744 | 379 | -44.671 | -36.3359 | -37.1653 | -44.6649 | -41.7924 | -36.1616 | -45.4909 | -36.5595 | -37.6406 | -44.0686 | -41.4478 | -36.4133 | -34.4139 | -34.45 | -39.6294 | -49.0782 | -42.1041 | -30.685 | -35.2338 | -34.6736 | -40.1047 | -48.4819 | -41.7595 | -30.9367
380 | -6.7156 | 0 | -5.9967 | 0 | -6.5204 | 0 | -6.3653 | 0 | -43.8018 | 94.3215 | -34.6776 | 84.0609 | -48.1097 | -179.5136 | -46.3426 | -95.7622 | -45.3238 | 46.8723 | -49.0035 | -92.3195 | -46.5252 | -147.997 | -38.5828 | 133.5543 | -44.9922 | -112.7147 | -51.8931 | -8.0615 | -52.4498 | -64.3565 | -41.2656 | -9.1712 | -10.9715 | -107.8917 | -16.9835 | -8.7354 | -19.9685 | -155.4056 | -17.7637 | 7.9016 | -9.6664 | -50.6049 | -17.9868 | 12.6356 | -17.4928 | -53.748 | -13.7621 | 42.1461 | -45.8412 | -42.6735 | -40.5523 | -44.6069 | -50.4272 | -50.4821 | -42.696 | -59.3056 | -43.0516 | -48.1725 | -52.9694 | -51.9931 | -35.7208 | 380 | -34.0042 | -40.2579 | -34.2436 | -42.4121 | -37.1552 | -44.6327 | -36.5802 | -39.5044 | 380 | -52.59 | -36.336 | -37.8913 | -44.4305 | -44.4854 | -36.1756 | -53.3089 | -36.5312 | -38.2416 | -43.9068 | -44.1168 | -36.3307 | -35.9579 | -33.8367 | -41.4569 | -46.9727 | -45.9964 | -29.2004 | -36.6768 | -34.0319 | -41.8072 | -46.449 | -45.6278 | -29.3555
381 | -6.6179 | 0 | -6.0202 | 0 | -6.6296 | 0 | -6.3718 | 0 | -48.5406 | 91.1433 | -35.5902 | 84.7718 | -46.5187 | 164.3214 | -41.6609 | -104.7443 | -47.1723 | 25.1582 | -44.2299 | -79.5225 | -45.0322 | -131.2183 | -39.0741 | 150.8298 | -43.3335 | -138.3707 | -46.2877 | -39.4381 | -51.3223 | -61.1229 | -38.0395 | 3.9461 | -12.3387 | -121.1746 | -15.3281 | -18.3967 | -19.9843 | -169.7458 | -17.5468 | -17.5539 | -10.6839 | -60.8445 | -16.169 | 4.9207 | -17.9039 | -64.5179 | -13.3075 | 32.1183 | -45.9702 | -44.9233 | -39.6069 | -45.771 | -50.3452 | -43.7241 | -43.0359 | -47.0202 | -42.3054 | -52.1843 | -52.0554 | -44.5163 | -34.9744 | 381 | -35.0539 | -39.94 | -34.1791 | -41.0113 | -36.9558 | -42.057 | -35.1666 | -36.7604 | 381 | -40.4023 | -35.6875 | -39.1531 | -44.325 | -37.7039 | -36.4063 | -41 | -35.6758 | -39.3992 | -43.7156 | -37.3523 | -36.6641 | -38.3054 | -32.989 | -45.5664 | -46.0352 | -38.4961 | -28.3448 | -38.9031 | -32.9773 | -45.8125 | -45.4258 | -38.1445 | -28.6026
382 | -6.4821 | 0 | -6.042 | 0 | -6.8283 | 0 | -6.312 | 0 | -50.5374 | 136.7726 | -36.0572 | 86.2262 | -45.6456 | 150.011 | -39.2558 | -123.1235 | -51.1176 | 7.9451 | -40.4954 | -98.8655 | -42.0689 | -132.5042 | -36.8791 | 155.9018 | -43.1263 | -161.5231 | -43.9466 | -67.4981 | -50.9069 | -63.0287 | -34.2622 | -6.1025 | -14.6583 | -129.6716 | -14.5065 | -31.026 | -19.8461 | 176.4525 | -18.4481 | -45.2192 | -12.1951 | -65.7194 | -15.0046 | -7.4552 | -18.7273 | -73.7019 | -13.3697 | 24.1356 | -46.5232 | -46.3446 | -38.85 | -47.488 | -50.3318 | -39.243 | -43.6787 | -42.5158 | -41.3922 | -55.6279 | -52.3701 | -39.5431 | -35.2666 | 382 | -35.4669 | -38.6883 | -33.4121 | -39.0586 | -35.0039 | -39.5655 | -32.0744 | -33.6494 | 382 | -36.0337 | -34.9101 | -41.0059 | -44.2898 | -33.201 | -36.8504 | -36.4738 | -34.5639 | -41.176 | -43.5035 | -32.931 | -37.3667 | -39.8625 | -32.3679 | -49.1458 | -46.3281 | -33.5011 | -28.4383 | -40.3026 | -32.0217 | -49.3159 | -45.5418 | -33.2311 | -28.9546
383 | -6.3921 | 0 | -6.0295 | 0 | -7.0392 | 0 | -6.2586 | 0 | -44.5427 | 150.0978 | -36.0481 | 87.3131 | -45.1602 | 134.6687 | -38.1352 | -142.0497 | -60.0208 | 10.0165 | -39.7108 | -123.3974 | -39.904 | -143.2635 | -34.9523 | 145.9338 | -43.9708 | 177.009 | -43.5096 | -89.2932 | -50.2012 | -60.1374 | -32.2449 | -26.2105 | -17.0185 | -123.3162 | -14.4645 | -44.7108 | -19.4989 | 162.1691 | -20.1695 | -77.88 | -13.7819 | -61.7705 | -14.9452 | -20.3546 | -19.9924 | -84.6123 | -13.6994 | 19.8298 | -47.3076 | -44.8016 | -38.6897 | -48.8506 | -50.2373 | -36.9227 | -44.2795 | -40.5275 | -40.8803 | -49.6311 | -53.0608 | -37.0079 | -37.1688 | 383 | -35.0302 | -37.2179 | -32.9333 | -38.5899 | -33.3533 | -38.059 | -30.1743 | -31.8978 | 383 | -34.1354 | -34.4882 | -42.4585 | -44.2078 | -30.8932 | -37.2403 | -34.498 | -33.8411 | -42.592 | -43.1981 | -30.6641 | -38.0209 | -38.4095 | -32.2976 | -43.239 | -47.0313 | -30.9784 | -30.1296 | -38.7721 | -31.6505 | -43.3725 | -46.0216 | -30.7493 | -30.9102
384 | -6.4018 | 0 | -6.012 | 0 | -7.1661 | 0 | -6.2239 | 0 | -40.7387 | 137.0005 | -35.3022 | 84.3078 | -45.7328 | 118.3445 | -37.6572 | -160.5332 | -56.4705 | 107.6337 | -40.7709 | -137.4817 | -38.6293 | -159.0274 | -33.9802 | 129.0666 | -46.121 | 158.3582 | -43.7792 | -102.4272 | -48.4599 | -62.9708 | -31.9382 | -48.3721 | -16.3237 | -105.8482 | -15.1605 | -56.2212 | -19.6633 | 146.6439 | -22.6583 | -119.0839 | -13.807 | -52.4074 | -15.9614 | -34.3195 | -21.7875 | -98.805 | -13.9707 | 18.8302 | -47.5987 | -42.3074 | -39.0744 | -48.0674 | -50.126 | -36.0848 | -44.3909 | -40.0645 | -40.9721 | -45.4964 | -53.2464 | -36.0099 | -41.9167 | 384 | -33.9143 | -35.8818 | -32.5947 | -39.4807 | -32.5068 | -37.1387 | -29.6585 | -31.6833 | 384 | -33.6627 | -34.5703 | -41.6656 | -44.114 | -30.0728 | -37.2248 | -34.0525 | -33.806 | -41.8435 | -42.9599 | -29.8609 | -38.167 | -35.9056 | -32.6726 | -39.0946 | -47.2344 | -29.9979 | -34.7506 | -36.2954 | -31.9083 | -39.2725 | -46.0803 | -29.786 | -35.6928
385 | -6.5249 | 0 | -5.9858 | 0 | -7.1382 | 0 | -6.2437 | 0 | -38.6645 | 117.4267 | -34.795 | 75.282 | -47.8664 | 107.9986 | -37.7789 | 179.706 | -48.5523 | 97.0222 | -41.0448 | -138.1881 | -38.1717 | -175.4155 | -33.9141 | 110.0812 | -50.5586 | 147.1942 | -43.6117 | -111.3314 | -47.2646 | -75.4475 | -32.817 | -65.952 | -13.8364 | -105.6629 | -16.4793 | -63.4191 | -20.6272 | 131.4397 | -24.6521 | 177.705 | -12.319 | -50.4313 | -17.5895 | -45.2598 | -24.4856 | -112.7524 | -13.6474 | 17.2992 | -46.8303 | -40.3733 | -39.7404 | -46.1701 | -50.3694 | -36.1623 | -43.9194 | -40.6616 | -41.7671 | -43.2476 | -52.8647 | -35.9702 | -54.8456 | 385 | -33.1528 | -34.9932 | -32.389 | -39.629 | -32.4626 | -36.6826 | -30.1218 | -32.5938 | 385 | -34.1367 | -35.2422 | -39.6452 | -44.3836 | -30.1765 | -36.7812 | -34.6758 | -34.6289 | -39.9264 | -43.2312 | -29.9186 | -37.6757 | -33.8484 | -33.2155 | -36.7227 | -46.8789 | -29.9844 | -47.7074 | -34.3875 | -32.6022 | -37.0039 | -45.7265 | -29.7265 | -48.6019
386 | -6.6987 | 0 | -5.986 | 0 | -7.0185 | 0 | -6.3474 | 0 | -37.8499 | 96.7774 | -35.1026 | 62.5237 | -49.2091 | 115.874 | -38.8574 | 158.4751 | -44.8494 | 71.5827 | -39.5303 | -145.3022 | -38.5584 | 168.4185 | -34.5912 | 89.9612 | -57.6213 | -176.8218 | -43.1794 | -122.8029 | -48.1989 | -89.1378 | -34.3646 | -77.5461 | -12.0045 | -116.6105 | -18.1913 | -63.8744 | -21.8076 | 121.5545 | -22.8888 | 113.9019 | -10.6833 | -56.819 | -20.2121 | -46.7107 | -28.3079 | -109.05 | -12.8384 | 14.0091 | -45.2171 | -39.2301 | -40.5119 | -44.7718 | -50.803 | -36.8551 | -43.3414 | -42.163 | -43.1518 | -42.0602 | -52.4313 | -36.5653 | -48.1633 | 386 | -33.1434 | -34.8559 | -32.5935 | -38.0644 | -33.111 | -36.9337 | -31.1828 | -34.1689 | 386 | -35.4643 | -36.4531 | -38.0731 | -44.817 | -30.8691 | -36.3229 | -36.177 | -36.1333 | -38.4244 | -43.7845 | -30.5077 | -36.994 | -32.5314 | -33.8132 | -35.3615 | -46.4453 | -30.5793 | -41.1448 | -33.2441 | -33.4934 | -35.7128 | -45.4128 | -30.2179 | -41.8159
387 | -6.8446 | 0 | -5.9864 | 0 | -6.862 | 0 | -6.4507 | 0 | -38.2483 | 75.9231 | -36.208 | 49.8415 | -48.1851 | 118.0048 | -41.5752 | 139.3024 | -43.7582 | 43.5982 | -38.8556 | -163.398 | -39.7816 | 153.7972 | -35.9122 | 69.8737 | -49.7724 | -132.4886 | -43.7387 | -138.4559 | -49.6038 | -83.9452 | -35.9407 | -81.7874 | -10.9496 | -131.3632 | -18.4155 | -55.9256 | -23.2591 | 119.345 | -20.3859 | 67.2119 | -9.6994 | -67.6299 | -22.6957 | -31.2088 | -29.5938 | -86.531 | -12.1186 | 8.0914 | -43.6551 | -38.8197 | -41.5991 | -43.9637 | -49.9246 | -38.2416 | -42.8497 | -44.6316 | -44.1688 | -41.5333 | -52.5958 | -37.6355 | -42.3661 | 387 | -33.9328 | -35.8277 | -33.5737 | -37.2717 | -34.2944 | -38.0027 | -32.5709 | -35.5888 | 387 | -37.787 | -37.3242 | -37.1191 | -43.9382 | -32.2552 | -35.9877 | -38.6452 | -37.3068 | -37.513 | -43.0626 | -31.7909 | -36.399 | -31.9751 | -34.7545 | -34.6887 | -46.6094 | -31.6491 | -35.5041 | -32.8333 | -34.7371 | -35.0826 | -45.7338 | -31.1848 | -35.9154
388 | -6.9273 | 0 | -6.017 | 0 | -6.7041 | 0 | -6.5299 | 0 | -39.7895 | 58.0214 | -37.9608 | 39.5187 | -47.4011 | 111.1359 | -47.2438 | 132.0001 | -44.4931 | 17.5252 | -40.0011 | 177.683 | -42.0879 | 144.9964 | -37.8354 | 50.7286 | -45.211 | -148.196 | -46.0872 | -148.2831 | -48.0795 | -80.1798 | -37.2253 | -80.7747 | -10.7302 | -147.4845 | -17.1332 | -52.0512 | -23.2962 | 123.6128 | -18.8167 | 31.4244 | -9.3693 | -79.7378 | -20.8829 | -9.3563 | -27.4029 | -86.2426 | -11.6693 | -0.2867 | -42.6622 | -39.1188 | -41.7873 | -43.7325 | -49.588 | -41.0251 | -42.1732 | -48.7783 | -43.9312 | -41.7279 | -50.8021 | -39.583 | -39.6455 | 388 | -35.4808 | -37.976 | -35.5476 | -38.1331 | -35.908 | -39.9135 | -34.2174 | -36.287 | 388 | -41.851 | -37.0039 | -36.8052 | -43.571 | -35.0081 | -35.4691 | -42.7613 | -37.2271 | -37.2026 | -42.8839 | -34.4952 | -35.6433 | -32.1915 | -34.86 | -34.8006 | -44.7851 | -33.566 | -32.9414 | -33.1018 | -35.0832 | -35.198 | -44.098 | -33.0531 | -33.1156
389 | -6.9241 | 0 | -6.0745 | 0 | -6.6311 | 0 | -6.5667 | 0 | -42.8908 | 46.8754 | -40.0637 | 30.0739 | -48.1335 | 102.2794 | -49.9222 | -176.9451 | -47.1073 | -1.3779 | -42.9335 | 176.6613 | -44.7141 | 152.7505 | -40.1462 | 34.2611 | -43.3647 | -166.8194 | -48.2904 | -130.6581 | -46.4612 | -89.8546 | -37.6752 | -72.8005 | -11.2616 | -162.9015 | -15.5479 | -57.492 | -22.6422 | 124.486 | -18.1222 | -0.7203 | -9.7667 | -92.1454 | -17.8699 | -9.0368 | -25.4476 | -102.5551 | -11.513 | -9.9213 | -42.2391 | -40.3424 | -40.6029 | -44.2354 | -50.8257 | -45.1891 | -41.7207 | -55.2835 | -42.368 | -43.1342 | -49.366 | -42.1989 | -37.9123 | 389 | -37.8171 | -40.9129 | -37.9692 | -40.6688 | -37.5314 | -41.476 | -35.4927 | -36.2075 | 389 | -48.3594 | -35.4439 | -37.3113 | -44.7512 | -39.1146 | -35.0896 | -49.209 | -35.7369 | -37.6687 | -44.1946 | -38.6224 | -35.154 | -33.4183 | -33.6788 | -36.2101 | -43.2915 | -36.1244 | -31.2812 | -34.2679 | -33.9718 | -36.5675 | -42.7349 | -35.6322 | -31.3456
390 | -6.8251 | 0 | -6.1348 | 0 | -6.6496 | 0 | -6.5228 | 0 | -47.2504 | 60.3799 | -43.6986 | 18.0117 | -49.3543 | 108.4297 | -44.2434 | -162.549 | -50.2151 | -4.6058 | -41.986 | -168.0014 | -44.3317 | 172.2334 | -42.513 | 19.7789 | -42.6727 | 176.2629 | -45.1041 | -114.8809 | -46.384 | -105.6827 | -35.9495 | -64.971 | -12.2728 | -177.7883 | -14.5357 | -69.3207 | -20.7438 | 123.3049 | -18.5344 | -29.5393 | -10.7439 | -103.5936 | -15.6672 | -19.2261 | -24.7053 | -132.9768 | -12.0219 | -18.879 | -42.34 | -42.3565 | -39.2114 | -45.9909 | -53.6082 | -43.7854 | -41.6406 | -53.2604 | -40.8393 | -46.2149 | -49.6182 | -41.3512 | -36.7957 | 390 | -41.3603 | -41.8051 | -38.4281 | -40.7356 | -38.3271 | -40.4215 | -34.6716 | -34.7996 | 390 | -46.4353 | -34.0142 | -39.1658 | -47.4734 | -37.6506 | -34.991 | -47.1256 | -34.1897 | -39.4681 | -46.9586 | -37.2626 | -35.1178 | -35.5314 | -32.3863 | -39.3898 | -43.4834 | -35.2164 | -30.1461 | -36.2217 | -32.5618 | -39.6921 | -42.9686 | -34.8284 | -30.2729
391 | -6.6709 | 0 | -6.1841 | 0 | -6.7915 | 0 | -6.4349 | 0 | -46.1934 | 98.0001 | -53.5932 | 24.2163 | -47.4128 | 116.7924 | -41.2506 | -174.6638 | -51.951 | -2.7751 | -39.1196 | -178.6922 | -41.4558 | 177.5524 | -44.8303 | 5.9977 | -42.5517 | 161.3781 | -41.8659 | -124.2895 | -47.9255 | -116.7149 | -33.3549 | -72.3943 | -14.2391 | 171.8678 | -13.8843 | -82.4919 | -19.2652 | 113.8638 | -19.0347 | -57.0112 | -12.3898 | -111.9162 | -14.5904 | -33.4367 | -24.2821 | -165.0707 | -12.9403 | -26.8983 | -42.9386 | -44.5811 | -38.355 | -49.7354 | -57.212 | -39.5733 | -41.9184 | -48.0063 | -39.9482 | -50.8442 | -51.3833 | -37.9985 | -36.6034 | 391 | -43.3217 | -39.7722 | -36.9503 | -38.3269 | -37.9596 | -38.1611 | -32.5195 | -32.7282 | 391 | -41.3354 | -33.2773 | -43.0645 | -51.0279 | -33.3892 | -35.1269 | -41.8222 | -33.1567 | -43.3005 | -50.4205 | -33.1384 | -35.4835 | -37.9102 | -31.6841 | -44.1733 | -45.1992 | -31.8144 | -29.8119 | -38.397 | -31.5635 | -44.4093 | -44.5918 | -31.5636 | -30.1685
392 | -6.512 | 0 | -6.232 | 0 | -6.9351 | 0 | -6.2908 | 0 | -41.4618 | 102.0286 | -48.7712 | 116.4448 | -45.1589 | 104.0811 | -39.6195 | 169.7024 | -54.808 | -0.6468 | -38.6813 | 158.1295 | -38.9778 | 169.149 | -46.7732 | -1.9489 | -43.2208 | 144.7629 | -40.2519 | -140.5176 | -49.4886 | -113.4248 | -31.9998 | -88.769 | -16.3317 | 171.3512 | -13.954 | -98.734 | -18.0298 | 99.9272 | -20.793 | -86.0219 | -14.2595 | -109.6592 | -14.1093 | -49.646 | -23.9394 | 163.5964 | -13.8884 | -30.9728 | -43.8068 | -45.3575 | -38.1611 | -55.3459 | -58.506 | -37.3028 | -42.1539 | -45.2319 | -39.6253 | -49.4117 | -53.6187 | -35.9194 | -38.5555 | 392 | -39.3863 | -37.3546 | -35.8854 | -37.7142 | -37.0953 | -36.3423 | -31.2704 | -31.6123 | 392 | -38.7199 | -33.1133 | -48.8339 | -52.274 | -31.0708 | -35.2188 | -38.9999 | -32.6902 | -49.0551 | -51.5709 | -31.012 | -35.8631 | -38.8455 | -31.6491 | -42.8997 | -47.3867 | -29.6874 | -31.6204 | -39.1255 | -31.226 | -43.1209 | -46.6836 | -29.6286 | -32.2647
393 | -6.4562 | 0 | -6.257 | 0 | -7.046 | 0 | -6.2101 | 0 | -38.3103 | 89.9501 | -43.3252 | 104.3404 | -45.0288 | 86.7422 | -38.6502 | 152.2153 | -56.7233 | 37.5275 | -40.215 | 141.4652 | -37.4055 | 154.2143 | -46.6133 | -4.2619 | -45.0452 | 130.1312 | -39.4712 | -157.3534 | -48.759 | -107.4026 | -32.0125 | -106.089 | -17.3074 | -176.2914 | -14.5378 | -111.7103 | -17.8623 | 81.4316 | -24.107 | -113.9371 | -14.9528 | -98.9298 | -14.3959 | -65.356 | -23.6517 | 130.6633 | -14.7062 | -31.2907 | -44.4802 | -44.0817 | -38.402 | -52.4763 | -57.027 | -36.2028 | -41.9327 | -43.7335 | -39.7921 | -45.0499 | -55.2765 | -34.9601 | -44.5569 | 393 | -36.469 | -35.4342 | -35.5576 | -38.9039 | -36.2922 | -35.1146 | -31.1696 | -31.715 | 393 | -37.2773 | -33.3359 | -46.0201 | -50.77 | -29.9458 | -34.8867 | -37.4765 | -32.7461 | -46.2662 | -49.981 | -29.9927 | -35.7226 | -37.6255 | -31.9458 | -38.5937 | -49.0195 | -28.7031 | -37.5109 | -37.8247 | -31.356 | -38.8398 | -48.2305 | -28.75 | -38.3468
394 | -6.52 | 0 | -6.2659 | 0 | -7.0895 | 0 | -6.1673 | 0 | -36.5105 | 72.8817 | -42.1694 | 87.775 | -46.5662 | 75.131 | -38.5181 | 130.4554 | -50.8483 | 55.3734 | -42.3958 | 136.8622 | -36.7812 | 136.6665 | -44.4258 | -15.9037 | -49.2216 | 127.4948 | -39.2215 | -174.8953 | -47.5645 | -114.3323 | -32.8195 | -119.4974 | -15.4734 | -171.4106 | -15.5883 | -126.6719 | -18.6953 | 65.7238 | -30.9961 | -147.7129 | -13.8357 | -94.8963 | -15.4743 | -82.5388 | -23.0154 | 103.5012 | -15.3902 | -30.3155 | -44.243 | -42.1486 | -38.9111 | -47.5829 | -54.4501 | -35.7501 | -41.1761 | -43.0113 | -40.3715 | -42.1409 | -55.9808 | -34.5543 | -57.5339 | 394 | -35.1419 | -34.292 | -35.8679 | -40.5614 | -35.8856 | -34.5968 | -31.6865 | -32.5811 | 394 | -36.4913 | -33.8515 | -41.0629 | -48.1842 | -29.4842 | -34.0866 | -36.7454 | -33.282 | -41.4156 | -47.3606 | -29.5828 | -35.0088 | -35.6286 | -32.3911 | -35.6209 | -49.7149 | -28.2884 | -50.4444 | -35.8827 | -31.8216 | -35.9736 | -48.8913 | -28.387 | -51.3666
395 | -6.6676 | 0 | -6.2214 | 0 | -7.0543 | 0 | -6.2024 | 0 | -35.8534 | 54.0389 | -43.0661 | 76.9089 | -48.1681 | 79.4947 | -39.6918 | 106.6148 | -46.7864 | 39.8373 | -42.5648 | 141.5008 | -37.1365 | 118.7382 | -42.1436 | -35.0332 | -51.1506 | 162.5221 | -39.694 | 165.6934 | -47.5274 | -125.2682 | -33.8785 | -126.7907 | -13.4952 | -177.1573 | -17.1404 | -136.7231 | -20.769 | 51.9551 | -39.9604 | 24.1531 | -12.2073 | -99.7509 | -17.5528 | -97.149 | -23.4228 | 79.341 | -15.4147 | -28.8152 | -43.1399 | -40.6837 | -39.5431 | -44.6087 | -51.6868 | -35.8009 | -40.1785 | -42.8941 | -41.3902 | -40.3582 | -53.866 | -34.4254 | -47.2096 | 395 | -34.8889 | -34.1103 | -36.7342 | -40.3807 | -35.8158 | -34.9713 | -32.3826 | -33.6176 | 395 | -36.2265 | -34.7226 | -37.9411 | -45.4654 | -29.5795 | -33.1242 | -36.6727 | -34.3359 | -38.4063 | -44.6325 | -29.5985 | -33.9761 | -34.0161 | -32.8755 | -33.6906 | -47.6446 | -28.204 | -40.1553 | -34.4623 | -32.4888 | -34.1558 | -46.8117 | -28.223 | -41.0072
396 | -6.8469 | 0 | -6.1672 | 0 | -6.9875 | 0 | -6.2496 | 0 | -36.1761 | 36.3942 | -44.8334 | 74.7763 | -46.816 | 85.6802 | -42.8073 | 82.1222 | -45.4961 | 16.4086 | -41.1866 | 133.1887 | -38.4624 | 103.4553 | -40.4614 | -56.6072 | -46.2188 | 175.8265 | -41.2436 | 145.1187 | -48.5743 | -131.5068 | -34.2307 | -131.7419 | -12.2291 | 171.4413 | -18.8084 | -143.2349 | -24.2441 | 52.2623 | -26.8715 | -18.8156 | -11.144 | -111.0955 | -20.6261 | -109.8244 | -25.1306 | 69.9173 | -15.0152 | -30.2218 | -42.0154 | -39.9098 | -40.074 | -42.8279 | -49.8357 | -36.488 | -39.4094 | -43.507 | -42.2297 | -39.5149 | -50.1672 | -34.6554 | -43.0997 | 396 | -35.3035 | -34.924 | -37.9225 | -39.0268 | -35.9127 | -36.3551 | -32.6557 | -33.8166 | 396 | -36.6601 | -35.3828 | -35.981 | -43.6685 | -30.3208 | -32.4219 | -37.3398 | -35.2422 | -36.5783 | -42.8482 | -30.2384 | -33.1598 | -33.0629 | -33.2271 | -32.668 | -44 | -28.4882 | -36.1122 | -33.7426 | -33.0865 | -33.2653 | -43.1797 | -28.4058 | -36.8501
397 | -6.9606 | 0 | -6.152 | 0 | -6.902 | 0 | -6.3161 | 0 | -37.4481 | 21.3028 | -46.6821 | 79.3223 | -45.2049 | 72.9472 | -50.1071 | 61.3098 | -46.2336 | -2.8469 | -41.329 | 112.1197 | -40.7268 | 93.9124 | -39.4248 | -74.6974 | -43.5681 | 161.9464 | -44.9975 | 124.3757 | -48.2997 | -129.4221 | -34.6603 | -141.0005 | -11.5237 | 156.5168 | -19.7844 | -142.8726 | -26.2612 | 79.4947 | -22.5652 | -50.2563 | -10.7881 | -124.3363 | -25.0134 | -103.6182 | -27.7174 | 68.2874 | -14.2519 | -32.84 | -41.3048 | -39.8243 | -40.129 | -41.8126 | -49.797 | -38.3321 | -39.027 | -45.2223 | -41.8512 | -39.5114 | -47.9528 | -35.695 | -41.0493 | 397 | -36.3526 | -36.7055 | -39.7938 | -38.9413 | -36.1489 | -38.8265 | -33.118 | -33.9716 | 397 | -38.2617 | -34.8906 | -34.852 | -43.645 | -32.1801 | -32.125 | -39.0703 | -34.9492 | -35.4965 | -42.895 | -32.016 | -32.7109 | -32.8637 | -33.1684 | -32.5508 | -41.8008 | -29.543 | -34.1473 | -33.6723 | -33.227 | -33.1953 | -41.0508 | -29.3789 | -34.7332
398 | -6.9698 | 0 | -6.1337 | 0 | -6.7841 | 0 | -6.3723 | 0 | -39.7458 | 13.9574 | -50.4548 | 94.5741 | -46.529 | 56.4252 | -57.8151 | -173.6799 | -48.4813 | -11.2056 | -44.5944 | 94.6708 | -43.4049 | 96.8825 | -38.815 | -88.1147 | -42.5862 | 148.237 | -55.0404 | 134.3874 | -46.7633 | -141.9042 | -36.3568 | -148.1276 | -11.615 | 142.7515 | -19.9252 | -141.8653 | -23.0168 | 98.3388 | -20.0799 | -78.9634 | -11.1497 | -139.0436 | -26.0503 | -74.2629 | -26.6143 | 91.364 | -13.9242 | -39.5259 | -41.0052 | -40.5697 | -39.564 | -41.6419 | -51.763 | -41.6126 | -39.1141 | -49.6122 | -40.4347 | -40.6102 | -48.3095 | -38.0146 | -39.7243 | 398 | -38.6242 | -39.1411 | -43.4315 | -41.4787 | -36.3422 | -41.5577 | -34.3666 | -35.1205 | 398 | -42.6424 | -33.4649 | -34.6721 | -45.6293 | -35.4789 | -32.33 | -43.4785 | -33.6506 | -35.2696 | -44.9789 | -35.2403 | -32.7418 | -33.5999 | -32.5942 | -33.6404 | -42.1758 | -31.8809 | -32.9402 | -34.436 | -32.7799 | -34.2379 | -41.5254 | -31.6423 | -33.352
399 | -6.8666 | 0 | -6.1447 | 0 | -6.7346 | 0 | -6.3729 | 0 | -41.8337 | 21.0375 | -47.4538 | 155.2975 | -48.7242 | 62.829 | -46.5528 | 177.4303 | -48.8701 | -3.8577 | -47.9773 | 114.9338 | -44.3766 | 113.3858 | -37.8413 | -96.7143 | -42.4484 | 138.6194 | -48.7828 | -148.9726 | -47.8266 | -167.9267 | -37.5931 | -138.1718 | -12.1124 | 128.466 | -19.427 | -142.9783 | -20.0403 | 91.801 | -18.7422 | -103.7173 | -12.2349 | -153.1593 | -22.4812 | -60.684 | -22.8168 | 91.4451 | -13.8945 | -47.3737 | -41.0982 | -41.86 | -38.7068 | -42.5826 | -54.7506 | -43.3287 | -39.5744 | -61.5549 | -39.3353 | -42.9142 | -50.0744 | -40.7893 | -38.8856 | 399 | -40.1347 | -39.972 | -42.5164 | -43.7347 | -35.8872 | -41.7892 | -34.5385 | -36.065 | 399 | -54.6883 | -32.4687 | -35.716 | -48.6059 | -37.184 | -32.8398 | -55.4102 | -32.6007 | -36.2097 | -48.016 | -36.9558 | -33.2015 | -34.9934 | -31.8402 | -36.0476 | -43.9297 | -34.6446 | -32.151 | -35.7153 | -31.9722 | -36.5413 | -43.3398 | -34.4164 | -32.5127
400 | -6.7174 | 0 | -6.1842 | 0 | -6.7698 | 0 | -6.3419 | 0 | -41.4275 | 35.2191 | -40.2288 | 153.863 | -47.1568 | 70.502 | -42.9631 | 159.8169 | -47.9746 | -8.7104 | -44.6446 | 121.1502 | -42.4213 | 125.4636 | -36.3259 | -106.9339 | -42.0106 | 129.3264 | -43.3796 | -162.7977 | -52.5401 | 170.2213 | -35.6615 | -133.9277 | -13.1296 | 117.4846 | -18.7049 | -150.6231 | -18.0048 | 78.2131 | -18.2134 | -128.457 | -14.1336 | -165.4293 | -19.6736 | -69.4512 | -20.7562 | 76.939 | -14.0745 | -53.8785 | -41.7158 | -43.2467 | -38.3115 | -44.7978 | -57.5166 | -41.3053 | -40.3912 | -52.2776 | -38.8893 | -46.0006 | -52.3482 | -40.5667 | -38.7684 | 400 | -37.3025 | -38.5863 | -37.4537 | -41.5798 | -34.5194 | -39.6354 | -32.5924 | -34.6844 | 400 | -45.5602 | -32.1719 | -38.0804 | -51.3324 | -35.1211 | -33.6214 | -46.0934 | -32.1195 | -38.4559 | -50.7468 | -34.9634 | -34.0493 | -36.5293 | -31.5941 | -39.2832 | -46.164 | -34.3825 | -31.9986 | -37.0625 | -31.5417 | -39.6587 | -45.5784 | -34.2248 | -32.4265
401 | -6.5626 | 0 | -6.1994 | 0 | -6.8673 | 0 | -6.3048 | 0 | -39.1454 | 38.985 | -36.659 | 135.6628 | -45.7671 | 60.4663 | -40.9544 | 141.0628 | -48.1534 | -16.8896 | -43.3943 | 101.5699 | -39.7714 | 123.4919 | -35.2133 | -122.0335 | -42.1466 | 118.2044 | -40.9445 | 179.5794 | -64.4144 | -162.8765 | -34.1142 | -144.4281 | -14.6215 | 111.3744 | -17.9326 | -162.7355 | -17.2614 | 61.6922 | -18.0546 | -152.7596 | -17.1987 | -170.0234 | -18.0905 | -84.2754 | -19.3509 | 61.2612 | -14.4078 | -61.4753 | -42.7075 | -44.3989 | -38.3208 | -47.9849 | -58.6841 | -39.4731 | -41.297 | -46.797 | -38.758 | -46.8126 | -53.5744 | -38.9298 | -40.5339 | 401 | -34.3881 | -36.6291 | -34.6615 | -40.5764 | -33.3024 | -37.2997 | -31.139 | -33.4762 | 401 | -40.2344 | -32.1954 | -41.4223 | -52.4847 | -33.2737 | -34.4297 | -40.5976 | -31.8907 | -41.6801 | -51.8168 | -33.1683 | -34.9922 | -37.8363 | -31.7582 | -40.25 | -47.375 | -32.7304 | -33.6666 | -38.1995 | -31.4535 | -40.5078 | -46.7071 | -32.625 | -34.2291
402 | -6.5027 | 0 | -6.2412 | 0 | -6.962 | 0 | -6.2649 | 0 | -36.8909 | 32.8686 | -35.1121 | 117.0128 | -46.2162 | 48.0292 | -40.0545 | 117.9617 | -49.1872 | -20.858 | -44.455 | 81.548 | -37.7456 | 111.4182 | -34.8566 | -135.8048 | -42.8106 | 106.934 | -39.524 | 160.8519 | -54.8955 | -92.8788 | -33.9236 | -159.423 | -16.0095 | 113.239 | -17.7952 | -175.8548 | -17.697 | 41.7662 | -19.0674 | -171.9379 | -19.4583 | -157.6288 | -17.4689 | -105.3889 | -18.958 | 50.228 | -14.9155 | -70.5577 | -43.722 | -44.7396 | -38.5303 | -49.8392 | -60.1165 | -38.3568 | -41.8936 | -44.1651 | -38.8386 | -44.0576 | -53.5811 | -37.8135 | -46.1323 | 402 | -32.7029 | -35.0112 | -33.5382 | -41.4383 | -32.6182 | -35.4841 | -30.7386 | -33.3652 | 402 | -37.6624 | -32.3359 | -43.3365 | -53.8753 | -32.1156 | -34.9316 | -37.9239 | -31.8766 | -43.5743 | -53.1545 | -32.0919 | -35.6287 | -38.2369 | -32.0276 | -37.5549 | -47.3399 | -31.5723 | -39.1703 | -38.4984 | -31.5683 | -37.7927 | -46.6191 | -31.5486 | -39.8674
403 | -6.5308 | 0 | -6.2645 | 0 | -7.0636 | 0 | -6.2487 | 0 | -35.4028 | 19.0087 | -34.7827 | 102.5641 | -47.9354 | 42.3311 | -40.7298 | 90.0339 | -49.6863 | -14.4602 | -47.3164 | 67.2564 | -36.7238 | 94.4917 | -35.0521 | -146.845 | -44.3891 | 103.1155 | -38.7867 | 138.5546 | -49.9014 | -109.145 | -34.546 | -171.6728 | -15.6914 | 118.7854 | -17.982 | 169.6572 | -19.7959 | 26.9173 | -20.5533 | 171.9681 | -17.9557 | -140.969 | -17.5544 | -125.432 | -18.8453 | 36.6543 | -15.739 | -78.7558 | -43.8429 | -43.7006 | -38.8162 | -47.0538 | -62.6202 | -37.681 | -41.7879 | -42.7511 | -39.1245 | -41.1043 | -53.7332 | -37.0597 | -51.7807 | 403 | -31.9603 | -34.1624 | -33.6098 | -43.4308 | -32.5066 | -34.4966 | -30.9922 | -34.0044 | 403 | -36.2203 | -32.5937 | -40.523 | -56.3557 | -31.4165 | -34.7243 | -36.4866 | -32.0609 | -40.8051 | -55.5566 | -31.4323 | -35.5392 | -37.1698 | -32.2854 | -34.5735 | -47.4687 | -30.7952 | -44.7171 | -37.4361 | -31.7526 | -34.8556 | -46.6696 | -30.811 | -45.532
404 | -6.6265 | 0 | -6.2707 | 0 | -7.1504 | 0 | -6.2118 | 0 | -34.8821 | 2.9667 | -35.0124 | 92.3697 | -48.8488 | 52.4417 | -43.9122 | 58.0471 | -48.1397 | -11.4194 | -50.3616 | 72.7581 | -36.7722 | 77.5743 | -35.3034 | -151.7894 | -45.4741 | 109.1378 | -38.9511 | 112.9719 | -48.3337 | -128.5338 | -35.5262 | -177.4436 | -14.322 | 118.4248 | -18.4041 | 155.6431 | -23.7266 | 21.414 | -22.5788 | 165.1698 | -15.5698 | -139.8282 | -18.6598 | -142.2492 | -19.2831 | 22.6443 | -16.9403 | -81.5731 | -42.8373 | -42.2483 | -39.1463 | -43.5756 | -59.6615 | -37.3108 | -41.0988 | -42.3066 | -39.6461 | -39.091 | -54.5285 | -36.498 | -46.344 | 404 | -31.8489 | -34.1919 | -34.3753 | -44.25 | -32.7285 | -34.5313 | -31.5345 | -34.9057 | 404 | -35.6801 | -33.0196 | -36.9491 | -53.3908 | -31.0401 | -33.9484 | -36.0359 | -32.4957 | -37.3638 | -52.5111 | -31.099 | -34.887 | -35.6218 | -32.5198 | -32.4645 | -48.2578 | -30.2273 | -39.1936 | -35.9776 | -31.9959 | -32.8792 | -47.3781 | -30.2862 | -40.1322
405 | -6.7623 | 0 | -6.2467 | 0 | -7.1725 | 0 | -6.1881 | 0 | -35.2769 | -13.0496 | -35.4367 | 85.1458 | -46.9303 | 59.0616 | -53.0329 | 11.9687 | -46.9074 | -20.3334 | -49.5213 | 74.3532 | -37.729 | 62.3182 | -35.153 | -154.7038 | -44.0311 | 116.2197 | -40.4045 | 82.3633 | -48.3237 | -143.281 | -35.6966 | 177.5524 | -12.9325 | 111.9112 | -19.8634 | 143.7295 | -27.5548 | 47.9549 | -24.1292 | 174.6181 | -13.8752 | -152.4409 | -20.3651 | -158.1082 | -20.467 | 13.9776 | -18.3573 | -83.1612 | -41.5789 | -41.1532 | -39.5907 | -41.1063 | -55.8172 | -37.5438 | -40.2897 | -42.8834 | -40.1686 | -37.9616 | -54.1373 | -36.2272 | -43.4481 | 405 | -32.1972 | -34.9207 | -35.1983 | -42.8547 | -32.8946 | -35.6144 | -31.7669 | -34.8999 | 405 | -36.1211 | -33.4063 | -34.344 | -49.5705 | -31.2971 | -33.1172 | -36.6367 | -32.9961 | -34.9182 | -48.6447 | -31.3557 | -34.1016 | -34.3909 | -32.8284 | -31.1993 | -47.8906 | -29.9805 | -36.2756 | -34.9065 | -32.4182 | -31.7735 | -46.9648 | -30.0391 | -37.26
406 | -6.8395 | 0 | -6.2095 | 0 | -7.0902 | 0 | -6.1933 | 0 | -36.4122 | -25.09 | -36.3552 | 79.6727 | -45.2474 | 50.1293 | -51.0097 | -149.411 | -46.8949 | -27.3217 | -50.2485 | 45.2862 | -39.4323 | 51.4951 | -34.7612 | -158.0043 | -42.5175 | 109.1425 | -44.003 | 43.9296 | -48.6248 | -157.3102 | -35.968 | 166.7984 | -12.1156 | 100.1556 | -22.0106 | 137.3367 | -24.5813 | 72.6733 | -22.9316 | -173.6728 | -13.1051 | -169.6963 | -23.0745 | -165.8186 | -22.0853 | 13.1622 | -18.9192 | -76.4052 | -40.694 | -40.8247 | -39.703 | -39.6002 | -54.944 | -39.0005 | -39.7095 | -44.93 | -40.1286 | -37.6157 | -52.4321 | -36.8128 | -42.0259 | 406 | -33.1 | -35.9039 | -36.0409 | -42.2361 | -32.975 | -37.7606 | -32.0278 | -34.9109 | 406 | -38.0905 | -33.2891 | -32.7607 | -48.7345 | -32.791 | -32.6193 | -38.7205 | -33.0384 | -33.4069 | -47.8538 | -32.8072 | -33.5162 | -33.9852 | -32.8635 | -30.7762 | -46.2226 | -30.6033 | -34.9357 | -34.6152 | -32.6128 | -31.4224 | -45.3419 | -30.6195 | -35.8326
407 | -6.8336 | 0 | -6.1923 | 0 | -6.8838 | 0 | -6.2388 | 0 | -37.9731 | -32.223 | -37.9708 | 85.0876 | -44.7893 | 39.9598 | -44.0799 | 171.9432 | -46.1074 | -31.5713 | -58.7489 | -14.5696 | -41.6092 | 48.7473 | -34.3578 | -159.0635 | -42.017 | 97.9746 | -51.0664 | -26.0129 | -50.1937 | -170.7122 | -37.9742 | 155.2013 | -11.7978 | 88.367 | -23.8089 | 145.4061 | -21.6802 | 72.7782 | -20.4231 | -175.5047 | -13.2896 | 171.4722 | -24.9298 | -158.2006 | -22.0116 | 20.5494 | -18.5109 | -72.0865 | -40.3213 | -41.1925 | -39.3454 | -39.2666 | -57.2432 | -41.4386 | -39.4813 | -49.0127 | -39.6891 | -38.1298 | -51.3798 | -38.4776 | -41.3468 | 407 | -34.5318 | -36.5157 | -36.9902 | -42.289 | -33.0233 | -40.6337 | -32.7256 | -36.348 | 407 | -42.1791 | -32.8555 | -32.433 | -51.0509 | -35.2463 | -32.5975 | -42.8204 | -32.8053 | -33.0278 | -50.3594 | -35.1998 | -33.2425 | -34.3589 | -32.5118 | -31.2962 | -45.1875 | -32.2853 | -34.463 | -35.0002 | -32.4616 | -31.891 | -44.496 | -32.2388 | -35.108
408 | -6.754 | 0 | -6.2115 | 0 | -6.7528 | 0 | -6.2854 | 0 | -39.5677 | -33.5214 | -36.8483 | 103.9712 | -44.7915 | 30.4806 | -42.0347 | 148.0063 | -45.5836 | -45.5004 | -56.4112 | -174.8678 | -43.2603 | 56.2819 | -33.076 | -158.4586 | -42.4073 | 90.0638 | -48.946 | -135.5493 | -52.259 | -172.7659 | -40.6575 | 164.0359 | -12.0265 | 75.1052 | -23.3157 | 161.2764 | -20.0521 | 65.0922 | -18.6775 | 174.7838 | -14.1572 | 152.8791 | -23.1916 | -146.683 | -20.8448 | 20.7329 | -17.5895 | -73.1505 | -40.5202 | -41.663 | -39.1955 | -40.1061 | -66.9889 | -42.2372 | -39.7701 | -53.4911 | -39.3751 | -39.5474 | -51.9654 | -40.1668 | -41.2509 | 408 | -34.5561 | -36.9744 | -35.6623 | -41.9991 | -32.2392 | -41.8115 | -32.2827 | -38.2582 | 408 | -46.7371 | -32.6211 | -33.3521 | -60.7774 | -36.0257 | -33.0173 | -47.2796 | -32.6223 | -33.8207 | -60.2361 | -35.9518 | -33.4847 | -34.909 | -32.4415 | -32.7934 | -45.7539 | -33.9553 | -34.4981 | -35.4515 | -32.4427 | -33.262 | -45.2126 | -33.8814 | -34.9655
409 | -6.6691 | 0 | -6.2589 | 0 | -6.7277 | 0 | -6.3136 | 0 | -40.3675 | -26.1472 | -33.3298 | 105.339 | -44.9222 | 22.2348 | -41.0494 | 132.6165 | -46.7384 | -54.9725 | -51.1202 | 144.0342 | -42.8872 | 68.3371 | -31.2009 | -164.6162 | -42.3458 | 85.0078 | -44.612 | 177.8031 | -54.9047 | -175.2721 | -39.4759 | 176.7247 | -12.898 | 62.8097 | -20.6176 | 167.3168 | -19.4344 | 51.6289 | -17.6387 | 162.8324 | -16.0437 | 135.0257 | -20.3396 | -149.2619 | -20.1164 | 11.3062 | -16.5672 | -79.8346 | -41.1066 | -42.048 | -39.3215 | -41.6262 | -61.2629 | -41.0246 | -40.2902 | -53.2082 | -39.1964 | -41.5714 | -54.7746 | -40.7316 | -42.1085 | 409 | -32.3017 | -37.1758 | -32.5901 | -42.1387 | -30.6142 | -40.494 | -30.4296 | -37.5864 | 409 | -46.5391 | -32.5273 | -34.9571 | -55.004 | -34.7657 | -33.5625 | -46.9493 | -32.4687 | -35.3126 | -54.5352 | -34.711 | -33.9766 | -35.3789 | -32.6524 | -34.9023 | -48.5157 | -34.4727 | -35.3808 | -35.7891 | -32.5938 | -35.2578 | -48.0469 | -34.418 | -35.7949
410 | -6.572 | 0 | -6.2885 | 0 | -6.7381 | 0 | -6.3337 | 0 | -39.5079 | -18.8386 | -30.7896 | 93.1423 | -45.3555 | 13.5561 | -40.2472 | 118.3099 | -47.3752 | -57.865 | -50.5513 | 119.243 | -40.8498 | 73.0732 | -29.7324 | -176.6734 | -42.5383 | 79.9941 | -42.7552 | 148.644 | -57.6885 | -141.34 | -37.5479 | 172.4885 | -14.1867 | 54.0273 | -17.9146 | 160.8381 | -19.926 | 36.9779 | -17.4069 | 150.2297 | -19.3486 | 120.5434 | -17.8915 | -163.0226 | -20.0929 | 2.1104 | -16.0232 | -91.1681 | -41.8901 | -42.6952 | -39.4704 | -43.4409 | -58.6206 | -39.9413 | -40.7065 | -51.1366 | -39.072 | -43.6245 | -56.5581 | -40.4725 | -45.2009 | 410 | -30.1104 | -36.4827 | -30.2825 | -42.4991 | -29.2027 | -38.6342 | -28.8858 | -36.3205 | 410 | -44.5646 | -32.5 | -36.8689 | -52.3321 | -33.6528 | -33.9684 | -44.8481 | -32.3339 | -37.1072 | -51.8825 | -33.6076 | -34.3728 | -36.1232 | -32.8984 | -37.0525 | -50.2696 | -34.184 | -38.4628 | -36.4067 | -32.7323 | -37.2908 | -49.82 | -34.1388 | -38.8672
411 | -6.4992 | 0 | -6.3521 | 0 | -6.8343 | 0 | -6.3435 | 0 | -37.8207 | -19.9371 | -29.5177 | 77.4345 | -46.5632 | 7.662 | -40.2218 | 100.9961 | -47.6375 | -60.7623 | -52.4028 | 108.5188 | -38.7274 | 66.1864 | -29.0208 | 168.9949 | -42.5885 | 74.125 | -42.0094 | 122.6457 | -52.474 | -122.0352 | -36.9414 | 160.7388 | -15.6183 | 51.816 | -16.0554 | 148.1025 | -21.8934 | 25.5841 | -17.6336 | 140.2632 | -24.8314 | 122.4499 | -16.4023 | 179.8455 | -20.6724 | -4.7599 | -15.9986 | -102.1089 | -42.7348 | -43.7132 | -39.5734 | -44.9106 | -60.0317 | -39.303 | -41.0161 | -49.3773 | -38.9875 | -44.6763 | -55.7036 | -40.0843 | -53.1173 | 411 | -28.8449 | -35.5686 | -29.1427 | -43.4637 | -28.4102 | -36.9322 | -28.187 | -35.8005 | 411 | -42.8781 | -32.4883 | -38.4114 | -53.6796 | -32.9509 | -34.1818 | -43.0252 | -32.1532 | -38.5671 | -53.1974 | -32.9595 | -34.6726 | -37.214 | -33.0742 | -38.1771 | -49.3515 | -33.7322 | -46.283 | -37.3611 | -32.7391 | -38.3328 | -48.8693 | -33.7408 | -46.7738
412 | -6.4765 | 0 | -6.4158 | 0 | -6.9421 | 0 | -6.299 | 0 | -36.3596 | -28.2681 | -29.2846 | 62.1301 | -47.9282 | 10.7103 | -41.8031 | 83.1878 | -48.0471 | -62.2423 | -54.3852 | 123.4789 | -37.4053 | 52.6358 | -29.0911 | 155.2157 | -43.0368 | 70.5652 | -42.135 | 94.9691 | -48.7391 | -133.9916 | -37.2835 | 148.2978 | -16.5783 | 56.9655 | -14.7417 | 133.8183 | -25.5814 | 29.9261 | -18.2362 | 134.1102 | -25.2967 | 168.4963 | -15.3505 | 161.3609 | -21.536 | -9.4407 | -16.6325 | -115.3449 | -42.9861 | -44.5397 | -39.6209 | -44.4782 | -63.5642 | -38.8366 | -40.9744 | -47.7312 | -39.0233 | -43.7049 | -54.6385 | -39.7585 | -49.8969 | 412 | -28.4576 | -35.0456 | -29.0353 | -44.5058 | -28.3439 | -35.9128 | -28.2948 | -36.0209 | 412 | -41.2547 | -32.5468 | -38.0017 | -57.1484 | -32.4208 | -34.0323 | -41.3154 | -32.0812 | -38.1792 | -56.6221 | -32.5376 | -34.6754 | -38.0632 | -33.1444 | -37.2284 | -48.2227 | -33.3427 | -42.9548 | -38.1239 | -32.6788 | -37.4059 | -47.6964 | -33.4595 | -43.5979
413 | -6.5173 | 0 | -6.4509 | 0 | -7.0681 | 0 | -6.2516 | 0 | -35.6148 | -40.9295 | -29.8631 | 49.4186 | -47.5389 | 21.5467 | -45.9193 | 77.7982 | -47.5456 | -60.8629 | -51.1772 | 141.0791 | -37.0253 | 37.1146 | -29.799 | 144.5434 | -43.3213 | 68.4151 | -43.3879 | 61.0732 | -47.161 | -153.0616 | -38.6733 | 140.21 | -15.8418 | 60.2778 | -14.3978 | 116.8271 | -26.44 | 59.9819 | -19.291 | 130.6585 | -21.4155 | 174.1392 | -15.5886 | 141.7041 | -20.7805 | -12.7587 | -18.6703 | -121.7207 | -42.2437 | -44.443 | -39.6265 | -42.3609 | -60.025 | -38.2359 | -40.5446 | -46.3766 | -39.2438 | -41.9313 | -54.6891 | -39.2634 | -45.1556 | 413 | -28.7807 | -34.9802 | -29.7255 | -43.6808 | -28.8864 | -35.7933 | -29.1047 | -36.9573 | 413 | -39.8593 | -32.7265 | -35.8436 | -53.5741 | -31.785 | -33.4765 | -39.9257 | -32.1757 | -36.1093 | -52.9569 | -31.9843 | -34.293 | -37.9257 | -33.1092 | -35.414 | -48.2382 | -32.8125 | -38.0875 | -37.9921 | -32.5584 | -35.6797 | -47.621 | -33.0118 | -38.904
414 | -6.5545 | 0 | -6.4282 | 0 | -7.1394 | 0 | -6.231 | 0 | -35.6262 | -53.4441 | -30.9827 | 40.6939 | -45.2949 | 22.593 | -48.4562 | 117.351 | -46.4507 | -66.9528 | -47.8668 | 129.0072 | -37.469 | 22.1402 | -30.824 | 138.6241 | -42.9746 | 71.1295 | -45.9389 | 15.4099 | -47.128 | -171.2726 | -39.6241 | 140.0351 | -14.6934 | 58.412 | -14.7937 | 102.6719 | -23.1502 | 73.9159 | -19.7908 | 135.6593 | -17.9198 | 159.7724 | -16.1555 | 125.3304 | -21.8001 | -20.926 | -20.5201 | -122.6167 | -41.1859 | -43.5026 | -39.7458 | -40.3656 | -55.7562 | -37.5768 | -39.8266 | -45.5769 | -39.6092 | -40.4399 | -55.7134 | -38.5691 | -42.3909 | 414 | -29.5829 | -35.0769 | -30.8191 | -41.6411 | -29.7605 | -36.4985 | -30.1696 | -37.4757 | 414 | -39.0224 | -33.0547 | -33.8111 | -49.328 | -31.1486 | -32.6872 | -39.1487 | -32.4698 | -34.1346 | -48.6168 | -31.3458 | -33.5956 | -36.9481 | -33.1913 | -33.8854 | -49.2852 | -32.1409 | -35.2515 | -37.0744 | -32.6064 | -34.2089 | -48.574 | -32.3381 | -36.1599
415 | -6.6036 | 0 | -6.3752 | 0 | -7.0934 | 0 | -6.2535 | 0 | -36.2418 | -64.4864 | -32.3249 | 39.7497 | -43.4297 | 11.719 | -43.0546 | 132.8658 | -46.1436 | -78.3737 | -47.6617 | 109.1306 | -38.6243 | 9.4217 | -31.5752 | 139.1379 | -41.7203 | 65.5686 | -47.5981 | -55.573 | -47.8334 | 174.3034 | -39.7283 | 136.3267 | -13.7459 | 50.4165 | -15.9116 | 90.5464 | -20.5798 | 67.7645 | -19.2068 | 141.9822 | -16.7605 | 138.7885 | -17.8207 | 110.1734 | -22.0425 | -25.5784 | -21.0889 | -111.0496 | -40.2735 | -42.5971 | -40.0058 | -38.9961 | -54.1602 | -37.5073 | -39.1057 | -45.6402 | -39.8927 | -39.465 | -56.8596 | -38.2457 | -41.4463 | 415 | -30.6125 | -35.0671 | -31.8568 | -40.6132 | -30.4559 | -37.6669 | -30.8638 | -37.2075 | 415 | -39.0366 | -33.2891 | -32.3925 | -47.785 | -31.1321 | -32.0123 | -39.265 | -32.7993 | -32.7426 | -47.0668 | -31.2538 | -32.8522 | -35.9935 | -33.4022 | -32.8614 | -50.4844 | -31.8705 | -34.3529 | -36.2219 | -32.9124 | -33.2115 | -49.7662 | -31.9922 | -35.1928
416 | -6.6398 | 0 | -6.3181 | 0 | -6.9524 | 0 | -6.3396 | 0 | -37.1826 | -72.1218 | -33.1196 | 46.7852 | -42.7525 | -4.0992 | -39.6853 | 119.8963 | -46.6008 | -87.2737 | -50.1652 | 105.6833 | -40.5567 | 1.2494 | -31.5832 | 143.2589 | -41.3224 | 55.5952 | -44.9837 | -124.7278 | -49.042 | 161.2003 | -40.8378 | 127.5999 | -13.2007 | 37.8328 | -17.7044 | 86.5127 | -19.5014 | 56.4159 | -17.6472 | 144.5321 | -16.6933 | 115.6001 | -20.3672 | 109.1787 | -22.3387 | -32.2316 | -19.101 | -105.1106 | -39.7476 | -42.3038 | -40.0068 | -38.4429 | -54.3883 | -38.2374 | -38.6228 | -46.8509 | -39.8234 | -39.1385 | -57.6033 | -38.8196 | -41.5866 | 416 | -31.3552 | -34.939 | -32.1845 | -40.7284 | -30.6741 | -38.7884 | -30.9221 | -37.7295 | 416 | -40.2111 | -33.1836 | -31.8031 | -48.0702 | -31.9193 | -31.6704 | -40.5328 | -32.871 | -32.1033 | -47.4359 | -31.8978 | -32.2832 | -35.664 | -33.367 | -32.4987 | -51.2852 | -32.5015 | -34.6342 | -35.9857 | -33.0544 | -32.7989 | -50.6509 | -32.48 | -35.247
417 | -6.6194 | 0 | -6.3264 | 0 | -6.7991 | 0 | -6.4671 | 0 | -38.1829 | -76.0496 | -31.8473 | 57.1707 | -43.0629 | -19.1371 | -38.4064 | 104.2029 | -46.8218 | -94.3936 | -49.6133 | 126.204 | -43.0857 | 2.8756 | -30.357 | 147.3526 | -41.7158 | 46.371 | -42.5151 | -170.4313 | -51.1248 | 153.0788 | -43.9607 | 132.6502 | -13.3381 | 25.0474 | -18.9694 | 93.1768 | -19.3455 | 46.3597 | -16.0587 | 141.3899 | -17.1048 | 94.7555 | -22.0385 | 126.9857 | -22.0013 | -43.5215 | -16.7753 | -112.693 | -39.6973 | -42.291 | -39.7989 | -38.8028 | -56.0996 | -39.1387 | -38.5022 | -48.3108 | -39.6038 | -39.4866 | -58.0452 | -39.9593 | -42.5269 | 417 | -30.6809 | -34.9884 | -30.9216 | -40.9088 | -29.8398 | -39.4732 | -29.9255 | -39.3835 | 417 | -41.6914 | -32.9844 | -32.1834 | -49.7732 | -32.8123 | -31.7031 | -41.9844 | -32.8047 | -32.3357 | -49.3005 | -32.6716 | -32.0351 | -35.6716 | -33.1795 | -32.8672 | -51.7188 | -33.6329 | -35.7278 | -35.9646 | -32.9998 | -33.0195 | -51.2461 | -33.4922 | -36.0598
418 | -6.6047 | 0 | -6.377 | 0 | -6.7559 | 0 | -6.5955 | 0 | -39.1594 | -74.8359 | -29.3403 | 55.8583 | -44.2784 | -31.7598 | -38.0623 | 92.0484 | -47.4118 | -105.6027 | -46.7247 | 128.3695 | -43.9552 | 20.5957 | -28.4083 | 142.6289 | -42.5433 | 43.7464 | -41.5869 | 155.9767 | -53.0762 | 154.1092 | -42.9691 | 158.2509 | -14.2539 | 13.2667 | -17.7373 | 106.528 | -19.8237 | 38.8265 | -14.7442 | 134.558 | -18.6178 | 72.4794 | -19.3572 | 144.2606 | -22.79 | -59.7989 | -15.1439 | -127.8339 | -40.2986 | -42.3885 | -39.8193 | -39.9002 | -57.9041 | -39.2752 | -38.8223 | -49.4317 | -39.5305 | -40.3614 | -58.5762 | -40.7403 | -44.4563 | 418 | -28.7853 | -35.291 | -28.724 | -41.1495 | -28.1288 | -39.4104 | -28.0617 | -39.5437 | 418 | -42.827 | -32.9258 | -33.2955 | -51.5271 | -32.8982 | -32.0664 | -43.0547 | -32.7746 | -33.3047 | -51.1482 | -32.6797 | -32.2268 | -35.7838 | -33.2146 | -33.7567 | -52.1992 | -34.3633 | -37.7004 | -36.0115 | -33.0634 | -33.7659 | -51.8203 | -34.1448 | -37.8608
419 | -6.5712 | 0 | -6.4784 | 0 | -6.7637 | 0 | -6.6666 | 0 | -38.9992 | -70.0873 | -27.3763 | 45.6792 | -45.9603 | -36.2131 | -37.7564 | 82.1547 | -49.0326 | -111.1173 | -44.5486 | 122.428 | -41.3707 | 30.9491 | -26.8126 | 131.6476 | -42.0983 | 43.7808 | -41.9305 | 128.1196 | -54.8177 | 155.5536 | -39.8772 | 157.7098 | -15.8112 | 3.3674 | -15.2753 | 106.0227 | -20.6949 | 32.1394 | -13.6618 | 126.4397 | -20.9891 | 47.9199 | -16.253 | 139.9382 | -24.3092 | -69.5012 | -14.6261 | -145.7763 | -41.3414 | -42.8689 | -40.024 | -41.3336 | -56.357 | -38.8572 | -39.3729 | -51.0957 | -39.415 | -41.7558 | -60.1854 | -40.8301 | -48.4991 | 419 | -27.0313 | -35.1422 | -26.92 | -41.3709 | -26.5407 | -38.528 | -26.4777 | -37.7508 | 419 | -44.5245 | -32.8438 | -34.7624 | -49.8786 | -32.3788 | -32.6092 | -44.6173 | -32.6513 | -34.667 | -49.5933 | -32.1906 | -32.7063 | -36.2977 | -33.4528 | -35.1846 | -53.707 | -34.3517 | -41.7354 | -36.3905 | -33.2603 | -35.0892 | -53.4217 | -34.1635 | -41.8325
420 | -6.5335 | 0 | -6.5813 | 0 | -6.8608 | 0 | -6.6925 | 0 | -37.6875 | -69.844 | -26.3562 | 30.4908 | -47.1578 | -33.4538 | -37.8314 | 70.474 | -50.0932 | -109.9107 | -42.8775 | 114.0165 | -38.7245 | 25.6396 | -26.0212 | 117.8616 | -41.6297 | 38.4353 | -43.4122 | 104.1815 | -55.973 | 173.4235 | -38.2205 | 146.7155 | -17.7113 | -1.091 | -13.3089 | 95.7655 | -21.842 | 28.5077 | -13.0641 | 117.0961 | -25.3819 | 29.2199 | -13.972 | 128.3125 | -26.4007 | -74.6444 | -14.5885 | -165.2794 | -42.2997 | -43.8722 | -40.0449 | -42.6201 | -56.4091 | -38.4269 | -39.7883 | -53.5093 | -39.3069 | -43.2532 | -60.0266 | -40.646 | -53.7563 | 420 | -26.0143 | -34.6235 | -25.9681 | -40.9377 | -25.6823 | -37.3934 | -25.693 | -36.5388 | 420 | -46.9758 | -32.7734 | -36.0866 | -49.8278 | -31.8456 | -32.9275 | -46.928 | -32.4461 | -35.9276 | -49.5483 | -31.7344 | -33.0958 | -37.3387 | -33.5114 | -36.7197 | -53.4453 | -34.0647 | -46.8955 | -37.2909 | -33.1841 | -36.5607 | -53.1658 | -33.9535 | -47.0638
421 | -6.5028 | 0 | -6.6591 | 0 | -6.9638 | 0 | -6.6474 | 0 | -36.3659 | -76.7419 | -26.2725 | 14.9989 | -47.1883 | -26.9822 | -38.7505 | 60.8003 | -50.6798 | -109.0062 | -41.4119 | 104.7756 | -37.0132 | 11.3479 | -26.0663 | 102.1214 | -41.3398 | 31.0984 | -46.4717 | 81.7921 | -53.5472 | -177.3749 | -38.037 | 133.5826 | -19.7125 | 3.6944 | -12.1517 | 83.0131 | -23.4835 | 32.9116 | -12.7726 | 107.9999 | -32.6792 | 32.0151 | -12.6705 | 113.0864 | -27.1035 | -80.2149 | -15.3844 | 174.6196 | -42.6744 | -45.0455 | -39.9634 | -43.3658 | -58.0064 | -37.8228 | -39.9481 | -53.1786 | -39.288 | -44.2255 | -58.5966 | -40.1825 | -46.8747 | 421 | -25.8351 | -34.2855 | -25.9096 | -40.0042 | -25.6127 | -36.4614 | -25.7618 | -36.289 | 421 | -46.6758 | -32.7852 | -36.863 | -51.3473 | -31.1637 | -32.9843 | -46.5195 | -32.3242 | -36.7184 | -51.0426 | -31.1754 | -33.3007 | -38.5427 | -33.4606 | -37.7227 | -51.9375 | -33.5234 | -39.9109 | -38.3864 | -32.9996 | -37.5781 | -51.6328 | -33.5351 | -40.2273
422 | -6.489 | 0 | -6.7126 | 0 | -7.0604 | 0 | -6.6207 | 0 | -35.5322 | -87.5751 | -27.0183 | 1.8728 | -45.8619 | -23.6142 | -40.2009 | 59.3643 | -50.5932 | -105.4402 | -40.039 | 92.9806 | -36.1739 | -4.5042 | -26.9184 | 89.8534 | -41.8105 | 23.3009 | -54.2177 | 60.7908 | -51.6398 | 173.979 | -38.3031 | 126.5417 | -19.8685 | 13.8396 | -11.6972 | 67.1485 | -23.9319 | 40.0161 | -12.865 | 99.3934 | -32.8481 | 100.8969 | -12.1872 | 99.3513 | -26.4244 | -98.4459 | -17.1142 | 156.0362 | -42.0676 | -45.5092 | -39.9964 | -43.0637 | -58.1536 | -37.0209 | -39.8376 | -50.0291 | -39.3796 | -44.1266 | -57.7946 | -39.4588 | -42.8931 | 422 | -26.3968 | -34.1571 | -26.6125 | -38.7367 | -26.3072 | -35.9865 | -26.6061 | -36.5645 | 422 | -43.5401 | -32.8906 | -36.5747 | -51.441 | -30.3083 | -32.7772 | -43.3165 | -32.3192 | -36.443 | -51.0932 | -30.4002 | -33.2169 | -39.0202 | -33.5074 | -37.6376 | -51.082 | -32.7462 | -35.8327 | -38.7966 | -32.936 | -37.5059 | -50.7342 | -32.8381 | -36.2724
423 | -6.5009 | 0 | -6.6727 | 0 | -7.1063 | 0 | -6.5585 | 0 | -35.2656 | -99.6351 | -28.4298 | -5.376 | -44.185 | -29.9361 | -40.3332 | 67.9973 | -49.8075 | -106.6094 | -39.079 | 78.0212 | -36.03 | -20.6433 | -28.3648 | 82.9619 | -42.1052 | 22.054 | -56.3612 | -149.3838 | -51.2111 | 161.9546 | -38.0903 | 120.2707 | -18.807 | 17.3533 | -11.9271 | 51.8647 | -23.7197 | 45.2411 | -13.2661 | 92.7405 | -27.5614 | 99.4032 | -12.4792 | 85.039 | -25.3155 | -118.7846 | -20.6888 | 143.0947 | -40.9536 | -44.7543 | -40.2544 | -42.0903 | -55.6762 | -36.2309 | -39.5399 | -48.1609 | -39.6845 | -43.1337 | -57.954 | -38.6922 | -41.3022 | 423 | -27.5174 | -33.9736 | -27.8204 | -37.639 | -27.5246 | -35.8613 | -27.919 | -36.4902 | 423 | -41.66 | -33.1836 | -35.5894 | -49.0035 | -29.5582 | -32.4336 | -41.4882 | -32.5782 | -35.5318 | -48.5699 | -29.6724 | -32.9814 | -38.2534 | -33.7535 | -36.6328 | -51.2813 | -32.0195 | -34.1959 | -38.0816 | -33.1481 | -36.5752 | -50.8477 | -32.1337 | -34.7437
424 | -6.5246 | 0 | -6.6164 | 0 | -7.0756 | 0 | -6.5545 | 0 | -35.5015 | -111.9554 | -30.0902 | -5.2106 | -43.0006 | -42.3655 | -38.4686 | 70.4835 | -49.2685 | -113.5924 | -39.0621 | 62.0054 | -36.5156 | -37.3875 | -29.788 | 84.4585 | -41.838 | 18.9981 | -45.5861 | -172.2045 | -51.965 | 150.8233 | -37.9161 | 109.3677 | -17.8614 | 12.2538 | -13.1376 | 38.9722 | -23.9758 | 54.3181 | -13.7745 | 90.0766 | -24.4516 | 66.6529 | -13.4015 | 72.3239 | -26.1533 | -134.2098 | -27.7485 | 148.9208 | -39.9675 | -43.583 | -40.6452 | -41.3074 | -53.5378 | -35.9307 | -39.2726 | -48.0366 | -40.0246 | -42.1047 | -58.9797 | -38.228 | -41.248 | 424 | -28.823 | -33.6066 | -29.0454 | -37.3037 | -28.7335 | -35.8996 | -29.0685 | -36.3183 | 424 | -41.512 | -33.5 | -34.7828 | -46.9214 | -29.3143 | -32.197 | -41.4202 | -32.949 | -34.7529 | -46.4622 | -29.3762 | -32.7181 | -37.0584 | -34.1206 | -35.5801 | -52.3633 | -31.6116 | -34.1724 | -36.9666 | -33.5696 | -35.5502 | -51.9041 | -31.6735 | -34.6935
425 | -6.5504 | 0 | -6.5308 | 0 | -6.9644 | 0 | -6.6129 | 0 | -36.1961 | -123.5887 | -30.6586 | 4.8137 | -42.69 | -57.669 | -36.7245 | 62.5139 | -49.4976 | -122.6256 | -40.1317 | 49.0318 | -37.7651 | -54.0339 | -29.9639 | 92.5271 | -41.5036 | 13.6827 | -41.3742 | 162.4032 | -53.1988 | 145.1341 | -38.9956 | 93.9441 | -17.3003 | 2.9582 | -15.0961 | 30.9762 | -22.9514 | 61.583 | -13.9186 | 90.148 | -24.2803 | 43.7945 | -15.0665 | 65.9363 | -24.6713 | -161.9229 | -24.4311 | -148.2164 | -39.3116 | -42.546 | -40.9405 | -41.0929 | -52.3624 | -36.3351 | -39.105 | -48.98 | -40.3121 | -41.4527 | -60.8433 | -38.3043 | -42.4452 | 425 | -29.3809 | -33.3356 | -29.3222 | -37.9031 | -29.0435 | -36.109 | -29.1821 | -36.9563 | 425 | -42.4296 | -33.7617 | -34.5425 | -45.8316 | -29.8043 | -32.1406 | -42.4492 | -33.3477 | -34.48 | -45.398 | -29.7222 | -32.4921 | -35.9956 | -34.3901 | -34.9023 | -54.3125 | -31.7735 | -35.4808 | -36.0152 | -33.9761 | -34.8398 | -53.8789 | -31.6914 | -35.8323
426 | -6.5752 | 0 | -6.4834 | 0 | -6.8753 | 0 | -6.6898 | 0 | -37.4211 | -133.646 | -28.9478 | 12.3912 | -43.3001 | -72.5453 | -35.8522 | 49.8181 | -50.2061 | -128.375 | -41.4708 | 46.3213 | -40.0812 | -67.5963 | -28.3893 | 97.839 | -41.4593 | 5.9761 | -39.503 | 137.6534 | -54.5772 | 143.9774 | -42.3085 | 86.7527 | -18.0395 | -7.8229 | -17.4515 | 35.4198 | -21.2927 | 64.0936 | -13.3629 | 92.0528 | -23.872 | 15.3144 | -16.8985 | 71.6427 | -24.4743 | 175.6165 | -18.4123 | -152.6917 | -39.061 | -41.7029 | -41.0474 | -41.4712 | -51.9985 | -37.1522 | -39.1474 | -50.6878 | -40.4581 | -41.3701 | -63.456 | -38.8479 | -44.9771 | 426 | -28.2333 | -33.463 | -27.9444 | -38.9421 | -27.9086 | -36.7008 | -27.9051 | -38.7382 | 426 | -44.1126 | -33.8829 | -34.896 | -45.5151 | -30.6688 | -32.2721 | -44.2044 | -33.5828 | -34.7814 | -45.1232 | -30.4624 | -32.4576 | -35.1277 | -34.4722 | -34.7949 | -56.9726 | -32.3645 | -38.1018 | -35.2195 | -34.1721 | -34.6803 | -56.5807 | -32.1581 | -38.2873
427 | -6.5929 | 0 | -6.4865 | 0 | -6.8021 | 0 | -6.8226 | 0 | -39.2529 | -138.7226 | -26.6992 | 9.0115 | -44.6714 | -84.3016 | -35.6894 | 36.5997 | -50.7073 | -129.6388 | -41.639 | 51.4755 | -43.8846 | -71.0999 | -26.4138 | 93.1679 | -41.8436 | 1.718 | -39.073 | 114.9052 | -56.0084 | 148.9379 | -45.1692 | 109.5731 | -19.07 | -18.6051 | -17.5334 | 51.681 | -20.0349 | 58.5754 | -12.2639 | 89.4762 | -24.1988 | -13.9294 | -16.5505 | 82.5689 | -24.811 | 151.1272 | -15.3493 | -170.7373 | -39.2673 | -41.1453 | -41.0768 | -42.1188 | -52.2712 | -37.8641 | -39.3849 | -53.3763 | -40.5226 | -41.7482 | -64.4826 | -39.47 | -49.3022 | 427 | -26.3993 | -34.0112 | -26.0612 | -39.5401 | -26.2162 | -37.7681 | -26.13 | -40.0731 | 427 | -46.7834 | -33.9297 | -35.5259 | -45.7847 | -31.3776 | -32.5828 | -46.8898 | -33.7205 | -35.2962 | -45.4691 | -31.0415 | -32.5623 | -34.5524 | -34.4839 | -35.1553 | -57.9961 | -32.9835 | -42.5001 | -34.6588 | -34.2747 | -34.9256 | -57.6805 | -32.6474 | -42.4796
428 | -6.6023 | 0 | -6.521 | 0 | -6.7753 | 0 | -6.8866 | 0 | -40.9853 | -133.0258 | -25.1868 | -3.0093 | -46.636 | -89.3954 | -36.1483 | 25.7201 | -50.6774 | -131.7125 | -40.4044 | 53.3857 | -46.3931 | -44.5374 | -25.0023 | 81.5925 | -41.8288 | -1.0526 | -39.8274 | 94.9231 | -56.2008 | 157.6852 | -42.6315 | 128.8967 | -21.2007 | -28.3899 | -15.4284 | 56.9694 | -19.8163 | 51.2057 | -11.2189 | 82.6634 | -25.1752 | -41.5847 | -14.6641 | 87.1561 | -25.9431 | 133.2191 | -13.7033 | 168.5681 | -39.8674 | -40.9721 | -41.2559 | -42.7361 | -52.5869 | -38.1694 | -39.7952 | -53.9382 | -40.6198 | -42.2194 | -61.7902 | -39.8883 | -51.5246 | 428 | -25.0438 | -34.8015 | -24.7327 | -39.1592 | -24.8823 | -38.8807 | -24.7896 | -39.1155 | 428 | -47.3359 | -34.0175 | -36.1338 | -46.0659 | -31.6484 | -33.0199 | -47.4172 | -33.8445 | -35.8495 | -45.8116 | -31.2828 | -32.9086 | -34.3698 | -34.6536 | -35.6171 | -55.2692 | -33.3673 | -44.7493 | -34.4511 | -34.4806 | -35.3328 | -55.0149 | -33.0017 | -44.638
429 | -6.6275 | 0 | -6.5962 | 0 | -6.8072 | 0 | -6.942 | 0 | -40.4882 | -122.2128 | -24.5254 | -17.4957 | -47.9569 | -87.0075 | -36.9032 | 17.9524 | -50.4931 | -136.3599 | -38.9367 | 49.3959 | -43.0257 | -25.8542 | -24.3446 | 67.1991 | -41.5859 | -5.807 | -41.5636 | 79.6741 | -56.1483 | 169.1167 | -39.7212 | 126.8481 | -23.9074 | -35.0997 | -13.4746 | 49.5894 | -20.7593 | 48.3395 | -10.5619 | 73.993 | -26.3163 | -66.1122 | -12.8681 | 82.8386 | -29.4312 | 123.4446 | -12.9168 | 148.1815 | -40.8193 | -41.1284 | -41.3789 | -43.2818 | -52.1162 | -37.9349 | -40.3472 | -50.5277 | -40.8207 | -42.7218 | -59.2808 | -40.0318 | -46.9622 | 429 | -24.3976 | -35.1954 | -24.135 | -38.1623 | -24.206 | -39.1358 | -24.1411 | -37.4845 | 429 | -43.9002 | -34.1932 | -36.6543 | -45.52 | -31.3387 | -33.54 | -43.9315 | -34.0135 | -36.3398 | -45.309 | -30.9929 | -33.4052 | -34.5009 | -34.7514 | -36.0943 | -52.6846 | -33.4356 | -40.155 | -34.5322 | -34.5717 | -35.7798 | -52.4736 | -33.0898 | -40.0202
430 | -6.6178 | 0 | -6.6579 | 0 | -6.8449 | 0 | -6.9216 | 0 | -38.5618 | -122.5928 | -24.6533 | -31.8704 | -47.74 | -80.8817 | -37.6239 | 12.5365 | -50.1781 | -142.1845 | -37.5686 | 40.525 | -39.8753 | -34.5892 | -24.4396 | 52.2853 | -41.4971 | -13.4209 | -44.2819 | 72.0012 | -53.5592 | 179.9242 | -38.047 | 116.9665 | -27.1696 | -25.5805 | -12.229 | 36.3409 | -21.3618 | 50.0902 | -10.1471 | 62.5115 | -26.7991 | -90.3213 | -11.901 | 74.2948 | -32.0903 | 164.8347 | -12.8523 | 128.6637 | -41.2589 | -41.649 | -41.3633 | -43.7628 | -51.9855 | -37.4498 | -40.6032 | -47.423 | -41.0748 | -43.4509 | -57.6228 | -39.923 | -43.356 | 430 | -24.4598 | -34.9257 | -24.2332 | -36.958 | -24.2348 | -38.3975 | -24.2114 | -36.3445 | 430 | -40.8052 | -34.457 | -37.145 | -45.3276 | -30.7919 | -33.7583 | -40.7651 | -34.2299 | -36.8412 | -45.1406 | -30.5282 | -33.6816 | -35.0312 | -34.7455 | -36.8331 | -50.9649 | -33.2651 | -36.5111 | -34.9911 | -34.5184 | -36.5293 | -50.7779 | -33.0014 | -36.4344
431 | -6.6113 | 0 | -6.7234 | 0 | -6.8968 | 0 | -6.8353 | 0 | -37.2823 | -133.173 | -25.6583 | -43.2007 | -46.7845 | -82.3006 | -38.2583 | 10.87 | -50.0321 | -152.2525 | -36.5043 | 29.2754 | -38.4206 | -50.6182 | -25.4464 | 40.2629 | -41.9752 | -18.7975 | -46.9885 | 85.6097 | -50.5871 | 171.3137 | -37.0136 | 105.2764 | -29.9061 | -1.626 | -12.2867 | 21.258 | -21.0133 | 60.3873 | -10.5418 | 51.6607 | -26.6443 | -110.4832 | -11.5036 | 62.7829 | -24.9542 | -179.4702 | -13.8971 | 110.6602 | -40.6593 | -42.487 | -41.5123 | -43.8047 | -52.4405 | -36.9577 | -40.374 | -45.9242 | -41.3942 | -44.0485 | -56.4984 | -39.6043 | -41.6581 | 431 | -25.3381 | -34.6063 | -25.0997 | -35.9424 | -25.1418 | -37.6296 | -25.1254 | -35.6688 | 431 | -39.3129 | -34.7829 | -37.1934 | -45.7171 | -30.2343 | -33.4772 | -39.2008 | -34.4974 | -36.9694 | -45.5437 | -30.1224 | -33.5387 | -35.8757 | -34.901 | -37.4372 | -49.775 | -32.8809 | -34.7613 | -35.7636 | -34.6155 | -37.2132 | -49.6016 | -32.769 | -34.8228
432 | -6.6129 | 0 | -6.7306 | 0 | -6.9296 | 0 | -6.7214 | 0 | -36.7165 | -146.52 | -27.1932 | -49.1705 | -45.9875 | -89.5346 | -38.4165 | 10.2888 | -50.3493 | -164.9941 | -35.8411 | 16.7281 | -37.8509 | -68.6762 | -27.0259 | 33.5016 | -42.2622 | -21.6929 | -46.2068 | 107.0239 | -48.982 | 156.2543 | -36.4311 | 92.1149 | -28.5992 | 24.0542 | -13.1056 | 6.3417 | -19.4708 | 66.2265 | -11.3471 | 42.199 | -26.9915 | -118.4546 | -11.6801 | 53.423 | -21.5244 | 170.5801 | -15.5151 | 93.8741 | -39.801 | -43.2914 | -41.8035 | -43.5944 | -52.7315 | -36.604 | -39.9261 | -45.5522 | -41.8223 | -44.254 | -55.8816 | -39.2381 | -41.516 | 432 | -26.6824 | -34.3627 | -26.3583 | -35.3023 | -26.5623 | -36.9763 | -26.5076 | -35.2361 | 432 | -38.9393 | -35.2094 | -36.9815 | -46.0009 | -29.8734 | -32.9965 | -38.8216 | -34.8927 | -36.873 | -45.8019 | -29.8826 | -33.2047 | -36.6785 | -35.1906 | -37.6411 | -49.151 | -32.5075 | -34.5864 | -36.5608 | -34.8739 | -37.5326 | -48.952 | -32.5167 | -34.7946
433 | -6.6264 | 0 | -6.7201 | 0 | -6.9428 | 0 | -6.6147 | 0 | -36.7978 | -160.8641 | -28.8251 | -46.5885 | -45.4784 | -99.0994 | -37.96 | 9.6585 | -51.323 | -179.5084 | -35.6644 | 1.9065 | -38.036 | -87.6843 | -28.8158 | 35.008 | -42.2854 | -24.4712 | -42.7453 | 114.6778 | -48.4871 | 139.2903 | -36.3266 | 77.4205 | -25.2053 | 30.5361 | -14.7601 | -8.364 | -17.335 | 61.8706 | -12.5536 | 34.3762 | -26.2462 | -130.5595 | -12.2334 | 45.7906 | -19.0484 | 156.1927 | -18.294 | 80.3998 | -39.0203 | -43.7586 | -42.2351 | -43.4148 | -52.7976 | -36.5125 | -39.4311 | -45.9819 | -42.3256 | -44.1498 | -55.8022 | -38.9311 | -43.0551 | 433 | -28.1022 | -34.2439 | -27.5896 | -35.1277 | -28.1538 | -36.4879 | -27.9599 | -35.1394 | 433 | -39.3555 | -35.6992 | -36.7884 | -46.0775 | -29.7924 | -32.4883 | -39.2618 | -35.3828 | -36.8001 | -45.8548 | -29.8978 | -32.8164 | -37.1322 | -35.6087 | -37.5234 | -49.0821 | -32.211 | -36.1123 | -37.0385 | -35.2923 | -37.5351 | -48.8594 | -32.3164 | -36.4404
434 | -6.6378 | 0 | -6.658 | 0 | -6.9378 | 0 | -6.5241 | 0 | -37.7945 | -175.7634 | -28.6179 | -35.564 | -45.4478 | -109.6933 | -37.31 | 3.812 | -53.4415 | 167.9878 | -36.3191 | -10.8704 | -39.352 | -107.9571 | -28.8932 | 46.1877 | -41.9589 | -27.0935 | -39.9891 | 102.6322 | -48.9997 | 123.1637 | -37.4005 | 60.0908 | -24.1699 | 26.7249 | -18.1992 | -15.5422 | -16.1317 | 53.0889 | -14.2788 | 34.4856 | -25.7104 | -139.4981 | -12.9685 | 41.9633 | -18.0799 | 137.8267 | -22.4619 | 88.0113 | -38.6378 | -43.566 | -42.5434 | -43.4464 | -52.6066 | -36.8629 | -39.1111 | -46.8011 | -42.7159 | -44.0252 | -56.5642 | -38.8792 | -47.3663 | 434 | -28.0427 | -34.4797 | -27.4621 | -35.7439 | -28.3267 | -36.4029 | -28.0342 | -35.8798 | 434 | -40.1633 | -36.0781 | -36.8086 | -45.9486 | -30.2049 | -32.1733 | -40.1431 | -35.7781 | -36.9223 | -45.6688 | -30.3388 | -32.587 | -36.9282 | -35.9056 | -37.3874 | -49.9062 | -32.2212 | -40.4285 | -36.908 | -35.6056 | -37.5011 | -49.6264 | -32.3551 | -40.8422
435 | -6.659 | 0 | -6.6146 | 0 | -6.8972 | 0 | -6.5139 | 0 | -39.5963 | 174.3952 | -26.6684 | -32.4029 | -45.8082 | -120.8648 | -37.0229 | -3.7157 | -56.5635 | 163.5674 | -37.6178 | -19.9485 | -42.2258 | -126.4612 | -27.0252 | 51.021 | -41.7163 | -32.8307 | -38.6574 | 85.2002 | -50.4889 | 108.5566 | -40.2076 | 48.3629 | -23.6098 | 19.3987 | -22.9099 | 2.1639 | -15.76 | 41.3115 | -15.0952 | 42.9031 | -24.9151 | -150.2083 | -13.4734 | 42.82 | -17.7883 | 121.4175 | -22.1901 | 122.6551 | -38.7662 | -43.0254 | -42.4982 | -43.6959 | -52.3639 | -37.4082 | -39.0911 | -47.5456 | -42.7371 | -43.9935 | -57.9661 | -39.155 | -56.6497 | 435 | -26.4025 | -35.0804 | -25.9772 | -36.9566 | -26.7552 | -36.8812 | -26.5457 | -37.6543 | 435 | -40.8866 | -36.0781 | -37.0369 | -45.7493 | -30.7936 | -32.1939 | -40.931 | -35.8399 | -37.182 | -45.4667 | -30.8943 | -32.5772 | -36.3664 | -35.8392 | -37.3345 | -51.3515 | -32.5404 | -49.7525 | -36.4108 | -35.601 | -37.4796 | -51.0689 | -32.6411 | -50.1358
436 | -6.695 | 0 | -6.5812 | 0 | -6.885 | 0 | -6.5411 | 0 | -41.6895 | 172.8414 | -24.7572 | -39.8554 | -46.605 | -133.6497 | -37.1179 | -12.766 | -58.9448 | 172.113 | -38.9586 | -20.2516 | -47.7299 | -132.5141 | -25.0282 | 45.3006 | -41.6477 | -38.939 | -38.4554 | 66.4654 | -53.5632 | 99.5818 | -43.9332 | 56.4679 | -24.9347 | 10.6176 | -21.1432 | 39.224 | -16.5527 | 30.1956 | -14.2156 | 49.5676 | -24.8987 | -155.6191 | -13.2452 | 44.0122 | -18.5282 | 108.9006 | -18.2415 | 126.1665 | -39.3227 | -42.5445 | -42.0967 | -43.9907 | -52.2602 | -37.8804 | -39.3742 | -47.7131 | -42.5856 | -44.1281 | -59.2961 | -39.5998 | -52.9577 | 436 | -24.6423 | -35.7967 | -24.3588 | -38.2326 | -24.9119 | -37.8521 | -24.7821 | -39.4593 | 436 | -41.0181 | -35.8906 | -37.2957 | -45.679 | -31.2992 | -32.4892 | -41.1319 | -35.7006 | -37.4496 | -45.3752 | -31.3393 | -32.8331 | -35.8495 | -35.4017 | -37.4331 | -52.7149 | -33.0186 | -46.0727 | -35.9633 | -35.2117 | -37.587 | -52.4111 | -33.0587 | -46.4166
437 | -6.7327 | 0 | -6.6038 | 0 | -6.8968 | 0 | -6.6038 | 0 | -42.7418 | 179.9594 | -23.5398 | -52.0042 | -48.2038 | -144.3208 | -37.426 | -19.6841 | -58.9014 | 179.8536 | -39.133 | -15.1568 | -51.6118 | -85.0239 | -23.6909 | 32.8251 | -41.5774 | -45.4265 | -39.2202 | 49.664 | -57.9801 | 114.9855 | -43.8602 | 82.337 | -26.7857 | 10.6548 | -16.8601 | 40.4279 | -18.1423 | 24.4067 | -12.6633 | 47.9531 | -25.0438 | -156.2389 | -12.4991 | 42.4629 | -20.0383 | 102.5831 | -15.7541 | 113.8481 | -40.0172 | -42.4039 | -41.6422 | -44.1773 | -52.5172 | -38.0562 | -39.7132 | -47.0647 | -42.5178 | -44.4202 | -59.26 | -40.0139 | -46.4537 | 437 | -23.4733 | -36.2827 | -23.2522 | -38.5853 | -23.6139 | -38.9225 | -23.5306 | -39.4982 | 437 | -40.332 | -35.7851 | -37.4446 | -45.9134 | -31.4524 | -32.8164 | -40.4609 | -35.621 | -37.5735 | -45.6204 | -31.4524 | -33.1094 | -35.6712 | -34.9095 | -37.6875 | -52.6562 | -33.4101 | -39.5569 | -35.8001 | -34.7454 | -37.8164 | -52.3632 | -33.4101 | -39.8499
438 | -6.7566 | 0 | -6.6317 | 0 | -6.9252 | 0 | -6.643 | 0 | -42.2461 | -175.7099 | -23.1186 | -66.2525 | -50.4868 | -148.9995 | -37.8659 | -25.5389 | -57.9396 | 176.1756 | -37.9671 | -13.2465 | -45.8095 | -67.4814 | -23.1633 | 18.02 | -41.7877 | -53.4037 | -40.892 | 36.0471 | -56.2657 | 152.9905 | -40.8104 | 88.6212 | -30.2545 | 34.4956 | -14.8036 | 27.9362 | -20.1261 | 32.3231 | -11.6707 | 40.0035 | -23.6295 | -155.8266 | -11.7258 | 37.6352 | -20.7966 | 107.4854 | -14.4819 | 97.0275 | -40.6193 | -42.9128 | -41.3614 | -44.3146 | -53.0763 | -37.991 | -39.7801 | -46.1284 | -42.6941 | -44.7293 | -58.2762 | -40.2416 | -43.2125 | 438 | -23.058 | -36.4842 | -22.84 | -37.6894 | -23.0809 | -39.5845 | -23.0178 | -38.1931 | 438 | -39.3718 | -35.9375 | -37.558 | -46.4446 | -31.3593 | -32.8549 | -39.4967 | -35.7689 | -37.6716 | -46.1511 | -31.348 | -33.1371 | -36.1562 | -34.6048 | -37.9727 | -51.6445 | -33.6099 | -36.2873 | -36.2811 | -34.4362 | -38.0863 | -51.351 | -33.5986 | -36.5695
439 | -6.7822 | 0 | -6.6709 | 0 | -6.9689 | 0 | -6.6694 | 0 | -41.1938 | -178.8475 | -23.4844 | -80.5103 | -52.6645 | -142.7331 | -38.3102 | -30.0356 | -57.3861 | 158.6726 | -36.485 | -18.3761 | -42.3251 | -80.0828 | -23.4849 | 2.7164 | -42.4248 | -59.4254 | -43.5052 | 29.5436 | -51.8897 | 155.7147 | -38.3689 | 80.8642 | -26.7053 | 71.2906 | -13.879 | 12.9636 | -19.2009 | 50.2017 | -11.3372 | 29.9818 | -20.7718 | -159.6151 | -11.8062 | 29.458 | -19.2976 | 124.2298 | -14.6449 | 80.6574 | -40.8811 | -44.1792 | -41.3753 | -44.4007 | -53.7249 | -37.9409 | -39.7021 | -45.422 | -42.9893 | -45.0732 | -57.3896 | -40.2267 | -41.4357 | 439 | -23.4063 | -36.4713 | -23.138 | -36.3472 | -23.3742 | -39.6006 | -23.3044 | -36.7929 | 439 | -38.6398 | -36.2071 | -37.6185 | -47.054 | -31.27 | -32.7332 | -38.7511 | -36.0204 | -37.7313 | -46.756 | -31.2715 | -33.0327 | -37.397 | -34.5931 | -38.291 | -50.7187 | -33.5558 | -34.4668 | -37.5083 | -34.4064 | -38.4038 | -50.4207 | -33.5573 | -34.7663
440 | -6.8177 | 0 | -6.6782 | 0 | -7.0171 | 0 | -6.6396 | 0 | -40.4712 | 171.9029 | -24.6402 | -92.2695 | -53.1295 | -128.7081 | -38.5859 | -33.2458 | -57.5737 | 128.2818 | -35.3234 | -29.2855 | -40.6824 | -100.0513 | -24.6425 | -10.3006 | -42.9321 | -60.4936 | -46.3231 | 37.0881 | -49.0206 | 145.399 | -36.9746 | 66.4203 | -21.8307 | 73.4923 | -14.0748 | -2.4752 | -16.5094 | 54.0511 | -11.5618 | 19.9841 | -19.2128 | -166.7063 | -11.8327 | 22.0736 | -16.843 | 118.5923 | -15.5104 | 64.7229 | -40.8767 | -46.0633 | -41.5631 | -44.6189 | -54.5212 | -38.0008 | -39.5766 | -45.2203 | -43.2709 | -45.2602 | -56.9243 | -40.1929 | -40.7064 | 440 | -24.5222 | -36.3836 | -24.1258 | -35.2266 | -24.4734 | -39.1611 | -24.368 | -35.7817 | 440 | -38.4026 | -36.4532 | -37.8012 | -47.843 | -31.3226 | -32.5595 | -38.5421 | -36.2538 | -37.9793 | -47.5041 | -31.3612 | -32.937 | -39.2456 | -34.7454 | -38.4425 | -50.2461 | -33.5147 | -33.6893 | -39.3851 | -34.546 | -38.6206 | -49.9072 | -33.5533 | -34.0668
441 | -6.8039 | 0 | -6.6749 | 0 | -7.0617 | 0 | -6.6046 | 0 | -40.4026 | 160.3194 | -26.4326 | -97.2483 | -51.323 | -119.5714 | -38.652 | -36.3075 | -57.9514 | 84.6331 | -34.7411 | -42.1903 | -40.35 | -122.174 | -26.5677 | -17.4829 | -42.7997 | -61.613 | -46.3071 | 58.1698 | -47.4074 | 130.5551 | -36.5812 | 49.8076 | -18.6036 | 64.2338 | -15.6191 | -17.1687 | -14.5186 | 46.8929 | -12.6651 | 11.7945 | -17.9152 | 178.3807 | -12.4533 | 15.5603 | -14.8014 | 108.2407 | -17.669 | 52.7915 | -40.8031 | -48.1664 | -41.7836 | -45.1898 | -55.7641 | -38.3266 | -39.6476 | -45.3859 | -43.3507 | -45.3507 | -57.0382 | -40.1788 | -41.0437 | 441 | -26.2484 | -36.3989 | -25.6133 | -34.6265 | -26.2915 | -38.7346 | -26.1133 | -35.3704 | 441 | -38.582 | -36.5468 | -38.3859 | -49.0892 | -31.6517 | -32.5859 | -38.711 | -36.289 | -38.5852 | -48.7024 | -31.722 | -33.043 | -41.3625 | -34.9797 | -38.5468 | -50.3633 | -33.5039 | -33.982 | -41.4915 | -34.7219 | -38.7461 | -49.9765 | -33.5742 | -34.4391
442 | -6.8112 | 0 | -6.6145 | 0 | -7.1141 | 0 | -6.5524 | 0 | -40.8255 | 148.503 | -27.9712 | -91.8421 | -49.1068 | -124.0524 | -38.6491 | -39.9808 | -57.0196 | 35.5126 | -34.7671 | -55.6726 | -41.1375 | -144.6707 | -28.5351 | -13.5286 | -42.4977 | -66.708 | -43.6161 | 65.2618 | -46.776 | 115.3312 | -37.1617 | 31.4967 | -16.7729 | 50.8501 | -18.3252 | -26.4881 | -13.475 | 34.4027 | -13.9833 | 9.7014 | -16.6509 | 164.5645 | -13.3572 | 12.0117 | -13.975 | 95.3466 | -21.5551 | 54.3417 | -40.6372 | -49.3477 | -42.037 | -46.27 | -58.0318 | -38.9219 | -40.0325 | -45.4851 | -43.2292 | -45.5247 | -57.3801 | -40.3367 | -42.3108 | 442 | -27.7201 | -36.5529 | -26.8496 | -34.5852 | -28.1406 | -38.4938 | -27.8598 | -35.6943 | 442 | -38.6739 | -36.418 | -39.4588 | -51.4173 | -32.3074 | -32.9184 | -38.8706 | -36.1151 | -39.7176 | -50.9177 | -32.3695 | -33.4801 | -42.5365 | -35.2258 | -38.7135 | -50.7656 | -33.7222 | -35.1967 | -42.7332 | -34.9229 | -38.9723 | -50.266 | -33.7843 | -35.7584
443 | -6.809 | 0 | -6.5722 | 0 | -7.1352 | 0 | -6.5406 | 0 | -41.6615 | 137.3008 | -27.4893 | -81.6375 | -47.8014 | -137.358 | -38.5663 | -43.6426 | -54.8646 | -5.2954 | -35.4272 | -68.2268 | -42.9583 | -165.6776 | -28.5352 | -1.2339 | -42.4273 | -72.0107 | -41.2131 | 58.0899 | -46.8439 | 102.4065 | -38.7886 | 14.0701 | -15.9753 | 36.0549 | -21.8888 | -18.4985 | -13.2804 | 21.0226 | -14.6486 | 15.3453 | -16.1925 | 150.1194 | -14.1553 | 11.8767 | -13.7853 | 82.9555 | -23.5553 | 87.2649 | -40.5363 | -49.0525 | -42.3785 | -47.8645 | -61.9074 | -39.7165 | -40.623 | -44.9985 | -43.1684 | -45.9394 | -57.3379 | -40.686 | -43.7888 | 443 | -27.2875 | -36.7657 | -26.5593 | -35.1363 | -28.2133 | -38.3294 | -27.9346 | -36.777 | 443 | -38.1895 | -36.3594 | -41.0555 | -55.3352 | -33.1443 | -33.4878 | -38.4263 | -36.0332 | -41.3239 | -54.7722 | -33.1759 | -34.0824 | -42.2435 | -35.5695 | -39.1304 | -50.7657 | -34.1138 | -36.6536 | -42.4803 | -35.2433 | -39.3988 | -50.2027 | -34.1454 | -37.2482
444 | -6.8071 | 0 | -6.5315 | 0 | -7.1636 | 0 | -6.5716 | 0 | -42.9717 | 126.6325 | -25.4889 | -79.5803 | -47.6577 | -153.2773 | -38.2905 | -48.6404 | -52.7031 | -34.7471 | -36.6719 | -78.2994 | -45.7743 | 176.5637 | -26.5499 | 3.1529 | -42.301 | -77.7868 | -39.8162 | 43.4601 | -47.3021 | 91.9376 | -42.021 | -0.6893 | -16.1554 | 21.3288 | -22.1515 | 9.5714 | -13.9665 | 9.6274 | -14.0794 | 20.5378 | -16.4863 | 136.4133 | -14.2433 | 15.1033 | -14.5025 | 72.1091 | -19.2458 | 103.084 | -40.6128 | -48.3464 | -42.6813 | -50.0229 | -69.1088 | -40.4831 | -41.2659 | -43.8003 | -43.2016 | -46.5823 | -56.6252 | -41.2066 | -44.5435 | 444 | -25.3862 | -36.9027 | -24.9634 | -36.2397 | -26.3856 | -38.2567 | -26.2338 | -38.5302 | 444 | -36.9932 | -36.3945 | -43.2158 | -62.5773 | -33.9516 | -34.1023 | -37.2688 | -36.038 | -43.4513 | -61.9452 | -33.9115 | -34.6943 | -41.5393 | -35.8742 | -39.7752 | -50.0937 | -34.6751 | -37.3799 | -41.8149 | -35.5177 | -40.0107 | -49.4616 | -34.635 | -37.9719
445 | -6.8047 | 0 | -6.5352 | 0 | -7.1211 | 0 | -6.6406 | 0 | -44.7189 | 118.9847 | -23.7354 | -88.137 | -48.5153 | -167.9718 | -37.9971 | -56.1491 | -51.0321 | -58.8265 | -38.2764 | -82.7544 | -49.8599 | 165.5496 | -24.609 | -4.3458 | -42.2448 | -84.5204 | -39.45 | 27.3224 | -47.9381 | 83.5688 | -47.933 | 1.4516 | -17.3552 | 9.5542 | -19.2526 | 17.8627 | -15.6896 | 3.7226 | -12.526 | 19.1614 | -17.3354 | 126.6094 | -13.9259 | 16.3133 | -15.7444 | 66.5717 | -16.0157 | 96.1354 | -40.886 | -48.1555 | -42.9485 | -51.7649 | -81.1868 | -41.0071 | -41.8672 | -42.4219 | -43.3281 | -47.3125 | -55.711 | -41.7305 | -44.1376 | 445 | -23.6866 | -36.985 | -23.4309 | -37.6782 | -24.5221 | -38.5417 | -24.4493 | -40.3711 | 445 | -35.6172 | -36.5234 | -44.9602 | -74.6516 | -34.4719 | -34.7461 | -35.8867 | -36.207 | -45.1243 | -74.0657 | -34.3665 | -35.2266 | -41.3508 | -36.1438 | -40.5078 | -49.1758 | -35.1953 | -37.0165 | -41.6203 | -35.8274 | -40.6719 | -48.5899 | -35.0899 | -37.497
446 | -6.8222 | 0 | -6.5638 | 0 | -7.1172 | 0 | -6.7447 | 0 | -46.5694 | 116.9197 | -22.7658 | -101.3295 | -50.4047 | -179.4151 | -38.0319 | -65.5127 | -49.8731 | -79.7972 | -39.4535 | -78.7098 | -54.5139 | 174.4032 | -23.4527 | -17.5062 | -42.3445 | -91.7481 | -40.0726 | 10.7545 | -48.4759 | 79.6182 | -49.9992 | 58.0113 | -19.3908 | 7.8939 | -17.0324 | 10.3574 | -16.9965 | 9.9313 | -11.3225 | 10.5603 | -18.3031 | 126.7027 | -13.6067 | 13.3831 | -17.0768 | 71.1239 | -14.0977 | 82.4564 | -41.2231 | -48.7922 | -43.2003 | -51.7583 | -66.9653 | -41.2376 | -42.3802 | -41.3907 | -43.4433 | -47.8138 | -54.9192 | -42.2188 | -43.0242 | 446 | -22.7403 | -37.2203 | -22.549 | -38.7675 | -23.3936 | -39.3523 | -23.3497 | -40.836 | 446 | -34.5685 | -36.6211 | -44.9361 | -60.4015 | -34.6738 | -35.263 | -34.8269 | -36.3261 | -45.0136 | -59.8481 | -34.4929 | -35.6355 | -41.97 | -36.3781 | -40.9916 | -48.3554 | -35.655 | -35.907 | -42.2284 | -36.0831 | -41.0691 | -47.802 | -35.4741 | -36.2795
447 | -6.8685 | 0 | -6.6038 | 0 | -7.1448 | 0 | -6.8411 | 0 | -47.9049 | 118.5251 | -22.6327 | -116.4111 | -53.2722 | 179.1829 | -38.5992 | -74.6398 | -49.3645 | -99.6586 | -39.1645 | -71.5969 | -54.8467 | -161.106 | -23.1852 | -33.4468 | -42.563 | -99.7879 | -41.7228 | -3.5658 | -48.6292 | 77.4282 | -43.9936 | 72.1943 | -21.4349 | 25.3464 | -16.3644 | -3.0922 | -16.381 | 21.6454 | -10.7377 | -0.6282 | -17.9108 | 131.9076 | -13.2605 | 9.3108 | -16.5809 | 80.8871 | -13.2965 | 66.9674 | -41.5562 | -50.3042 | -43.5904 | -50.7515 | -61.689 | -41.2299 | -42.8538 | -41.0784 | -43.5599 | -47.807 | -54.4749 | -42.68 | -41.6766 | 447 | -22.6161 | -37.8031 | -22.431 | -38.6171 | -23.1324 | -40.7447 | -23.0894 | -39.6255 | 447 | -34.2099 | -36.6914 | -43.883 | -55.0852 | -34.6261 | -35.709 | -34.4746 | -36.4151 | -43.9104 | -54.5442 | -34.3888 | -36.0127 | -43.4357 | -36.7219 | -40.9385 | -47.8711 | -36.0762 | -34.5318 | -43.7004 | -36.4456 | -40.9659 | -47.3301 | -35.8389 | -34.8355
448 | -6.9332 | 0 | -6.6197 | 0 | -7.2424 | 0 | -6.8643 | 0 | -48.376 | 118.7313 | -23.2999 | -131.1856 | -55.2346 | -163.6645 | -39.617 | -83.0638 | -49.5973 | -117.4882 | -37.8103 | -71.2825 | -52.5405 | -162.0661 | -23.8024 | -48.6384 | -42.9237 | -106.8634 | -44.4029 | -9.6058 | -48.3168 | 73.6384 | -40.4607 | 61.123 | -19.2905 | 45.8138 | -16.8514 | -17.9565 | -14.429 | 22.7878 | -10.8488 | -13.9627 | -16.3625 | 134.0867 | -13.332 | 4.119 | -14.8255 | 83.5643 | -13.2735 | 51.227 | -41.8064 | -52.4486 | -44.0301 | -50.0408 | -58.4627 | -41.2337 | -43.19 | -41.3752 | -43.6324 | -47.4479 | -54.3346 | -43.1252 | -40.6529 | 448 | -23.2837 | -38.7055 | -23.052 | -37.4586 | -23.7438 | -42.4727 | -23.6728 | -38.0778 | 448 | -34.442 | -36.6992 | -43.1076 | -51.843 | -34.614 | -35.9476 | -34.7555 | -36.39 | -43.1765 | -51.2203 | -34.3694 | -36.3257 | -45.5154 | -37.0969 | -40.5147 | -47.7149 | -36.5055 | -33.4105 | -45.8289 | -36.7877 | -40.5836 | -47.0922 | -36.2609 | -33.7886
449 | -7.0282 | 0 | -6.5946 | 0 | -7.3485 | 0 | -6.8524 | 0 | -48.5693 | 115.5368 | -24.7602 | -140.6061 | -53.2038 | -148.0647 | -40.8672 | -86.7882 | -50.6983 | -131.4086 | -36.4635 | -77.0812 | -51.3516 | -178.8009 | -25.2673 | -59.8971 | -43.3728 | -113.1012 | -47.225 | -0.8268 | -47.9805 | 68.2281 | -38.646 | 45.4773 | -15.8071 | 45.0544 | -18.5607 | -29.9171 | -12.7748 | 14.0382 | -11.4944 | -26.7279 | -14.3221 | 129.5446 | -13.7852 | -0.354 | -13.0303 | 76.5444 | -14.0398 | 35.9304 | -42.043 | -54.1993 | -44.5626 | -50.1329 | -56.379 | -41.4337 | -43.5282 | -42.0478 | -43.7626 | -47.1728 | -54.4384 | -43.5282 | -40.1729 | 449 | -24.736 | -39.8165 | -24.3777 | -36.215 | -25.1901 | -43.7478 | -25.0459 | -37.0224 | 449 | -35.0196 | -36.7344 | -43.1047 | -49.7844 | -34.8391 | -36.1797 | -35.4532 | -36.4141 | -43.2805 | -49.0305 | -34.5813 | -36.6758 | -47.1711 | -37.5344 | -40.1446 | -47.8438 | -36.9336 | -32.8244 | -47.6047 | -37.2141 | -40.3204 | -47.0899 | -36.6758 | -33.3205
450 | -7.0925 | 0 | -6.5054 | 0 | -7.4284 | 0 | -6.7836 | 0 | -49.0624 | 107.2091 | -26.7447 | -144.5957 | -50.7513 | -152.3586 | -42.0393 | -87.2412 | -52.8378 | -140.5677 | -35.5899 | -88.3674 | -51.2159 | 155.8933 | -27.377 | -65.4339 | -43.6311 | -120.0652 | -46.7628 | 18.9044 | -47.8308 | 60.1164 | -37.9738 | 25.4635 | -13.1604 | 34.3882 | -21.8547 | -35.639 | -11.6913 | 1.8986 | -12.7306 | -36.0541 | -12.9131 | 118.7815 | -14.2973 | -4.2943 | -12.126 | 65.5474 | -15.5426 | 22.0386 | -42.1048 | -54.2114 | -44.9966 | -51.0072 | -55.1205 | -41.8286 | -43.7437 | -42.4674 | -44.0261 | -47.1109 | -54.2671 | -43.7839 | -40.1165 | 450 | -26.7022 | -40.9615 | -26.1001 | -35.3808 | -27.2578 | -43.4573 | -26.9683 | -36.5903 | 450 | -35.3749 | -36.9336 | -43.9147 | -48.6151 | -35.3232 | -36.3153 | -35.962 | -36.5977 | -44.2236 | -47.6921 | -35.045 | -36.9601 | -47.1189 | -37.9041 | -40.0184 | -47.7617 | -37.2785 | -32.6881 | -47.706 | -37.5682 | -40.3273 | -46.8387 | -37.0003 | -33.3329
451 | -7.1931 | 0 | -6.486 | 0 | -7.4956 | 0 | -6.6923 | 0 | -49.9149 | 100.2991 | -28.071 | -136.234 | -49.3265 | -163.501 | -42.5906 | -83.6723 | -55.4569 | -132.2997 | -35.2728 | -100.7288 | -51.8497 | 129.3265 | -29.2898 | -58.4614 | -43.9112 | -127.1541 | -44.2368 | 22.7817 | -47.9632 | 54.0207 | -38.3656 | 7.792 | -12.11 | 19.7721 | -26.6556 | -22.5426 | -11.7586 | -13.0902 | -14.5347 | -44.3044 | -11.9925 | 104.1085 | -14.6297 | -4.7135 | -11.5652 | 53.5009 | -18.0063 | 12.5154 | -42.2135 | -53.5472 | -45.5182 | -52.9244 | -54.9244 | -42.6488 | -43.8884 | -42.1948 | -44.4822 | -47.3454 | -53.5212 | -44.0542 | -40.604 | 451 | -28.0105 | -41.6674 | -27.1868 | -35.0654 | -29.1193 | -42.203 | -28.6613 | -36.9398 | 451 | -35.0017 | -37.2891 | -45.7313 | -48.4384 | -36.1628 | -36.3928 | -35.7088 | -36.9866 | -46.2321 | -47.4288 | -35.9565 | -37.1961 | -46.3541 | -38.3251 | -40.1523 | -47.0352 | -37.5682 | -33.1084 | -47.0612 | -38.0226 | -40.6531 | -46.0256 | -37.3619 | -33.9117
452 | -7.2322 | 0 | -6.4747 | 0 | -7.4843 | 0 | -6.6115 | 0 | -50.7369 | 91.7584 | -27.0653 | -125.4292 | -48.6119 | -175.1147 | -42.0728 | -81.0135 | -54.3705 | -109.4016 | -35.5009 | -113.9481 | -52.8052 | 100.3631 | -28.8354 | -44.8445 | -44.3584 | -136.6215 | -42.3309 | 13.9746 | -48.1444 | 47.2442 | -39.7199 | -11.1665 | -11.6908 | 5.3829 | -25.3909 | 20.3449 | -12.5406 | -26.7669 | -16.3507 | -43.814 | -11.8886 | 90.6334 | -14.8513 | -6.8361 | -12.0253 | 42.3554 | -21.2897 | 13.9296 | -42.2334 | -53.4501 | -45.9518 | -55.8779 | -55.4561 | -43.6962 | -43.9122 | -41.2656 | -44.9001 | -47.7012 | -52.0294 | -44.1484 | -41.4168 | 452 | -27.0165 | -41.2994 | -26.3652 | -35.2404 | -28.6984 | -41.0216 | -28.3189 | -37.9956 | 452 | -34.0334 | -37.6679 | -48.6457 | -48.9814 | -37.2215 | -36.4279 | -34.7909 | -37.4158 | -49.2664 | -47.9718 | -37.0847 | -37.3007 | -46.2179 | -38.7196 | -40.469 | -45.5547 | -37.6737 | -33.9325 | -46.9754 | -38.4675 | -41.0897 | -44.5451 | -37.5369 | -34.8053
453 | -7.2314 | 0 | -6.458 | 0 | -7.4111 | 0 | -6.5518 | 0 | -51.2976 | 79.3976 | -25.0422 | -127.3649 | -48.1039 | 173.8782 | -41.0669 | -84.2289 | -50.9246 | -108.3989 | -36.287 | -125.8986 | -53.6897 | 75.4732 | -26.694 | -42.0228 | -45.0027 | -146.0323 | -41.4711 | -0.0071 | -48.7426 | 41.8933 | -42.4361 | -28.6283 | -12.1908 | -8.011 | -21.4887 | 27.162 | -14.0874 | -35.6943 | -17.1827 | -39.2324 | -12.4945 | 78.5422 | -15.047 | -9.8492 | -13.0219 | 33.6365 | -24.1297 | 31.9237 | -42.2636 | -54.3066 | -46.5488 | -58.2011 | -56.1425 | -44.7753 | -43.9307 | -40.3096 | -45.2275 | -47.9775 | -50.4971 | -44.1924 | -42.1521 | 453 | -25.0106 | -40.2818 | -24.6281 | -35.8723 | -26.6218 | -40.5109 | -26.4412 | -39.9128 | 453 | -33.0782 | -37.9961 | -50.9697 | -49.6845 | -38.3173 | -36.5196 | -33.8516 | -37.8164 | -51.6493 | -48.7314 | -38.2235 | -37.3789 | -47.0752 | -39.3174 | -40.7461 | -44.0391 | -37.7344 | -34.741 | -47.8486 | -39.1377 | -41.4257 | -43.086 | -37.6406 | -35.6003
454 | -7.1968 | 0 | -6.474 | 0 | -7.3368 | 0 | -6.515 | 0 | -51.9819 | 58.5648 | -23.5126 | -137.7134 | -47.7327 | 159.7007 | -40.5671 | -95.061 | -48.6428 | -120.2999 | -37.5098 | -134.5196 | -53.6585 | 58.4895 | -24.8214 | -51.2881 | -45.8146 | -156.8598 | -41.5015 | -13.8351 | -49.3484 | 43.8115 | -47.8549 | -41.793 | -13.5909 | -17.3634 | -19.4796 | 19.549 | -16.1978 | -36.9277 | -16.9751 | -38.3099 | -13.7324 | 70.6705 | -15.4055 | -13.9978 | -14.4981 | 30.9977 | -23.3024 | 54.9394 | -42.4359 | -56.1151 | -47.3266 | -56.557 | -55.8304 | -45.3338 | -44.1224 | -39.8368 | -45.5444 | -48.392 | -49.6771 | -44.2938 | -42.433 | 454 | -23.49 | -39.6753 | -23.2614 | -36.8204 | -24.7814 | -40.62 | -24.708 | -42.6584 | 454 | -32.64 | -38.3476 | -49.3602 | -49.3564 | -38.8598 | -36.7856 | -33.3628 | -38.2076 | -50.042 | -48.4936 | -38.8188 | -37.6074 | -48.9183 | -40.1298 | -41.1952 | -43.2031 | -37.8198 | -35.0962 | -49.6411 | -39.9898 | -41.877 | -42.3403 | -37.7788 | -35.918
455 | -7.1402 | 0 | -6.4664 | 0 | -7.2719 | 0 | -6.5225 | 0 | -53.0093 | 29.2289 | -22.8029 | -151.8454 | -48.0702 | 143.1824 | -41.0565 | -107.8936 | -47.4275 | -135.2503 | -38.8143 | -138.4271 | -52.4697 | 45.0446 | -23.8164 | -65.2531 | -47.0112 | -168.6547 | -42.2696 | -27.4348 | -48.3958 | 45.5762 | -58.1308 | 15.1135 | -15.6286 | -16.4735 | -18.6335 | 10.7834 | -17.2326 | -27.5397 | -16.7584 | -44.685 | -15.0947 | 72.0198 | -16.0903 | -16.6296 | -15.4623 | 36.0447 | -21.1377 | 62.2772 | -42.6861 | -58.1089 | -48.0826 | -53.9634 | -55.0103 | -45.3315 | -44.2789 | -40.0102 | -45.6871 | -49.0914 | -49.4703 | -44.5962 | -41.9345 | 455 | -22.7859 | -39.9358 | -22.6326 | -37.8233 | -23.7897 | -41.0002 | -23.7532 | -44.4481 | 455 | -32.87 | -38.5469 | -46.8232 | -48.5439 | -38.8651 | -37.007 | -33.5438 | -38.4152 | -47.4409 | -47.7384 | -38.809 | -37.7564 | -50.9687 | -40.9424 | -41.9512 | -43.0039 | -38.1298 | -34.6626 | -51.6425 | -40.8107 | -42.5689 | -42.1984 | -38.0737 | -35.412
456 | -7.1721 | 0 | -6.4498 | 0 | -7.3018 | 0 | -6.5412 | 0 | -53.5952 | -7.1821 | -22.9323 | -167.5819 | -49.3239 | 125.0053 | -42.5966 | -120.0241 | -46.9513 | -151.3478 | -39.7395 | -138.1975 | -50.8584 | 32.135 | -23.7233 | -80.4441 | -48.7362 | 179.0828 | -43.7158 | -37.5068 | -46.903 | 39.2752 | -47.6211 | 59.618 | -16.0527 | -1.4733 | -18.6624 | 4.1725 | -15.8169 | -18.363 | -17.2962 | -53.2532 | -15.2144 | 81.6127 | -17.1566 | -20.222 | -14.9982 | 42.6123 | -19.7172 | 60.2722 | -42.8571 | -58.502 | -48.5364 | -52.5016 | -54.4781 | -45.3926 | -44.2623 | -40.9659 | -45.5667 | -49.8404 | -49.6061 | -45.1534 | -40.5618 | 456 | -22.9186 | -40.9939 | -22.7969 | -38.5998 | -23.7013 | -41.4805 | -23.6625 | -42.9179 | 456 | -33.7938 | -38.3946 | -45.3295 | -48.0283 | -38.9428 | -36.9605 | -34.5161 | -38.2649 | -45.9604 | -47.1763 | -38.8514 | -37.7211 | -51.3299 | -41.3643 | -42.6683 | -43.1563 | -38.7036 | -33.26 | -52.0522 | -41.2346 | -43.2992 | -42.3043 | -38.6122 | -34.0206
457 | -7.2906 | 0 | -6.4469 | 0 | -7.4 | 0 | -6.5641 | 0 | -52.9436 | -44.143 | -23.8909 | 179.204 | -51.4263 | 109.9587 | -45.1474 | -125.0061 | -47.2871 | -166.4949 | -39.7803 | -137.1055 | -49.1653 | 19.9966 | -24.5285 | -95.5878 | -50.7511 | 168.075 | -45.693 | -42.8607 | -46.1194 | 26.7732 | -42.8365 | 44.8526 | -13.9255 | 6.4014 | -19.3885 | 1.5478 | -14.1859 | -23.857 | -19.0531 | -63.7302 | -13.1737 | 84.5511 | -18.2216 | -14.6158 | -13.5098 | 42.3357 | -18.6901 | 56.7777 | -42.9245 | -56.7057 | -48.7604 | -52.1432 | -54.276 | -45.8698 | -44.0484 | -42.3336 | -45.4391 | -50.4352 | -49.9898 | -45.8531 | -38.6247 | 457 | -23.8779 | -42.6503 | -23.7488 | -38.8251 | -24.5033 | -41.9712 | -24.4322 | -40.7114 | 457 | -35.043 | -38.1485 | -44.8526 | -47.8291 | -39.4229 | -36.6484 | -35.8867 | -38.0391 | -45.5791 | -46.876 | -39.3057 | -37.4843 | -49.4151 | -41.4698 | -43.1446 | -43.5429 | -39.4062 | -31.2247 | -50.2588 | -41.3604 | -43.8711 | -42.5898 | -39.289 | -32.0606
458 | -7.5111 | 0 | -6.4227 | 0 | -7.5134 | 0 | -6.6002 | 0 | -51.4605 | -75.0534 | -25.691 | 168.8859 | -54.2291 | 96.4823 | -47.9749 | -116.7383 | -48.6817 | 179.1884 | -39.2145 | -139.9157 | -47.4844 | 6.9703 | -26.1988 | -106.9152 | -52.7376 | 156.0297 | -47.4063 | -37.8021 | -46.22 | 13.3634 | -40.62 | 25.3471 | -11.5376 | 1.6381 | -19.7835 | 4.6566 | -13.1784 | -36.0182 | -22.3513 | -69.0915 | -11.3602 | 79.599 | -18.8826 | -8.8027 | -12.6781 | 36.2511 | -18.564 | 52.6193 | -42.9355 | -54.8816 | -48.8637 | -52.6855 | -54.0995 | -46.6277 | -43.7665 | -43.3415 | -45.39 | -50.7977 | -50.6727 | -46.4235 | -37.2575 | 458 | -25.6735 | -44.3614 | -25.4777 | -38.6281 | -26.1571 | -42.2261 | -26.013 | -39.3592 | 458 | -35.8304 | -37.8789 | -45.1744 | -47.6768 | -40.205 | -36.2531 | -36.9188 | -37.8766 | -46.0853 | -46.5861 | -40.0275 | -37.1663 | -47.3705 | -41.3526 | -43.2866 | -44.25 | -40.0008 | -29.7441 | -48.4589 | -41.3503 | -44.1975 | -43.1593 | -39.8233 | -30.6573
459 | -7.7573 | 0 | -6.4187 | 0 | -7.6023 | 0 | -6.602 | 0 | -50.0468 | -99.7086 | -27.9615 | 167.5903 | -58.0135 | 80.6596 | -48.606 | -97.9683 | -51.2058 | 173.4086 | -38.7757 | -147.5604 | -46.1286 | -6.6555 | -28.5184 | -112.2893 | -54.7398 | 135.1333 | -47.5009 | -30.3608 | -47.0238 | 1.0185 | -39.8777 | 3.7208 | -9.9715 | -8.675 | -19.4497 | 8.5146 | -13.1126 | -50.0813 | -27.0977 | -46.036 | -10.1722 | 68.6179 | -18.5864 | -5.494 | -12.3659 | 25.9928 | -18.5053 | 49.2193 | -42.8845 | -53.7479 | -48.8951 | -53.4353 | -53.822 | -47.3885 | -43.4812 | -43.1843 | -45.5268 | -51.2312 | -51.6335 | -46.5242 | -36.6197 | 459 | -27.9305 | -45.051 | -27.5812 | -38.4857 | -28.4336 | -42.0755 | -28.161 | -38.9943 | 459 | -35.427 | -37.7695 | -45.678 | -47.4033 | -40.9698 | -35.8789 | -36.7656 | -37.9245 | -46.8333 | -46.2197 | -40.7865 | -36.8792 | -45.9906 | -41.1378 | -43.4739 | -45.2148 | -40.1055 | -29.0174 | -47.3292 | -41.2928 | -44.6292 | -44.0312 | -39.9222 | -30.0177
460 | -7.9436 | 0 | -6.4507 | 0 | -7.6011 | 0 | -6.591 | 0 | -49.1473 | -119.982 | -29.2323 | 179.0771 | -64.7793 | 45.4804 | -46.9791 | -87.8059 | -53.8807 | -176.7867 | -38.6115 | -155.6655 | -45.1483 | -19.4161 | -30.4259 | -103.1385 | -56.5149 | 100.877 | -46.4993 | -30.7142 | -48.3883 | -4.7285 | -40.2951 | -17.4779 | -9.3061 | -23.7054 | -18.8074 | 7.4124 | -13.867 | -65.547 | -25.3783 | -12.8591 | -9.3192 | 56.4243 | -17.6886 | -1.1964 | -12.3316 | 17.6454 | -18.2166 | 47.6975 | -42.7759 | -53.3209 | -48.8236 | -53.2642 | -53.6666 | -48.0084 | -43.185 | -42.312 | -45.7366 | -51.6499 | -52.4507 | -46.1948 | -36.6769 | 460 | -29.187 | -44.3997 | -28.6932 | -38.4741 | -30.2716 | -41.7105 | -29.9038 | -39.5799 | 460 | -34.3684 | -37.793 | -45.3206 | -47.2159 | -41.5577 | -35.5839 | -35.8613 | -38.1355 | -46.6732 | -46.0655 | -41.4174 | -36.594 | -45.3773 | -40.88 | -43.7063 | -46 | -39.7441 | -29.0758 | -46.8702 | -41.2225 | -45.0589 | -44.8496 | -39.6038 | -30.0859
461 | -7.9983 | 0 | -6.4592 | 0 | -7.5178 | 0 | -6.5881 | 0 | -49.1083 | -137.6745 | -28.0719 | -170.4525 | -63.9809 | -74.9865 | -45.3602 | -88.2916 | -53.5437 | -153.8749 | -38.509 | -165.6895 | -44.7107 | -32.2082 | -29.819 | -89.4546 | -56.2774 | 50.7041 | -45.7714 | -37.6596 | -49.5718 | -4.2434 | -41.8955 | -39.7533 | -9.2761 | -36.2861 | -18.0067 | 5.5248 | -15.6637 | -77.2967 | -21.1411 | -6.7043 | -9.0822 | 44.0594 | -17.083 | -2.6859 | -12.9645 | 10.4834 | -17.8636 | 45.9897 | -42.6322 | -53.1556 | -48.7259 | -52.1673 | -53.9916 | -48.6205 | -42.9084 | -41.3694 | -45.9475 | -52.0725 | -52.3655 | -46.0295 | -37.2029 | 461 | -28.0367 | -43.3907 | -27.6222 | -38.3629 | -29.6709 | -41.4683 | -29.4551 | -41.0777 | 461 | -33.3711 | -37.9492 | -44.169 | -47.5324 | -42.1613 | -35.3906 | -34.9102 | -38.4297 | -45.5792 | -46.4738 | -42.0324 | -36.3203 | -45.1573 | -40.7276 | -44.0742 | -45.9063 | -39.5703 | -29.6851 | -46.6964 | -41.2081 | -45.4844 | -44.8477 | -39.4414 | -30.6148
462 | -7.9182 | 0 | -6.4922 | 0 | -7.4357 | 0 | -6.6257 | 0 | -50.2646 | -150.3802 | -26.1278 | -172.8481 | -55.58 | -119.4734 | -44.2188 | -93.7012 | -50.3477 | -144.7146 | -38.5104 | -178.5063 | -44.8288 | -41.9867 | -27.6842 | -88.0364 | -53.9102 | 5.8671 | -45.7447 | -48.6418 | -49.6707 | -0.6685 | -44.9123 | -64.1323 | -9.919 | -49.9751 | -17.8567 | 0.6612 | -18.1016 | -83.4661 | -18.866 | -16.9379 | -9.8809 | 32.0189 | -17.1447 | -9.533 | -14.3205 | 4.1161 | -18.0443 | 40.9953 | -42.5012 | -52.7337 | -48.6459 | -51.298 | -55.0246 | -49.1243 | -42.7891 | -40.7599 | -46.0784 | -52.1875 | -50.8946 | -46.4865 | -37.8745 | 462 | -26.1062 | -42.48 | -25.8206 | -38.1555 | -27.591 | -41.5291 | -27.5366 | -43.268 | 462 | -32.8417 | -38.1602 | -43.3798 | -48.5324 | -42.6321 | -35.3534 | -34.2677 | -38.6427 | -44.6723 | -47.5889 | -42.4986 | -36.1634 | -44.8155 | -40.7277 | -44.2693 | -44.4024 | -39.9943 | -30.4388 | -46.2415 | -41.2102 | -45.5618 | -43.4589 | -39.8608 | -31.2488
463 | -7.74 | 0 | -6.4825 | 0 | -7.3687 | 0 | -6.6279 | 0 | -52.7423 | -147.6397 | -24.6975 | 176.9193 | -51.5394 | -150.6259 | -43.75 | -103.5628 | -47.174 | -152.6331 | -39.0279 | 165.1248 | -45.2979 | -46.9688 | -25.9739 | -98.2444 | -51.9135 | -27.7659 | -46.7625 | -61.8314 | -49.2676 | -1.3203 | -50.4662 | -101.6772 | -11.3757 | -58.8586 | -18.1604 | -2.8148 | -20.2252 | -71.9649 | -18.0643 | -30.6055 | -11.0142 | 23.4795 | -17.8155 | -12.0394 | -15.4804 | 5.4235 | -18.3272 | 36.8915 | -42.5969 | -51.6667 | -48.831 | -51.1828 | -56.6516 | -48.9518 | -42.9434 | -40.5366 | -46.2048 | -51.5293 | -48.9903 | -47.4077 | -38.2644 | 463 | -24.6817 | -41.7615 | -24.4884 | -38.2024 | -25.9125 | -42.0455 | -25.9226 | -45.6454 | 463 | -32.7966 | -38.4648 | -43.4428 | -50.1691 | -42.4693 | -35.5747 | -34.0541 | -38.8361 | -44.5549 | -49.2829 | -42.3239 | -36.3155 | -43.9267 | -41.091 | -43.7893 | -42.5078 | -40.9252 | -30.8957 | -45.1842 | -41.4623 | -44.9014 | -41.6216 | -40.7798 | -31.6365
464 | -7.5688 | 0 | -6.4928 | 0 | -7.4123 | 0 | -6.6638 | 0 | -52.0438 | -119.4871 | -24.084 | 162.9229 | -49.9168 | -178.5291 | -44.6408 | -115.5784 | -45.5769 | -168.6575 | -40.3503 | 147.4187 | -44.9807 | -44.7043 | -25.2206 | -113.162 | -51.1978 | -53.5332 | -48.951 | -70.1908 | -48.5745 | -1.5292 | -54.2285 | 154.7839 | -13.2505 | -60.2104 | -18.6993 | -3.0736 | -19.2088 | -59.0371 | -18.4175 | -44.3534 | -12.3833 | 21.9169 | -18.781 | -10.1617 | -15.5767 | 12.5566 | -18.9068 | 33.7716 | -43.0525 | -50.5463 | -49.2965 | -51.6736 | -57.0721 | -47.5502 | -43.3561 | -40.8303 | -46.3384 | -50.7389 | -48.11 | -48.4514 | -38.2024 | 464 | -24.0658 | -41.6568 | -23.9454 | -38.8561 | -25.1641 | -42.3373 | -25.1968 | -45.9771 | 464 | -33.2615 | -38.7696 | -44.1048 | -50.5793 | -41.0574 | -35.9438 | -34.3375 | -38.9261 | -45.0098 | -49.6598 | -40.8864 | -36.6923 | -42.9775 | -41.7277 | -43.1701 | -41.6172 | -41.9586 | -30.7901 | -44.0535 | -41.8842 | -44.0751 | -40.6977 | -41.7876 | -31.5386
465 | -7.5067 | 0 | -6.495 | 0 | -7.5184 | 0 | -6.6591 | 0 | -47.4787 | -114.4644 | -24.376 | 147.9575 | -49.8629 | 157.2638 | -47.4424 | -117.5347 | -45.3309 | 175.8557 | -42.5669 | 128.3257 | -43.4946 | -44.9912 | -25.4592 | -129.7736 | -51.7968 | -73.7589 | -51.7866 | -68.7263 | -47.1921 | -7.4532 | -46.7101 | 90.4542 | -13.993 | -50.6719 | -18.9975 | -1.8274 | -16.9534 | -63.6066 | -19.5788 | -54.5738 | -12.9476 | 28.9321 | -19.3368 | -2.4539 | -14.7333 | 14.4783 | -19.7109 | 33.1782 | -43.6094 | -49.9337 | -49.8087 | -52.2891 | -56.418 | -45.9884 | -43.5458 | -41.5341 | -46.2294 | -50.9677 | -48.1591 | -48.8974 | -37.449 | 465 | -24.3426 | -41.858 | -24.2896 | -40.2229 | -25.3815 | -41.5218 | -25.4167 | -43.2762 | 465 | -34.0274 | -38.7227 | -44.7824 | -49.923 | -39.4934 | -36.0274 | -35.0391 | -38.711 | -45.63 | -48.8996 | -39.3293 | -36.8867 | -42.427 | -42.302 | -43.461 | -41.6641 | -42.4024 | -29.9306 | -43.4387 | -42.2903 | -44.3086 | -40.6407 | -42.2383 | -30.7899
466 | -7.6373 | 0 | -6.5144 | 0 | -7.6631 | 0 | -6.6704 | 0 | -44.1875 | -125.2767 | -25.6022 | 133.4839 | -50.9117 | 134.9022 | -49.3505 | -93.9666 | -45.7848 | 162.5944 | -46.1947 | 111.0941 | -41.839 | -51.7997 | -26.6698 | -144.8166 | -53.8337 | -85.3896 | -53.5197 | -54.5623 | -46.3293 | -21.0853 | -42.8119 | 56.0074 | -12.5765 | -42.264 | -18.2479 | 4.8202 | -15.6212 | -76.1022 | -21.2321 | -54.2636 | -11.9139 | 34.1374 | -18.7439 | 5.1982 | -13.6976 | 10.6823 | -20.761 | 35.1283 | -44.039 | -50.0237 | -50.0447 | -52.9413 | -56.6483 | -44.7581 | -43.4245 | -42.0694 | -45.9967 | -52.4909 | -48.5534 | -47.3272 | -35.9725 | 466 | -25.5299 | -41.1841 | -25.5463 | -42.327 | -26.5316 | -40.3054 | -26.5567 | -40.9822 | 466 | -34.4321 | -38.3594 | -45.304 | -50.1339 | -38.2437 | -35.7614 | -35.555 | -38.3336 | -46.2709 | -48.9852 | -38.0877 | -36.7541 | -42.3864 | -42.4074 | -44.8536 | -42.039 | -40.8128 | -28.3094 | -43.5093 | -42.3816 | -45.8205 | -40.8903 | -40.6568 | -29.3021
467 | -7.8998 | 0 | -6.5518 | 0 | -7.7781 | 0 | -6.6983 | 0 | -42.2765 | -139.4574 | -27.6762 | 126.1944 | -53.1596 | 110.3564 | -46.2535 | -77.0461 | -46.7747 | 154.3189 | -51.3879 | 102.6927 | -40.6317 | -62.5198 | -28.8011 | -154.452 | -57.155 | -74.9397 | -53.1162 | -41.7816 | -46.8768 | -36.5269 | -41.7663 | 27.1338 | -10.7379 | -47.4814 | -17.2817 | 3.9251 | -15.298 | -92.5216 | -21.5675 | -48.3601 | -10.3554 | 29.8939 | -17.5255 | 4.758 | -13.3443 | 0.5235 | -21.7175 | 42.6948 | -44.2286 | -50.9295 | -49.8441 | -53.0717 | -57.9022 | -43.4411 | -43.1977 | -41.732 | -45.9029 | -55.2559 | -48.9054 | -44.3438 | -34.1595 | 467 | -27.5163 | -39.8333 | -27.5982 | -44.8003 | -28.5192 | -39.5129 | -28.5718 | -40.5043 | 467 | -33.8322 | -38.0031 | -45.1719 | -51.3504 | -36.8893 | -35.4196 | -35.1802 | -38.1248 | -46.3734 | -50.1241 | -36.7428 | -36.4994 | -43.0297 | -41.9443 | -47.3561 | -42.3536 | -37.792 | -26.3814 | -44.3777 | -42.066 | -48.5576 | -41.1273 | -37.6455 | -27.4612
468 | -8.1565 | 0 | -6.5888 | 0 | -7.8309 | 0 | -6.7145 | 0 | -41.1018 | -153.4518 | -29.9079 | 128.4245 | -57.065 | 72.3529 | -43.3217 | -77.138 | -47.7474 | 151.9079 | -58.7485 | 126.1616 | -39.8639 | -73.9411 | -31.4662 | -154.8396 | -57.004 | -41.575 | -51.9065 | -34.9647 | -48.4079 | -48.7952 | -42.4694 | 1.8862 | -9.524 | -57.7173 | -16.4057 | 0.8615 | -15.53 | -109.8354 | -20.714 | -46.4364 | -9.2458 | 21.5547 | -16.6234 | 0.4849 | -13.4443 | -9.5005 | -21.7931 | 54.6657 | -44.2306 | -52.4977 | -49.4604 | -52.0464 | -58.9679 | -42.2223 | -43.0222 | -41.0179 | -46.0523 | -58.923 | -49.2491 | -41.9395 | -32.9158 | 468 | -29.5822 | -38.5099 | -29.709 | -46.9685 | -30.869 | -39.0637 | -31.0983 | -41.3636 | 468 | -32.8614 | -37.8958 | -43.8899 | -52.3791 | -35.6335 | -35.1913 | -34.4291 | -38.2214 | -45.3319 | -51.137 | -35.5078 | -36.3077 | -44.3412 | -41.3039 | -50.7665 | -42.6603 | -35.3507 | -25.0849 | -45.9089 | -41.6295 | -52.2085 | -41.4182 | -35.225 | -26.2013
469 | -8.3513 | 0 | -6.6013 | 0 | -7.824 | 0 | -6.7419 | 0 | -40.4613 | -167.0196 | -31.0847 | 141.2053 | -62.1144 | -7.4527 | -41.2501 | -85.6175 | -47.9292 | 154.7737 | -61.2033 | -165.1375 | -39.4873 | -86.5849 | -33.7693 | -143.7469 | -51.9864 | -18.1451 | -50.5802 | -35.5693 | -50.8897 | -55.4903 | -45.0115 | -18.0277 | -8.8567 | -70.2019 | -15.8234 | -3.7103 | -16.3604 | -127.8858 | -19.4604 | -54.0582 | -8.567 | 10.4607 | -16.2129 | -6.0091 | -13.998 | -20.7235 | -20.9379 | 64.8425 | -44.0791 | -55.1104 | -49.083 | -50.208 | -59.2393 | -41.3916 | -42.9724 | -40.3357 | -46.406 | -60.9021 | -49.5818 | -40.3748 | -32.3944 | 469 | -30.6072 | -37.4227 | -30.6817 | -47.5741 | -32.6866 | -38.8797 | -33.3713 | -43.3709 | 469 | -31.9844 | -38.0547 | -41.8567 | -52.638 | -34.7903 | -35.1484 | -33.7344 | -38.582 | -43.4661 | -51.4153 | -34.6497 | -36.2305 | -46.7591 | -40.7317 | -52.5508 | -42.9805 | -33.7735 | -24.5704 | -48.5091 | -41.259 | -54.1602 | -41.7578 | -33.6329 | -25.6525
470 | -8.3465 | 0 | -6.6145 | 0 | -7.7441 | 0 | -6.7741 | 0 | -40.4275 | -179.3233 | -29.5341 | 150.0207 | -54.652 | -86.8888 | -40.015 | -96.2055 | -46.943 | 153.3134 | -53.6932 | -162.1399 | -39.6791 | -98.4236 | -32.5191 | -126.7561 | -47.0909 | -27.363 | -49.9717 | -44.2471 | -53.1764 | -43.8301 | -49.4741 | -23.9719 | -8.8746 | -83.3507 | -15.6774 | -8.8868 | -17.9813 | -143.2623 | -18.972 | -69.6003 | -8.4908 | -0.3622 | -16.7997 | -12.5191 | -15.3162 | -26.9905 | -18.9366 | 71.5865 | -43.7994 | -60.2258 | -48.8751 | -48.608 | -58.7134 | -41.2297 | -43.1262 | -40.0449 | -46.7176 | -56.2473 | -49.8997 | -39.9082 | -32.4667 | 470 | -29.1819 | -36.7675 | -29.1465 | -45.5417 | -31.6299 | -39.117 | -32.3565 | -44.4807 | 470 | -31.6984 | -38.3711 | -40.2615 | -52.0989 | -34.6152 | -35.3821 | -33.4304 | -38.9735 | -41.8339 | -50.9693 | -34.4556 | -36.3521 | -51.8793 | -40.5286 | -47.9008 | -43.2852 | -33.2937 | -24.7226 | -53.6113 | -41.131 | -49.4732 | -42.1556 | -33.1341 | -25.6926
471 | -8.1761 | 0 | -6.6275 | 0 | -7.6423 | 0 | -6.8114 | 0 | -40.8517 | 171.056 | -27.5522 | 146.1985 | -49.2572 | -123.3196 | -39.2946 | -108.2772 | -46.0873 | 146.6519 | -49.654 | 169.64 | -40.5379 | -108.3362 | -29.9599 | -127.3908 | -43.94 | -44.9917 | -50.6166 | -53.4626 | -52.171 | -25.9101 | -56.0066 | -4.4908 | -9.6124 | -96.098 | -15.652 | -10.869 | -20.5936 | -153.8313 | -19.5913 | -90.8476 | -9.0258 | -12.0613 | -18.3865 | -16.3731 | -17.3254 | -31.3553 | -17.2492 | 71.5655 | -43.578 | -75.3662 | -48.7165 | -47.8593 | -58.0077 | -41.5732 | -43.444 | -40.0485 | -46.6996 | -52.5455 | -50.0885 | -40.2751 | -32.646 | 471 | -27.3257 | -36.4889 | -27.2457 | -43.2501 | -29.4386 | -39.8677 | -29.912 | -43.1035 | 471 | -31.8724 | -38.5235 | -39.6832 | -51.3802 | -34.9457 | -35.8017 | -33.421 | -39.0573 | -41.0479 | -50.3654 | -34.7618 | -36.6326 | -67.1901 | -40.5404 | -44.3694 | -43.461 | -33.6476 | -25.0037 | -68.7387 | -41.0742 | -45.7341 | -42.4462 | -33.4637 | -25.8346
472 | -7.9229 | 0 | -6.6588 | 0 | -7.5619 | 0 | -6.8478 | 0 | -41.4817 | 166.4782 | -26.2762 | 134.7168 | -46.0348 | -152.1578 | -39.1852 | -120.9891 | -45.6007 | 139.2493 | -47.282 | 129.4061 | -42.112 | -113.0177 | -28.2383 | -139.903 | -42.1486 | -66.0117 | -52.7603 | -59.1381 | -49.3657 | -26.126 | -54.7863 | 78.1329 | -11.0155 | -105.5629 | -15.4823 | -11.682 | -22.9619 | -150.7564 | -21.5617 | -116.6163 | -10.072 | -20.4359 | -20.4348 | -12.1133 | -19.4969 | -25.9006 | -15.7584 | 68.2678 | -43.4335 | -63.3132 | -48.5804 | -47.9139 | -57.3944 | -42.2468 | -43.8853 | -40.4369 | -46.3057 | -50.2369 | -49.9439 | -41.1596 | -32.8115 | 472 | -26.1028 | -36.5902 | -26.0268 | -41.478 | -27.8975 | -41.0592 | -28.2134 | -41.1994 | 472 | -32.514 | -38.3828 | -39.991 | -50.7356 | -35.588 | -36.3234 | -33.7781 | -38.7438 | -41.0661 | -49.8325 | -35.399 | -37.0375 | -55.3903 | -40.6575 | -42.314 | -43.2851 | -34.5008 | -25.2496 | -56.6544 | -41.0185 | -43.3891 | -42.382 | -34.3118 | -25.9637
473 | -7.684 | 0 | -6.7309 | 0 | -7.5434 | 0 | -6.8715 | 0 | -41.7691 | 166.293 | -25.892 | 119.3644 | -44.3644 | -179.6166 | -39.9898 | -133.6794 | -45.0059 | 131.3699 | -45.4401 | 82.6566 | -43.4888 | -106.3805 | -27.6474 | -156.7418 | -41.6532 | -88.147 | -56.264 | -48.7665 | -47.657 | -39.5023 | -45.9747 | 88.6223 | -12.8547 | -107.8025 | -14.8671 | -12.481 | -22.4267 | -139.517 | -25.4298 | -153.3123 | -11.5201 | -23.9105 | -20.8992 | 11.1688 | -19.7306 | -9.7634 | -14.7223 | 62.1956 | -43.576 | -57.7322 | -48.7283 | -48.951 | -57.9353 | -42.8846 | -44.395 | -40.9965 | -45.7505 | -48.9341 | -49.1489 | -41.7036 | -32.9491 | 473 | -25.7214 | -37.0255 | -25.68 | -40.143 | -27.3706 | -41.918 | -27.5781 | -39.5563 | 473 | -33.3125 | -38.0665 | -41.267 | -51.2044 | -36.1537 | -36.8516 | -34.2656 | -38.2071 | -42.0795 | -50.3919 | -36.0131 | -37.5235 | -50.0482 | -41.0443 | -41.2501 | -42.418 | -34.9727 | -25.4057 | -51.0013 | -41.1849 | -42.0626 | -41.6055 | -34.8321 | -26.0776
474 | -7.6073 | 0 | -6.8388 | 0 | -7.5573 | 0 | -6.9028 | 0 | -41.0869 | 169.572 | -26.4761 | 103.5649 | -43.8841 | 155.3086 | -42.2293 | -138.5542 | -44.5926 | 118.4383 | -43.4363 | 38.1097 | -42.4361 | -93.5862 | -28.2233 | -174.987 | -42.5246 | -107.1429 | -56.1075 | -5.8963 | -47.8422 | -54.0147 | -40.7034 | 74.9746 | -13.9491 | -99.7909 | -14.0421 | -15.5795 | -20.9171 | -143.0086 | -29.6248 | 133.9943 | -12.4557 | -17.5393 | -18.2188 | 25.3863 | -17.8567 | -4.3054 | -13.9185 | 56.3666 | -43.8479 | -55.8203 | -49.4758 | -51.5979 | -61.7463 | -42.6289 | -44.6786 | -41.1745 | -45.2831 | -48.7958 | -47.9989 | -41.0261 | -33.209 | 474 | -26.2528 | -37.6335 | -26.2778 | -39.174 | -27.909 | -41.1945 | -27.978 | -38.03 | 474 | -33.5672 | -37.6758 | -43.9906 | -54.9075 | -35.7901 | -37.1213 | -34.3357 | -37.7258 | -44.6951 | -54.189 | -35.7261 | -37.7758 | -48.213 | -41.8685 | -41.1885 | -41.1601 | -34.1873 | -25.6517 | -48.9815 | -41.9185 | -41.893 | -40.4416 | -34.1233 | -26.3062
475 | -7.7076 | 0 | -6.9356 | 0 | -7.6533 | 0 | -6.9319 | 0 | -39.6862 | 166.7963 | -28.014 | 89.6267 | -44.5031 | 132.3823 | -43.4216 | -122.2311 | -45.6991 | 103.0767 | -41.426 | 0.4567 | -40.0351 | -94.013 | -29.9398 | 167.5091 | -44.4408 | -119.3876 | -50.8821 | 6.7592 | -48.1751 | -59.9458 | -37.6277 | 55.8801 | -12.8198 | -92.6999 | -13.2716 | -23.0695 | -19.2849 | -156.1087 | -25.91 | 58.4743 | -11.7178 | -12.2966 | -15.7167 | 21.3292 | -16.3797 | -12.0679 | -13.5473 | 49.5772 | -43.7572 | -55.4671 | -50.6699 | -57.1752 | -71.2181 | -41.5726 | -44.3887 | -40.3876 | -44.7974 | -50.5488 | -47.5879 | -39.497 | -33.6329 | 475 | -27.6378 | -37.4498 | -27.7025 | -38.7164 | -29.3963 | -39.1158 | -29.2271 | -36.5001 | 475 | -32.68 | -37.0898 | -49.4676 | -64.2825 | -34.637 | -36.7354 | -33.452 | -37.1441 | -50.2433 | -63.5648 | -34.6407 | -37.4568 | -47.7595 | -42.9623 | -42.8412 | -40.6523 | -32.5614 | -25.9796 | -48.5315 | -43.0166 | -43.6169 | -39.9346 | -32.5651 | -26.701
476 | -7.925 | 0 | -7.0051 | 0 | -7.7749 | 0 | -6.9871 | 0 | -38.4424 | 159.4269 | -30.4383 | 82.0873 | -46.2203 | 110.7102 | -41.1462 | -113.7343 | -48.0521 | 97.9401 | -39.8115 | -31.402 | -38.3016 | -102.9149 | -32.7976 | 156.6649 | -46.9756 | -122.8031 | -47.6392 | -0.5197 | -47.9978 | -69.5926 | -36.2407 | 35.659 | -11.2016 | -95.5323 | -12.8323 | -30.3006 | -18.2011 | -172.6889 | -21.9943 | 19.2898 | -10.3163 | -13.2433 | -13.9817 | 13.25 | -16.0505 | -24.4172 | -13.4357 | 43.8699 | -43.2135 | -55.413 | -51.1177 | -62.9127 | -74.2448 | -40.1981 | -43.5755 | -39.2632 | -44.5226 | -54.1692 | -47.8684 | -37.9038 | -33.6254 | 476 | -29.702 | -36.2782 | -29.6447 | -38.4172 | -31.5925 | -37.4248 | -31.0792 | -35.6294 | 476 | -31.3382 | -36.5976 | -54.9877 | -67.2397 | -33.193 | -35.8006 | -32.2581 | -36.7477 | -55.9256 | -66.4699 | -33.211 | -36.5884 | -47.488 | -43.1927 | -46.2442 | -40.8633 | -30.8987 | -25.8505 | -48.4079 | -43.3428 | -47.1821 | -40.0935 | -30.9167 | -26.6383
477 | -8.1301 | 0 | -7.0129 | 0 | -7.9308 | 0 | -7.0129 | 0 | -37.5678 | 150.1577 | -33.3398 | 84.8122 | -49.6443 | 89.2567 | -39.1053 | -118.9589 | -49.4578 | 108.3737 | -38.5632 | -58.1137 | -37.2024 | -113.4937 | -36.8512 | 154.2284 | -49.3371 | -108.2032 | -45.5471 | -8.7953 | -48.8846 | -84.1786 | -35.8148 | 20.0293 | -9.9204 | -105.6103 | -12.7423 | -39.4181 | -17.7445 | 169.3808 | -20.2271 | -9.7843 | -9.1533 | -21.5231 | -13.128 | 3.5097 | -16.7678 | -38.1703 | -13.5688 | 39.351 | -42.5885 | -55.3931 | -50.7252 | -55.065 | -86.0963 | -38.8384 | -42.7004 | -38.6691 | -44.634 | -58.8215 | -48.1262 | -36.5676 | -32.5 | 477 | -31.8749 | -35.0965 | -31.3933 | -37.9211 | -33.8873 | -36.3592 | -33.0409 | -35.4256 | 477 | -30.539 | -36.5039 | -46.9349 | -79.0834 | -31.8255 | -34.7696 | -31.6562 | -36.7032 | -48.0521 | -78.1655 | -31.8255 | -35.6875 | -47.263 | -42.5951 | -50.6914 | -41.1133 | -29.5547 | -24.5692 | -48.3802 | -42.7944 | -51.8086 | -40.1954 | -29.5547 | -25.4871
478 | -8.2384 | 0 | -6.9771 | 0 | -8.0231 | 0 | -7.0559 | 0 | -37.0605 | 140.1515 | -34.5685 | 101.7473 | -58.5995 | 66.5088 | -37.8179 | -127.6978 | -48.0583 | 117.9604 | -37.5621 | -81.2991 | -36.5769 | -126.008 | -40.5179 | 177.9526 | -47.792 | -84.5436 | -43.9483 | -18.5999 | -50.8128 | -95.196 | -35.5716 | 7.4823 | -9.3877 | -118.6788 | -13.0817 | -48.9962 | -17.7156 | 150.5388 | -20.0571 | -35.8103 | -8.4969 | -33.4184 | -12.9408 | -9.3281 | -18.0357 | -54.2453 | -13.7198 | 36.0737 | -42.0331 | -55.7588 | -50.2593 | -50.3261 | -68.9277 | -37.9073 | -41.9732 | -38.7379 | -44.965 | -58.481 | -48.1021 | -35.6949 | -31.0178 | 478 | -32.6169 | -34.2288 | -31.6125 | -37.1597 | -34.8768 | -35.7102 | -33.9118 | -35.1978 | 478 | -30.4995 | -36.7266 | -42.0877 | -61.9506 | -30.9302 | -33.9501 | -31.7608 | -36.9419 | -43.2702 | -60.9046 | -30.8514 | -34.9173 | -47.5204 | -42.0209 | -50.2426 | -41.125 | -28.7178 | -22.9947 | -48.7817 | -42.2362 | -51.4251 | -40.079 | -28.639 | -23.9619
479 | -8.1796 | 0 | -6.9149 | 0 | -8.0606 | 0 | -7.0555 | 0 | -36.9455 | 129.5862 | -32.7936 | 113.2112 | -57.5526 | -136.959 | -37.0349 | -137.995 | -45.9103 | 113.6222 | -37.0439 | -105.4871 | -36.4326 | -137.8792 | -38.0976 | -154.6868 | -44.0009 | -81.1767 | -42.8428 | -29.4842 | -53.7105 | -97.6867 | -35.4795 | -5.3181 | -9.3266 | -132.2987 | -13.741 | -56.6328 | -18.2433 | 134.5502 | -21.3117 | -61.3613 | -8.4808 | -45.1194 | -13.5924 | -18.2971 | -21.2068 | -64.2875 | -13.7959 | 34.7803 | -41.5608 | -56.5112 | -50.0326 | -47.6194 | -61.5022 | -37.4136 | -41.4735 | -39.3731 | -45.1874 | -54.575 | -47.9461 | -35.3692 | -30.1958 | 479 | -31.3704 | -33.7098 | -30.3573 | -36.4797 | -33.7454 | -35.473 | -33.0971 | -34.8515 | 479 | -31.1935 | -37.0078 | -39.4398 | -54.5873 | -30.4987 | -33.4129 | -32.4582 | -37.1268 | -40.5639 | -53.4416 | -30.3581 | -34.418 | -48.3316 | -41.853 | -46.3954 | -41.0312 | -28.4543 | -22.1352 | -49.5963 | -41.972 | -47.5195 | -39.8855 | -28.3137 | -23.1403
480 | -7.9997 | 0 | -6.8637 | 0 | -8.0242 | 0 | -7.0493 | 0 | -37.2456 | 120.4774 | -30.8068 | 108.5911 | -48.033 | -160.5799 | -36.6928 | -148.7636 | -44.59 | 100.7437 | -37.5196 | -131.5165 | -36.8717 | -149.8105 | -34.7739 | -157.5056 | -41.0926 | -91.0941 | -42.0576 | -39.7904 | -57.6697 | -81.2432 | -36.0864 | -19.0515 | -9.9616 | -145.407 | -14.6358 | -60.5629 | -19.371 | 122.1273 | -24.6305 | -86.739 | -9.139 | -55.7387 | -14.9757 | -22.2855 | -27.6695 | -57.8018 | -13.7341 | 35.2796 | -41.2284 | -57.4514 | -49.7589 | -46.0019 | -57.0644 | -37.1662 | -41.1528 | -40.4539 | -45.1012 | -52.02 | -47.9028 | -35.6023 | -29.7842 | 480 | -29.8517 | -33.5906 | -29.1306 | -36.43 | -32.1014 | -35.6947 | -31.9271 | -34.8717 | 480 | -32.4542 | -37.1015 | -38.0022 | -50.2007 | -30.3025 | -33.1286 | -33.5902 | -37.077 | -38.9526 | -49.0402 | -30.1169 | -34.1035 | -49.4517 | -41.7592 | -44.0203 | -41.0391 | -28.7386 | -21.76 | -50.5877 | -41.7347 | -44.9707 | -39.8786 | -28.553 | -22.7349
481 | -7.7558 | 0 | -6.8612 | 0 | -7.9667 | 0 | -7.037 | 0 | -37.7932 | 114.0123 | -29.795 | 96.4549 | -43.8335 | 174.1245 | -36.8478 | -160.2511 | -44.4589 | 87.1032 | -39.7108 | -159.47 | -37.9787 | -158.4769 | -33.0508 | -173.4788 | -39.3834 | -108.2622 | -41.53 | -49.8649 | -55.1402 | -41.6708 | -37.938 | -29.7819 | -11.3264 | -156.7026 | -15.5665 | -57.9411 | -20.5023 | 112.9223 | -37.0251 | -105.93 | -10.1481 | -66.0469 | -16.2815 | -19.8493 | -29.2609 | -9.7846 | -13.4634 | 34.426 | -41.1088 | -58.1478 | -49.2455 | -45.1283 | -54.4759 | -37.1673 | -41.0448 | -41.9159 | -44.5839 | -50.8144 | -48.3104 | -36.412 | -29.6524 | 481 | -29.0104 | -33.8862 | -28.6587 | -37.3501 | -31.1358 | -36.3332 | -31.388 | -35.5426 | 481 | -34.1601 | -36.8281 | -37.3725 | -47.6147 | -30.3061 | -33.0781 | -35.0547 | -36.6172 | -38.0913 | -46.5092 | -30.1303 | -34.0078 | -50.392 | -41.4897 | -43.0586 | -41.4492 | -29.5508 | -21.6857 | -51.2866 | -41.2788 | -43.7774 | -40.3437 | -29.375 | -22.6154
482 | -7.5431 | 0 | -6.9018 | 0 | -7.8705 | 0 | -7.0159 | 0 | -38.2013 | 111.8425 | -29.816 | 81.8166 | -41.6552 | 150.4574 | -37.5004 | -167.8537 | -45.1619 | 76.4112 | -45.7438 | 172.6705 | -39.38 | -160.1646 | -32.8549 | 164.7671 | -38.8388 | -128.3914 | -41.3836 | -60.8475 | -50.0941 | -45.8301 | -40.881 | -24.5975 | -13.2448 | -162.7017 | -15.16 | -56.2919 | -21.4562 | 114.014 | -29.6215 | 42.3207 | -11.7373 | -70.8509 | -16.3525 | -9.6444 | -23.3743 | 6.242 | -13.0024 | 33.3466 | -41.1845 | -58.5204 | -48.6305 | -44.911 | -53.6923 | -37.6493 | -40.9799 | -43.3822 | -43.922 | -50.4799 | -49.1635 | -37.8549 | -29.9427 | 482 | -28.9863 | -34.4419 | -29.0388 | -39.0163 | -31.1679 | -37.0367 | -31.7226 | -36.5349 | 482 | -35.8391 | -36.3789 | -37.3679 | -46.7905 | -30.7475 | -33.1094 | -36.4804 | -36.0515 | -37.8951 | -45.8218 | -30.6334 | -33.964 | -50.9773 | -41.0874 | -42.9368 | -42.2617 | -30.9531 | -22.0722 | -51.6186 | -40.76 | -43.464 | -41.293 | -30.839 | -22.9268
483 | -7.4404 | 0 | -7.0061 | 0 | -7.8001 | 0 | -7.0611 | 0 | -38.1096 | 111.9264 | -30.8692 | 67.031 | -40.8203 | 125.7397 | -38.5015 | -173.0916 | -45.8175 | 71.0055 | -56.9205 | -57.4936 | -39.9178 | -153.7922 | -34.2421 | 140.1438 | -39.5326 | -145.8783 | -41.9838 | -69.5899 | -47.7988 | -65.6661 | -40.451 | 0.5264 | -14.8703 | -158.1868 | -14.316 | -57.4352 | -20.9722 | 119.873 | -21.9971 | 19.61 | -13.1796 | -66.6729 | -14.874 | -2.3834 | -20.2758 | -5.8021 | -12.4402 | 31.1398 | -41.2888 | -59.7196 | -48.3638 | -45.7576 | -54.8201 | -38.5985 | -40.7913 | -43.2298 | -43.3623 | -51.0803 | -49.9006 | -39.4876 | -30.7199 | 483 | -29.7636 | -34.9222 | -30.1689 | -39.5461 | -32.293 | -37.403 | -32.7573 | -36.6135 | 483 | -35.7894 | -35.9219 | -38.3172 | -47.814 | -31.5924 | -32.9912 | -36.2237 | -35.5622 | -38.6965 | -47.02 | -31.5374 | -33.7302 | -52.2792 | -40.9234 | -43.6399 | -42.8945 | -32.4815 | -22.9198 | -52.7135 | -40.5637 | -44.0192 | -42.1005 | -32.4265 | -23.6588
484 | -7.464 | 0 | -7.1121 | 0 | -7.8259 | 0 | -7.1424 | 0 | -37.5541 | 110.7594 | -32.8977 | 54.7173 | -41.1352 | 102.5941 | -39.4463 | -172.3017 | -45.9382 | 63.3528 | -42.2452 | -72.5153 | -38.8894 | -147.8719 | -37.4131 | 114.6851 | -41.5036 | -159.73 | -42.8824 | -70.1435 | -47.5157 | -83.6104 | -36.9022 | 5.5466 | -14.5698 | -148.3969 | -13.2985 | -63.8955 | -19.098 | 116.871 | -18.5416 | -3.9806 | -12.8861 | -58.8793 | -13.0894 | -5.7866 | -19.5101 | -27.7886 | -11.9109 | 27.5896 | -41.2659 | -64.1086 | -48.7741 | -48.4378 | -57.0315 | -39.4602 | -40.4597 | -41.2907 | -42.9601 | -53.0183 | -49.1277 | -40.0095 | -32.1908 | 484 | -31.1591 | -35.021 | -31.6345 | -37.9019 | -34.1874 | -37.0256 | -33.5953 | -35.3384 | 484 | -33.8267 | -35.4961 | -40.9738 | -49.9194 | -32.3481 | -32.6338 | -34.1786 | -35.1342 | -41.2954 | -49.2056 | -32.3178 | -33.3173 | -56.6446 | -41.3101 | -45.5543 | -42.0156 | -32.8974 | -24.3649 | -56.9965 | -40.9482 | -45.8759 | -41.3018 | -32.8671 | -25.0484
485 | -7.5807 | 0 | -7.1783 | 0 | -7.9674 | 0 | -7.2486 | 0 | -36.6215 | 108.0247 | -36.1127 | 47.429 | -42.7688 | 78.95 | -39.2426 | -166.2726 | -47.4256 | 51.4997 | -37.898 | -95.8988 | -37.2339 | -150.3207 | -42.7221 | 83.028 | -44.4933 | -161.9899 | -41.9717 | -64.9886 | -47.456 | -97.6491 | -34.3807 | -4.3562 | -12.9309 | -148.3324 | -12.7658 | -73.696 | -17.3503 | 107.026 | -16.8166 | -27.0591 | -11.5217 | -59.0252 | -11.9194 | -14.2826 | -20.675 | -51.5887 | -11.5006 | 22.592 | -41.1564 | -89.2033 | -49.7736 | -53.5275 | -57.0627 | -38.9923 | -40.1275 | -39.4479 | -42.7838 | -57.6354 | -47.651 | -38.5025 | -33.8829 | 485 | -32.8793 | -34.4997 | -32.7896 | -36.3226 | -35.5591 | -35.6777 | -33.1728 | -33.7862 | 485 | -31.8672 | -35.2031 | -45.9468 | -49.8844 | -31.814 | -32.1601 | -32.2696 | -34.8164 | -46.2789 | -49.0953 | -31.7437 | -32.8789 | -81.6226 | -42.1929 | -50.0547 | -40.4727 | -31.3242 | -25.9155 | -82.025 | -41.8062 | -50.3868 | -39.6836 | -31.2539 | -26.6343
486 | -7.7303 | 0 | -7.1575 | 0 | -8.2122 | 0 | -7.3113 | 0 | -35.6148 | 101.1163 | -40.7746 | 56.7474 | -46.1518 | 59.0133 | -37.8501 | -164.0689 | -49.8987 | 61.6726 | -35.638 | -117.6533 | -35.8112 | -158.5289 | -48.6724 | 13.2814 | -46.6854 | -143.4743 | -40.4397 | -70.6123 | -47.5116 | -117.1989 | -32.9604 | -17.7784 | -11.3904 | -156.4368 | -12.5887 | -85.2105 | -16.332 | 94.0508 | -16.1305 | -50.1439 | -10.2102 | -66.7095 | -11.2769 | -25.6764 | -23.1897 | -79.9934 | -11.2841 | 16.7019 | -40.7801 | -64.1552 | -50.6772 | -52.4832 | -58.2645 | -37.7216 | -39.6848 | -38.5052 | -42.6756 | -73.4192 | -47.3137 | -36.5521 | -34.1314 | 486 | -34.1748 | -33.4797 | -32.8338 | -35.1213 | -35.2669 | -34.3126 | -32.1487 | -32.6363 | 486 | -30.7749 | -34.9453 | -44.7529 | -51.107 | -30.5641 | -31.4726 | -31.3477 | -34.4634 | -45.1719 | -50.0523 | -30.4103 | -32.3735 | -56.4249 | -42.9469 | -65.6889 | -40.1562 | -29.3946 | -25.9192 | -56.9977 | -42.465 | -66.1079 | -39.1015 | -29.2408 | -26.8201
487 | -7.7894 | 0 | -7.1025 | 0 | -8.4652 | 0 | -7.3529 | 0 | -35.0103 | 90.8896 | -41.6409 | 95.4092 | -53.8925 | 45.2477 | -36.4241 | -169.9573 | -47.6846 | 76.4639 | -34.2826 | -140.2855 | -34.9148 | -169.9934 | -44.242 | -59.5445 | -44.5735 | -122.0156 | -39.527 | -79.566 | -48.8497 | -141.2954 | -32.1252 | -31.2852 | -10.5486 | -169.2359 | -12.9362 | -97.4006 | -15.8119 | 79.842 | -16.4728 | -71.1775 | -9.7094 | -78.366 | -11.3917 | -36.7237 | -28.8387 | -120.8299 | -11.3033 | 10.5285 | -40.2681 | -58.7949 | -51.1112 | -48.4283 | -60.2564 | -36.5488 | -39.1689 | -38.3441 | -42.6761 | -58.0087 | -47.4931 | -34.8715 | -32.4859 | 487 | -34.1106 | -32.5155 | -31.7433 | -34.0434 | -34.0337 | -33.4966 | -31.1794 | -31.7983 | 487 | -30.5547 | -34.8867 | -40.6389 | -53.1539 | -29.4463 | -30.7037 | -31.2416 | -34.2109 | -41.0754 | -51.7912 | -29.1959 | -31.816 | -51.0055 | -43.3218 | -50.2193 | -40.3906 | -27.769 | -24.0207 | -51.6924 | -42.646 | -50.6558 | -39.0279 | -27.5186 | -25.133
488 | -7.782 | 0 | -7.011 | 0 | -8.6324 | 0 | -7.321 | 0 | -34.807 | 81.2159 | -38.04 | 107.268 | -55.9145 | 165.197 | -35.4248 | -179.8834 | -44.894 | 67.6405 | -33.7603 | -164.023 | -34.552 | 176.9977 | -40.2005 | -91.4417 | -40.9216 | -120.5245 | -38.9893 | -88.9274 | -51.824 | -170.4357 | -31.7436 | -45.0449 | -10.3399 | 176.7604 | -13.6731 | -108.5028 | -15.9594 | 65.0645 | -17.6416 | -90.5902 | -9.6304 | -91.4351 | -12.0649 | -46.8588 | -31.1012 | 149.8672 | -11.5942 | 4.4083 | -39.7314 | -55.7082 | -51.3422 | -45.997 | -56.8954 | -35.5871 | -38.7962 | -38.7926 | -42.6805 | -52.2259 | -47.5306 | -33.6402 | -30.8443 | 488 | -33.0963 | -31.8725 | -30.6324 | -33.4136 | -32.7822 | -33.1573 | -30.5011 | -31.2103 | 488 | -31.0106 | -34.8985 | -38.215 | -49.8844 | -28.5761 | -30.1638 | -31.7816 | -34.0481 | -38.676 | -48.263 | -28.2661 | -31.4752 | -47.9262 | -43.5602 | -44.4439 | -40.5196 | -26.6292 | -22.2119 | -48.6972 | -42.7098 | -44.9049 | -38.8982 | -26.3192 | -23.5233
489 | -7.6985 | 0 | -6.9446 | 0 | -8.6751 | 0 | -7.2259 | 0 | -35.003 | 71.6995 | -35.9502 | 101.4274 | -45.7679 | 153.8597 | -34.9614 | 168.6906 | -43.754 | 49.7503 | -34.387 | 168.906 | -34.8058 | 163.6351 | -38.5665 | -113.2702 | -38.1565 | -132.102 | -38.6656 | -97.775 | -57.8392 | 140.0351 | -32.0717 | -60.1317 | -10.7159 | 161.7483 | -15.2216 | -116.6328 | -16.5567 | 52.4266 | -20.0691 | -105.2078 | -10.1937 | -104.5193 | -13.4281 | -53.6306 | -26.3914 | 92.5153 | -12.2087 | -0.802 | -39.3798 | -53.0908 | -51.2119 | -44.6611 | -53.0673 | -34.9111 | -38.6478 | -39.6829 | -42.6907 | -49.2884 | -47.6282 | -32.9329 | -30.004 | 489 | -32.2432 | -31.6929 | -30.2812 | -33.6372 | -32.0574 | -33.2947 | -30.4784 | -31.1061 | 489 | -31.9844 | -34.9922 | -36.9626 | -46.1227 | -27.9665 | -29.9727 | -32.7383 | -34.0156 | -37.4352 | -44.3922 | -27.6852 | -31.4219 | -45.3923 | -43.5134 | -41.5899 | -40.6836 | -25.9883 | -21.3289 | -46.1462 | -42.5368 | -42.0625 | -38.9531 | -25.707 | -22.7781
490 | -7.5658 | 0 | -6.8994 | 0 | -8.5962 | 0 | -7.1376 | 0 | -35.4789 | 64.5067 | -35.357 | 92.4179 | -41.5077 | 130.2407 | -35.1136 | 155.6837 | -44.2237 | 30.7948 | -36.5219 | 138.9138 | -35.7763 | 152.5207 | -38.983 | -129.4762 | -36.4363 | -149.1987 | -38.5161 | -107.9348 | -58.6058 | 24.5692 | -33.3774 | -72.4996 | -11.7652 | 149.4469 | -16.6624 | -117.8558 | -17.998 | 41.417 | -23.0658 | -108.7651 | -11.6529 | -116.1271 | -15.0302 | -53.4382 | -22.1574 | 64.9378 | -13.0849 | -2.7135 | -39.3229 | -50.7072 | -50.3956 | -44.0886 | -50.905 | -34.7502 | -38.7315 | -41.1313 | -42.6869 | -47.5283 | -48.1143 | -32.7329 | -29.8663 | 490 | -31.9034 | -32.0129 | -30.8508 | -34.7987 | -32.0899 | -33.9086 | -31.3871 | -31.6239 | 490 | -33.5655 | -35.1211 | -36.5228 | -44.0056 | -27.8508 | -30.1353 | -34.2319 | -34.0907 | -36.951 | -42.3088 | -27.6126 | -31.5939 | -43.1414 | -42.8298 | -39.9625 | -41.2149 | -25.8335 | -21.2701 | -43.8078 | -41.7994 | -40.3907 | -39.5181 | -25.5953 | -22.7287
491 | -7.4225 | 0 | -6.8912 | 0 | -8.4198 | 0 | -7.056 | 0 | -36.0597 | 59.5626 | -35.781 | 85.3262 | -39.4654 | 104.9303 | -36.0244 | 144.1959 | -46.0626 | 16.6532 | -41.5735 | 100.437 | -37.3775 | 146.3094 | -41.3777 | -131.1624 | -35.7398 | -168.5107 | -38.7393 | -117.9522 | -52.2853 | -34.2 | -35.6279 | -75.9103 | -13.2912 | 139.6957 | -17.6887 | -113.7667 | -19.4643 | 38.8659 | -25.5036 | -86.9296 | -13.7494 | -122.8928 | -15.734 | -45.1086 | -20.8104 | 43.5772 | -13.9109 | -0.8343 | -39.5139 | -48.6715 | -49.3577 | -44.2444 | -50.178 | -35.3277 | -38.9927 | -42.9081 | -42.6959 | -46.6607 | -49.1763 | -33.0292 | -30.1937 | 491 | -32.0409 | -32.8208 | -32.3391 | -36.8305 | -32.8197 | -34.9146 | -33.1862 | -32.626 | 491 | -35.4856 | -35.2734 | -36.8219 | -43.2868 | -28.4365 | -30.5729 | -36.0169 | -34.2761 | -37.1884 | -41.7582 | -28.2717 | -31.9367 | -41.249 | -41.9352 | -39.2382 | -42.2851 | -26.138 | -21.7739 | -41.7803 | -40.9379 | -39.6047 | -40.7565 | -25.9732 | -23.1377
492 | -7.317 | 0 | -6.9419 | 0 | -8.2377 | 0 | -7.0567 | 0 | -36.3708 | 58.5885 | -36.7582 | 80.8993 | -38.8469 | 80.0713 | -37.6877 | 139.3197 | -48.6149 | 12.8489 | -50.669 | -11.3329 | -38.7489 | 150.0413 | -41.8853 | -105.3231 | -36.0842 | 171.9891 | -39.5911 | -126.0434 | -49.8151 | -73.3623 | -36.6708 | -62.1481 | -15.2349 | 138.8633 | -16.776 | -109.4084 | -20.8022 | 42.5305 | -22.4359 | -73.423 | -15.8676 | -118.0921 | -14.6451 | -37.9533 | -21.3162 | 23.994 | -14.1214 | 4.4986 | -39.7796 | -47.3175 | -48.8187 | -45.5999 | -50.8538 | -36.8526 | -39.231 | -43.14 | -42.7116 | -46.8287 | -50.7544 | -33.7181 | -30.8981 | 492 | -32.4261 | -33.8227 | -34.0913 | -38.1605 | -33.5209 | -35.9569 | -34.0905 | -33.2602 | 492 | -35.823 | -35.3946 | -38.2829 | -43.9119 | -29.9107 | -30.9933 | -36.1981 | -34.4739 | -38.5432 | -42.6161 | -29.7959 | -32.1743 | -40.0005 | -41.5017 | -39.5117 | -43.8125 | -26.7762 | -22.6604 | -40.3756 | -40.581 | -39.772 | -42.5167 | -26.6614 | -23.8414
493 | -7.2969 | 0 | -7.0156 | 0 | -8.1562 | 0 | -7.1328 | 0 | -36.1853 | 58.1428 | -38.4327 | 79.7326 | -39.4437 | 55.1258 | -38.9992 | 144.5369 | -50.332 | 22.0379 | -40.2221 | -99.6772 | -38.5817 | 158.2334 | -38.1321 | -92.84 | -37.5408 | 152.6844 | -40.7485 | -126.8462 | -49.9485 | -107.1776 | -34.395 | -52.4532 | -15.8928 | 146.2543 | -15.4905 | -114.3122 | -20.6763 | 49.2461 | -19.4197 | -82.5645 | -16.0883 | -106.1061 | -13.2367 | -39.3598 | -23.4315 | 20.7546 | -13.4834 | 8.8265 | -39.8767 | -47.0603 | -49.1892 | -49.2361 | -53.0095 | -38.9001 | -39.3398 | -40.7539 | -42.5039 | -48.3242 | -52.4141 | -34.4609 | -32.1446 | 493 | -33.0293 | -34.2495 | -34.3843 | -36.6165 | -33.2926 | -36.3281 | -32.2083 | -32.5981 | 493 | -33.457 | -35.207 | -41.9392 | -45.9939 | -31.8845 | -31.1836 | -33.7383 | -34.3477 | -42.1033 | -44.8533 | -31.7673 | -32.207 | -39.7634 | -41.8923 | -41.0273 | -45.3985 | -27.4453 | -23.9884 | -40.0447 | -41.033 | -41.1914 | -44.2579 | -27.3281 | -25.0118
494 | -7.3419 | 0 | -7.0762 | 0 | -8.2826 | 0 | -7.2454 | 0 | -35.542 | 56.4466 | -41.114 | 92.1625 | -41.2916 | 29.0769 | -38.5985 | 152.1206 | -49.9453 | 33.7208 | -35.3919 | -133.0874 | -37.138 | 160.1021 | -35.2962 | -97.0369 | -40.2032 | 140.0563 | -40.391 | -121.0713 | -52.3377 | -138.0347 | -31.8506 | -60.0193 | -14.7427 | 151.4167 | -14.372 | -124.8342 | -19.2981 | 50.3774 | -17.7893 | -99.801 | -14.415 | -102.9374 | -12.0758 | -46.7584 | -24.9823 | 38.7468 | -12.4711 | 8.6271 | -39.7615 | -48.0109 | -50.4335 | -60.8318 | -56.4451 | -39.0031 | -39.3653 | -38.4583 | -42.0763 | -51.4082 | -53.2637 | -34.5521 | -34.0481 | 494 | -33.6575 | -33.6923 | -32.9722 | -34.2789 | -32.3352 | -35.3683 | -29.8305 | -31.2245 | 494 | -31.1164 | -34.7344 | -53.4899 | -49.3689 | -31.9269 | -31.0827 | -31.3821 | -33.7937 | -53.5864 | -48.1625 | -31.7577 | -32.1199 | -40.669 | -43.0916 | -44.0663 | -46.1875 | -27.4759 | -25.7655 | -40.9347 | -42.1509 | -44.1628 | -44.9811 | -27.3067 | -26.8027
495 | -7.4167 | 0 | -7.1045 | 0 | -8.5865 | 0 | -7.3428 | 0 | -34.6084 | 51.3568 | -40.222 | 124.5272 | -45.1949 | 0.2003 | -37.4097 | 154.9169 | -48.343 | 40.0083 | -33.0072 | -162.7064 | -35.5376 | 155.3895 | -33.305 | -103.0734 | -44.3105 | 139.8041 | -38.6466 | -124.025 | -57.2793 | -170.682 | -30.2032 | -73.8385 | -12.931 | 145.2271 | -13.9319 | -139.5994 | -17.9847 | 43.7343 | -17.3571 | -120.1184 | -12.7613 | -110.7166 | -11.4432 | -58.0988 | -22.084 | 55.5713 | -11.6627 | 3.9782 | -39.4579 | -50.2523 | -52.6216 | -54.1688 | -58.2118 | -36.6117 | -39.3233 | -37.2076 | -41.5613 | -56.0342 | -52.6241 | -33.8169 | -36.18 | 495 | -33.2669 | -32.6578 | -31.0961 | -32.6341 | -31.0587 | -33.7898 | -28.0742 | -30.0295 | 495 | -29.7909 | -34.1446 | -46.7521 | -51.1073 | -29.5072 | -30.7368 | -30.1031 | -32.9748 | -46.826 | -49.6253 | -29.2689 | -31.9805 | -42.8356 | -45.2049 | -48.6175 | -45.5196 | -26.7124 | -27.5935 | -43.1478 | -44.0351 | -48.6914 | -44.0376 | -26.4741 | -28.8372
496 | -7.513 | 0 | -7.1132 | 0 | -8.9493 | 0 | -7.3895 | 0 | -33.8632 | 42.8709 | -36.0004 | 133.5093 | -54.4231 | -46.3706 | -35.7615 | 151.2286 | -45.7215 | 37.8594 | -32.0135 | 169.7021 | -34.376 | 144.4484 | -31.5679 | -109.4931 | -46.6699 | 172.1125 | -37.8218 | -137.2325 | -64.2044 | 116.2924 | -29.472 | -91.628 | -11.8527 | 134.3468 | -14.0825 | -155.0515 | -17.6585 | 31.2456 | -17.8588 | -140.8817 | -11.9659 | -124.4564 | -11.5813 | -69.9215 | -18.6013 | 54.1745 | -11.297 | -2.1795 | -38.9509 | -54.2128 | -56.339 | -47.7595 | -55.8571 | -34.201 | -39.121 | -36.8985 | -41.1419 | -65.91 | -52.0311 | -32.9375 | -35.9098 | 496 | -31.7677 | -31.5305 | -29.4099 | -31.8086 | -29.6514 | -32.7523 | -27.0085 | -29.3886 | 496 | -29.3855 | -33.6289 | -40.2465 | -48.7439 | -27.0878 | -30.1717 | -29.7853 | -32.1926 | -40.37 | -46.9078 | -26.8115 | -31.7315 | -46.6998 | -48.826 | -58.397 | -44.9179 | -25.8243 | -26.9605 | -47.0996 | -47.3897 | -58.5205 | -43.0818 | -25.548 | -28.5203
497 | -7.5827 | 0 | -7.0632 | 0 | -9.1921 | 0 | -7.3835 | 0 | -33.5615 | 33.4778 | -33.1444 | 127.9013 | -51.7508 | 161.9132 | -34.4503 | 141.3583 | -43.5232 | 23.2445 | -32.1012 | 142.3102 | -33.8379 | 131.5688 | -30.1328 | -118.7107 | -42.6168 | -168.3351 | -37.909 | -147.4626 | -56.9489 | 27.0587 | -29.6073 | -110.2245 | -11.2903 | 120.4739 | -14.909 | -171.4689 | -18.2601 | 18.4967 | -19.5818 | -161.7898 | -11.8889 | -140.5376 | -12.2869 | -81.1387 | -16.5764 | 42.4959 | -11.3498 | -8.0973 | -38.3345 | -63.6314 | -63.2876 | -45.5572 | -52.5064 | -32.5025 | -38.7546 | -37.3679 | -40.8679 | -60.3561 | -51.8757 | -32.0749 | -33.1095 | 497 | -30.3064 | -30.738 | -28.3561 | -31.7552 | -28.4228 | -32.3874 | -26.524 | -29.3877 | 497 | -29.7852 | -33.2852 | -37.9745 | -45.4432 | -25.4393 | -29.5625 | -30.3047 | -31.6758 | -38.1737 | -43.3143 | -25.119 | -31.3711 | -56.0487 | -55.7049 | -52.7734 | -44.8125 | -25.0117 | -23.9174 | -56.5682 | -54.0955 | -52.9726 | -42.6836 | -24.6914 | -25.726
498 | -7.6016 | 0 | -7.0359 | 0 | -9.2671 | 0 | -7.3276 | 0 | -33.6772 | 22.9106 | -31.4736 | 118.3908 | -44.0084 | 124.4996 | -33.7512 | 129.3812 | -42.6588 | 4.4197 | -33.3018 | 113.0228 | -33.9916 | 117.1043 | -29.2224 | -129.6635 | -39.0795 | -176.2951 | -38.082 | -155.9395 | -50.9829 | -8.8617 | -30.5881 | -128.2668 | -11.3163 | 105.9314 | -16.5409 | 174.4799 | -19.5717 | 8.984 | -23.4316 | 177.7639 | -12.5509 | -156.3386 | -13.3799 | -88.2207 | -15.5102 | 28.1692 | -11.7114 | -12.9964 | -37.9088 | -59.4721 | -62.4238 | -44.612 | -49.901 | -31.4721 | -38.5047 | -38.5953 | -40.793 | -53.4968 | -51.6843 | -31.5249 | -31.3133 | 498 | -29.2782 | -30.4353 | -27.955 | -32.5066 | -27.6483 | -32.4997 | -26.5268 | -29.9786 | 498 | -30.9937 | -33.1914 | -37.0104 | -42.8651 | -24.4362 | -29.2376 | -31.5594 | -31.5259 | -37.2844 | -40.6339 | -24.1445 | -31.1771 | -51.8705 | -54.8222 | -45.8952 | -44.6484 | -24.489 | -22.0462 | -52.4362 | -53.1567 | -46.1692 | -42.4172 | -24.1973 | -23.9857
499 | -7.5616 | 0 | -6.9827 | 0 | -9.1158 | 0 | -7.306 | 0 | -34.15 | 14.7037 | -30.4177 | 111.4884 | -40.6698 | 96.2079 | -33.7275 | 113.8753 | -42.8985 | -15.2312 | -35.9969 | 83.8464 | -34.9209 | 104.6464 | -28.7877 | -138.256 | -37.0983 | 168.2555 | -38.3997 | -165.6751 | -47.6303 | -35.8467 | -32.6005 | -145.3339 | -12.1671 | 92.6916 | -19.2055 | 168.6856 | -21.221 | 5.5796 | -32.2868 | -177.9161 | -13.9496 | -172.1468 | -14.8093 | -90.2493 | -15.1233 | 15.0385 | -12.0948 | -14.3846 | -37.7267 | -50.4888 | -55.1064 | -44.3478 | -48.2619 | -31.0396 | -38.3303 | -40.6314 | -40.9639 | -50.4905 | -51.5725 | -31.3853 | -30.5016 | 499 | -28.6056 | -30.6561 | -28.0037 | -34.1074 | -27.354 | -33.1529 | -26.955 | -31.1816 | 499 | -33.0698 | -33.4023 | -36.7862 | -41.2792 | -24.0569 | -29.2145 | -33.6487 | -31.8481 | -37.0418 | -39.1461 | -23.7336 | -31.0243 | -42.9272 | -47.5448 | -42.9289 | -44.5898 | -24.4026 | -21.3858 | -43.5061 | -45.9906 | -43.1845 | -42.4567 | -24.0793 | -23.1956
500 | -7.4854 | 0 | -6.983 | 0 | -8.8299 | 0 | -7.3197 | 0 | -34.8538 | 9.2336 | -29.5715 | 103.5295 | -39.2821 | 70.8203 | -34.7148 | 98.7724 | -44.1009 | -33.4403 | -41.5964 | 52.947 | -36.6327 | 97.0347 | -28.5545 | -145.5428 | -36.3905 | 150.3087 | -39.3441 | -175.3811 | -45.9357 | -62.8188 | -36.0287 | -155.7997 | -13.4722 | 81.4964 | -21.7551 | 177.5574 | -22.0536 | 8.2896 | -28.7555 | -78.8883 | -16.2172 | 175.5826 | -15.4566 | -86.1342 | -15.4864 | 4.1872 | -12.1004 | -13.2116 | -37.8325 | -46.0388 | -51.1592 | -44.9575 | -47.5904 | -31.2693 | -38.2955 | -43.4705 | -41.3604 | -49.3033 | -51.7369 | -31.7361 | -30.2741 | 500 | -28.1003 | -31.5265 | -28.2084 | -36.4568 | -27.3479 | -34.4499 | -27.543 | -32.9704 | 500 | -35.9851 | -33.875 | -37.4721 | -40.6074 | -24.2863 | -29.4656 | -36.4875 | -32.5305 | -37.6378 | -38.7605 | -23.9496 | -30.9758 | -38.5534 | -43.6738 | -41.8179 | -44.7539 | -24.7531 | -21.4442 | -39.0558 | -42.3293 | -41.9836 | -42.907 | -24.4164 | -22.9544
501 | -7.3802 | 0 | -7.0052 | 0 | -8.4896 | 0 | -7.3958 | 0 | -35.4135 | 7.2579 | -28.9767 | 93.9741 | -39.2191 | 46.787 | -36.976 | 89.7865 | -46.2325 | -48.4402 | -58.4071 | -39.0695 | -38.4838 | 99.3936 | -28.3528 | -151.7448 | -36.8382 | 131.196 | -41.0766 | -179.6123 | -45.7564 | -88.3468 | -41.0117 | -147.1044 | -15.2734 | 77.2356 | -20.7011 | -162.8746 | -21.9334 | 9.1832 | -21.018 | -86.46 | -19.4082 | 172.395 | -14.8056 | -83.2323 | -16.2305 | -6.4518 | -11.521 | -13.2759 | -38.1712 | -43.6517 | -48.9212 | -46.7806 | -47.8236 | -32.1868 | -38.2943 | -44.5638 | -41.7396 | -49.4779 | -52.1576 | -32.6263 | -30.4962 | 501 | -27.7653 | -32.9077 | -28.3334 | -38.3878 | -27.4229 | -36.0837 | -27.9089 | -35.0461 | 501 | -37.1836 | -34.3594 | -39.4004 | -40.8184 | -25.1816 | -29.8047 | -37.5586 | -33.25 | -39.3848 | -39.334 | -24.791 | -30.8985 | -36.2715 | -41.541 | -42.0977 | -45.1524 | -25.6211 | -22.0066 | -36.6465 | -40.4316 | -42.0821 | -43.668 | -25.2305 | -23.1004
502 | -7.3273 | 0 | -7.084 | 0 | -8.2431 | 0 | -7.5086 | 0 | -35.4668 | 7.1204 | -29.164 | 83.7301 | -40.3109 | 23.1577 | -39.5507 | 95.7521 | -49.2824 | -56.754 | -43.3424 | -158.0202 | -38.6582 | 111.0961 | -28.3621 | -156.8116 | -38.4477 | 115.5609 | -42.1059 | -172.8782 | -47.01 | -110.52 | -41.4089 | -104.3617 | -16.7289 | 81.9816 | -17.5549 | -161.7604 | -22.0671 | 4.2214 | -17.1121 | -105.1916 | -21.3635 | -174.2179 | -13.5973 | -87.411 | -17.4607 | -11.9571 | -10.6279 | -16.9213 | -38.4414 | -42.7373 | -47.9269 | -50.3633 | -48.8437 | -33.6709 | -38.2207 | -41.876 | -41.7804 | -50.4863 | -52.7558 | -34.126 | -31.2769 | 502 | -27.9878 | -33.9073 | -28.6344 | -38.2043 | -27.6013 | -36.6217 | -27.9806 | -36.2862 | 502 | -34.5487 | -34.4531 | -43.036 | -41.7597 | -26.5869 | -29.9776 | -34.792 | -33.5373 | -42.8547 | -40.6006 | -26.1623 | -30.7121 | -35.41 | -40.5996 | -43.159 | -45.6718 | -27.042 | -23.0338 | -35.6533 | -39.6838 | -42.9777 | -44.5127 | -26.6174 | -23.7683
503 | -7.2996 | 0 | -7.1568 | 0 | -8.2058 | 0 | -7.6056 | 0 | -34.9563 | 6.0897 | -30.281 | 78.5889 | -42.7893 | -0.5012 | -39.4174 | 110.9835 | -53.4528 | -51.8702 | -38.004 | 173.4147 | -36.8053 | 115.4796 | -28.5239 | -159.2133 | -41.3069 | 106.3642 | -41.4743 | -169.2035 | -49.7845 | -125.762 | -36.5829 | -92.8275 | -16.5898 | 90.1415 | -15.1062 | -171.9416 | -22.6338 | -6.0937 | -14.7335 | -124.2564 | -19.9448 | -161.5965 | -12.5787 | -96.8162 | -18.7287 | -11.1994 | -9.9099 | -24.6858 | -38.5611 | -43.0555 | -47.8758 | -56.4205 | -50.4127 | -35.3758 | -38.0123 | -39.2488 | -41.2723 | -51.4302 | -53.9107 | -35.8621 | -32.5559 | 503 | -28.8293 | -33.5823 | -29.172 | -36.6661 | -27.7276 | -35.3701 | -27.7067 | -35.169 | 503 | -31.9492 | -33.9727 | -49.1209 | -43.2559 | -28.219 | -29.8065 | -32.092 | -33.0665 | -48.8149 | -42.2069 | -27.7702 | -30.4067 | -35.7559 | -40.5762 | -44.1306 | -46.7539 | -28.7053 | -24.3501 | -35.8987 | -39.67 | -43.8246 | -45.7049 | -28.2565 | -24.9503
504 | -7.3473 | 0 | -7.2561 | 0 | -8.3858 | 0 | -7.6848 | 0 | -34.187 | 1.6766 | -31.0083 | 86.485 | -48.1705 | -25.526 | -37.7443 | 114.3778 | -54.6553 | -17.5598 | -35.3034 | 147.4398 | -34.8249 | 109.7979 | -28.0932 | -157.187 | -45.018 | 115.9076 | -40.9733 | -172.2995 | -53.5449 | -125.1784 | -33.2044 | -103.2716 | -14.8625 | 90.6585 | -13.5385 | 171.9056 | -23.4081 | -10.6326 | -13.5305 | -143.1638 | -17.7934 | -166.783 | -12.1762 | -110.4198 | -19.0326 | -4.0633 | -9.59 | -35.2405 | -38.3519 | -44.2316 | -48.7322 | -57.5784 | -52.0511 | -36.2199 | -37.7131 | -37.6631 | -40.5309 | -51.2131 | -55.9748 | -36.4522 | -34.2513 | 504 | -29.2468 | -32.5739 | -29.0108 | -35.0369 | -27.1852 | -33.8344 | -26.7586 | -32.8899 | 504 | -30.3158 | -33.1836 | -50.2311 | -44.795 | -28.9638 | -29.3273 | -30.407 | -32.1451 | -49.8936 | -43.6653 | -28.5351 | -30.0283 | -36.8843 | -41.3849 | -43.8658 | -48.7187 | -29.1961 | -25.8655 | -36.9755 | -40.3464 | -43.5283 | -47.589 | -28.7674 | -26.5665
505 | -7.4512 | 0 | -7.3262 | 0 | -8.6777 | 0 | -7.666 | 0 | -33.4784 | -5.4546 | -29.5626 | 94.0878 | -72.1925 | 137.662 | -36.5026 | 110.6184 | -50.7838 | -6.2173 | -34.126 | 117.706 | -33.4677 | 97.9262 | -26.7118 | -157.301 | -44.4929 | 147.6451 | -40.6807 | -173.9754 | -55.3684 | -102.4597 | -31.3065 | -120.8163 | -13.5203 | 83.3138 | -12.7227 | 155.5471 | -24.4073 | -22.3846 | -12.943 | -160.3959 | -16.4907 | 177.9271 | -12.3268 | -124.6342 | -17.8411 | -0.4076 | -9.8018 | -47.1311 | -37.879 | -46.3946 | -50.5431 | -52.1798 | -52.4728 | -35.4571 | -37.334 | -36.9082 | -39.9551 | -50.2442 | -58.416 | -35.0723 | -36.2345 | 505 | -28.0829 | -31.6685 | -27.6538 | -34.0326 | -25.8208 | -32.6888 | -25.2902 | -31.0866 | 505 | -29.457 | -32.5039 | -44.7286 | -45.1466 | -28.1309 | -28.6563 | -29.582 | -31.2774 | -44.5138 | -43.7951 | -27.7911 | -29.668 | -38.9434 | -43.0919 | -42.793 | -51.0898 | -27.7461 | -27.5568 | -39.0684 | -41.8654 | -42.5782 | -49.7383 | -27.4063 | -28.5685
506 | -7.5554 | 0 | -7.3349 | 0 | -8.962 | 0 | -7.5981 | 0 | -33.1342 | -15.1253 | -27.4115 | 91.3921 | -46.8746 | 105.7842 | -35.5139 | 104.7475 | -48.264 | -15.7107 | -34.6439 | 86.1432 | -32.8805 | 83.2822 | -25.2698 | -164.7518 | -40.3948 | 150.812 | -40.084 | -177.5416 | -53.5054 | -88.4958 | -30.7739 | -140.4921 | -12.8505 | 71.9554 | -12.7454 | 139.6587 | -26.7651 | -36.8478 | -12.9815 | -175.6052 | -16.252 | 158.3881 | -13.3168 | -139.3803 | -16.5141 | -4.7399 | -10.6784 | -58.7963 | -37.3609 | -50.785 | -52.9804 | -49.0065 | -50.8766 | -33.959 | -36.9916 | -36.8474 | -39.7527 | -49.7044 | -57.7637 | -33.2894 | -36.3826 | 506 | -26.3426 | -31.0691 | -26.1277 | -34.217 | -24.4633 | -32.0921 | -24.0819 | -30.3033 | 506 | -29.292 | -32.1973 | -41.4511 | -43.5417 | -26.6241 | -28.0296 | -29.5125 | -30.7907 | -41.4084 | -41.9146 | -26.3609 | -29.3935 | -43.2296 | -45.425 | -42.149 | -50.4288 | -25.9545 | -27.4206 | -43.4501 | -44.0184 | -42.1063 | -48.8017 | -25.6913 | -28.7845
507 | -7.6151 | 0 | -7.3084 | 0 | -9.1215 | 0 | -7.4742 | 0 | -33.1631 | -25.0961 | -25.828 | 83.5147 | -41.6812 | 80.0189 | -34.7069 | 95.5066 | -46.8981 | -29.4486 | -36.563 | 52.6638 | -32.9082 | 67.8525 | -24.2757 | -174.5945 | -37.5791 | 140.0366 | -39.5418 | 176.4996 | -51.2713 | -84.5862 | -31.2275 | -159.9973 | -12.7839 | 59.2298 | -13.1642 | 125.7466 | -30.4417 | -52.8735 | -13.2972 | 171.6304 | -16.5239 | 137.9541 | -14.7545 | -152.6922 | -15.6493 | -13.7256 | -12.303 | -69.4548 | -36.9497 | -57.4159 | -53.8731 | -47.4972 | -49.1009 | -32.7235 | -36.704 | -37.3101 | -39.8599 | -49.5389 | -56.1334 | -32.018 | -34.6738 | 507 | -24.9977 | -30.7497 | -24.9862 | -35.1008 | -23.5431 | -32.0033 | -23.3714 | -30.2878 | 507 | -29.695 | -32.2448 | -39.8821 | -41.7925 | -25.4151 | -27.5825 | -30.0017 | -30.7384 | -40.023 | -39.9794 | -25.2493 | -29.2298 | -49.8008 | -46.258 | -41.9238 | -48.825 | -24.7096 | -25.5523 | -50.1075 | -44.7516 | -42.0647 | -47.0119 | -24.5438 | -27.1996
508 | -7.6484 | 0 | -7.2537 | 0 | -9.0908 | 0 | -7.3497 | 0 | -33.5868 | -34.4743 | -24.7608 | 73.4971 | -39.2487 | 55.3859 | -34.3942 | 83.1974 | -46.3616 | -46.0782 | -40.6647 | 15.3984 | -33.6324 | 52.888 | -23.6907 | 176.0268 | -35.9049 | 122.226 | -39.2444 | 167.4795 | -49.0117 | -86.3826 | -32.7024 | -177.618 | -13.0808 | 47.1348 | -14.0303 | 114.5632 | -39.2911 | -58.5464 | -13.7964 | 161.7145 | -17.4182 | 114.9428 | -16.9909 | -162.9104 | -15.0788 | -25.1056 | -14.9514 | -77.2997 | -36.7051 | -53.3352 | -51.9943 | -47.17 | -47.791 | -31.8977 | -36.5233 | -38.3135 | -40.3476 | -49.8592 | -55.1014 | -31.2549 | -32.9242 | 508 | -24.0915 | -30.838 | -24.2128 | -36.4243 | -23.0408 | -32.4808 | -23.0709 | -30.9364 | 508 | -30.6651 | -32.6992 | -39.5216 | -40.5373 | -24.644 | -27.4325 | -31.0598 | -31.2568 | -39.8203 | -38.7002 | -24.548 | -29.1736 | -45.6868 | -44.3459 | -42.2108 | -47.8477 | -24.0012 | -23.8334 | -46.0815 | -42.9035 | -42.5095 | -46.0106 | -23.9052 | -25.5745
509 | -7.5965 | 0 | -7.2176 | 0 | -8.8426 | 0 | -7.2879 | 0 | -34.4325 | -41.4845 | -24.1296 | 62.3612 | -38.4907 | 33.078 | -35.1447 | 71.4805 | -47.0821 | -64.2205 | -48.7432 | -52.3844 | -35.347 | 41.4815 | -23.4125 | 166.4049 | -35.4706 | 104.2217 | -39.7774 | 157.6762 | -46.846 | -97.7408 | -35.6013 | 170.1501 | -14.1106 | 36.5093 | -15.2885 | 111.1282 | -50.7692 | -18.9802 | -14.4164 | 156.2231 | -19.1256 | 93.8681 | -19.4687 | -159.9063 | -15.4845 | -33.2814 | -18.3815 | -68.4134 | -36.7979 | -46.501 | -49.1456 | -48.2745 | -47.2628 | -31.7784 | -36.5692 | -39.8387 | -41.2606 | -51.6317 | -54.9363 | -31.1238 | -32.1446 | 509 | -23.5992 | -31.6379 | -23.7849 | -37.5823 | -22.8959 | -33.7895 | -23.0642 | -32.3675 | 509 | -32.2422 | -33.6641 | -40.678 | -40.0452 | -24.5608 | -27.7266 | -32.6211 | -32.418 | -40.9866 | -38.4202 | -24.4905 | -29.2813 | -38.9045 | -41.5491 | -44.0352 | -47.7187 | -23.9062 | -23.302 | -39.2834 | -40.303 | -44.3438 | -46.0937 | -23.8359 | -24.8567
510 | -7.5157 | 0 | -7.2127 | 0 | -8.5137 | 0 | -7.2723 | 0 | -35.3418 | -44.533 | -23.9059 | 51.0135 | -38.9007 | 12.6633 | -36.7901 | 66.0923 | -49.0615 | -79.3845 | -45.193 | -163.9304 | -37.661 | 38.9565 | -23.3265 | 157.1941 | -36.119 | 84.7358 | -41.3773 | 151.2351 | -45.7903 | -115.0213 | -39.7539 | 173.113 | -15.6175 | 28.8007 | -15.7109 | 116.1147 | -46.2593 | -179.0316 | -14.5359 | 155.5802 | -21.9619 | 72.4651 | -19.9535 | -142.5579 | -15.7818 | -40.5646 | -18.7726 | -40.9529 | -37.0743 | -43.4183 | -47.264 | -51.2579 | -47.3165 | -32.2582 | -36.7635 | -40.8848 | -42.4024 | -55.9549 | -55.1658 | -31.5098 | -31.8742 | 510 | -23.4781 | -32.8894 | -23.6573 | -37.6583 | -22.9545 | -35.6777 | -23.1627 | -34.2413 | 510 | -33.3691 | -34.8867 | -43.7422 | -40.1038 | -25.0455 | -28.2498 | -33.6721 | -33.8887 | -43.9856 | -38.8028 | -24.9859 | -29.4912 | -35.9026 | -39.7483 | -48.4392 | -47.9531 | -24.2971 | -23.3605 | -36.2056 | -38.7503 | -48.6826 | -46.6521 | -24.2375 | -24.6019
511 | -7.4287 | 0 | -7.2832 | 0 | -8.2736 | 0 | -7.3278 | 0 | -35.7491 | -42.7054 | -24.3592 | 38.6869 | -40.3402 | -4.2603 | -38.3121 | 70.8186 | -52.5706 | -88.8157 | -40.1007 | 157.2086 | -38.897 | 49.7766 | -23.6422 | 148.2239 | -37.8645 | 68.46 | -42.7714 | 156.4955 | -46.1405 | -132.9391 | -41.045 | -155.9395 | -17.2469 | 28.0293 | -14.6253 | 120.802 | -32.6228 | 166.4378 | -13.9437 | 154.3714 | -26.3307 | 58.1775 | -17.4676 | -138.5181 | -15.8647 | -47.8297 | -15.805 | -31.4419 | -37.4886 | -42.1703 | -46.2981 | -57.1839 | -47.9535 | -33.3383 | -36.9981 | -40.4571 | -43.2568 | -64.0918 | -55.6817 | -32.4142 | -32.3174 | 511 | -23.9538 | -33.7762 | -24.0779 | -37.084 | -23.3579 | -36.86 | -23.5121 | -35.7439 | 511 | -33.0284 | -35.8281 | -49.7552 | -40.6703 | -26.0551 | -28.7245 | -33.1739 | -34.9832 | -49.8561 | -39.6799 | -26.0105 | -29.6703 | -34.7416 | -38.8694 | -56.6631 | -48.3985 | -25.131 | -24.0438 | -34.8871 | -38.0245 | -56.764 | -47.4081 | -25.0864 | -24.9896
512 | -7.3819 | 0 | -7.4323 | 0 | -8.1978 | 0 | -7.4023 | 0 | -35.2925 | -41.4288 | -25.6234 | 31.4979 | -42.9678 | -16.2564 | -38.1144 | 79.9933 | -57.5466 | -71.3458 | -37.5366 | 132.4305 | -37.4684 | 59.0092 | -24.436 | 141.6774 | -40.6959 | 58.3429 | -42.5865 | 163.2172 | -47.8594 | -147.8 | -37.613 | -142.0191 | -18.2771 | 33.0854 | -12.7744 | 117.8801 | -26.1096 | 138.2894 | -12.9496 | 149.9692 | -32.8008 | 61.1863 | -15.2818 | -146.1722 | -16.3181 | -55.8679 | -13.4515 | -38.7125 | -37.8564 | -42.0712 | -46.0873 | -56.5635 | -48.9658 | -34.8368 | -37.2878 | -39.0767 | -43.3155 | -56.7253 | -56.7331 | -33.6548 | -33.265 | 512 | -25.1067 | -33.4509 | -25.1284 | -36.4095 | -24.1284 | -36.0098 | -24.1689 | -35.6094 | 512 | -31.6948 | -35.9336 | -49.1816 | -41.5335 | -27.4045 | -29.09 | -31.6444 | -35.1177 | -49.1612 | -40.768 | -27.4345 | -29.8855 | -34.6893 | -38.7054 | -49.3434 | -49.3008 | -26.2225 | -25.0672 | -34.6389 | -37.8895 | -49.323 | -48.5353 | -26.2525 | -25.8627
513 | -7.3706 | 0 | -7.6088 | 0 | -8.2885 | 0 | -7.4643 | 0 | -34.352 | -45.0599 | -26.9056 | 34.9068 | -46.7898 | -11.0916 | -36.7631 | 83.38 | -55.6077 | -29.4235 | -36.126 | 108.1993 | -35.4247 | 54.748 | -25.0281 | 142.6965 | -44.4382 | 64.0052 | -42.1655 | 165.8358 | -50.6194 | -149.047 | -34.6365 | -147.9001 | -18.2276 | 36.8375 | -11.2596 | 108.5976 | -23.5992 | 119.3375 | -11.9913 | 142.5556 | -32.8261 | 107.4071 | -13.6613 | -161.3293 | -16.8821 | -62.3172 | -12.2472 | -52.2835 | -37.951 | -42.619 | -46.6268 | -51.0994 | -50.0135 | -36.3065 | -37.4877 | -37.5581 | -42.6948 | -50.8901 | -58.8979 | -34.7456 | -34.4024 | 513 | -26.149 | -32.3614 | -26.0313 | -35.7236 | -24.6034 | -34.4834 | -24.5021 | -34.1061 | 513 | -30.1875 | -35.3242 | -43.7288 | -42.4047 | -28.6977 | -29.1992 | -29.9493 | -34.4063 | -43.6351 | -41.725 | -28.8422 | -30.0234 | -35.2484 | -39.2562 | -43.5195 | -51.2891 | -27.1368 | -26.1139 | -35.0102 | -38.3383 | -43.4258 | -50.6094 | -27.2813 | -26.9381
514 | -7.4149 | 0 | -7.762 | 0 | -8.5348 | 0 | -7.5055 | 0 | -33.5054 | -51.7805 | -26.4413 | 43.7713 | -46.8485 | 20.3919 | -35.3412 | 79.8533 | -50.9702 | -27.6458 | -35.7837 | 84.42 | -34.0503 | 42.9252 | -24.4946 | 145.9788 | -45.3585 | 95.3913 | -41.2842 | 170.7672 | -51.8066 | -134.4304 | -32.7515 | -162.954 | -17.5561 | 37.3431 | -10.3538 | 97.3747 | -22.4821 | 104.1931 | -11.3325 | 133.0888 | -28.1521 | 105.0552 | -12.8658 | -177.9719 | -17.1104 | -65.9037 | -12.0149 | -67.8149 | -37.776 | -43.7559 | -47.8001 | -48.1003 | -50.6042 | -36.795 | -37.6292 | -36.3786 | -42.0439 | -47.7542 | -63.2854 | -34.9294 | -35.6681 | 514 | -25.6289 | -31.2699 | -25.489 | -35.3361 | -24.0064 | -33.2374 | -23.8115 | -32.4687 | 514 | -28.9637 | -34.629 | -40.6854 | -42.8422 | -29.033 | -29.0944 | -28.6166 | -33.5091 | -40.5948 | -42.0694 | -29.2895 | -30.1237 | -36.341 | -40.3852 | -40.3393 | -55.5234 | -27.1674 | -27.1333 | -35.9939 | -39.2653 | -40.2487 | -54.7506 | -27.4239 | -28.1626
515 | -7.4661 | 0 | -7.8618 | 0 | -8.7852 | 0 | -7.4859 | 0 | -33.0616 | -62.439 | -24.6842 | 45.0285 | -42.5898 | 27.9038 | -34.1575 | 74.6827 | -48.3131 | -40.5107 | -36.9128 | 60.3008 | -33.4636 | 28.5966 | -23.2408 | 143.2211 | -41.2618 | 107.9091 | -39.313 | 168.8669 | -50.2977 | -125.1656 | -32.0044 | 178.7566 | -16.9488 | 31.5945 | -9.9364 | 85.1823 | -21.8945 | 93.7871 | -11.0599 | 123.1943 | -25.3478 | 86.1028 | -12.5133 | 164.2173 | -17.2168 | -71.6965 | -12.6452 | -84.055 | -37.4305 | -45.7485 | -49.57 | -46.4032 | -50.4579 | -35.8696 | -37.7993 | -35.7344 | -41.8138 | -46.3383 | -73.6391 | -34.1484 | -37.1292 | 515 | -24.034 | -30.4924 | -23.9921 | -35.632 | -22.7846 | -32.3888 | -22.6051 | -31.4603 | 515 | -28.2683 | -34.3477 | -38.9371 | -42.5961 | -28.0078 | -29.0141 | -27.8726 | -33.0286 | -38.9173 | -41.6727 | -28.3837 | -30.3134 | -38.2824 | -42.1039 | -38.8722 | -65.7773 | -26.2866 | -28.344 | -37.8867 | -40.7848 | -38.8524 | -64.8539 | -26.6625 | -29.6433
516 | -7.5275 | 0 | -7.8615 | 0 | -8.9438 | 0 | -7.4467 | 0 | -33.081 | -73.0025 | -23.0863 | 38.4891 | -39.6992 | 14.9073 | -33.2299 | 65.5268 | -47.0405 | -56.8022 | -40.052 | 40.8999 | -33.5682 | 13.8957 | -22.167 | 136.4104 | -37.9298 | 98.267 | -37.7841 | 158.3051 | -48.3932 | -127.8809 | -32.4201 | 158.3738 | -16.7337 | 25.278 | -10.0711 | 73.3737 | -21.8666 | 85.553 | -11.1569 | 113.037 | -23.973 | 60.5735 | -12.7773 | 146.9466 | -17.0855 | -79.5418 | -14.2363 | -100.258 | -37.0631 | -47.9189 | -51.065 | -45.1686 | -49.5045 | -34.5243 | -37.9514 | -35.7641 | -42.1212 | -46.4201 | -66.842 | -33.2016 | -38.194 | 516 | -22.5866 | -30.0567 | -22.6063 | -36.4637 | -21.7572 | -32.0707 | -21.668 | -31.2591 | 516 | -28.2366 | -34.5937 | -37.6411 | -41.643 | -26.6628 | -29.0076 | -27.9026 | -33.1774 | -37.7219 | -40.5607 | -27.0776 | -30.5047 | -40.3914 | -43.5375 | -38.8926 | -58.9805 | -25.3401 | -29.2502 | -40.0574 | -42.1212 | -38.9734 | -57.8982 | -25.7549 | -30.7473
517 | -7.5469 | 0 | -7.7618 | 0 | -8.9376 | 0 | -7.3946 | 0 | -33.6099 | -84.3531 | -21.9671 | 28.2778 | -38.252 | -2.9826 | -32.683 | 53.2261 | -46.6771 | -72.0847 | -46.0914 | 41.3743 | -34.3235 | -1.3635 | -21.4276 | 126.4237 | -36.0949 | 80.746 | -37.6953 | 144.3356 | -47.3579 | -138.6357 | -34.2563 | 139.037 | -17.0614 | 15.8783 | -10.722 | 63.1559 | -22.5586 | 80.3147 | -11.6097 | 104.5673 | -23.234 | 32.595 | -13.6729 | 131.4092 | -17.1806 | -88.9503 | -16.9898 | -114.5868 | -36.8462 | -47.0181 | -50.8853 | -44.5611 | -47.9829 | -33.3423 | -38.0274 | -36.4532 | -42.9415 | -47.6602 | -60.6758 | -32.6524 | -37.0235 | 517 | -21.5848 | -30.0167 | -21.5981 | -37.0854 | -21.0714 | -32.5343 | -21.1105 | -31.9421 | 517 | -28.9063 | -35.3946 | -37.0142 | -40.2211 | -25.5805 | -29.0898 | -28.6914 | -34.0039 | -37.1665 | -39.0453 | -25.9477 | -30.6328 | -39.4712 | -43.3384 | -40.1133 | -52.914 | -24.8906 | -28.0859 | -39.2563 | -41.9477 | -40.2656 | -51.7382 | -25.2578 | -29.6289
518 | -7.5215 | 0 | -7.6333 | 0 | -8.7548 | 0 | -7.3276 | 0 | -34.5714 | -92.5023 | -21.2835 | 17.9515 | -37.8986 | -21.9344 | -32.941 | 40.586 | -46.9303 | -87.806 | -46.7967 | 92.1938 | -35.7876 | -13.4269 | -21.0025 | 117.2583 | -35.4463 | 61.6902 | -38.6348 | 133.9309 | -46.9155 | -144.838 | -38.2752 | 129.0715 | -17.8825 | 5.5798 | -11.7246 | 56.9159 | -24.3175 | 84.0584 | -12.3987 | 98.7673 | -23.1605 | 7.1606 | -15.1795 | 120.5108 | -17.4942 | -97.6906 | -21.3383 | -118.0832 | -36.8701 | -43.9526 | -49.1216 | -45.3037 | -46.9834 | -32.6986 | -37.9693 | -37.6454 | -44.0919 | -48.8716 | -58.063 | -32.5985 | -35.2312 | 518 | -20.9949 | -30.5683 | -20.9853 | -36.9161 | -20.712 | -33.7566 | -20.849 | -33.4252 | 518 | -30.1239 | -36.5704 | -37.7822 | -39.3501 | -25.0653 | -29.2145 | -30.0121 | -35.3371 | -37.9761 | -38.2286 | -25.371 | -30.6417 | -36.4311 | -41.6001 | -41.3501 | -50.4297 | -24.9652 | -26.4764 | -36.3193 | -40.3668 | -41.544 | -49.3082 | -25.2709 | -27.9036
519 | -7.5007 | 0 | -7.5261 | 0 | -8.5322 | 0 | -7.2937 | 0 | -35.7075 | -96.0006 | -21.1307 | 4.8004 | -38.3978 | -39.3403 | -33.9237 | 31.8451 | -48.0255 | -104.4867 | -41.6413 | 100.6348 | -38.0203 | -19.8387 | -20.943 | 106.1539 | -35.9088 | 43.2991 | -39.7596 | 131.7388 | -46.3934 | -154.5959 | -42.7372 | 154.5159 | -19.4243 | -2.3604 | -12.6531 | 56.1737 | -23.8486 | 104.2559 | -13.2156 | 96.4849 | -23.5361 | -18.6843 | -17.1473 | 118.6339 | -17.6465 | -107.8445 | -24.8928 | -86.4136 | -37.0208 | -41.7183 | -47.3 | -46.5716 | -46.677 | -32.7339 | -37.8855 | -39.0557 | -45.2234 | -49.6082 | -56.8152 | -32.9424 | -34.5007 | 519 | -20.9039 | -31.614 | -20.8717 | -36.4035 | -20.725 | -35.4305 | -20.8581 | -34.7794 | 519 | -31.555 | -37.7227 | -39.0709 | -39.1509 | -25.2078 | -29.3533 | -31.5296 | -36.6912 | -39.2779 | -38.1448 | -25.4402 | -30.5918 | -34.2176 | -39.7993 | -42.1075 | -49.2891 | -25.4163 | -25.9685 | -34.1922 | -38.7678 | -42.3145 | -48.283 | -25.6487 | -27.207
520 | -7.4633 | 0 | -7.5261 | 0 | -8.3695 | 0 | -7.2575 | 0 | -36.4556 | -95.0654 | -21.6558 | -7.2821 | -39.6625 | -54.0338 | -35.1894 | 28.6782 | -50.3551 | -118.3614 | -38.6028 | 91.8777 | -40.1749 | -12.9942 | -21.4258 | 95.2626 | -37.2294 | 27.3905 | -40.2664 | 134.4246 | -46.4434 | -167.7805 | -39.5934 | -176.4286 | -21.7721 | -8.3741 | -12.8681 | 59.3566 | -20.3697 | 111.8693 | -13.7169 | 99.0707 | -23.3616 | -41.2312 | -18.2248 | 127.3045 | -17.5427 | -117.8506 | -22.3072 | -69.5377 | -37.2825 | -40.6923 | -45.9814 | -46.8294 | -46.7942 | -33.3291 | -37.8269 | -40.2719 | -45.8461 | -49.4792 | -56.3347 | -33.5805 | -34.2832 | 520 | -21.4483 | -32.6912 | -21.3843 | -35.9304 | -21.2571 | -36.7206 | -21.3046 | -34.9247 | 520 | -32.8086 | -38.3828 | -39.3661 | -39.2681 | -25.803 | -29.4574 | -32.7458 | -37.4766 | -39.5719 | -38.4247 | -26.0716 | -30.5694 | -33.229 | -38.5181 | -42.0159 | -48.8086 | -26.0544 | -25.9137 | -33.1662 | -37.6119 | -42.2217 | -47.9652 | -26.323 | -27.0257
521 | -7.4303 | 0 | -7.5983 | 0 | -8.2545 | 0 | -7.2545 | 0 | -36.3106 | -93.291 | -22.9337 | -15.6847 | -41.6538 | -64.519 | -36.0074 | 31.4043 | -54.4585 | -122.461 | -36.7012 | 78.4395 | -39.745 | 0.1158 | -22.5152 | 88.5306 | -39.1039 | 17.3101 | -40.0156 | 136.9645 | -47.5371 | -179.8152 | -36.3363 | -179.2148 | -25.5689 | -3.5615 | -12.0832 | 60.591 | -17.3745 | 103.3256 | -13.3897 | 101.3594 | -23.6734 | -60.7756 | -16.8497 | 136.8608 | -17.7393 | -132.187 | -19.3537 | -75.8197 | -37.5657 | -40.4797 | -45.0891 | -45.5149 | -47.1828 | -34.3196 | -37.7819 | -40.8405 | -45.7663 | -48.3639 | -56.4538 | -34.3952 | -34.5196 | 521 | -22.6832 | -33.1141 | -22.5544 | -35.4416 | -22.3413 | -36.5107 | -22.2651 | -34.2827 | 521 | -33.4102 | -38.336 | -38.0846 | -39.5845 | -26.7213 | -29.5274 | -33.2422 | -37.5118 | -38.2604 | -38.9283 | -27.0651 | -30.5274 | -33.0494 | -37.6588 | -40.9336 | -48.8555 | -26.7969 | -26.2651 | -32.8814 | -36.8346 | -41.1094 | -48.1993 | -27.1407 | -27.2651
522 | -7.4395 | 0 | -7.7394 | 0 | -8.2637 | 0 | -7.278 | 0 | -35.4561 | -95.7984 | -24.5249 | -16.0355 | -44.145 | -67.6479 | -35.7214 | 37.5545 | -57.7341 | -92.4056 | -35.4525 | 62.8267 | -37.7164 | 1.0444 | -23.6673 | 88.5044 | -41.2836 | 14.3861 | -39.4943 | 138.8709 | -49.6371 | 174.5593 | -34.4332 | 171.7867 | -28.3733 | 26.9909 | -11.0396 | 57.3366 | -16.067 | 89.9947 | -12.5455 | 101.5478 | -24.292 | -79.7514 | -14.6179 | 135.1008 | -18.4972 | -148.3068 | -18.1109 | -94.5203 | -37.7185 | -40.5241 | -44.5709 | -43.8669 | -47.6169 | -35.5163 | -37.8175 | -40.3067 | -45.2207 | -46.7081 | -57.3722 | -35.334 | -35.0326 | 522 | -24.1442 | -32.5632 | -23.8927 | -34.8795 | -23.4279 | -35.3402 | -23.2142 | -33.5106 | 522 | -32.8672 | -37.7812 | -36.4274 | -39.8775 | -27.7769 | -29.5538 | -32.5673 | -36.957 | -36.5889 | -39.3532 | -28.2383 | -30.5395 | -33.0846 | -37.1314 | -39.2686 | -49.6328 | -27.5946 | -26.7689 | -32.7847 | -36.3072 | -39.4301 | -49.1085 | -28.056 | -27.7546
523 | -7.4506 | 0 | -7.878 | 0 | -8.3322 | 0 | -7.3365 | 0 | -34.6336 | -102.7591 | -24.8217 | -6.6287 | -45.923 | -57.1137 | -34.4211 | 38.7807 | -54.0392 | -69.8775 | -34.8938 | 47.1768 | -36.1962 | -8.8511 | -23.679 | 94.7068 | -43.2703 | 20.3662 | -38.4544 | 140.8716 | -51.4108 | -176.1314 | -33.0904 | 159.1711 | -25.422 | 55.449 | -10.2628 | 49.9134 | -15.8948 | 77.5376 | -11.6194 | 97.4619 | -24.8823 | -94.7049 | -12.8599 | 126.232 | -19.8508 | -159.9266 | -18.1764 | -116.1939 | -37.7282 | -40.4168 | -44.4141 | -42.7243 | -47.7594 | -36.62 | -37.9209 | -38.8127 | -44.599 | -44.9639 | -59.2139 | -36.1643 | -35.6556 | 523 | -24.3599 | -31.4915 | -24.001 | -34.5153 | -23.3974 | -34.0886 | -23.0803 | -32.6346 | 523 | -31.3621 | -37.1484 | -35.2737 | -39.8814 | -28.742 | -29.5887 | -30.9347 | -36.2668 | -35.3878 | -39.4272 | -29.2835 | -30.5844 | -32.9662 | -36.9635 | -37.5133 | -51.3359 | -28.2863 | -27.3234 | -32.5388 | -36.0819 | -37.6274 | -50.8817 | -28.8278 | -28.3191
524 | -7.5035 | 0 | -7.9631 | 0 | -8.46 | 0 | -7.4009 | 0 | -34.3021 | -113.0543 | -23.2686 | -2.1381 | -44.8163 | -43.8223 | -32.9087 | 34.6219 | -50.8193 | -77.0299 | -35.1637 | 30.7385 | -35.5073 | -22.3746 | -22.3801 | 96.2505 | -43.2576 | 35.54 | -36.764 | 137.7932 | -50.5613 | -164.1822 | -32.3441 | 143.8525 | -22.2805 | 55.7108 | -9.9222 | 40.2505 | -16.5469 | 68.8376 | -10.9418 | 91.3075 | -25.6761 | -102.1278 | -11.8165 | 114.1875 | -21.3115 | -162.6816 | -19.0349 | -145.3347 | -37.6845 | -40.322 | -44.7404 | -42.2587 | -47.5009 | -37.1462 | -38.1116 | -37.4718 | -44.3667 | -43.5569 | -61.596 | -36.5304 | -36.2794 | 524 | -22.911 | -30.4989 | -22.5746 | -34.6118 | -22.14 | -33.0032 | -21.8214 | -31.9456 | 524 | -29.9683 | -36.8632 | -34.7552 | -39.5378 | -29.1831 | -29.6516 | -29.5087 | -35.9067 | -34.8578 | -39.0409 | -29.7453 | -30.7107 | -32.8185 | -37.2369 | -36.0534 | -53.6329 | -28.5673 | -27.8194 | -32.3589 | -36.2804 | -36.156 | -53.136 | -29.1295 | -28.8785
525 | -7.5363 | 0 | -7.9504 | 0 | -8.5754 | 0 | -7.4816 | 0 | -34.5554 | -124.8877 | -21.483 | -7.1634 | -42.6154 | -46.9408 | -31.8385 | 23.1224 | -49.1264 | -91.8081 | -36.4279 | 15.5808 | -35.5479 | -37.2736 | -20.9894 | 89.8922 | -40.9061 | 40.5597 | -35.3193 | 127.6643 | -48.6397 | -163.4353 | -32.6361 | 124.3124 | -20.7367 | 46.8478 | -10.048 | 30.377 | -17.5626 | 67.0609 | -10.645 | 84.0873 | -25.9511 | -107.6464 | -11.4366 | 101.5485 | -21.3714 | -160.9985 | -20.8446 | -179.1043 | -37.6717 | -40.492 | -45.4647 | -42.4686 | -47.0311 | -36.66 | -38.3449 | -36.8176 | -44.6613 | -42.8488 | -62.4855 | -36.3137 | -36.8595 | 525 | -21.2423 | -29.9251 | -20.9747 | -35.3076 | -20.7974 | -32.3193 | -20.5544 | -31.9393 | 525 | -29.2813 | -37.125 | -34.9323 | -39.0807 | -28.7096 | -29.7695 | -28.8672 | -36.0859 | -34.987 | -38.4557 | -29.1784 | -30.8633 | -32.9557 | -37.9284 | -35.3125 | -54.5351 | -28.3633 | -28.2841 | -32.5416 | -36.8893 | -35.3672 | -53.9101 | -28.8321 | -29.3779
526 | -7.5605 | 0 | -7.8494 | 0 | -8.626 | 0 | -7.5152 | 0 | -35.3081 | -134.9156 | -20.2459 | -17.3447 | -41.1125 | -58.5814 | -31.3905 | 11.9931 | -48.4941 | -110.4273 | -38.6253 | 9.5908 | -36.2859 | -51.1144 | -20.0367 | 80.6019 | -38.8243 | 31.304 | -34.695 | 114.0262 | -47.0441 | -169.6854 | -34.3227 | 107.7532 | -20.6324 | 36.2931 | -10.6523 | 21.1176 | -17.9255 | 72.6574 | -10.5732 | 76.8183 | -25.7885 | -107.9536 | -11.5723 | 88.9229 | -20.531 | -161.7906 | -22.2908 | 140.4601 | -37.688 | -40.7927 | -46.1374 | -43.2622 | -46.6606 | -35.781 | -38.4705 | -36.9385 | -45.541 | -42.7713 | -60.7401 | -35.9619 | -37.3553 | 526 | -20.0782 | -29.8517 | -19.8662 | -36.4058 | -19.8792 | -32.2609 | -19.7368 | -32.8363 | 526 | -29.378 | -37.9805 | -35.7017 | -38.8112 | -27.9316 | -29.8445 | -29.0891 | -36.915 | -35.747 | -38.0346 | -28.2658 | -30.9553 | -33.2322 | -38.5769 | -35.2108 | -52.8907 | -28.1125 | -28.7293 | -32.9433 | -37.5114 | -35.2561 | -52.1141 | -28.4467 | -29.8401
527 | -7.5937 | 0 | -7.7259 | 0 | -8.601 | 0 | -7.4999 | 0 | -36.3951 | -141.4028 | -19.7131 | -29.7917 | -40.7691 | -74.4155 | -31.6043 | -0.6778 | -48.9772 | -131.2859 | -39.9318 | 18.8855 | -37.9017 | -62.4434 | -19.6274 | 69.0902 | -38.0174 | 16.2154 | -35.0452 | 100.8047 | -46.3864 | -179.6668 | -37.2087 | 102.3648 | -22.25 | 29.6076 | -11.7255 | 15.7927 | -16.9058 | 79.3524 | -10.8555 | 71.1139 | -24.5758 | -108.5693 | -12.3431 | 80.2017 | -19.0629 | -167.5666 | -24.4853 | 94.3898 | -37.7347 | -40.9375 | -46.1818 | -44.4321 | -46.4749 | -35.2187 | -38.3798 | -37.6949 | -46.6127 | -43.2659 | -58.4031 | -35.8139 | -37.099 | 527 | -19.5876 | -30.3005 | -19.4022 | -37.0332 | -19.5017 | -33.0273 | -19.4314 | -34.3063 | 527 | -30.1012 | -39.019 | -36.8384 | -38.749 | -27.4928 | -29.7788 | -29.969 | -38.0117 | -36.9322 | -37.8739 | -27.7188 | -30.8799 | -33.3438 | -38.5881 | -35.6722 | -50.6772 | -28.088 | -28.498 | -33.2116 | -37.5808 | -35.766 | -49.8021 | -28.314 | -29.5991
528 | -7.618 | 0 | -7.6404 | 0 | -8.5709 | 0 | -7.4676 | 0 | -37.5523 | -145.1396 | -19.7312 | -43.3135 | -41.2394 | -91.3898 | -32.3179 | -11.5462 | -50.4693 | -155.8191 | -39.201 | 28.6316 | -40.0506 | -65.9695 | -19.6965 | 57.1589 | -38.0084 | 0.5057 | -35.97 | 90.7636 | -46.2581 | 169.6818 | -39.4849 | 113.298 | -25.0452 | 36.8181 | -12.8977 | 14.8089 | -15.1728 | 79.8618 | -11.1709 | 66.9565 | -22.9323 | -111.4911 | -13.233 | 74.9973 | -17.5646 | -176.2442 | -25.0745 | 48.0668 | -37.8362 | -41.1921 | -45.7652 | -45.5618 | -46.5429 | -35.114 | -38.1093 | -38.8556 | -47.4412 | -43.8173 | -56.501 | -35.8827 | -36.5403 | 528 | -19.63 | -31.1289 | -19.4519 | -36.8963 | -19.5936 | -34.2546 | -19.5509 | -35.31 | 528 | -31.2376 | -39.8232 | -37.9438 | -38.9025 | -27.4736 | -29.5384 | -31.2152 | -38.8703 | -38.0942 | -37.972 | -27.6464 | -30.6417 | -33.5741 | -38.1472 | -36.1993 | -48.8606 | -28.2423 | -27.9694 | -33.5517 | -37.1943 | -36.3497 | -47.9301 | -28.4151 | -29.0727
529 | -7.6344 | 0 | -7.5993 | 0 | -8.5524 | 0 | -7.4079 | 0 | -38.5085 | -144.8263 | -20.3379 | -55.2914 | -42.5503 | -106.4367 | -33.4636 | -19.6813 | -53.6018 | 175.9898 | -37.2031 | 30.235 | -41.913 | -58.9735 | -20.3161 | 45.3517 | -38.5866 | -13.3837 | -37.2497 | 85.9598 | -46.531 | 158.9043 | -39.0274 | 130.5316 | -26.0773 | 71.6975 | -13.7243 | 19.5725 | -13.3328 | 74.9869 | -11.4148 | 64.1824 | -20.8493 | -116.8 | -14.0238 | 74.8861 | -15.9713 | 173.2515 | -24.1241 | 3.2762 | -38.0121 | -41.7504 | -45.1722 | -46.1605 | -46.9027 | -35.5082 | -37.7829 | -40.3454 | -47.8571 | -44.1422 | -55.1618 | -36.2438 | -36.2384 | 529 | -20.2466 | -32.2491 | -20.047 | -36.0143 | -20.2224 | -35.607 | -20.1721 | -35.4395 | 529 | -32.711 | -40.2227 | -38.5261 | -39.3034 | -27.9089 | -29.2305 | -32.7461 | -39.3047 | -38.7526 | -38.3503 | -28.1003 | -30.375 | -34.116 | -37.5378 | -36.5078 | -47.5625 | -28.6445 | -27.686 | -34.1511 | -36.6198 | -36.7343 | -46.6094 | -28.8359 | -28.8305
530 | -7.6937 | 0 | -7.6604 | 0 | -8.5446 | 0 | -7.3614 | 0 | -38.5967 | -142.8174 | -21.7059 | -63.7027 | -44.8541 | -116.4202 | -34.8543 | -21.9923 | -59.6543 | 128.5988 | -35.427 | 21.4885 | -40.9868 | -49.3082 | -21.6305 | 37.4431 | -39.7651 | -24.4297 | -38.3682 | 87.7535 | -47.4198 | 148.3578 | -37.1296 | 131.679 | -21.269 | 90.442 | -13.326 | 24.8747 | -12.261 | 63.8195 | -11.4195 | 62.6936 | -18.8584 | -127.2466 | -13.8134 | 78.5614 | -14.9321 | 158.5256 | -25.4705 | -38.5876 | -38.2139 | -42.3793 | -44.7862 | -45.4014 | -47.5381 | -36.2191 | -37.762 | -41.654 | -47.8343 | -44.0393 | -54.7425 | -36.8923 | -36.2305 | 530 | -21.5974 | -33.3139 | -21.3281 | -34.9431 | -21.515 | -36.1369 | -21.4212 | -34.9849 | 530 | -33.9603 | -40.1406 | -37.7077 | -39.8777 | -28.5587 | -29.2174 | -33.9936 | -39.2897 | -38.04 | -38.9935 | -28.8577 | -30.4006 | -34.6856 | -37.0925 | -36.3456 | -47.0821 | -29.2319 | -27.6859 | -34.7189 | -36.2416 | -36.6779 | -46.1979 | -29.5309 | -28.8691
531 | -7.7837 | 0 | -7.74 | 0 | -8.497 | 0 | -7.3616 | 0 | -37.9798 | -143.9738 | -23.3504 | -64.0686 | -47.5587 | -114.8522 | -35.7984 | -18.1824 | -60.8188 | 24.6445 | -34.3483 | 9.7236 | -39.0944 | -52.0266 | -23.1641 | 36.6024 | -41.4723 | -33.6983 | -38.5667 | 94.3634 | -48.9707 | 144.2494 | -35.6912 | 127.3012 | -17.3669 | 85.5369 | -12.2632 | 25.3501 | -12.0175 | 51.6102 | -11.1961 | 60.919 | -17.2635 | -139.9598 | -12.6894 | 78.3865 | -14.5832 | 143.3848 | -27.4753 | -89.4959 | -38.4497 | -42.1247 | -44.6302 | -44.0005 | -48.2309 | -37.0544 | -38.0056 | -41.8955 | -47.6431 | -43.4509 | -54.8337 | -37.6845 | -36.3273 | 531 | -23.1874 | -33.7347 | -22.7952 | -34.1364 | -22.9926 | -35.6073 | -22.811 | -34.5146 | 531 | -34.1118 | -39.8594 | -36.2168 | -40.4909 | -29.3144 | -29.5086 | -34.1555 | -39.1461 | -36.6389 | -39.7339 | -29.6928 | -30.644 | -34.341 | -36.8465 | -35.6672 | -47.0937 | -29.9445 | -27.8303 | -34.3847 | -36.1332 | -36.0893 | -46.3367 | -30.3229 | -28.9657
532 | -7.884 | 0 | -7.8458 | 0 | -8.4205 | 0 | -7.4157 | 0 | -37.304 | -150.4382 | -23.8814 | -55.5247 | -48.7818 | -102.7024 | -35.4264 | -12.0327 | -54.9483 | -27.3593 | -33.8468 | -3.8711 | -37.8235 | -63.9773 | -23.6179 | 44.8615 | -43.762 | -36.7115 | -37.4168 | 99.4511 | -50.0284 | 149.6503 | -34.5057 | 118.1292 | -15.0296 | 73.0927 | -11.2949 | 20.4728 | -12.5081 | 40.4164 | -10.8614 | 57.4657 | -16.0235 | -154.3046 | -11.6651 | 73.2288 | -14.9306 | 129.7326 | -28.3059 | -155.0023 | -38.6493 | -40.7435 | -44.5898 | -42.704 | -48.4306 | -37.7904 | -38.5724 | -40.7721 | -47.591 | -42.4044 | -55.3849 | -38.4987 | -36.5906 | 532 | -23.6749 | -33.2249 | -23.1963 | -33.6771 | -23.4158 | -34.4823 | -23.1133 | -33.9111 | 532 | -32.8881 | -39.707 | -34.82 | -40.5848 | -29.9446 | -30.1519 | -32.9263 | -39.1705 | -35.2883 | -40.0101 | -30.3747 | -31.1567 | -32.8595 | -36.7058 | -34.5204 | -47.5391 | -30.6529 | -28.1701 | -32.8977 | -36.1693 | -34.9887 | -46.9644 | -31.083 | -29.1749
533 | -7.9981 | 0 | -7.8927 | 0 | -8.3614 | 0 | -7.4825 | 0 | -37.0792 | -160.3753 | -22.6038 | -50.0938 | -47.4976 | -93.4292 | -34.0352 | -12.1197 | -51.9618 | -56.9008 | -33.949 | -17.1136 | -37.3564 | -78.7279 | -22.3577 | 50.2903 | -45.8209 | -26.8267 | -35.5965 | 96.7312 | -49.1182 | 157.3467 | -33.7481 | 105.1319 | -13.7547 | 59.664 | -10.7512 | 13.241 | -13.5896 | 34.8681 | -10.4153 | 52.283 | -15.4379 | -169.0045 | -10.9074 | 64.1003 | -15.9193 | 120.1996 | -24.7578 | 145.1247 | -38.9305 | -39.1063 | -44.6688 | -41.8719 | -47.9852 | -38.2469 | -39.2989 | -39.2638 | -47.7403 | -41.1934 | -56.1036 | -39.1466 | -36.9415 | 533 | -22.438 | -32.239 | -22.0147 | -33.696 | -22.2035 | -33.2633 | -21.8654 | -33.3695 | 533 | -31.2657 | -39.7422 | -33.8738 | -40.0925 | -30.3542 | -30.9375 | -31.3711 | -39.3789 | -34.3894 | -39.6238 | -30.7644 | -31.8164 | -31.1082 | -36.6707 | -33.1953 | -48.2109 | -31.2539 | -28.5801 | -31.2136 | -36.3074 | -33.7109 | -47.7422 | -31.6641 | -29.459
534 | -8.0667 | 0 | -7.8834 | 0 | -8.3484 | 0 | -7.5719 | 0 | -37.4697 | -171.6804 | -20.8908 | -53.5608 | -45.778 | -98.3631 | -32.6963 | -18.1367 | -50.7324 | -81.8727 | -34.6103 | -27.6804 | -37.6952 | -95.476 | -20.6868 | 45.2777 | -45.1649 | -11.4905 | -34.075 | 85.5175 | -47.3553 | 155.0665 | -33.8379 | 89.275 | -13.4496 | 45.4997 | -10.6727 | 3.7626 | -14.7107 | 34.8303 | -10.2763 | 45.6602 | -15.3499 | 177.5307 | -10.8035 | 53.3303 | -17.0744 | 117.3304 | -21.2468 | 106.4276 | -39.2845 | -37.9761 | -44.8077 | -41.5424 | -47.222 | -38.2691 | -40.2076 | -38.1336 | -48.0824 | -40.3131 | -56.8092 | -39.5554 | -37.2917 | 534 | -20.7826 | -31.3966 | -20.4436 | -34.193 | -20.586 | -32.3681 | -20.2957 | -33.3529 | 534 | -30.0669 | -40.0157 | -33.4757 | -39.3386 | -30.3857 | -31.8592 | -30.2502 | -39.734 | -33.9705 | -38.8736 | -30.6972 | -32.6357 | -29.9094 | -36.741 | -32.2464 | -48.9258 | -31.672 | -28.9433 | -30.0927 | -36.4593 | -32.7412 | -48.4608 | -31.9835 | -29.7198
535 | -8.0655 | 0 | -7.8049 | 0 | -8.3916 | 0 | -7.6275 | 0 | -38.4654 | 178.0123 | -19.6597 | -63.1234 | -44.6877 | -109.6167 | -31.9035 | -28.7751 | -50.9364 | -105.6213 | -35.6618 | -35.3458 | -38.7888 | -111.8612 | -19.4859 | 35.5808 | -42.9324 | -10.7208 | -33.4039 | 70.6144 | -46.1541 | 145.5378 | -34.9903 | 73.1321 | -14.0251 | 34.515 | -11.1094 | -4.3377 | -14.8704 | 40.9566 | -10.3092 | 39.5746 | -15.7902 | 166.2063 | -11.0946 | 43.4243 | -17.4106 | 121.4657 | -19.0874 | 79.2891 | -39.5967 | -37.492 | -44.8065 | -41.6201 | -46.5225 | -37.8904 | -41.0823 | -37.6025 | -48.2921 | -39.9768 | -57.051 | -39.9072 | -37.5028 | 535 | -19.5894 | -30.9932 | -19.3064 | -35.0366 | -19.4158 | -32.1248 | -19.1972 | -34.0662 | 535 | -29.537 | -40.2266 | -33.5546 | -38.7176 | -30.0855 | -32.6907 | -29.7976 | -39.9005 | -33.9926 | -38.1309 | -30.2629 | -33.4548 | -29.4265 | -36.741 | -31.9113 | -49.2461 | -32.1023 | -29.1112 | -29.6871 | -36.4149 | -32.3493 | -48.6594 | -32.2797 | -29.8753
536 | -8.0383 | 0 | -7.7278 | 0 | -8.4575 | 0 | -7.626 | 0 | -40.0269 | 170.5245 | -19.0828 | -77.4641 | -44.2331 | -124.6212 | -31.7453 | -41.8498 | -53.0499 | -130.3711 | -36.7293 | -37.3323 | -40.7588 | -126.0032 | -18.9729 | 22.3527 | -41.2121 | -22.1739 | -33.7729 | 54.6096 | -45.8807 | 132.9462 | -37.2655 | 63.6338 | -15.3729 | 29.3951 | -11.9771 | -11.1099 | -13.8213 | 44.6896 | -10.4413 | 33.2149 | -16.5933 | 158.7989 | -12.0473 | 35.2065 | -16.361 | 125.2948 | -18.0516 | 54.2218 | -39.7774 | -37.6047 | -44.5801 | -41.9883 | -46.1954 | -37.5462 | -41.6731 | -37.7622 | -48.1125 | -40.2044 | -56.513 | -40.1841 | -37.5335 | 536 | -19.0349 | -31.1159 | -18.7834 | -35.9339 | -18.9185 | -32.7633 | -18.7696 | -35.3886 | 536 | -29.7239 | -40.0742 | -33.95 | -38.4676 | -29.8184 | -33.2156 | -30.0344 | -39.655 | -34.3623 | -37.7379 | -29.9202 | -34.0471 | -29.5664 | -36.5418 | -32.1661 | -48.7852 | -32.4563 | -29.076 | -29.8769 | -36.1226 | -32.5784 | -48.0555 | -32.5581 | -29.9075
537 | -8.0102 | 0 | -7.6469 | 0 | -8.5375 | 0 | -7.5766 | 0 | -41.7083 | 168.5687 | -19.1807 | -89.1445 | -44.5211 | -143.0097 | -32.271 | -55.0271 | -59.1441 | -154.252 | -37.1027 | -33.7827 | -43.5837 | -132.9864 | -19.1687 | 8.5143 | -40.3829 | -38.0654 | -35.1081 | 39.8086 | -46.2199 | 120.1691 | -39.8468 | 66.9559 | -16.7777 | 34.2211 | -13.1425 | -13.6544 | -12.511 | 41.7452 | -10.8939 | 27.2731 | -17.2259 | 160.6439 | -13.3911 | 32.5653 | -14.6949 | 122.7022 | -17.9007 | 31.2956 | -39.9075 | -38.4036 | -44.1965 | -42.6575 | -46.2785 | -37.5676 | -41.85 | -38.8071 | -47.5532 | -40.7446 | -55.3032 | -40.2875 | -37.6017 | 537 | -19.1439 | -31.7948 | -18.9063 | -36.3565 | -19.1204 | -34.2464 | -19.0234 | -36.595 | 537 | -30.7969 | -39.543 | -34.6473 | -38.6316 | -29.9207 | -33.3125 | -31.1602 | -39.0157 | -35.0809 | -37.741 | -29.991 | -34.2734 | -30.3934 | -36.1863 | -32.7344 | -47.6563 | -32.6406 | -29.0642 | -30.7567 | -35.659 | -33.168 | -46.7657 | -32.7109 | -30.0251
538 | -8.0616 | 0 | -7.5974 | 0 | -8.5895 | 0 | -7.5002 | 0 | -42.5685 | 173.0085 | -19.9624 | -100.9848 | -45.7799 | -162.3618 | -33.4051 | -65.6127 | -69.0453 | 4.1019 | -36.2392 | -32.2952 | -46.1062 | -126.2675 | -20.0676 | -3.0134 | -40.5112 | -55.7881 | -37.217 | 31.936 | -47.0422 | 108.8464 | -40.6083 | 80.6048 | -16.301 | 47.6836 | -14.0764 | -11.4317 | -11.4949 | 33.8786 | -11.3743 | 22.3377 | -16.6133 | 165.9395 | -14.5241 | 36.6549 | -13.319 | 115.7093 | -18.0336 | 10.6806 | -40.0103 | -39.8618 | -44.1424 | -43.2329 | -46.7837 | -38.061 | -41.9099 | -40.488 | -47.1241 | -41.2497 | -54.1013 | -40.4528 | -37.849 | 538 | -19.9273 | -32.907 | -19.6733 | -35.7794 | -20.0179 | -36.3065 | -19.9472 | -37.0866 | 538 | -32.4264 | -39.0625 | -35.1713 | -39.1863 | -30.4636 | -33.3204 | -32.8906 | -38.5346 | -35.7327 | -38.1942 | -30.5608 | -34.4097 | -31.8002 | -36.0808 | -33.1881 | -46.5039 | -32.8554 | -29.2595 | -32.2644 | -35.5529 | -33.7495 | -45.5118 | -32.9526 | -30.3488
539 | -8.245 | 0 | -7.6204 | 0 | -8.6051 | 0 | -7.4478 | 0 | -42.3043 | 175.7679 | -21.4032 | -108.8794 | -47.9622 | -179.8242 | -35.0257 | -72.2487 | -54.4007 | -21.0912 | -34.9833 | -35.6296 | -46.0953 | -115.8596 | -21.6256 | -10.8257 | -41.7393 | -75.0235 | -39.6152 | 33.1814 | -48.2559 | 98.7659 | -39.527 | 89.5039 | -14.1046 | 52.4377 | -14.1903 | -7.2761 | -11.0356 | 23.9109 | -11.891 | 18.4673 | -14.8771 | 165.4811 | -14.3372 | 43.6092 | -12.4029 | 103.7339 | -20.2526 | -9.1795 | -40.1036 | -41.393 | -44.4235 | -42.9864 | -47.4278 | -38.7251 | -42.1907 | -41.8825 | -46.8973 | -41.6243 | -53.347 | -40.9294 | -38.134 | 539 | -21.3585 | -34.2387 | -21.0398 | -34.7229 | -21.5682 | -38.2745 | -21.4884 | -37.1344 | 539 | -33.6375 | -38.6523 | -34.7414 | -39.8074 | -31.1047 | -33.5856 | -34.2621 | -38.2922 | -35.5386 | -38.8227 | -31.2773 | -34.7429 | -33.148 | -36.1785 | -33.3793 | -45.7266 | -33.309 | -29.5289 | -33.7726 | -35.8184 | -34.1765 | -44.7419 | -33.4816 | -30.6862
540 | -8.4565 | 0 | -7.6514 | 0 | -8.5009 | 0 | -7.4045 | 0 | -41.6247 | 170.8963 | -22.9973 | -108.3372 | -51.0571 | 163.97 | -36.7255 | -71.4677 | -49.6595 | -45.3998 | -33.9795 | -44.5688 | -44.8197 | -119.0659 | -23.3248 | -10.607 | -44.3144 | -93.5012 | -40.8268 | 45.612 | -49.9124 | 94.5444 | -37.9142 | 87.9802 | -12.0605 | 47.1979 | -13.6239 | -6.0086 | -11.1821 | 14.3099 | -12.3082 | 15.6783 | -13.0481 | 158.2559 | -13.2313 | 45.2618 | -12.0965 | 91.4408 | -24.2752 | -25.8067 | -40.2049 | -41.6677 | -44.7287 | -41.9588 | -48.0017 | -39.4334 | -42.7021 | -41.6259 | -46.6713 | -41.6787 | -53.1904 | -41.7431 | -38.3149 | 540 | -22.9314 | -35.3439 | -22.4968 | -33.7815 | -23.2599 | -39.0021 | -23.1024 | -36.8009 | 540 | -33.1694 | -38.2148 | -33.5023 | -40.3503 | -31.782 | -34.2012 | -33.9745 | -38.1704 | -34.5543 | -39.5008 | -32.0289 | -35.2976 | -33.2112 | -36.2722 | -33.2222 | -45.539 | -34.0917 | -29.814 | -34.0163 | -36.2278 | -34.2742 | -44.6895 | -34.3386 | -30.9104
541 | -8.6433 | 0 | -7.6941 | 0 | -8.3738 | 0 | -7.4128 | 0 | -41.4329 | 159.5159 | -23.5175 | -100.9977 | -55.75 | 148.7116 | -37.3092 | -62.6868 | -47.6036 | -68.8965 | -33.3387 | -55.1274 | -44.1317 | -130.5281 | -23.8215 | -1.804 | -48.7695 | -108.0962 | -39.7847 | 57.0329 | -51.5624 | 99.8 | -36.5102 | 79.6034 | -10.7332 | 36.6942 | -12.9986 | -9.8645 | -11.8864 | 5.0007 | -12.6342 | 12.4207 | -11.7321 | 147.632 | -12.173 | 40.5292 | -12.4854 | 80.0585 | -33.1591 | -20.2596 | -40.3296 | -40.3062 | -44.7398 | -40.7789 | -48.3726 | -40.0132 | -43.2878 | -40.1003 | -46.3308 | -41.3699 | -53.7175 | -42.9793 | -38.4611 | 541 | -23.4453 | -35.6055 | -22.9258 | -33.155 | -23.7675 | -38.2194 | -23.4906 | -36.1332 | 541 | -31.457 | -37.6875 | -32.1356 | -40.6785 | -32.3191 | -34.914 | -32.4062 | -37.957 | -33.3661 | -39.9988 | -32.6004 | -35.875 | -31.6629 | -36.0965 | -32.7266 | -46.0234 | -35.2852 | -30.0873 | -32.6121 | -36.366 | -33.9571 | -45.3437 | -35.5665 | -31.0483
542 | -8.7724 | 0 | -7.7117 | 0 | -8.2561 | 0 | -7.429 | 0 | -42.2527 | 146.41 | -22.4445 | -96.405 | -67.1047 | 147.3672 | -36.212 | -57.2486 | -47.3241 | -90.3344 | -33.0664 | -66.3265 | -44.1815 | -145.9162 | -22.581 | 3.6379 | -57.1018 | -106.0164 | -37.8421 | 57.6375 | -51.5717 | 111.5402 | -35.7086 | 66.3621 | -10.1454 | 25.2301 | -12.7237 | -16.311 | -12.9591 | 1.3852 | -13.002 | 9.2498 | -11.0512 | 135.0163 | -11.6995 | 32.3721 | -13.4885 | 71.7669 | -30.5265 | 76.549 | -40.6441 | -38.6495 | -44.4118 | -39.9488 | -48.6714 | -40.4463 | -43.7156 | -38.5491 | -45.9443 | -40.7507 | -54.7585 | -44.5217 | -38.613 | 542 | -22.3992 | -34.9857 | -21.9189 | -32.9048 | -22.5495 | -36.7881 | -22.253 | -35.5668 | 542 | -29.7767 | -37.1719 | -31.1764 | -40.9597 | -32.7346 | -35.4595 | -30.8374 | -37.6882 | -32.5198 | -40.4153 | -33.0173 | -36.2866 | -29.8771 | -35.6394 | -31.9783 | -47.0468 | -36.81 | -30.3569 | -30.9378 | -36.1557 | -33.3217 | -46.5024 | -37.0927 | -31.184
543 | -8.7493 | 0 | -7.6879 | 0 | -8.1954 | 0 | -7.4497 | 0 | -44.0542 | 134.868 | -20.9243 | -100.133 | -62.3755 | -105.2705 | -34.7288 | -60.9942 | -48.4031 | -107.0466 | -33.2569 | -78.1585 | -44.9084 | -163.6621 | -20.9827 | -0.6349 | -57.6264 | -18.9417 | -36.1493 | 49.9885 | -49.9043 | 114.0432 | -35.7183 | 50.6973 | -10.2368 | 13.6972 | -12.9629 | -24.8265 | -13.8267 | 1.9196 | -13.3821 | 5.3263 | -10.9545 | 122.1246 | -11.8538 | 22.9496 | -14.8219 | 69.8689 | -23.0147 | 70.5066 | -41.1007 | -37.5067 | -43.8809 | -39.5968 | -48.9211 | -40.7137 | -43.8675 | -37.5235 | -45.636 | -39.9769 | -55.4261 | -46.129 | -38.8451 | 543 | -20.9029 | -34.0853 | -20.51 | -33.1209 | -20.9642 | -35.4482 | -20.7131 | -35.5289 | 543 | -28.7742 | -36.8867 | -30.8475 | -41.2332 | -33.0258 | -35.6721 | -29.8356 | -37.4406 | -32.1471 | -40.7257 | -33.264 | -36.4178 | -28.7574 | -35.1316 | -31.2276 | -47.7382 | -38.4411 | -30.6497 | -29.8188 | -35.6855 | -32.5272 | -47.2307 | -38.6793 | -31.3954
544 | -8.6228 | 0 | -7.6354 | 0 | -8.2407 | 0 | -7.4495 | 0 | -46.5354 | 128.3302 | -19.7706 | -109.8802 | -57.0266 | -123.6104 | -33.71 | -71.733 | -50.5359 | -114.6201 | -33.9317 | -88.7012 | -46.376 | 176.3935 | -19.8835 | -12.0413 | -50.5947 | -17.1453 | -35.2004 | 35.8108 | -48.4048 | 104.6536 | -36.7031 | 34.795 | -10.9714 | 4.7471 | -13.8059 | -32.7078 | -13.8221 | 6.0251 | -13.9861 | 0.7671 | -11.3554 | 111.1483 | -12.6347 | 15.5158 | -15.3559 | 75.8475 | -20.0636 | 58.2958 | -41.5757 | -37.0207 | -43.3677 | -39.603 | -48.9507 | -40.845 | -43.9909 | -37.1352 | -45.4509 | -39.4401 | -55.0925 | -47.3618 | -39.0896 | 544 | -19.7606 | -33.4042 | -19.4415 | -33.817 | -19.8701 | -34.6924 | -19.6708 | -36.2561 | 544 | -28.5124 | -36.8281 | -30.9802 | -41.3153 | -33.2096 | -35.7502 | -29.4998 | -37.2102 | -32.1535 | -40.71 | -33.3955 | -36.5414 | -28.3979 | -34.7449 | -30.8173 | -47.4571 | -39.7264 | -30.8489 | -29.3853 | -35.127 | -31.9906 | -46.8518 | -39.9123 | -31.6401
545 | -8.4969 | 0 | -7.583 | 0 | -8.3095 | 0 | -7.4424 | 0 | -48.928 | 129.0026 | -19.315 | -122.6625 | -57.2151 | -153.5319 | -33.4178 | -84.6844 | -52.2813 | -103.5559 | -34.909 | -96.3514 | -48.7275 | 155.9885 | -19.5757 | -24.6247 | -47.8266 | -32.8434 | -35.3366 | 19.6309 | -47.7477 | 91.3091 | -38.9412 | 22.2712 | -12.1608 | 1.9715 | -15.2595 | -36.6839 | -12.9837 | 5.9539 | -14.7209 | -1.7918 | -12.2988 | 106.0101 | -13.9388 | 12.8737 | -14.2946 | 80.4845 | -18.9156 | 44.7146 | -42.1082 | -37.3151 | -43.0024 | -39.8828 | -48.8095 | -40.9898 | -44.1452 | -37.5369 | -45.3192 | -39.2647 | -54.1955 | -48.205 | -39.176 | 545 | -19.3096 | -33.2428 | -19.0356 | -34.8052 | -19.5639 | -34.9101 | -19.4133 | -37.9344 | 545 | -29.04 | -36.8223 | -31.3859 | -41.2265 | -33.4068 | -35.8357 | -29.9539 | -37.0097 | -32.4404 | -40.5 | -33.5474 | -36.7028 | -28.8182 | -34.5055 | -30.7678 | -46.6125 | -40.622 | -30.8665 | -29.7321 | -34.6929 | -31.8223 | -45.886 | -40.7626 | -31.7336
546 | -8.4498 | 0 | -7.5469 | 0 | -8.3992 | 0 | -7.424 | 0 | -50.9908 | 131.9595 | -19.4712 | -135.6575 | -60.9514 | 168.401 | -33.7259 | -98.676 | -51.2987 | -87.2537 | -35.8448 | -99.4762 | -51.7126 | 136.687 | -19.8881 | -38.2882 | -47.153 | -49.9121 | -36.4159 | 3.8219 | -47.7697 | 76.4492 | -42.5245 | 17.2924 | -13.0201 | 5.9695 | -16.8793 | -35.5975 | -12.1321 | 1.5527 | -15.7844 | -2.8582 | -13.0069 | 105.9703 | -15.1397 | 14.8154 | -12.8705 | 78.1799 | -18.5906 | 33.1131 | -42.6952 | -38.2722 | -42.7862 | -40.3323 | -48.4528 | -41.1786 | -44.2869 | -38.6066 | -45.2954 | -39.3855 | -53.59 | -49.0666 | -39.3004 | 546 | -19.4678 | -33.5712 | -19.2157 | -35.7098 | -19.8771 | -35.9911 | -19.7695 | -40.3672 | 546 | -30.1568 | -36.8456 | -31.8825 | -40.9059 | -33.6317 | -35.8877 | -31.0597 | -36.8962 | -32.9083 | -40.0536 | -33.7546 | -36.8629 | -29.8224 | -34.3364 | -30.9357 | -46.0431 | -41.5197 | -30.9012 | -30.7253 | -34.387 | -31.9615 | -45.1908 | -41.6426 | -31.8764
547 | -8.5194 | 0 | -7.5549 | 0 | -8.443 | 0 | -7.4236 | 0 | -52.8678 | 134.7125 | -20.2733 | -147.127 | -68.1178 | 46.3635 | -34.7033 | -113.6419 | -48.3562 | -81.8938 | -36.4352 | -100.32 | -54.9045 | 122.3999 | -20.8625 | -50.4624 | -48.0926 | -65.3412 | -38.6467 | -10.1693 | -48.546 | 61.9042 | -47.3657 | 34.2142 | -12.7187 | 13.6582 | -18.0327 | -28.6906 | -11.5085 | -6.2407 | -17.1003 | -1.4155 | -13.058 | 110.9169 | -15.6591 | 20.7083 | -11.7571 | 70.8347 | -18.1342 | 24.9727 | -43.1787 | -39.8949 | -42.6744 | -40.9091 | -47.917 | -41.4339 | -44.4182 | -40.3219 | -45.3944 | -39.8088 | -53.5432 | -50.1656 | -39.5651 | 547 | -20.2708 | -34.4569 | -20.0192 | -36.162 | -20.8526 | -38.1313 | -20.7812 | -43.2028 | 547 | -31.8025 | -36.875 | -32.3897 | -40.3621 | -33.879 | -35.9752 | -32.767 | -36.9514 | -33.4855 | -39.474 | -34.0103 | -36.9946 | -31.3755 | -34.155 | -31.2894 | -45.9883 | -42.6107 | -31.1221 | -32.34 | -34.2314 | -32.3852 | -45.1002 | -42.742 | -32.1415
548 | -8.7929 | 0 | -7.5569 | 0 | -8.4325 | 0 | -7.4455 | 0 | -55.1448 | 137.4768 | -21.786 | -155.8026 | -56.6225 | -23.8884 | -36.6802 | -125.3501 | -46.0823 | -93.0604 | -36.2445 | -100.1814 | -55.5072 | 113.1031 | -22.6348 | -58.7544 | -51.0807 | -73.4988 | -42.5416 | -13.8943 | -50.6598 | 49.7279 | -44.8535 | 72.1415 | -11.1236 | 14.909 | -17.7969 | -21.3178 | -11.4209 | -16.3615 | -17.3917 | 7.0863 | -11.5525 | 112.6975 | -15.0395 | 25.2482 | -11.1575 | 60.0293 | -18.9474 | 22.2922 | -43.2041 | -41.8337 | -42.5964 | -41.5556 | -47.4345 | -41.7985 | -44.4084 | -42.0302 | -45.6679 | -40.4553 | -54.4592 | -51.9989 | -40.1289 | 548 | -21.7826 | -36.1533 | -21.4994 | -35.7797 | -22.6264 | -41.7326 | -22.5649 | -43.0896 | 548 | -33.2373 | -36.875 | -32.7627 | -39.8776 | -34.2416 | -35.9759 | -34.4733 | -37.2354 | -34.1101 | -39.002 | -34.353 | -36.9629 | -33.0408 | -33.8035 | -31.6624 | -46.9023 | -44.442 | -31.6964 | -34.2768 | -34.1639 | -33.0098 | -46.0267 | -44.5534 | -32.6834
549 | -9.0696 | 0 | -7.5657 | 0 | -8.3509 | 0 | -7.4954 | 0 | -59.1716 | 140.3308 | -23.4138 | -156.1976 | -51.4324 | -53.3122 | -39.7294 | -130.9815 | -45.0658 | -107.4712 | -35.6359 | -102.9465 | -53.9366 | 92.7754 | -24.5697 | -57.1034 | -54.4753 | -56.1423 | -46.2825 | 9.9679 | -53.875 | 52.9686 | -40.6593 | 69.3229 | -9.6301 | 9.3062 | -17.0387 | -20.0488 | -11.8124 | -26.3585 | -16.63 | 14.0071 | -9.9898 | 106.8371 | -14.2938 | 24.0761 | -11.3372 | 48.5773 | -18.3651 | 25.2969 | -42.8106 | -42.4942 | -42.4356 | -41.9551 | -47.3262 | -42.2481 | -44.3118 | -41.8899 | -45.9095 | -41.1009 | -56.3509 | -55.011 | -40.5746 | 549 | -23.4058 | -38.5765 | -23.0663 | -35.0655 | -24.5602 | -44.993 | -24.4357 | -40.2881 | 549 | -32.8203 | -36.8399 | -32.8855 | -39.7605 | -34.6824 | -35.9609 | -34.3242 | -37.5586 | -34.4597 | -38.9753 | -34.7527 | -36.8164 | -33.4246 | -33.366 | -32.0313 | -48.7852 | -47.4453 | -32.2237 | -34.9285 | -34.0847 | -33.6055 | -48 | -47.5156 | -33.0792
550 | -9.2674 | 0 | -7.5515 | 0 | -8.2462 | 0 | -7.5938 | 0 | -66.9799 | -168.5032 | -24.0669 | -149.3299 | -48.4083 | -76.8276 | -43.2726 | -119.4337 | -45.0991 | -119.8782 | -34.9685 | -108.3808 | -51.9284 | 67.4513 | -25.1946 | -47.8053 | -52.6931 | -31.8557 | -43.7447 | 38.594 | -54.2575 | 73.8037 | -38.422 | 52.6034 | -8.686 | -0.2625 | -16.7114 | -24.1333 | -12.7062 | -34.0936 | -15.2618 | 14.8841 | -8.8685 | 97.0324 | -13.9756 | 19.2244 | -12.2515 | 38.7752 | -17.3377 | 25.7252 | -42.2807 | -41.3543 | -42.2466 | -41.7651 | -47.726 | -42.9168 | -44.1335 | -39.9962 | -46.0721 | -41.532 | -59.4187 | -60.3282 | -41.1065 | 550 | -24.0507 | -41.0691 | -23.6797 | -34.3906 | -25.1777 | -42.8077 | -24.9353 | -38.1547 | 550 | -30.7288 | -36.8047 | -32.4977 | -40.1745 | -35.3653 | -35.8873 | -32.4447 | -37.8259 | -34.1713 | -39.4798 | -35.323 | -36.5397 | -32.0869 | -32.9792 | -32.2646 | -51.8672 | -52.7767 | -32.8603 | -33.8028 | -34.0004 | -33.9382 | -51.1725 | -52.7344 | -33.5127
551 | -9.3129 | 0 | -7.563 | 0 | -8.1751 | 0 | -7.6773 | 0 | -58.0537 | -107.339 | -23.243 | -145.2836 | -46.6448 | -99.2216 | -43.3075 | -91.839 | -45.6617 | -127.8268 | -34.4974 | -117.5574 | -50.157 | 44.3405 | -24.1104 | -42.9845 | -49.6134 | -32.3998 | -40.3316 | 38.6345 | -51.8848 | 77.7386 | -37.7721 | 32.325 | -8.3422 | -11.1769 | -17.1202 | -30.3625 | -13.7883 | -39.2686 | -14.1199 | 8.7062 | -8.3511 | 85.6551 | -14.2517 | 14.0243 | -13.7792 | 34.4946 | -15.7499 | 20.0836 | -41.847 | -39.7441 | -42.0343 | -40.8587 | -48.4524 | -43.6699 | -43.942 | -37.9485 | -46.0824 | -41.6841 | -64.3677 | -65.8157 | -42.0588 | 551 | -23.2218 | -41.2256 | -22.8896 | -33.938 | -24.0874 | -39.6348 | -23.8291 | -37.3415 | 551 | -28.6356 | -36.7695 | -31.5458 | -40.8894 | -36.1069 | -35.7669 | -30.3855 | -37.9073 | -33.1814 | -40.2773 | -35.9926 | -36.2647 | -30.4312 | -32.7214 | -32.3712 | -56.8047 | -58.2527 | -33.8837 | -32.1811 | -33.8592 | -34.0068 | -56.1926 | -58.1384 | -34.3815
552 | -9.2024 | 0 | -7.5473 | 0 | -8.1737 | 0 | -7.7503 | 0 | -52.0586 | -111.3283 | -21.906 | -147.5078 | -45.7002 | -121.106 | -40.2241 | -84.0292 | -46.4539 | -131.6401 | -34.3842 | -128.4823 | -48.9364 | 23.3562 | -22.7284 | -46.1337 | -47.7298 | -46.8082 | -38.2753 | 27.308 | -50.4691 | 68.4199 | -38.3984 | 12.0863 | -8.5328 | -21.6597 | -18.2637 | -33.5068 | -14.6584 | -39.3282 | -13.1539 | -0.0587 | -8.3971 | 74.3626 | -15.0079 | 10.7686 | -15.2501 | 38.9734 | -14.5009 | 10.316 | -41.5344 | -38.5552 | -41.9433 | -39.5969 | -49.05 | -44.1294 | -43.9028 | -36.4198 | -45.9485 | -41.6098 | -69.4926 | -59.2557 | -43.5496 | 552 | -21.8837 | -39.072 | -21.6071 | -33.8306 | -22.7043 | -37.6826 | -22.4959 | -37.6843 | 552 | -27.2174 | -36.7461 | -30.3945 | -41.5027 | -36.5821 | -35.7291 | -28.8725 | -37.7748 | -31.8466 | -40.8763 | -36.3791 | -36.1525 | -29.3528 | -32.7409 | -32.4074 | -61.9453 | -51.7084 | -35.3759 | -31.0079 | -33.7696 | -33.8595 | -61.3189 | -51.5054 | -35.7993
553 | -8.9643 | 0 | -7.519 | 0 | -8.2456 | 0 | -7.8159 | 0 | -48.8912 | -124.3874 | -20.9057 | -157.198 | -45.3493 | -141.9913 | -37.8206 | -92.0629 | -46.9612 | -129.0865 | -34.713 | -140.7089 | -48.3666 | 5.14 | -21.8029 | -56.6208 | -46.9896 | -68.8503 | -37.3491 | 12.661 | -49.9303 | 56.0584 | -40.2149 | -9.979 | -9.2882 | -30.545 | -19.8289 | -30.3552 | -14.7124 | -38.3733 | -12.8223 | -12.1205 | -8.989 | 64.7929 | -15.8768 | 13.6192 | -15.1496 | 48.5951 | -13.69 | -2.1337 | -41.4475 | -37.9553 | -42.0256 | -38.4748 | -48.8811 | -43.7873 | -44.1597 | -35.5268 | -45.769 | -41.4995 | -63.9253 | -54.7886 | -44.5629 | 553 | -20.8832 | -37.0287 | -20.6446 | -34.1213 | -21.7802 | -36.8018 | -21.623 | -39.0193 | 553 | -26.5625 | -36.8047 | -29.5105 | -41.3621 | -36.2683 | -35.9141 | -28.0078 | -37.5234 | -30.6589 | -40.6355 | -35.9714 | -36.3438 | -28.991 | -33.0613 | -32.5352 | -56.4063 | -47.2696 | -36.3173 | -30.4363 | -33.78 | -33.6836 | -55.6797 | -46.9727 | -36.747
554 | -8.729 | 0 | -7.5416 | 0 | -8.3549 | 0 | -7.8366 | 0 | -47.5759 | -138.1955 | -20.534 | -169.1557 | -45.5499 | -161.9041 | -36.5365 | -106.4776 | -46.1991 | -122.3031 | -35.5616 | -150.9985 | -48.5367 | -9.2074 | -21.4674 | -68.0609 | -47.5354 | -96.269 | -37.4609 | -3.8246 | -49.8376 | 42.5165 | -43.8353 | -32.8166 | -10.4749 | -34.7056 | -20.5421 | -17.7431 | -14.1557 | -40.8356 | -13.0005 | -24.943 | -10.0697 | 58.7739 | -16.066 | 19.3702 | -13.6561 | 51.4711 | -13.5366 | -17.0332 | -41.7513 | -38.0997 | -42.4035 | -37.7552 | -47.9154 | -43.0177 | -44.8619 | -35.3549 | -45.604 | -41.4518 | -59.3854 | -51.9916 | -44.3441 | 554 | -20.5118 | -35.7927 | -20.2952 | -34.8185 | -21.4482 | -36.9075 | -21.335 | -41.5884 | 554 | -26.6259 | -36.875 | -29.0262 | -40.3738 | -35.4761 | -36.507 | -27.8133 | -37.2491 | -29.9186 | -39.5605 | -35.1811 | -37.0253 | -29.3707 | -33.6745 | -32.7228 | -51.8438 | -44.45 | -35.9892 | -30.5581 | -34.0486 | -33.6152 | -51.0305 | -44.155 | -36.5075
555 | -8.6555 | 0 | -7.5773 | 0 | -8.4307 | 0 | -7.8601 | 0 | -47.8366 | -149.2583 | -20.8997 | 178.2692 | -46.3508 | 179.9824 | -36.3535 | -123.8829 | -43.9927 | -122.019 | -36.8893 | -158.4081 | -49.3082 | -16.3173 | -21.796 | -82.4124 | -49.7165 | -131.4474 | -38.7544 | -20.1666 | -50.2806 | 24.1701 | -52.3769 | -57.0319 | -11.3709 | -30.9732 | -19.5473 | -7.8879 | -13.6655 | -48.0471 | -13.7716 | -37.8552 | -11.0754 | 60.6553 | -15.4648 | 22.7936 | -12.2381 | 45.9287 | -13.9058 | -33.0275 | -42.4589 | -39.1286 | -42.9511 | -37.4979 | -46.5761 | -42.2575 | -46.132 | -36.0322 | -45.4719 | -41.5226 | -56.9289 | -50.1416 | -43.2909 | 555 | -20.8786 | -35.4078 | -20.6727 | -35.7231 | -21.7813 | -38.1158 | -21.7057 | -45.8781 | 555 | -27.3767 | -36.8164 | -28.8424 | -38.9988 | -34.6802 | -37.7013 | -28.4549 | -37.0412 | -29.6378 | -38.1454 | -34.3974 | -38.2719 | -30.4731 | -34.2956 | -32.8671 | -49.3516 | -42.5643 | -34.8602 | -31.5513 | -34.5204 | -33.6625 | -48.4982 | -42.2815 | -35.4308
556 | -8.7936 | 0 | -7.6253 | 0 | -8.4764 | 0 | -7.844 | 0 | -49.3931 | -151.3875 | -22.0015 | 168.4066 | -47.9694 | 161.3057 | -37.4222 | -143.6375 | -41.8297 | -131.7285 | -38.4743 | -161.4203 | -49.7041 | -10.9434 | -22.9297 | -93.6354 | -53.0208 | 178.3206 | -41.7945 | -34.3212 | -52.0517 | 4.0328 | -54.7765 | 105.8592 | -11.068 | -25.5719 | -18.1701 | -7.3558 | -13.4842 | -59.5717 | -15.2463 | -52.3646 | -10.7988 | 66.4814 | -14.7159 | 20.5839 | -11.4706 | 36.3873 | -14.9438 | -47.9933 | -43.4131 | -41.2798 | -43.3509 | -37.8272 | -45.5068 | -41.8345 | -47.7933 | -37.5701 | -45.317 | -41.8988 | -55.8597 | -49.0701 | -42.0319 | 556 | -21.9826 | -35.8811 | -21.7845 | -36.5039 | -22.9163 | -40.8044 | -22.8709 | -48.3707 | 556 | -28.7765 | -36.5234 | -29.0336 | -37.8815 | -34.2092 | -39.3169 | -29.9448 | -36.8406 | -29.9832 | -37.0304 | -33.9905 | -39.9493 | -32.4862 | -34.5573 | -33.1052 | -48.2344 | -41.4448 | -33.5555 | -33.6545 | -34.8745 | -34.0548 | -47.3833 | -41.2261 | -34.1879
557 | -9.0973 | 0 | -7.6481 | 0 | -8.4684 | 0 | -7.8122 | 0 | -50.1917 | -134.4962 | -23.589 | 162.9515 | -50.656 | 148.1128 | -40.1074 | -163.7453 | -40.6217 | -148.3594 | -39.4877 | -156.6707 | -48.2647 | -4.4159 | -24.8639 | -101.7562 | -52.4198 | 109.935 | -47.4092 | -31.1378 | -57.4516 | -12.8862 | -45.0547 | 79.4679 | -9.6904 | -25.0075 | -17.3714 | -12.0242 | -13.8482 | -72.7585 | -17.4184 | -65.6266 | -9.3892 | 66.947 | -14.4886 | 15.8305 | -11.3719 | 24.9039 | -16.9607 | -60.2481 | -44.0452 | -44.6351 | -43.264 | -38.8148 | -44.9867 | -41.932 | -49.2497 | -39.5505 | -44.984 | -42.6872 | -56.0583 | -49.027 | -40.9887 | 557 | -23.571 | -37.1267 | -23.3854 | -36.824 | -24.8365 | -44.5757 | -24.7987 | -44.1169 | 557 | -30.4532 | -35.8867 | -29.7175 | -37.3386 | -34.2839 | -40.7813 | -31.9024 | -36.5156 | -31.0026 | -36.5183 | -34.1198 | -41.4375 | -35.5378 | -34.1667 | -33.5899 | -48.4102 | -41.3789 | -32.5203 | -36.987 | -34.7956 | -34.875 | -47.5899 | -41.2148 | -33.1765
558 | -9.3991 | 0 | -7.6523 | 0 | -8.4265 | 0 | -7.7762 | 0 | -47.4887 | -119.1571 | -24.9452 | 164.5832 | -53.9484 | 149.1483 | -45.8431 | -179.4055 | -40.633 | -166.6301 | -39.0453 | -151.1609 | -45.8385 | -4.3173 | -26.9932 | -100.5191 | -48.5704 | 65.754 | -48.9838 | 21.3391 | -64.9191 | 67.9489 | -41.6364 | 54.6269 | -8.4511 | -31.4793 | -17.3142 | -17.5922 | -14.9287 | -85.9755 | -20.6704 | -76.09 | -8.0312 | 60.9996 | -14.9468 | 11.4878 | -12.0776 | 14.4472 | -19.4181 | -79.2779 | -43.7564 | -47.7689 | -42.8704 | -40.3111 | -45.0377 | -42.6166 | -49.8437 | -40.3406 | -44.3327 | -43.8788 | -57.2968 | -50.3601 | -40.4273 | 558 | -24.9157 | -38.8503 | -24.7456 | -36.6746 | -26.9072 | -44.0861 | -26.8201 | -40.8183 | 558 | -30.9415 | -34.9336 | -30.912 | -37.3854 | -34.9643 | -41.4172 | -32.6883 | -35.9062 | -32.5349 | -36.6112 | -34.8404 | -42.0675 | -38.3698 | -33.4713 | -34.4797 | -49.6445 | -42.7078 | -32.0008 | -40.1166 | -34.4439 | -36.1026 | -48.8703 | -42.5839 | -32.6511
559 | -9.608 | 0 | -7.6479 | 0 | -8.3715 | 0 | -7.7479 | 0 | -44.0772 | -120.0607 | -25.1599 | 170.1919 | -54.8931 | 167.3418 | -61.6102 | -110.2745 | -41.7737 | 178.2365 | -37.7419 | -151.4344 | -43.7442 | -13.9432 | -27.7637 | -90.7459 | -45.5548 | 38.3015 | -43.7791 | 37.0655 | -54.2705 | 80.3515 | -40.3828 | 26.1539 | -7.6708 | -41.436 | -18.034 | -22.556 | -16.6502 | -97.4115 | -25.0401 | -80.5528 | -7.1842 | 52.0388 | -15.8845 | 10.2567 | -13.4701 | 7.5889 | -23.6876 | -87.7615 | -42.9395 | -46.3702 | -42.4113 | -41.7208 | -45.5059 | -43.8194 | -49.7416 | -38.9575 | -43.4634 | -45.0971 | -59.1166 | -53.9028 | -40.4777 | 559 | -25.1 | -39.7359 | -24.9257 | -36.236 | -27.5856 | -40.5623 | -27.4305 | -39.0962 | 559 | -29.3495 | -33.8554 | -32.1128 | -37.858 | -36.1715 | -41.3701 | -31.3096 | -35.0919 | -33.9729 | -37.1344 | -36.0715 | -41.9937 | -36.7622 | -32.8033 | -35.4891 | -51.4687 | -46.2549 | -32.1062 | -38.7223 | -34.0398 | -37.3492 | -50.7451 | -46.1549 | -32.7298
560 | -9.6547 | 0 | -7.6544 | 0 | -8.3518 | 0 | -7.6885 | 0 | -41.5437 | -129.5989 | -24.3457 | 171.773 | -52.6659 | 173.0844 | -45.7749 | -56.9032 | -43.8343 | 169.4683 | -36.4711 | -158.077 | -42.3791 | -25.3844 | -26.9643 | -86.2484 | -43.7086 | 16.0681 | -40.4707 | 31.517 | -50.7107 | 59.4888 | -40.5259 | -2.9103 | -7.3751 | -52.3795 | -18.8742 | -20.2142 | -19.0271 | -103.0646 | -30.5531 | -56.4045 | -6.8605 | 40.7846 | -16.7732 | 14.8111 | -15.0554 | 6.4997 | -29.1064 | -85.772 | -42.1023 | -43.245 | -42.1651 | -41.9734 | -46.3601 | -44.9129 | -49.4435 | -36.9377 | -42.6039 | -45.6818 | -61.1075 | -62.7268 | -41.4462 | 560 | -24.2574 | -38.6044 | -24.058 | -35.6521 | -26.7528 | -38.0676 | -26.5954 | -38.5493 | 560 | -27.283 | -32.9492 | -32.3187 | -38.7057 | -37.2585 | -41.0917 | -29.2833 | -34.2521 | -34.2849 | -38.0083 | -37.2244 | -41.755 | -33.5903 | -32.5104 | -36.0271 | -53.4531 | -55.0724 | -33.0944 | -35.5906 | -33.8133 | -37.9933 | -52.7557 | -55.0383 | -33.7577
561 | -9.5194 | 0 | -7.66 | 0 | -8.3905 | 0 | -7.6834 | 0 | -39.8828 | -142.5358 | -23.3474 | 167.1567 | -50.7484 | 162.1486 | -40.5364 | -73.1767 | -46.1011 | 171.5099 | -35.4904 | -169.1697 | -41.6222 | -38.0673 | -25.9016 | -88.9101 | -42.9848 | -3.9232 | -38.3752 | 20.2984 | -49.8266 | 39.6186 | -41.7817 | -37.1375 | -7.5822 | -63.3656 | -19.1866 | -13.2175 | -21.0479 | -98.3088 | -30.4859 | -21.8983 | -7.0624 | 30.1482 | -16.7636 | 23.6315 | -15.9722 | 12.6734 | -32.694 | -46.6726 | -41.436 | -40.9672 | -42.1938 | -40.8266 | -47.4126 | -44.3305 | -49.0975 | -35.3201 | -41.9491 | -45.3319 | -62.8436 | -57.3436 | -43.6138 | 561 | -23.2443 | -36.6624 | -23.0125 | -35.0111 | -25.7048 | -36.4857 | -25.5577 | -38.9602 | 561 | -25.8007 | -32.4297 | -31.3072 | -39.7526 | -36.6705 | -40.707 | -27.6601 | -33.5586 | -33.1432 | -39.0221 | -36.6471 | -41.4141 | -31.4478 | -32.6744 | -35.8125 | -55.1836 | -49.6836 | -35.2233 | -33.3072 | -33.8033 | -37.6485 | -54.4531 | -49.6602 | -35.9304
562 | -9.2688 | 0 | -7.6827 | 0 | -8.4749 | 0 | -7.6764 | 0 | -39.0564 | -155.9915 | -22.6847 | 158.7877 | -50.0908 | 143.2578 | -38.1109 | -92.017 | -46.8076 | -175.7768 | -34.8749 | 175.7804 | -41.4398 | -49.9388 | -25.1436 | -97.2259 | -43.4559 | -21.2557 | -37.1772 | 5.8697 | -50.4497 | 25.2753 | -43.4301 | -81.0925 | -8.2982 | -73.608 | -18.3697 | -7.2189 | -21.0831 | -90.4269 | -28.6628 | -13.451 | -7.6909 | 20.5838 | -15.6898 | 28.4384 | -15.4428 | 17.4755 | -29.8113 | -20.5093 | -41.2009 | -39.5907 | -42.412 | -39.3923 | -48.115 | -42.1454 | -48.8507 | -34.3108 | -41.7688 | -44.5225 | -64.7374 | -50.3147 | -47.8154 | 562 | -22.578 | -35.2343 | -22.3142 | -34.4841 | -24.9807 | -35.6488 | -24.8196 | -40.0203 | 562 | -25.042 | -32.5 | -30.1235 | -40.4323 | -34.4627 | -40.3758 | -26.6281 | -33.2939 | -31.7159 | -39.6401 | -34.469 | -41.1743 | -30.3219 | -33.1432 | -35.2537 | -57.0547 | -42.632 | -39.3405 | -31.908 | -33.9371 | -36.8461 | -56.2625 | -42.6383 | -40.139
563 | -8.9871 | 0 | -7.7295 | 0 | -8.5616 | 0 | -7.6973 | 0 | -39.0972 | -169.7685 | -22.5529 | 148.09 | -51.07 | 122.2592 | -37.2194 | -111.7996 | -45.4363 | -164.8601 | -34.8543 | 157.7746 | -41.8759 | -59.9146 | -24.8455 | -107.1088 | -44.8821 | -30.0901 | -36.9211 | -9.5999 | -50.98 | 19.8149 | -43.5728 | -133.498 | -9.5093 | -80.8573 | -17.2881 | -7.79 | -19.7992 | -93.1054 | -28.8425 | -19.0171 | -8.9057 | 14.435 | -14.7006 | 27.4374 | -14.5982 | 15.5116 | -28.2177 | -22.6187 | -41.4821 | -39.111 | -42.8451 | -38.4156 | -47.3492 | -40.029 | -48.8623 | -33.9601 | -41.991 | -43.8506 | -68.9209 | -46.4249 | -52.1443 | 563 | -22.4517 | -34.6673 | -22.1666 | -34.3958 | -24.7183 | -35.5895 | -24.5298 | -40.7366 | 563 | -24.973 | -33.0039 | -29.4285 | -39.6197 | -32.2995 | -40.3007 | -26.2306 | -33.4294 | -30.7183 | -38.7876 | -32.3317 | -41.165 | -30.1239 | -33.858 | -34.8635 | -61.1914 | -38.6954 | -43.5827 | -31.3815 | -34.2835 | -36.1533 | -60.3593 | -38.7276 | -44.447
564 | -8.7564 | 0 | -7.7508 | 0 | -8.6265 | 0 | -7.7166 | 0 | -40.0569 | -178.272 | -23.0233 | 137.4227 | -53.8104 | 101.3434 | -37.6235 | -131.2222 | -43.1161 | -165.3473 | -35.7194 | 139.3676 | -42.7976 | -63.3305 | -25.2005 | -120.8753 | -46.0713 | -28.8298 | -37.6861 | -24.0251 | -50.3345 | 10.0192 | -42.0801 | 179.4276 | -10.8712 | -81.717 | -16.5579 | -11.6711 | -18.7535 | -104.4379 | -30.1899 | -9.8811 | -10.2129 | 15.0048 | -14.2806 | 22.377 | -14.1248 | 7.8807 | -28.5837 | -35.7064 | -42.3861 | -39.6447 | -43.3605 | -38.0385 | -45.515 | -38.6837 | -49.4813 | -34.3531 | -42.6118 | -43.45 | -84.3016 | -44.1031 | -47.963 | 564 | -22.9346 | -34.9439 | -22.6553 | -34.9362 | -25.0908 | -36.3426 | -24.8786 | -40.1813 | 564 | -25.5967 | -33.8554 | -29.2821 | -37.7642 | -30.9329 | -40.8548 | -26.6023 | -33.9853 | -30.3219 | -36.8885 | -30.9671 | -41.7647 | -30.8883 | -34.6041 | -34.6936 | -76.5508 | -36.3523 | -39.3365 | -31.8939 | -34.734 | -35.7334 | -75.6751 | -36.3865 | -40.2464
565 | -8.7422 | 0 | -7.8008 | 0 | -8.6406 | 0 | -7.7656 | 0 | -41.501 | -178.4121 | -24.0786 | 128.2301 | -59.3706 | 83.0488 | -39.6084 | -149.386 | -41.1091 | -174.9268 | -37.5959 | 121.2177 | -43.1952 | -58.4985 | -26.4979 | -133.5372 | -45.7368 | -21.8517 | -39.5395 | -34.8462 | -50.2758 | -6.7196 | -40.2039 | 139.8956 | -11.2379 | -76.3296 | -16.5582 | -16.8949 | -18.4097 | -120.8649 | -31.93 | 12.5361 | -10.3874 | 21.6518 | -14.5063 | 17.7354 | -14.3926 | -1.6952 | -30.8792 | -44.4374 | -43.7408 | -41.3424 | -43.3228 | -38.4049 | -43.8463 | -37.9439 | -50.8867 | -35.5313 | -43.457 | -43.5703 | -63.7852 | -42.918 | -44.0631 | 565 | -23.9994 | -35.8893 | -23.7747 | -35.9763 | -26.3556 | -37.7343 | -26.1147 | -38.8112 | 565 | -26.7891 | -34.7148 | -29.6627 | -36.0455 | -30.1431 | -42.2461 | -27.7305 | -34.8164 | -30.6393 | -35.2057 | -30.1783 | -43.1211 | -32.6002 | -34.5806 | -34.8281 | -55.9844 | -35.1172 | -35.4225 | -33.5416 | -34.6822 | -35.8047 | -55.1446 | -35.1524 | -36.2975
566 | -8.8921 | 0 | -7.8372 | 0 | -8.6537 | 0 | -7.7979 | 0 | -41.517 | -167.7561 | -25.4155 | 123.8672 | -87.7584 | -21.8674 | -44.3 | -166.039 | -40.1112 | 169.7309 | -40.9584 | 105.6172 | -41.88 | -51.8602 | -28.8658 | -142.5386 | -44.36 | -20.2759 | -42.2423 | -34.9994 | -52.0525 | -22.9833 | -39.1588 | 108.3727 | -10.2195 | -73.6323 | -16.8835 | -17.3491 | -18.8137 | -139.1871 | -30.0592 | 38.7295 | -9.2372 | 24.0336 | -15.2875 | 18.065 | -15.3551 | -11.3743 | -36.7918 | -53.5344 | -44.6366 | -44.2577 | -42.3555 | -39.617 | -42.9217 | -37.8163 | -52.6848 | -37.3216 | -43.8296 | -44.4426 | -58.013 | -43.0951 | -42.0292 | 566 | -25.3102 | -36.8794 | -25.2417 | -37.5038 | -28.5389 | -38.8349 | -28.2989 | -37.8449 | 566 | -28.4295 | -34.9375 | -30.7249 | -35.0845 | -29.9791 | -44.0311 | -29.4844 | -35.1759 | -31.8191 | -34.268 | -30.0184 | -44.8869 | -35.3656 | -33.4634 | -35.5505 | -50.1758 | -35.2579 | -33.3755 | -36.4205 | -33.7018 | -36.6447 | -49.3593 | -35.2972 | -34.2313
567 | -9.1767 | 0 | -7.8784 | 0 | -8.6038 | 0 | -7.7877 | 0 | -39.4295 | -162.0774 | -26.4781 | 123.8411 | -58.3401 | -130.6045 | -57.6903 | -124.9693 | -40.3047 | 154.5056 | -46.2499 | 108.9988 | -39.9048 | -55.2679 | -31.5711 | -138.9882 | -42.7898 | -22.1157 | -44.1544 | -17.3703 | -55.0652 | -18.1259 | -39.4814 | 79.7963 | -8.9373 | -78.8279 | -16.9924 | -13.9777 | -19.805 | -157.2173 | -27.0832 | 47.229 | -7.9335 | 18.9011 | -15.7297 | 26.0224 | -17.304 | -17.3401 | -46.6176 | 37.245 | -44.1153 | -48.0907 | -41.0972 | -41.67 | -42.7989 | -38.368 | -53.1011 | -38.553 | -43.1572 | -45.5894 | -55.1831 | -44.76 | -41.2489 | 567 | -26.2607 | -36.7993 | -26.4293 | -39.2663 | -30.6993 | -38.4239 | -30.7183 | -37.7365 | 567 | -29.3763 | -33.9805 | -32.4933 | -34.9205 | -30.4896 | -44.4973 | -30.6746 | -34.5534 | -33.8823 | -34.1951 | -30.5803 | -45.3134 | -38.914 | -31.9205 | -36.4127 | -47.3047 | -36.8816 | -32.6451 | -40.2123 | -32.4934 | -37.8017 | -46.5793 | -36.9723 | -33.4612
568 | -9.4027 | 0 | -7.9525 | 0 | -8.5756 | 0 | -7.7874 | 0 | -37.2497 | -167.0114 | -26.8853 | 126.6483 | -52.3099 | -153.5689 | -44.588 | -48.8616 | -41.4914 | 141.7878 | -47.3358 | 151.1109 | -38.3819 | -64.1405 | -32.7925 | -128.1537 | -41.4517 | -28.0195 | -42.5997 | 4.2483 | -54.2043 | -1.052 | -41.687 | 58.9162 | -8.1114 | -88.4179 | -16.0992 | -8.9952 | -21.456 | -172.1306 | -24.6863 | 47.0152 | -7.1122 | 9.6372 | -14.671 | 33.8935 | -19.5393 | -14.1347 | -32.717 | 75.2383 | -42.7518 | -48.6836 | -40.206 | -43.5409 | -43.3417 | -39.539 | -51.2259 | -37.9467 | -41.8324 | -45.8509 | -53.9173 | -48.2826 | -41.5644 | 568 | -26.4919 | -35.3153 | -26.7739 | -40.2101 | -31.2933 | -36.9057 | -31.881 | -38.4407 | 568 | -28.544 | -32.4297 | -34.1382 | -35.3892 | -31.5865 | -42.6503 | -29.9942 | -33.2568 | -35.7535 | -34.7661 | -31.7516 | -43.4385 | -39.2809 | -30.8033 | -36.4482 | -45.9648 | -40.3301 | -32.9888 | -40.7311 | -31.6304 | -38.0635 | -45.3417 | -40.4952 | -33.777
569 | -9.5314 | 0 | -8.0236 | 0 | -8.6017 | 0 | -7.7775 | 0 | -35.6931 | -175.5071 | -26.8362 | 125.6546 | -49.2956 | -176.1841 | -38.3821 | -62.9873 | -43.2257 | 136.2454 | -42.6772 | 160.0701 | -37.4275 | -75.5989 | -32.3111 | -120.7713 | -40.5488 | -35.7807 | -39.2869 | 9.1721 | -51.9695 | -4.9276 | -46.5518 | 52.7125 | -7.8224 | -100.6948 | -14.7676 | -10.5167 | -23.1712 | -178.8453 | -22.5898 | 44.4693 | -6.811 | -0.6429 | -12.9579 | 35.2542 | -20.4561 | -0.9826 | -28.6602 | 77.7425 | -41.4128 | -45.4089 | -39.8073 | -43.3425 | -44.3308 | -40.8972 | -48.7932 | -36.3166 | -40.633 | -44.3713 | -53.426 | -50.5197 | -43.2819 | 569 | -26.2832 | -33.3507 | -26.4377 | -39.4567 | -30.6738 | -35.1567 | -31.3828 | -39.3328 | 569 | -26.7852 | -31.1016 | -33.8111 | -36.3072 | -32.8736 | -40.1915 | -28.293 | -32.0313 | -35.565 | -35.7291 | -33.1197 | -41.0157 | -35.8775 | -30.2759 | -34.8399 | -45.4024 | -42.4961 | -34.6802 | -37.3853 | -31.2056 | -36.5938 | -44.8243 | -42.7422 | -35.5044
570 | -9.5053 | 0 | -8.1057 | 0 | -8.7415 | 0 | -7.7562 | 0 | -34.6945 | 172.2325 | -26.6413 | 123.8316 | -48.0489 | 160.6288 | -35.2119 | -82.4191 | -44.6909 | 140.9368 | -39.4092 | 147.5466 | -36.8528 | -86.1863 | -31.5945 | -119.1669 | -40.2284 | -44.6178 | -36.6637 | 0.3723 | -51.1948 | -16.1295 | -49.7341 | 104.151 | -8.0848 | -113.2334 | -13.4436 | -16.6786 | -23.799 | -178.6156 | -21.1333 | 39.0676 | -7.0979 | -11.3858 | -11.6696 | 30.8745 | -19.8862 | 7.9293 | -26.2166 | 75.9134 | -40.4948 | -42.6815 | -39.8749 | -41.6394 | -45.6589 | -41.4002 | -46.7463 | -34.8235 | -39.8178 | -42.383 | -53.2619 | -46.1829 | -46.738 | 570 | -25.9825 | -31.7108 | -25.8791 | -37.8463 | -30.0262 | -33.6695 | -30.3672 | -39.4653 | 570 | -25.3182 | -30.3125 | -32.1341 | -37.5532 | -33.2945 | -38.0048 | -26.7178 | -31.0763 | -33.8832 | -36.9174 | -33.644 | -38.9901 | -33.1762 | -30.3696 | -32.8777 | -45.1562 | -38.0772 | -37.9965 | -34.5758 | -31.1334 | -34.6268 | -44.5204 | -38.4267 | -38.9818
571 | -9.3469 | 0 | -8.1886 | 0 | -8.8968 | 0 | -7.7726 | 0 | -34.2035 | 160.6219 | -26.4789 | 119.9975 | -48.0003 | 139.9648 | -33.6377 | -101.9499 | -44.7041 | 150.0292 | -37.3318 | 127.48 | -36.6512 | -98.182 | -31.0513 | -123.1253 | -40.3699 | -49.4675 | -35.0168 | -12.3004 | -51.5651 | -28.343 | -43.2126 | 124.1371 | -8.8177 | -125.7401 | -12.788 | -26.8795 | -22.4676 | -179.3751 | -20.0989 | 32.2849 | -7.771 | -20.9186 | -10.7959 | 22.4361 | -18.9506 | 7.2471 | -23.784 | 70.2388 | -39.9098 | -41.0047 | -40.3962 | -39.9684 | -46.8825 | -40.4851 | -45.173 | -33.8147 | -39.554 | -40.88 | -52.9777 | -42.5022 | -51.737 | 571 | -25.7752 | -30.7238 | -25.4254 | -36.2976 | -29.6136 | -32.6906 | -29.4016 | -38.3406 | 571 | -24.4678 | -30.2071 | -30.6215 | -38.6939 | -32.2965 | -36.2762 | -25.6261 | -30.6572 | -32.1958 | -37.9857 | -32.7125 | -37.4004 | -31.6578 | -31.0493 | -31.5331 | -44.7891 | -34.3136 | -42.8402 | -32.8161 | -31.4994 | -33.1074 | -44.0809 | -34.7296 | -43.9644
572 | -9.0665 | 0 | -8.2066 | 0 | -9.0455 | 0 | -7.7793 | 0 | -34.2739 | 148.8207 | -26.5178 | 113.9922 | -49.3921 | 125.5392 | -33.2018 | -120.5229 | -43.4379 | 155.083 | -36.1478 | 103.3574 | -37.0221 | -110.4118 | -30.8235 | -130.7236 | -40.4758 | -51.2957 | -34.1067 | -27.6445 | -52.7063 | -32.4689 | -39.2924 | 115.3872 | -10.1337 | -135.83 | -12.7534 | -37.4045 | -20.923 | 169.3178 | -19.3388 | 22.6802 | -8.9484 | -27.5889 | -10.738 | 14.0701 | -18.6282 | 2.5121 | -21.3528 | 62.5685 | -39.7168 | -40.1183 | -41.1509 | -38.7871 | -47.6426 | -38.9894 | -44.1558 | -33.2799 | -39.7891 | -39.9683 | -52.4566 | -40.4791 | -50.5342 | 572 | -25.8255 | -30.4696 | -25.3006 | -35.2346 | -29.5256 | -32.2744 | -28.7503 | -36.7227 | 572 | -24.2134 | -30.7226 | -29.7206 | -39.436 | -30.7828 | -35.1103 | -25.0733 | -30.7436 | -31.0078 | -38.5971 | -31.2101 | -36.3765 | -31.0518 | -32.0844 | -30.9018 | -44.25 | -32.2725 | -41.4887 | -31.9117 | -32.1054 | -32.189 | -43.4111 | -32.6998 | -42.7549
573 | -8.8129 | 0 | -8.2465 | 0 | -9.1176 | 0 | -7.8129 | 0 | -34.9914 | 137.7702 | -26.9188 | 106.9028 | -51.0201 | 122.5116 | -33.6452 | -137.0695 | -41.7544 | 154.0575 | -35.7208 | 77.2781 | -38.084 | -117.3135 | -31.3665 | -141.0524 | -39.8295 | -50.9112 | -34.0012 | -43.4428 | -52.3357 | -26.4501 | -36.8957 | 105.9291 | -11.9705 | -138.8919 | -13.4264 | -45.4361 | -19.8303 | 153.8729 | -18.4236 | 15.2296 | -10.2115 | -27.9545 | -11.2436 | 7.1199 | -18.8605 | -3.6599 | -19.7152 | 52.2389 | -40.0848 | -40.0262 | -41.9559 | -38.2762 | -47.0223 | -37.7684 | -43.9027 | -33.2465 | -40.516 | -39.5746 | -52.2972 | -39.4691 | -45.4226 | 573 | -26.2752 | -30.8851 | -25.6339 | -34.6529 | -30.0458 | -32.5236 | -28.7536 | -35.0277 | 573 | -24.4336 | -31.7031 | -29.4633 | -38.7758 | -29.5219 | -34.7851 | -25 | -31.3984 | -30.4633 | -37.9047 | -29.9555 | -36.0898 | -31.2133 | -33.143 | -30.7617 | -44.0507 | -31.2226 | -36.305 | -31.7797 | -32.8383 | -31.7617 | -43.1796 | -31.6562 | -37.6097
574 | -8.6729 | 0 | -8.2732 | 0 | -9.1186 | 0 | -7.841 | 0 | -36.3555 | 133.2003 | -27.7586 | 100.7806 | -50.9743 | 126.2509 | -35.0054 | -149.1342 | -39.9411 | 146.088 | -36.0113 | 48.7634 | -39.286 | -116.8188 | -33.3583 | -153.9791 | -38.7706 | -54.9173 | -34.958 | -59.1483 | -50.3832 | -33.5278 | -34.6991 | 96.0704 | -13.0199 | -132.92 | -14.6632 | -49.9206 | -19.397 | 138.382 | -18.3095 | 3.4976 | -10.7493 | -22.8137 | -12.1944 | 5.589 | -19.8502 | -8.9364 | -18.506 | 42.5475 | -41.1194 | -40.6952 | -42.4058 | -38.6858 | -45.26 | -36.9452 | -44.6521 | -33.7436 | -41.4112 | -39.6209 | -52.4842 | -38.9389 | -41.9432 | 574 | -27.1785 | -31.8799 | -26.4939 | -34.4383 | -31.4747 | -33.5035 | -29.5089 | -33.1804 | 574 | -25.0707 | -32.7383 | -30.0129 | -36.9868 | -28.672 | -35.5335 | -25.4704 | -32.2926 | -30.8448 | -36.1414 | -29.1042 | -36.8111 | -32.0223 | -33.7329 | -30.948 | -44.211 | -30.6657 | -32.8246 | -32.422 | -33.2872 | -31.7799 | -43.3656 | -31.0979 | -34.1022
575 | -8.7132 | 0 | -8.319 | 0 | -9.0385 | 0 | -7.8387 | 0 | -36.9531 | 139.7955 | -28.764 | 96.9989 | -50.3589 | 122.599 | -37.3641 | -153.2188 | -38.7383 | 132.9323 | -37.2171 | 20.3541 | -39.0269 | -112.1174 | -37.2307 | -153.7292 | -38.0872 | -61.9534 | -37.2463 | -68.418 | -49.8467 | -49.0565 | -33.0453 | 80.4158 | -12.1651 | -127.7198 | -15.3067 | -44.359 | -19.7833 | 124.0733 | -18.3887 | -3.7236 | -10.1246 | -21.5315 | -12.7587 | 11.463 | -22.135 | -7.7668 | -18.8308 | 30.2661 | -42.2496 | -42.1683 | -41.901 | -40.3534 | -43.966 | -36.5951 | -46.1558 | -34.8584 | -42.0139 | -39.7777 | -51.9447 | -39.149 | -40.1064 | 575 | -28.1244 | -32.8493 | -27.6891 | -34.7793 | -33.2822 | -34.8946 | -30.5863 | -31.7935 | 575 | -26.1452 | -33.3007 | -31.6402 | -35.647 | -28.2761 | -37.1173 | -26.5394 | -32.9754 | -32.5147 | -34.9275 | -28.7564 | -38.3171 | -33.4551 | -33.1878 | -31.0645 | -43.6257 | -30.83 | -31.0679 | -33.8493 | -32.8625 | -31.939 | -42.9062 | -31.3103 | -32.2677
576 | -8.8693 | 0 | -8.4402 | 0 | -8.9466 | 0 | -7.8362 | 0 | -35.9668 | 145.6632 | -29.7515 | 96.5235 | -50.5235 | 119.733 | -39.3318 | -141.0199 | -38.3761 | 117.8182 | -39.5379 | -10.2516 | -37.9122 | -111.4486 | -41.0063 | -130.1308 | -37.5984 | -67.7916 | -40.2232 | -61.3164 | -50.0835 | -63.5517 | -32.3682 | 63.8603 | -10.7929 | -131.1944 | -14.5865 | -38.439 | -20.4247 | 113.7196 | -19.0739 | -13.0759 | -9.0642 | -24.2483 | -12.0249 | 17.5301 | -23.3823 | 4.4571 | -18.9795 | 23.6172 | -42.5048 | -44.2779 | -40.9258 | -42.6215 | -43.4195 | -36.6545 | -47.561 | -36.1672 | -41.9268 | -39.6335 | -51.0208 | -40.2024 | -39.1206 | 576 | -28.7914 | -32.8812 | -28.9051 | -35.7605 | -33.8207 | -35.7426 | -31.2264 | -31.1729 | 576 | -27.2979 | -33.0575 | -33.7522 | -34.9793 | -28.2143 | -38.6144 | -27.727 | -32.9802 | -34.7853 | -34.4729 | -28.8183 | -39.7248 | -35.4086 | -32.0565 | -30.7642 | -42.5806 | -31.7622 | -30.174 | -35.8377 | -31.9792 | -31.7973 | -42.0742 | -32.3662 | -31.2844
577 | -9.0982 | 0 | -8.6138 | 0 | -8.8834 | 0 | -7.8248 | 0 | -34.2026 | 144.542 | -30.7975 | 95.4448 | -50.8663 | 122.8688 | -38.3417 | -119.3933 | -38.7979 | 102.5344 | -43.7196 | -40.5983 | -36.7349 | -115.5782 | -40.7464 | -94.4234 | -37.0745 | -74.5466 | -40.9155 | -34.3809 | -50.6005 | -76.2616 | -32.6754 | 48.0219 | -9.7003 | -140.422 | -12.9526 | -37.2312 | -21.076 | 108.3522 | -20.1422 | -17.4797 | -8.3787 | -32.1507 | -10.6178 | 19.1364 | -22.9987 | 20.6705 | -19.9307 | 15.9298 | -41.6709 | -47.0459 | -39.9248 | -43.9677 | -43.6357 | -37.1826 | -48.1334 | -37.1763 | -41.1646 | -38.9498 | -50.2388 | -42.4341 | -38.911 | 577 | -29.135 | -31.8154 | -29.9089 | -37.3863 | -33.0766 | -35.203 | -31.5164 | -31.2789 | 577 | -28.0781 | -32.0664 | -34.8695 | -35.0219 | -28.5688 | -39.25 | -28.5625 | -32.2812 | -36.1429 | -34.7523 | -29.3578 | -40.3086 | -37.9477 | -30.8266 | -29.8516 | -41.625 | -33.8203 | -30.0276 | -38.4321 | -31.0414 | -31.125 | -41.3554 | -34.6093 | -31.0862
578 | -9.2716 | 0 | -8.8529 | 0 | -8.9253 | 0 | -7.802 | 0 | -32.7452 | 136.3489 | -32.1094 | 99.4046 | -48.9673 | 123.718 | -34.8197 | -118.5766 | -40.1693 | 90.4057 | -53.8793 | -63.5374 | -35.9599 | -123.1339 | -37.7767 | -79.4738 | -36.5241 | -81.469 | -36.6867 | -25.8741 | -51.4588 | -88.6569 | -34.0307 | 39.0935 | -9.2278 | -153.7662 | -11.5196 | -46.1958 | -20.8426 | 110.8246 | -21.5548 | -22.1772 | -8.2541 | -41.8897 | -9.305 | 13.7077 | -21.3504 | 24.3823 | -20.9952 | 16.8462 | -40.324 | -49.4628 | -39.2505 | -41.6091 | -44.5349 | -38.2557 | -47.6224 | -36.937 | -39.9747 | -37.8959 | -50.1263 | -46.1206 | -39.8552 | 578 | -29.3576 | -30.1896 | -30.2274 | -39.471 | -31.9179 | -33.232 | -31.098 | -32.0406 | 578 | -27.6654 | -30.7031 | -32.3375 | -35.682 | -29.4028 | -38.6971 | -28.0841 | -31.0494 | -33.8071 | -35.6096 | -30.4537 | -39.8204 | -40.1912 | -29.9789 | -28.6243 | -41.2734 | -37.2677 | -30.9299 | -40.6099 | -30.3252 | -30.0939 | -41.201 | -38.3186 | -32.0532
579 | -9.3189 | 0 | -9.0334 | 0 | -9.1008 | 0 | -7.7428 | 0 | -31.8239 | 125.7959 | -32.7146 | 110.1133 | -47.108 | 113.644 | -32.4969 | -128.9131 | -42.3273 | 84.3846 | -52.8925 | 69.7587 | -35.3719 | -130.142 | -34.8558 | -74.4434 | -36.3511 | -91.3086 | -33.791 | -37.2379 | -52.9772 | -97.9281 | -35.1556 | 41.5186 | -9.3585 | -167.0787 | -10.6894 | -57.8997 | -19.5471 | 109.4831 | -22.4623 | -19.3717 | -8.632 | -52.8478 | -8.506 | 5.379 | -20.4778 | 21.8475 | -21.9919 | 20.844 | -39.3873 | -49.5679 | -38.8876 | -39.274 | -45.7271 | -39.4 | -46.8381 | -35.7609 | -38.94 | -37.0178 | -50.6155 | -46.425 | -41.5151 | 579 | -29.1658 | -28.9336 | -29.5738 | -40.8032 | -30.7116 | -31.4688 | -29.7892 | -32.6615 | 579 | -26.442 | -29.6211 | -29.9551 | -36.6937 | -30.3666 | -37.7373 | -26.7275 | -29.8392 | -31.5312 | -36.6263 | -31.6572 | -39.0953 | -40.249 | -29.5687 | -27.6989 | -41.5821 | -37.3916 | -32.4143 | -40.5345 | -29.7868 | -29.275 | -41.5147 | -38.6822 | -33.7723
580 | -9.2544 | 0 | -9.1388 | 0 | -9.3375 | 0 | -7.7543 | 0 | -31.4317 | 113.0627 | -31.7289 | 118.7127 | -46.3609 | 97.4525 | -31.275 | -142.0841 | -44.5883 | 91.9905 | -44.266 | 49.0609 | -34.9021 | -138.6184 | -32.3665 | -78.9242 | -36.6738 | -99.9588 | -32.2667 | -51.681 | -54.4841 | -100.0326 | -34.616 | 47.5526 | -10.0749 | 179.5379 | -10.5041 | -71.9376 | -18.1457 | 99.5599 | -22.3599 | -12.9882 | -9.5517 | -62.3905 | -8.3636 | -4.0655 | -20.0524 | 19.0991 | -21.7045 | 29.7965 | -38.8832 | -47.7812 | -38.9637 | -37.8989 | -46.6098 | -39.9844 | -46.0763 | -34.4313 | -38.2974 | -36.5489 | -51.4005 | -42.4508 | -43.2284 | 580 | -28.4959 | -28.2405 | -28.3725 | -40.2078 | -29.5139 | -30.3604 | -28.1852 | -32.4863 | 580 | -25.1769 | -29.043 | -28.6445 | -37.471 | -30.8456 | -36.7388 | -25.2925 | -28.9599 | -30.1446 | -37.2723 | -32.2301 | -38.322 | -38.5268 | -29.7093 | -27.2945 | -42.2617 | -33.312 | -33.8909 | -38.6424 | -29.6262 | -28.7946 | -42.063 | -34.6965 | -35.4741
581 | -9.0515 | 0 | -9.1062 | 0 | -9.5437 | 0 | -7.7781 | 0 | -31.6822 | 100.3963 | -30.3115 | 118.46 | -46.7122 | 81.9581 | -30.6994 | -154.842 | -44.0079 | 110.618 | -40.2474 | 25.4811 | -34.7345 | -147.6366 | -30.8559 | -87.6253 | -37.3272 | -105.84 | -31.5496 | -66.8882 | -54.9324 | -98.8431 | -32.9946 | 47.6633 | -11.399 | 169.6051 | -10.9423 | -85.7141 | -17.3647 | 87.2252 | -21.7762 | -13.3929 | -10.8954 | -70.0288 | -8.5925 | -12.3706 | -20.1936 | 18.2882 | -20.2724 | 35.7398 | -38.792 | -45.9756 | -39.2881 | -37.1475 | -46.7413 | -39.4756 | -45.3835 | -33.4617 | -38.0593 | -36.3874 | -51.3562 | -39.5163 | -44.0712 | 581 | -27.8756 | -28.0414 | -27.2665 | -38.0821 | -28.7214 | -29.8327 | -26.9404 | -31.6111 | 581 | -24.4102 | -29.0078 | -28.096 | -37.6351 | -30.3694 | -35.8398 | -24.3555 | -28.5156 | -29.3694 | -37.1976 | -31.6975 | -37.6054 | -36.9241 | -30.2366 | -27.3359 | -42.25 | -30.4101 | -34.5275 | -36.8694 | -29.7444 | -28.6093 | -41.8125 | -31.7382 | -36.2931
582 | -8.8212 | 0 | -8.9812 | 0 | -9.6699 | 0 | -7.8118 | 0 | -32.7749 | 89.2338 | -29.4555 | 111.1485 | -48.1339 | 72.5017 | -30.5305 | -166.9815 | -41.2351 | 113.7871 | -37.7997 | 0.6766 | -35.1204 | -156.6482 | -30.4348 | -97.5609 | -37.9463 | -108.507 | -31.3022 | -82.2273 | -54.8657 | -100.4062 | -31.4947 | 41.0307 | -13.144 | 165.1628 | -12.1676 | -96.8952 | -17.0812 | 72.948 | -21.4541 | -17.7649 | -12.4308 | -70.2483 | -9.4017 | -18.645 | -20.2714 | 18.7265 | -19.467 | 31.8947 | -39.1241 | -44.6956 | -39.6828 | -36.8311 | -46.5811 | -38.4651 | -45.1648 | -32.9746 | -38.286 | -36.5086 | -49.9031 | -37.8223 | -43.5998 | 582 | -27.7552 | -28.2736 | -26.6064 | -35.9077 | -28.624 | -29.7808 | -26.2811 | -30.5922 | 582 | -24.1534 | -29.4648 | -28.0099 | -37.5999 | -29.4839 | -35.4949 | -23.9934 | -28.6161 | -29.0193 | -36.9112 | -30.6533 | -37.353 | -35.8744 | -30.8616 | -27.6874 | -40.9219 | -28.8411 | -33.9299 | -35.7144 | -30.0129 | -28.6968 | -40.2332 | -30.0105 | -35.788
583 | -8.6578 | 0 | -8.8879 | 0 | -9.6589 | 0 | -7.8697 | 0 | -34.6909 | 86.0792 | -29.367 | 103.4982 | -49.4572 | 69.0753 | -30.873 | -179.9947 | -38.8725 | 104.7728 | -36.2708 | -25.2582 | -35.9026 | -161.3403 | -30.8816 | -104.2805 | -38.1644 | -108.6215 | -31.6126 | -98.2207 | -53.7046 | -99.3371 | -30.4241 | 31.8857 | -14.3335 | 170.1991 | -14.0881 | -101.8904 | -17.5343 | 59.256 | -21.7474 | -19.6227 | -13.2963 | -65.5683 | -10.4616 | -20.05 | -20.1785 | 18.2864 | -18.7 | 31.6458 | -39.855 | -44.0127 | -39.9335 | -36.9136 | -46.5112 | -37.5713 | -45.6692 | -33.073 | -38.8922 | -36.9426 | -48.2707 | -36.9519 | -41.87 | 583 | -28.2166 | -28.9039 | -26.5545 | -34.2368 | -29.1159 | -30.2183 | -26.1743 | -29.7313 | 583 | -24.4152 | -30.2344 | -28.2558 | -37.6233 | -28.6834 | -36.0103 | -24.1851 | -29.2333 | -29.0439 | -36.8523 | -29.7016 | -37.7995 | -35.3549 | -31.2757 | -28.2848 | -39.3828 | -28.064 | -32.2111 | -35.1248 | -30.2746 | -29.0729 | -38.6118 | -29.0822 | -34.0003
584 | -8.6498 | 0 | -8.8853 | 0 | -9.5359 | 0 | -7.9357 | 0 | -35.4324 | 97.1511 | -30.077 | 96.4407 | -50.2383 | 71.1626 | -32.1782 | 169.4352 | -37.3764 | 90.305 | -35.724 | -50.414 | -35.9743 | -160.2503 | -31.5694 | -102.3916 | -37.9628 | -110.3066 | -33.1953 | -114.8225 | -50.911 | -112.1414 | -29.7367 | 21.1804 | -13.6323 | 174.7255 | -15.279 | -95.346 | -18.7881 | 48.2885 | -22.1934 | -14.7716 | -12.7737 | -61.8318 | -10.8471 | -15.3929 | -20.1008 | 18.4688 | -18.4538 | 32.5332 | -40.6042 | -44.0298 | -39.7461 | -37.7411 | -46.2137 | -36.9809 | -47.1868 | -33.8674 | -39.5594 | -37.3813 | -47.4529 | -36.6885 | -40.1166 | 584 | -28.9342 | -29.6867 | -27.3149 | -33.3715 | -29.5497 | -31.3081 | -26.5007 | -29.0993 | 584 | -25.2176 | -30.9096 | -29.0913 | -37.3284 | -28.0956 | -37.6509 | -24.9821 | -30.0235 | -29.8054 | -36.6778 | -29.0452 | -39.2511 | -35.38 | -31.0963 | -28.7315 | -38.5676 | -27.8032 | -30.5807 | -35.1445 | -30.2102 | -29.4456 | -37.917 | -28.7528 | -32.1809
585 | -8.7504 | 0 | -9.0273 | 0 | -9.3854 | 0 | -8.0222 | 0 | -34.0586 | 106.1775 | -31.4806 | 92.8615 | -50.1716 | 69.6094 | -34.0451 | 168.4011 | -36.6778 | 72.5506 | -35.8403 | -75.6161 | -35.3514 | -161.1092 | -31.5286 | -95.4302 | -37.6639 | -111.6778 | -36.3344 | -122.2774 | -48.8577 | -137.3074 | -29.4585 | 9.4565 | -12.346 | 172.0081 | -14.6205 | -88.136 | -20.498 | 42.5099 | -21.6883 | -6.9075 | -11.9478 | -64.5765 | -10.3843 | -11.7265 | -20.0871 | 19.7313 | -18.1343 | 34.7537 | -40.7576 | -44.4503 | -39.223 | -39.0106 | -45.9913 | -36.755 | -49.1438 | -35.111 | -40.052 | -37.3584 | -47.2391 | -36.8973 | -39.1058 | 585 | -29.5331 | -29.9928 | -28.6464 | -33.1417 | -29.3323 | -32.6984 | -26.8431 | -28.804 | 585 | -26.3606 | -31.3016 | -30.2602 | -36.964 | -27.7277 | -39.7584 | -26.0837 | -30.6666 | -30.9884 | -36.6059 | -28.7328 | -41.1216 | -35.6999 | -30.4726 | -28.608 | -38.2118 | -27.87 | -29.7204 | -35.423 | -29.8376 | -29.3362 | -37.8537 | -28.8751 | -31.0836
586 | -8.9287 | 0 | -9.2559 | 0 | -9.2519 | 0 | -8.1137 | 0 | -31.8783 | 105.0793 | -33.6917 | 97.1113 | -50.7418 | 63.8483 | -35.2162 | -179.611 | -36.8075 | 54.4404 | -36.7786 | -99.5712 | -34.5516 | -165.3731 | -30.4487 | -87.2604 | -37.2815 | -113.4093 | -40.6194 | -105.1995 | -47.7443 | -169.0998 | -29.737 | -3.1403 | -11.2313 | 163.6765 | -12.8717 | -88.7673 | -21.9082 | 46.8964 | -19.846 | 0.921 | -11.2239 | -71.1482 | -9.3113 | -11.2008 | -19.7876 | 21.6813 | -16.8436 | 41.5902 | -40.0784 | -45.1564 | -38.4972 | -39.7112 | -46.301 | -36.9259 | -50.9161 | -36.5449 | -40.1709 | -36.6739 | -47.3653 | -37.7206 | -38.8887 | 586 | -29.6468 | -29.3617 | -30.2769 | -33.6961 | -28.418 | -33.4281 | -26.8804 | -28.9748 | 586 | -27.6162 | -31.2422 | -30.7825 | -37.0451 | -27.67 | -41.6642 | -27.289 | -30.919 | -31.5975 | -37.0491 | -28.8122 | -42.8024 | -36.2277 | -29.5685 | -27.7452 | -38.1094 | -28.4647 | -29.6368 | -35.9005 | -29.2453 | -28.5602 | -38.1134 | -29.6069 | -30.775
587 | -9.092 | 0 | -9.537 | 0 | -9.2213 | 0 | -8.2172 | 0 | -30.2731 | 94.5591 | -34.6786 | 119.5427 | -51.0619 | 64.8872 | -33.3184 | -170.3882 | -38.0271 | 36.5704 | -39.1811 | -121.7155 | -34.0122 | -172.2645 | -28.419 | -85.4161 | -36.7737 | -116.7132 | -37.2676 | -76.2332 | -47.5688 | 156.827 | -30.7868 | -12.2988 | -10.7616 | 151.4047 | -11.4724 | -99.8461 | -21.2858 | 54.3639 | -17.3478 | -5.4611 | -11.1328 | -83.2581 | -8.3728 | -15.9947 | -19.1848 | 23.2988 | -15.1747 | 39.4362 | -39.0665 | -46.0438 | -37.7426 | -38.254 | -47.8985 | -37.8484 | -50.7988 | -36.9596 | -39.7482 | -35.6855 | -47.6933 | -39.5924 | -39.5261 | 587 | -28.9029 | -28.0623 | -30.3291 | -35.435 | -26.8903 | -32.2033 | -26.0888 | -29.7388 | 587 | -27.8676 | -30.6562 | -29.162 | -38.3615 | -28.3114 | -41.5775 | -27.4226 | -30.5269 | -30.0368 | -38.6772 | -29.6312 | -42.5816 | -36.9518 | -28.6506 | -26.5935 | -38.1563 | -30.0554 | -30.3048 | -36.5068 | -28.5213 | -27.4683 | -38.472 | -31.3752 | -31.3089
588 | -9.1619 | 0 | -9.728 | 0 | -9.3557 | 0 | -8.2892 | 0 | -29.4134 | 81.5867 | -31.5661 | 136.7287 | -50.9215 | 61.1492 | -31.1877 | -174.5049 | -40.0878 | 23.3096 | -43.3301 | -134.2289 | -33.5386 | -178.6689 | -26.3551 | -88.6979 | -36.2927 | -122.098 | -33.5049 | -82.4807 | -48.0855 | 121.8512 | -32.0829 | -15.1087 | -10.9346 | 139.0571 | -10.6599 | -114.2997 | -19.8343 | 49.8188 | -15.2302 | -15.0867 | -11.6743 | -95.2649 | -7.9317 | -23.8581 | -18.8057 | 24.9057 | -13.5396 | 33.3148 | -38.3786 | -47.0023 | -37.2108 | -36.5075 | -50.9137 | -39.6898 | -49.0132 | -35.8596 | -39.0017 | -35.0327 | -48.2476 | -42.5236 | -40.3987 | 588 | -27.3284 | -26.9824 | -28.2263 | -38.1662 | -25.2401 | -30.4361 | -24.711 | -30.6079 | 588 | -26.6977 | -29.8398 | -27.3456 | -41.1857 | -29.9618 | -39.6575 | -26.1316 | -29.646 | -28.2183 | -41.558 | -31.4006 | -40.724 | -37.8404 | -28.0489 | -25.8708 | -38.5196 | -32.7956 | -31.043 | -37.2743 | -27.8551 | -26.7435 | -38.8919 | -34.2344 | -32.1095
589 | -9.087 | 0 | -9.7745 | 0 | -9.6026 | 0 | -8.3565 | 0 | -29.1877 | 68.0832 | -28.372 | 133.992 | -51.8921 | 53.2422 | -29.7195 | 177.3199 | -43.084 | 17.3468 | -49.615 | -118.4262 | -33.0817 | 173.2786 | -24.8121 | -98.7133 | -35.9022 | -128.3203 | -31.6086 | -97.6543 | -49.1806 | 85.8856 | -32.9029 | -11.1244 | -11.6344 | 127.2927 | -10.7069 | -130.1552 | -18.8404 | 35.9227 | -13.7234 | -30.5419 | -12.9537 | -107.1651 | -7.8295 | -31.4998 | -17.7716 | 24.7513 | -12.1205 | 24.4121 | -38.0696 | -48.261 | -36.9133 | -35.3664 | -54.8743 | -42.7688 | -46.5558 | -34.2979 | -38.3761 | -34.7862 | -49.0675 | -46.0518 | -41.2355 | 589 | -25.7399 | -26.3422 | -25.9646 | -41.7683 | -23.9245 | -29.2286 | -23.463 | -31.0707 | 589 | -25.2109 | -29.2891 | -26.2794 | -45.0998 | -32.9943 | -36.9532 | -24.5234 | -28.7735 | -27.0099 | -45.2717 | -34.4123 | -38.1993 | -39.174 | -27.8263 | -25.6992 | -39.293 | -36.2773 | -31.6329 | -38.4865 | -27.3107 | -26.4297 | -39.4649 | -37.6953 | -32.879
590 | -8.9404 | 0 | -9.6461 | 0 | -9.877 | 0 | -8.404 | 0 | -29.5926 | 55.3287 | -26.4897 | 121.4269 | -54.8593 | 53.5225 | -28.7186 | 165.4373 | -46.377 | 28.7612 | -47.1234 | -63.6665 | -32.9242 | 163.4588 | -23.9858 | -110.4124 | -35.5491 | -134.6921 | -30.7873 | -112.6788 | -50.7924 | 52.4767 | -32.4277 | -4.5923 | -12.8062 | 118.1091 | -11.173 | -146.1469 | -18.9318 | 18.629 | -12.8899 | -45.4896 | -14.7873 | -115.4778 | -8.056 | -38.5212 | -16.9355 | 21.9319 | -11.2296 | 13.7844 | -38.074 | -50.0665 | -36.837 | -34.8006 | -54.9685 | -47.8556 | -44.2985 | -33.0801 | -38.0146 | -34.8102 | -49.7165 | -47.0684 | -41.6622 | 590 | -24.7552 | -26.0826 | -24.429 | -43.4018 | -23.2032 | -28.6885 | -22.676 | -30.6612 | 590 | -24.1397 | -29.0742 | -25.8602 | -45.3224 | -38.2095 | -34.4215 | -23.434 | -28.1376 | -26.3966 | -45.0915 | -39.4516 | -35.8945 | -41.1261 | -27.8966 | -25.8698 | -40.0704 | -37.4223 | -31.7852 | -40.4204 | -26.96 | -26.4062 | -39.8395 | -38.6644 | -33.2582
591 | -8.7498 | 0 | -9.4438 | 0 | -10.076 | 0 | -8.4345 | 0 | -30.6785 | 43.9788 | -25.7782 | 108.9287 | -56.0858 | 86.1059 | -28.129 | 154.5904 | -45.6218 | 55.1448 | -41.2874 | -63.3081 | -33.3281 | 153.8723 | -23.8435 | -121.2781 | -35.3118 | -141.869 | -30.5194 | -127.9324 | -52.7124 | 25.1634 | -30.8043 | -2.6104 | -14.2083 | 114.1052 | -12.5975 | -161.9132 | -20.0031 | 0.3325 | -12.5657 | -62.8697 | -17.318 | -117.4839 | -8.6064 | -44.0202 | -15.9772 | 16.8314 | -10.8906 | 2.3232 | -38.2818 | -53.3359 | -36.8456 | -34.5865 | -51.9459 | -54.5703 | -42.643 | -32.3729 | -37.9998 | -35.0219 | -49.5063 | -45.033 | -41.9354 | 591 | -24.5577 | -26.1596 | -23.7096 | -39.8208 | -23.1103 | -28.6731 | -22.3319 | -29.4668 | 591 | -23.6231 | -29.25 | -25.8367 | -42.5021 | -45.1265 | -32.567 | -22.9291 | -27.9238 | -26.152 | -41.8699 | -46.1358 | -34.2085 | -44.5861 | -28.0958 | -26.2721 | -40.0625 | -35.5892 | -31.8594 | -43.8921 | -26.7696 | -26.5874 | -39.4303 | -36.5985 | -33.5009
592 | -8.6256 | 0 | -9.232 | 0 | -10.1755 | 0 | -8.4351 | 0 | -32.3708 | 40.6188 | -26.0404 | 96.9592 | -51.669 | 99.7612 | -28.0952 | 141.1202 | -42.0492 | 58.7034 | -37.6369 | -75.5287 | -34.3497 | 145.6495 | -24.2517 | -129.2842 | -35.3336 | -149.5326 | -30.73 | -144.8182 | -54.8914 | -1.8348 | -29.1344 | -9.1088 | -15.1231 | 116.6384 | -15.0606 | -171.9715 | -22.4552 | -19.8688 | -12.7327 | -79.2362 | -19.1126 | -108.2618 | -9.369 | -47.4093 | -15.6053 | 9.6286 | -11.101 | -9.4882 | -38.7262 | -62.2127 | -36.8971 | -34.6676 | -50.0739 | -49.7987 | -41.8414 | -32.2459 | -38.3365 | -35.3492 | -48.2828 | -42.988 | -42.1365 | 592 | -25.1219 | -26.5911 | -23.7557 | -36.1708 | -23.5487 | -29.1513 | -22.3487 | -28.1911 | 592 | -23.6203 | -29.7109 | -26.042 | -40.8419 | -40.5667 | -31.6659 | -23.0139 | -28.161 | -26.2325 | -39.8984 | -41.3636 | -33.4063 | -53.5871 | -28.2715 | -26.7236 | -39.0508 | -33.756 | -31.961 | -52.9807 | -26.7216 | -26.9141 | -38.1073 | -34.5529 | -33.7014
593 | -8.5833 | 0 | -9.1301 | 0 | -10.1067 | 0 | -8.4153 | 0 | -33.6069 | 47.2574 | -27.1648 | 88.4915 | -48.7049 | 90.1357 | -28.8384 | 128.7701 | -39.4232 | 47.0122 | -35.3551 | -94.244 | -35.3713 | 145.3764 | -24.9976 | -133.6185 | -35.4314 | -155.3445 | -31.7335 | -161.798 | -57.6215 | -33.9771 | -28.0359 | -19.9839 | -14.8535 | 120.2118 | -18.2451 | -166.8105 | -27.1648 | -39.3535 | -13.5893 | -93.9218 | -18.1362 | -101.9397 | -9.8649 | -48.6205 | -15.6919 | 1.4271 | -11.6537 | -21.6582 | -39.1907 | -58.4798 | -36.9954 | -35.2376 | -49.679 | -45.1595 | -41.7278 | -32.6145 | -38.9387 | -35.638 | -46.7005 | -41.677 | -42.5872 | 593 | -26.252 | -27.3126 | -24.5358 | -33.777 | -24.2705 | -30.164 | -22.6706 | -27.3051 | 593 | -24.0312 | -30.3554 | -26.6543 | -40.5489 | -36.0294 | -31.6211 | -23.4844 | -28.832 | -26.8223 | -39.5723 | -36.7442 | -33.3125 | -49.8965 | -28.4121 | -27.0547 | -37.5704 | -32.5469 | -32.4805 | -49.3497 | -26.8887 | -27.2227 | -36.5938 | -33.2617 | -34.1719
594 | -8.6554 | 0 | -9.2193 | 0 | -9.9171 | 0 | -8.3799 | 0 | -32.6572 | 56.4158 | -28.9253 | 89.0071 | -47.843 | 72.9883 | -30.4468 | 120.2083 | -38.0763 | 28.1935 | -34.1375 | -115.849 | -35.351 | 149.712 | -25.5402 | -131.2834 | -35.3777 | -159.3786 | -34.4297 | 179.2066 | -62.6514 | -83.9046 | -27.4906 | -31.587 | -13.9539 | 119.0389 | -18.0564 | -144.3557 | -39.8058 | -72.4525 | -14.905 | -104.6868 | -17.5079 | -101.263 | -9.6722 | -46.1746 | -15.7356 | -3.597 | -13.2372 | -25.9054 | -39.2447 | -49.048 | -37.1613 | -36.4791 | -50.0845 | -42.8019 | -42.2544 | -33.4952 | -39.6241 | -35.6333 | -45.4693 | -41.171 | -42.7843 | 594 | -27.3529 | -27.9579 | -25.9029 | -32.5347 | -24.7186 | -31.8521 | -23.067 | -26.8349 | 594 | -24.8398 | -30.9687 | -27.8237 | -40.8652 | -33.5826 | -32.3373 | -24.2759 | -29.707 | -28.0992 | -40.1674 | -34.422 | -33.8745 | -40.3926 | -28.5059 | -26.9779 | -36.25 | -31.9517 | -32.8672 | -39.8287 | -27.2442 | -27.2534 | -35.5522 | -32.7911 | -34.4044
595 | -8.753 | 0 | -9.4514 | 0 | -9.716 | 0 | -8.3513 | 0 | -30.5925 | 55.4225 | -29.8023 | 103.4885 | -48.9651 | 59.9969 | -32.0009 | 124.2176 | -37.8291 | 6.9952 | -33.9302 | -138.6762 | -34.3496 | 150.9766 | -24.9845 | -124.7927 | -35.2642 | -163.8234 | -40.5582 | 177.8676 | -61.1418 | 158.2585 | -27.3877 | -42.6135 | -13.1467 | 111.678 | -15.0047 | -140.7486 | -32.6048 | 92.3146 | -16.557 | -108.0783 | -17.111 | -111.1401 | -9.1707 | -49.0257 | -15.8706 | -5.8471 | -14.9491 | -23.7939 | -38.8635 | -44.1672 | -37.1222 | -37.8987 | -50.719 | -41.9094 | -43.0842 | -34.7278 | -39.9562 | -35.1233 | -44.7405 | -41.3918 | -42.6887 | 595 | -27.1405 | -27.7777 | -26.8153 | -32.35 | -24.1584 | -33.4101 | -22.9359 | -26.7301 | 595 | -25.9748 | -31.2032 | -29.1457 | -41.2676 | -32.458 | -33.3682 | -25.2764 | -30.2402 | -29.5474 | -41.003 | -33.5581 | -34.7329 | -35.4142 | -28.3692 | -26.3703 | -35.2891 | -31.9404 | -32.9727 | -34.7158 | -27.4062 | -26.772 | -35.0245 | -33.0405 | -34.3374
596 | -8.8519 | 0 | -9.7137 | 0 | -9.5819 | 0 | -8.3713 | 0 | -28.9261 | 45.5207 | -27.6569 | 117.8576 | -51.1098 | 59.7143 | -31.7898 | 133.5628 | -38.7339 | -14.9972 | -34.7921 | -160.3917 | -33.1561 | 146.6602 | -23.3657 | -124.6318 | -35.2667 | -171.2687 | -40.9349 | -124.7004 | -53.6198 | 100.1502 | -27.831 | -53.6416 | -12.7347 | 103.1027 | -12.7661 | -151.2642 | -26.3529 | 63.0235 | -16.8674 | -102.6507 | -16.5412 | -128.8459 | -8.8245 | -55.0037 | -16.5715 | -11.5205 | -15.2888 | -17.1332 | -38.4226 | -41.1033 | -36.764 | -36.9734 | -52.3679 | -42.1736 | -44.0379 | -35.5662 | -39.7659 | -34.5769 | -44.5926 | -42.3514 | -42.6131 | 596 | -25.2238 | -26.8264 | -25.6716 | -33.2484 | -22.6857 | -32.4529 | -21.9822 | -27.1007 | 596 | -26.7143 | -30.914 | -28.1215 | -42.6542 | -32.4599 | -34.456 | -25.8525 | -30.184 | -28.6021 | -42.786 | -33.8023 | -35.6666 | -32.2514 | -27.9121 | -25.725 | -34.8789 | -32.6377 | -33.0312 | -31.3896 | -27.1821 | -26.2056 | -35.0107 | -33.9801 | -34.2418
597 | -8.8959 | 0 | -9.8569 | 0 | -9.6264 | 0 | -8.4506 | 0 | -27.9954 | 32.1485 | -24.6947 | 114.9994 | -52.1496 | 75.3561 | -30.2491 | 135.3127 | -40.9347 | -36.2178 | -36.8477 | -178.7509 | -32.1107 | 139.6552 | -21.6536 | -130.0672 | -35.5307 | -177.802 | -35.2756 | -124.3377 | -49.984 | 61.9417 | -28.7137 | -62.3321 | -12.8659 | 94.1143 | -11.39 | -165.7955 | -24.9234 | 31.6515 | -15.5216 | -100.126 | -17.6478 | -147.6196 | -8.6271 | -61.6121 | -16.911 | -12.7818 | -14.1963 | -9.3104 | -38.1439 | -39.2299 | -36.2924 | -34.8822 | -56.0502 | -43.9096 | -44.6303 | -35.1303 | -39.1147 | -34.3412 | -44.9701 | -44.3256 | -42.6927 | 597 | -23.0231 | -25.8312 | -23.4261 | -35.3257 | -21.1191 | -30.3532 | -20.7186 | -27.8659 | 597 | -26.2344 | -30.2188 | -25.9863 | -46.1933 | -34.0527 | -35.0039 | -25.2734 | -29.4883 | -26.4316 | -46.4238 | -35.459 | -36.1797 | -30.334 | -27.3965 | -25.4453 | -35.1132 | -34.4687 | -33.0663 | -29.373 | -26.666 | -25.8906 | -35.3437 | -35.875 | -34.2421
598 | -8.8852 | 0 | -9.8636 | 0 | -9.8275 | 0 | -8.577 | 0 | -27.8086 | 17.6087 | -22.6569 | 104.1547 | -50.5415 | 92.2508 | -28.6036 | 129.852 | -44.7511 | -52.0828 | -40.4933 | 168.6317 | -31.379 | 128.1559 | -20.4673 | -140.439 | -35.9213 | 176.6483 | -32.8923 | -139.7973 | -48.4369 | 28.6228 | -29.7021 | -65.5805 | -13.121 | 84.8183 | -10.8114 | 179.0342 | -25.2814 | -0.4967 | -13.7552 | -105.8297 | -19.9291 | -169.3074 | -8.6696 | -70.7759 | -16.7847 | -11.894 | -12.3634 | -10.3579 | -38.1507 | -38.3723 | -35.8793 | -33.5843 | -62.5257 | -47.5364 | -44.3519 | -33.8939 | -38.4711 | -34.4105 | -45.7425 | -47.5814 | -42.5891 | 598 | -21.4941 | -25.13 | -21.6163 | -38.8082 | -20.0158 | -29.0099 | -19.7615 | -28.7253 | 598 | -25.0087 | -29.5859 | -24.6991 | -52.6621 | -37.6728 | -34.5244 | -24.0303 | -28.6436 | -25.0073 | -52.6982 | -38.9594 | -35.7749 | -29.4871 | -26.9941 | -25.5253 | -35.8789 | -37.7178 | -32.7616 | -28.5087 | -26.0518 | -25.8335 | -35.915 | -39.0044 | -34.0121
599 | -8.8251 | 0 | -9.6997 | 0 | -10.0904 | 0 | -8.7117 | 0 | -28.2928 | 4.1756 | -21.6565 | 91.1099 | -47.2729 | 98.8298 | -27.3715 | 120.7952 | -51.6607 | -55.2187 | -46.88 | 179.4797 | -31.1047 | 115.3069 | -19.9505 | -152.5303 | -35.9794 | 173.4095 | -32.0911 | -156.6385 | -48.3523 | 1.5548 | -30.3793 | -65.23 | -13.5492 | 76.7431 | -10.8989 | 163.0532 | -27.2693 | -34.8778 | -12.4879 | -118.3674 | -23.8495 | 165.83 | -9.1108 | -80.0172 | -16.7243 | -15.4187 | -10.8645 | -18.3494 | -38.3188 | -38.2485 | -35.5926 | -32.9789 | -62.7875 | -52.2563 | -43.4263 | -32.8209 | -38.0673 | -34.5747 | -46.6372 | -52.7271 | -42.477 | 599 | -20.794 | -24.7885 | -20.6143 | -43.3657 | -19.5302 | -28.5143 | -19.3372 | -29.2688 | 599 | -23.9958 | -29.2422 | -24.1538 | -53.0878 | -42.5566 | -33.3359 | -23.1212 | -27.9769 | -24.2672 | -52.6971 | -43.5446 | -34.7146 | -29.4234 | -26.7675 | -25.7496 | -36.9375 | -43.0274 | -32.3866 | -28.5488 | -25.5022 | -25.863 | -36.5468 | -44.0154 | -33.7653
600 | -8.7207 | 0 | -9.4383 | 0 | -10.3184 | 0 | -8.8332 | 0 | -29.3618 | -6.4485 | -21.5055 | 76.9313 | -44.1194 | 92.1889 | -26.6936 | 109.0065 | -56.0387 | 23.8022 | -45.3653 | -117.6859 | -31.4623 | 102.9526 | -20.0455 | -164.0875 | -35.7266 | 170.5562 | -32.0856 | -170.9595 | -49.3078 | -20.7654 | -30.2483 | -61.6134 | -14.1537 | 70.1307 | -11.5361 | 148.6835 | -29.5111 | -86.1093 | -11.5721 | -133.1472 | -31.1374 | 116.1118 | -9.8407 | -87.5989 | -16.4128 | -19.1056 | -10.1581 | -27.9288 | -38.5222 | -38.7929 | -35.5116 | -32.7839 | -58.4402 | -51.3163 | -42.5047 | -32.2793 | -37.916 | -34.6883 | -47.4071 | -60.4785 | -42.3144 | 600 | -20.8262 | -24.8124 | -20.343 | -41.5309 | -19.6347 | -28.7144 | -19.4086 | -29.1234 | 600 | -23.5586 | -29.1953 | -24.0632 | -49.0019 | -41.878 | -32.1863 | -22.841 | -27.5976 | -23.9507 | -48.1218 | -42.4831 | -33.6715 | -30.0722 | -26.7909 | -25.9676 | -37.9688 | -51.0402 | -31.996 | -29.3546 | -25.1932 | -25.8551 | -37.0887 | -51.6453 | -33.4812
601 | -8.6148 | 0 | -9.1538 | 0 | -10.4273 | 0 | -8.9195 | 0 | -30.8588 | -12.0622 | -22.07 | 65.9422 | -41.9138 | 78.7477 | -26.6045 | 96.2855 | -47.3467 | 38.4656 | -38.6939 | -114.8937 | -32.4536 | 92.2384 | -20.6608 | -172.8217 | -35.3805 | 165.8034 | -32.595 | 174.9773 | -51.1371 | -38.3085 | -29.2622 | -61.59 | -14.9652 | 65.4129 | -12.7926 | 137.0685 | -29.5646 | -145.1213 | -11.2685 | -148.9668 | -32.7231 | 18.9505 | -10.987 | -93.7553 | -16.1729 | -23.7198 | -9.7035 | -39.5965 | -38.8276 | -39.9018 | -35.476 | -32.9135 | -56.3393 | -47.2377 | -41.8999 | -32.1773 | -38.0093 | -34.8257 | -47.8179 | -57.8218 | -42.517 | 601 | -21.4913 | -25.1935 | -20.6909 | -36.6181 | -20.2472 | -29.4836 | -19.8616 | -28.2899 | 601 | -23.5625 | -29.3945 | -24.2987 | -47.1855 | -38.0839 | -31.4726 | -23.0235 | -27.582 | -23.994 | -45.912 | -38.3182 | -32.9804 | -31.287 | -26.8612 | -26.2109 | -38.6641 | -48.668 | -32.0897 | -30.748 | -25.0487 | -25.9062 | -37.3906 | -48.9023 | -33.5975
602 | -8.576 | 0 | -8.9452 | 0 | -10.3652 | 0 | -8.936 | 0 | -32.0755 | -8.9873 | -23.2573 | 59.2333 | -40.7213 | 61.259 | -27.1757 | 81.745 | -43.027 | 22.3719 | -34.783 | -130.4425 | -33.8701 | 86.5801 | -21.6039 | -178.2019 | -35.1812 | 159.6381 | -33.8552 | 161.2645 | -54.8748 | -49.6287 | -28.092 | -67.5792 | -15.6379 | 62.4306 | -14.6276 | 134.4796 | -27.3261 | 170.9589 | -11.5404 | -165.065 | -27.9947 | -28.1767 | -12.4144 | -94.4934 | -16.415 | -29.2407 | -10.0761 | -51.4175 | -39.0916 | -41.3553 | -35.5896 | -33.3494 | -55.5877 | -44.7537 | -41.7147 | -32.5839 | -38.1971 | -34.9921 | -47.6171 | -53.0214 | -43.7011 | 602 | -22.6533 | -25.8736 | -21.5663 | -33.3074 | -21.1773 | -30.8352 | -20.5181 | -27.309 | 602 | -24.0079 | -29.6211 | -24.7734 | -46.6425 | -35.8085 | -31.3495 | -23.6387 | -27.8319 | -24.4134 | -45.2225 | -35.8177 | -32.7787 | -32.7793 | -27.0136 | -26.4161 | -38.6719 | -44.0762 | -33.3359 | -32.4101 | -25.2244 | -26.0561 | -37.2519 | -44.0854 | -34.7651
603 | -8.554 | 0 | -8.9205 | 0 | -10.2152 | 0 | -8.8802 | 0 | -31.7659 | -2.0609 | -24.5944 | 60.9732 | -40.5546 | 43.5373 | -28.5171 | 71.768 | -40.9171 | -1.5499 | -32.4662 | -151.0822 | -34.9041 | 88.6088 | -22.3469 | -176.1328 | -35.0562 | 150.0105 | -36.645 | 149.2947 | -61.0016 | -14.2201 | -27.3204 | -75.2222 | -16.3128 | 61.5679 | -15.543 | 139.3494 | -26.3358 | 145.9966 | -12.4035 | -179.4317 | -26.9362 | -61.8375 | -13.0752 | -91.8265 | -16.8568 | -32.0353 | -10.8526 | -62.169 | -39.184 | -42.2639 | -35.7784 | -34.0199 | -55.6801 | -43.7209 | -41.854 | -33.2933 | -38.3626 | -35.3189 | -46.9829 | -51.0121 | -46.8792 | 603 | -23.741 | -26.6678 | -22.6396 | -31.3329 | -21.8972 | -32.6712 | -21.0264 | -26.6428 | 603 | -24.7393 | -29.8086 | -25.4659 | -46.7596 | -34.8004 | -31.6388 | -24.3728 | -28.1474 | -25.1397 | -45.4649 | -34.8407 | -32.9738 | -33.7099 | -27.2244 | -26.7649 | -38.0624 | -42.0916 | -36.664 | -33.3434 | -25.5632 | -26.4387 | -36.7677 | -42.1319 | -37.999
604 | -8.5451 | 0 | -9.0755 | 0 | -10.0157 | 0 | -8.7718 | 0 | -30.2696 | -1.2193 | -24.5272 | 71.2988 | -41.42 | 26.7516 | -30.4719 | 69.2699 | -40.4872 | -27.6156 | -31.3311 | -174.7739 | -34.706 | 93.8902 | -22.0055 | -170.7485 | -35.1082 | 140.8739 | -42.1066 | 157.4581 | -53.3236 | 22.5612 | -27.0433 | -85.699 | -16.5401 | 61.6312 | -14.4787 | 144.6419 | -27.1391 | 126.6095 | -13.9338 | 169.3893 | -26.7965 | -92.9943 | -12.6436 | -91.1225 | -17.4344 | -39.2786 | -11.2935 | -69.1839 | -38.9132 | -41.08 | -36.039 | -34.6086 | -56.0929 | -43.8651 | -42.2943 | -34.0274 | -38.3068 | -35.8529 | -46.2669 | -51.2188 | -50.832 | 604 | -23.4314 | -27.1529 | -22.8743 | -30.4696 | -21.5811 | -33.9298 | -20.7891 | -26.4044 | 604 | -25.4823 | -29.7617 | -26.0635 | -47.0174 | -34.7896 | -32.2786 | -24.9519 | -28.2911 | -25.8368 | -46.0772 | -35.0933 | -33.5225 | -32.5349 | -27.4939 | -27.3078 | -37.1914 | -42.1433 | -40.8163 | -32.0045 | -26.0233 | -27.0811 | -36.2512 | -42.447 | -42.0602
605 | -8.5914 | 0 | -9.2476 | 0 | -9.8726 | 0 | -8.6617 | 0 | -28.8592 | -9.5316 | -22.5238 | 77.2435 | -43.4231 | 16.6506 | -31.631 | 79.9124 | -41.681 | -54.6211 | -31.2984 | 161.6718 | -33.5537 | 95.8251 | -20.5545 | -168.9996 | -35.6095 | 132.932 | -40.4997 | -149.2688 | -48.3922 | 6.5122 | -27.1175 | -93.8501 | -16.2058 | 61.4447 | -12.7804 | 141.0004 | -29.7449 | 127.8218 | -15.8958 | 165.1663 | -34.937 | -101.6762 | -12.0375 | -94.3333 | -17.371 | -37.6479 | -12.8832 | -71.8932 | -38.5697 | -38.6908 | -36.2416 | -34.9135 | -56.2806 | -45.7924 | -43.1109 | -34.3648 | -38.107 | -36.7437 | -46.064 | -54.4976 | -48.7984 | 605 | -21.5873 | -26.8714 | -21.5359 | -30.6806 | -20.2148 | -32.6376 | -19.6527 | -26.5144 | 605 | -25.7734 | -29.5156 | -26.3221 | -47.033 | -36.5448 | -33.2383 | -25.1172 | -28.2344 | -26.2518 | -46.408 | -37.1307 | -34.4492 | -30.0994 | -27.6502 | -28.1523 | -36.8164 | -45.25 | -38.9258 | -29.4432 | -26.369 | -28.082 | -36.1914 | -45.8359 | -40.1367
606 | -8.6413 | 0 | -9.3762 | 0 | -9.9194 | 0 | -8.5784 | 0 | -28.0595 | -21.5263 | -20.4368 | 70.0144 | -46.3128 | 18.5156 | -30.0911 | 89.974 | -44.5739 | -80.0549 | -32.4661 | 138.6205 | -32.102 | 89.1327 | -18.9298 | -175.743 | -36.478 | 126.5126 | -34.7085 | -151.9279 | -46.4674 | -15.2986 | -27.4087 | -103.7342 | -15.7263 | 57.8402 | -11.5564 | 131.8417 | -28.5949 | 157.0792 | -17.2512 | 173.9551 | -42.1654 | 10.5977 | -11.5297 | -102.0371 | -16.8683 | -39.7054 | -13.4346 | -68.3331 | -38.6983 | -36.9837 | -36.1743 | -34.6397 | -55.9717 | -51.3665 | -44.2044 | -34.0952 | -37.8366 | -37.5051 | -46.3333 | -66.6889 | -46.7163 | 606 | -19.7347 | -25.8881 | -19.7514 | -32.0412 | -18.6532 | -30.1008 | -18.254 | -26.8537 | 606 | -25.4539 | -29.1953 | -25.9984 | -46.5955 | -41.9903 | -34.285 | -24.719 | -27.9172 | -26.0613 | -46.0523 | -42.7881 | -35.626 | -28.3424 | -27.533 | -28.8638 | -36.9571 | -57.3127 | -36.7969 | -27.6075 | -26.2549 | -28.9267 | -36.4139 | -58.1105 | -38.1379
607 | -8.6883 | 0 | -9.3506 | 0 | -10.1429 | 0 | -8.571 | 0 | -27.9866 | -35.898 | -19.1318 | 59.7011 | -46.9842 | 39.4404 | -27.7991 | 85.4129 | -49.5803 | -101.1193 | -35.0744 | 117.241 | -30.9886 | 77.4411 | -17.8528 | 173.5902 | -37.3027 | 122.3956 | -32.0497 | -168.9417 | -45.8749 | -32.269 | -28.0264 | -110.9188 | -15.3648 | 50.8742 | -10.9712 | 120.8679 | -23.9876 | 163.3989 | -16.2057 | -176.4352 | -26.6073 | 16.6466 | -11.5022 | -112.2489 | -16.2782 | -44.5827 | -13.1435 | -64.8222 | -39.2507 | -36.0783 | -35.8072 | -33.9109 | -55.2546 | -55.8478 | -45.1201 | -33.4711 | -37.6258 | -37.1513 | -46.8271 | -57.5414 | -45.2445 | 607 | -18.5941 | -24.8668 | -18.4821 | -34.6611 | -17.6 | -28.3982 | -17.3062 | -27.4782 | 607 | -24.7828 | -28.9375 | -25.2226 | -45.904 | -46.4972 | -34.9772 | -24.1205 | -27.4829 | -25.3399 | -45.1117 | -47.2768 | -36.5491 | -27.39 | -27.1189 | -28.463 | -37.4765 | -48.1908 | -35.1016 | -26.7277 | -25.6643 | -28.5803 | -36.6842 | -48.9704 | -36.6735
608 | -8.7182 | 0 | -9.2503 | 0 | -10.4946 | 0 | -8.6433 | 0 | -28.5712 | -47.854 | -18.5546 | 46.5992 | -44.0433 | 50.4227 | -26.4087 | 73.7754 | -61.238 | -122.7766 | -39.9692 | 104.4662 | -30.5715 | 62.817 | -17.4601 | 159.878 | -37.6936 | 120.7824 | -31.1293 | 172.8272 | -45.9121 | -46.7892 | -28.8603 | -115.2807 | -15.128 | 41.159 | -10.6881 | 108.8963 | -20.6273 | 155.2592 | -14.1733 | -176.5585 | -21.2083 | 3.4672 | -12.0079 | -123.7294 | -15.7458 | -49.281 | -12.2207 | -67.4641 | -39.8848 | -35.7698 | -35.3684 | -33.3575 | -54.3379 | -46.8596 | -45.137 | -32.9517 | -37.6089 | -36.344 | -47.3245 | -51.2017 | -44.065 | 608 | -18.131 | -24.3455 | -17.8686 | -38.5115 | -17.2139 | -27.7641 | -16.9858 | -28.2513 | 608 | -24.2335 | -28.8907 | -24.6393 | -45.0876 | -37.6093 | -34.6424 | -23.7014 | -27.1143 | -24.7142 | -43.8433 | -38.2163 | -36.4937 | -27.0516 | -26.6502 | -27.6258 | -38.0742 | -41.9514 | -33.5704 | -26.5195 | -24.8738 | -27.7007 | -36.8299 | -42.5584 | -35.4217
609 | -8.7203 | 0 | -9.0132 | 0 | -10.7671 | 0 | -8.732 | 0 | -29.6591 | -57.8595 | -18.5752 | 33.6688 | -41.3321 | 42.8394 | -25.8569 | 59.4068 | -57.1821 | 41.2535 | -48.2203 | 141.0969 | -30.9329 | 48.1959 | -17.6999 | 148.2495 | -37.4945 | 119.0076 | -31.0392 | 156.7866 | -46.4279 | -57.0783 | -29.3388 | -115.255 | -15.6707 | 29.5287 | -10.9764 | 98.1679 | -18.3461 | 143.4977 | -12.5199 | 175.16 | -19.0596 | -17.3102 | -12.746 | -136.1829 | -15.3048 | -59.4056 | -11.3373 | -74.3162 | -40.3665 | -35.972 | -35.0306 | -33.179 | -53.5345 | -42.9798 | -44.1461 | -32.7984 | -37.6695 | -35.5679 | -47.7242 | -48.2867 | -42.9391 | 609 | -18.2281 | -24.342 | -17.8267 | -40.4305 | -17.4551 | -27.9138 | -17.2275 | -28.6478 | 609 | -24.0781 | -28.9492 | -24.4587 | -44.5213 | -33.9666 | -33.379 | -23.7852 | -26.9024 | -24.447 | -42.7674 | -34.2478 | -35.4141 | -27.2517 | -26.3103 | -26.8476 | -38.711 | -39.2735 | -32.172 | -26.9588 | -24.2635 | -26.8359 | -36.9571 | -39.5547 | -34.2071
610 | -8.688 | 0 | -8.8031 | 0 | -10.8788 | 0 | -8.829 | 0 | -31.022 | -63.136 | -19.1418 | 23.8319 | -39.6947 | 29.4529 | -25.9095 | 46.2215 | -49.5012 | 20.5077 | -40.7727 | -167.9509 | -32.0441 | 35.2992 | -18.4369 | 139.8827 | -36.9843 | 115.7851 | -31.4339 | 143.065 | -46.9161 | -64.0656 | -29.0963 | -115.538 | -16.9246 | 17.9483 | -11.5675 | 89.4842 | -16.7713 | 129.4243 | -11.4499 | 162.9504 | -17.6177 | -32.0622 | -14.3727 | -147.4841 | -15.2029 | -71.1374 | -11.1287 | -85.7146 | -40.5431 | -36.6148 | -34.8772 | -33.297 | -53.0782 | -40.8727 | -42.7172 | -33.0116 | -37.774 | -34.9672 | -48.2172 | -46.8358 | -42.0781 | 610 | -18.8331 | -24.7285 | -18.2876 | -36.9422 | -18.1939 | -28.6527 | -17.8829 | -28.3806 | 610 | -24.3236 | -29.086 | -24.609 | -44.2751 | -32.0696 | -31.8384 | -24.2085 | -26.8952 | -24.468 | -42.1994 | -32.0437 | -33.8882 | -27.9268 | -26.1892 | -26.2792 | -39.4141 | -38.0327 | -31.1993 | -27.8117 | -23.9984 | -26.1382 | -37.3384 | -38.0068 | -33.2491
611 | -8.6311 | 0 | -8.6572 | 0 | -10.7828 | 0 | -8.8528 | 0 | -32.0847 | -60.627 | -20.2219 | 17.7302 | -39.2002 | 12.5114 | -26.511 | 31.9979 | -46.1272 | -2.1691 | -35.3534 | -178.5303 | -33.7568 | 29.2747 | -19.5599 | 133.9292 | -36.595 | 108.4019 | -32.4009 | 128.633 | -47.3376 | -70.095 | -28.446 | -117.3954 | -19.4437 | 6.9173 | -12.4279 | 85.381 | -15.9766 | 115.6083 | -11.0915 | 151.1327 | -17.1374 | -46.7461 | -16.8229 | -154.1699 | -15.4932 | -83.4817 | -11.5145 | -96.183 | -40.5612 | -37.718 | -34.8671 | -33.7292 | -53.3073 | -39.8118 | -41.3721 | -33.4781 | -37.8108 | -34.4932 | -48.7275 | -46.3023 | -41.486 | 611 | -19.8966 | -25.4118 | -19.1986 | -33.6038 | -19.3157 | -29.9361 | -18.8366 | -27.7788 | 611 | -24.847 | -29.1797 | -25.0981 | -44.6501 | -31.1546 | -30.5893 | -24.8209 | -27.028 | -24.8764 | -42.5245 | -30.959 | -32.5193 | -29.0869 | -26.236 | -25.8621 | -40.0703 | -37.6451 | -30.7032 | -29.0608 | -24.0843 | -25.6404 | -37.9447 | -37.4495 | -32.6332
612 | -8.6269 | 0 | -8.6108 | 0 | -10.5324 | 0 | -8.8703 | 0 | -32.0197 | -57.1725 | -21.4281 | 17.267 | -39.7053 | -3.33 | -27.7972 | 20.4207 | -44.6522 | -29.1724 | -32.4171 | 161.7917 | -35.358 | 30.732 | -20.5779 | 135.8304 | -36.5868 | 97.4048 | -34.4669 | 116.4708 | -47.9715 | -73.6789 | -27.8846 | -123.7318 | -23.664 | 4.6096 | -13.057 | 86.4176 | -16.0347 | 102.8084 | -11.3089 | 140.631 | -17.2089 | -59.5475 | -19.1339 | -149.8887 | -16.0023 | -96.9104 | -12.3315 | -107.3142 | -40.3781 | -38.9012 | -35.0192 | -34.4132 | -55.0031 | -39.4988 | -40.3178 | -34.1222 | -37.8066 | -34.1889 | -48.9116 | -46.8761 | -42.0833 | 612 | -21.0058 | -26.3395 | -20.2542 | -31.4602 | -20.3317 | -31.7738 | -19.6903 | -27.2979 | 612 | -25.4953 | -29.1797 | -25.7863 | -46.3923 | -30.888 | -29.7854 | -25.5114 | -27.2742 | -25.5429 | -44.4707 | -30.6285 | -31.4475 | -30.2743 | -26.3923 | -25.562 | -40.3008 | -38.2653 | -31.5509 | -30.2904 | -24.4868 | -25.3186 | -38.3792 | -38.0058 | -33.213
613 | -8.6265 | 0 | -8.6968 | 0 | -10.1889 | 0 | -8.7554 | 0 | -31.0465 | -58.5636 | -21.5416 | 24.033 | -41.3234 | -14.4838 | -29.9164 | 15.1967 | -44.9048 | -58.0239 | -30.9102 | 141.1433 | -35.4915 | 37.9254 | -20.5267 | 140.8966 | -37.0095 | 84.3174 | -38.1888 | 117.0621 | -48.2312 | -72.2321 | -27.587 | -131.3419 | -27.3427 | 38.665 | -12.5111 | 87.5363 | -16.5038 | 93.1534 | -11.6597 | 132.5825 | -17.37 | -70.9701 | -18.7242 | -136.9677 | -16.9793 | -107.4398 | -13.8008 | -114.5268 | -40.0343 | -39.007 | -35.2648 | -35.0148 | -59.8156 | -39.7843 | -39.6811 | -34.5913 | -37.7827 | -34.2475 | -48.439 | -49.0522 | -44.2243 | 613 | -21.0394 | -27.3574 | -20.5343 | -30.3764 | -20.2968 | -33.4759 | -19.6848 | -27.0838 | 613 | -25.9648 | -29.1562 | -26.3883 | -51.1188 | -31.0875 | -29.4922 | -25.8945 | -27.5938 | -26.2594 | -49.6267 | -31.0289 | -30.9257 | -30.3805 | -26.6383 | -25.621 | -39.7422 | -40.3554 | -34.0354 | -30.3102 | -25.0759 | -25.4921 | -38.2501 | -40.2968 | -35.4689
614 | -8.6817 | 0 | -8.8338 | 0 | -9.9371 | 0 | -8.7195 | 0 | -30.0308 | -65.4382 | -20.0089 | 29.4801 | -43.6848 | -15.9586 | -31.9187 | 22.3187 | -47.1302 | -91.6784 | -30.4517 | 118.7452 | -34.0778 | 41.1454 | -19.219 | 143.1483 | -38.059 | 72.7508 | -39.4894 | 147.6754 | -47.2216 | -71.1797 | -27.3828 | -139.062 | -23.9579 | 67.2468 | -11.5049 | 84.8669 | -17.3926 | 89.9077 | -12.2751 | 128.9668 | -18.7469 | -69.3978 | -17.1846 | -137.18 | -18.406 | -113.9681 | -16.1768 | -119.293 | -39.9252 | -37.5559 | -35.5192 | -34.9994 | -66.3822 | -40.8372 | -39.5603 | -34.5856 | -37.8496 | -34.5877 | -47.6619 | -54.82 | -48.5897 | 614 | -19.58 | -27.8116 | -19.3841 | -30.162 | -19.0248 | -32.8193 | -18.5669 | -26.9849 | 614 | -25.9039 | -29.1679 | -26.3177 | -57.5484 | -32.0034 | -29.6232 | -25.7518 | -27.9125 | -26.2799 | -56.4451 | -32.1177 | -30.8408 | -28.8742 | -26.8375 | -25.906 | -38.8281 | -45.9862 | -38.6526 | -28.7221 | -25.5821 | -25.8682 | -37.7248 | -46.1005 | -39.8702
615 | -8.7353 | 0 | -8.9751 | 0 | -9.7983 | 0 | -8.6848 | 0 | -29.4496 | -77.0304 | -18.2232 | 23.6646 | -44.6454 | -2.171 | -31.1329 | 35.8708 | -52.1159 | -137.0251 | -30.932 | 96.7988 | -32.3631 | 34.424 | -17.719 | 137.249 | -39.7492 | 65.6475 | -35.3944 | 157.7616 | -46.2718 | -76.8324 | -27.2364 | -148.6364 | -20.6321 | 64.2648 | -10.6771 | 78.816 | -17.7736 | 93.293 | -12.4269 | 129.2995 | -18.9106 | -70.9209 | -15.759 | -147.842 | -19.9976 | -115.4916 | -18.0027 | -110.2723 | -40.5275 | -35.8155 | -35.7603 | -34.4689 | -57.7775 | -42.9756 | -40.1509 | -34.1889 | -38.0361 | -34.9634 | -47.3189 | -57.4897 | -54.9314 | 615 | -17.8983 | -27.1859 | -17.7905 | -30.7195 | -17.5462 | -30.4928 | -17.1927 | -26.9484 | 615 | -25.4536 | -29.3008 | -25.7336 | -48.8024 | -34.0005 | -30.3526 | -25.2138 | -28.2378 | -25.7841 | -47.9792 | -34.2908 | -31.4661 | -27.0802 | -27.025 | -26.2281 | -38.3438 | -48.5146 | -45.1331 | -26.8404 | -25.962 | -26.2786 | -37.5206 | -48.8049 | -46.2466
616 | -8.7313 | 0 | -8.9881 | 0 | -9.8182 | 0 | -8.7437 | 0 | -29.4318 | -89.5172 | -17.0325 | 12.6409 | -42.9624 | 8.1197 | -29.0652 | 35.0827 | -56.0107 | 130.4786 | -32.4553 | 76.0656 | -31.19 | 21.3658 | -16.7288 | 126.7883 | -41.9739 | 67.151 | -32.8106 | 145.6479 | -45.7379 | -82.701 | -27.5827 | -159.7921 | -19.4587 | 51.2926 | -10.2265 | 71.14 | -17.0091 | 95.8386 | -11.8086 | 129.6599 | -18.0351 | -74.3605 | -14.904 | -163.3791 | -19.5296 | -115.489 | -16.5127 | -91.1662 | -41.5873 | -34.5776 | -35.8266 | -33.8139 | -53.9232 | -45.6909 | -41.3631 | -33.7127 | -38.2899 | -34.9412 | -47.3904 | -48.6424 | -55.7052 | 616 | -16.779 | -26.2298 | -16.653 | -32.0676 | -16.5635 | -28.8255 | -16.2881 | -27.3639 | 616 | -24.9814 | -29.5586 | -25.0826 | -44.9351 | -36.7028 | -31.5449 | -24.7246 | -28.4717 | -25.0702 | -44.105 | -36.9472 | -32.6194 | -25.8463 | -27.0953 | -26.2099 | -38.4023 | -39.6543 | -45.887 | -25.5895 | -26.0084 | -26.1975 | -37.5722 | -39.8987 | -46.9615
617 | -8.7904 | 0 | -8.9427 | 0 | -9.9779 | 0 | -8.8841 | 0 | -30.0278 | -101.7157 | -16.5363 | 0.1322 | -40.6824 | 5.9896 | -27.7053 | 25.9493 | -50.2444 | 63.6081 | -35.6121 | 58.0756 | -30.8401 | 5.7417 | -16.4295 | 115.0545 | -43.031 | 80.3144 | -31.8214 | 130.6175 | -45.207 | -90.3586 | -28.6845 | -169.5202 | -19.9967 | 35.4292 | -10.0064 | 62.984 | -15.8382 | 93.6842 | -10.7376 | 126.1451 | -17.342 | -77.0398 | -14.5295 | 178.5824 | -18.6528 | -118.2587 | -14.3729 | -93.3533 | -42.8232 | -33.8817 | -35.6864 | -33.5888 | -51.6278 | -46.0966 | -42.7396 | -33.3216 | -38.5638 | -34.638 | -47.6419 | -44.4232 | -50.5759 | 617 | -16.3302 | -25.6876 | -16.1669 | -34.323 | -16.2658 | -28.2053 | -16.0616 | -28.4354 | 617 | -24.5312 | -29.7734 | -24.7984 | -42.6851 | -37.1539 | -32.7617 | -24.3789 | -28.5859 | -24.7047 | -41.6499 | -37.2125 | -33.8555 | -25.0913 | -26.896 | -25.8476 | -38.6992 | -35.4805 | -40.598 | -24.939 | -25.7085 | -25.7539 | -37.664 | -35.5391 | -41.6918
618 | -8.7932 | 0 | -8.8214 | 0 | -10.1448 | 0 | -9.0174 | 0 | -31.1392 | -112.6312 | -16.6641 | -11.465 | -38.6934 | -3.8095 | -27.1648 | 13.097 | -46.3894 | 32.2934 | -42.2614 | 54.8363 | -31.2869 | -10.4961 | -16.7707 | 103.2063 | -41.2402 | 90.3098 | -31.6142 | 117.1618 | -44.9446 | -97.75 | -30.1542 | -172.0545 | -22.245 | 21.4936 | -10.1027 | 54.6134 | -15.0366 | 87.9958 | -9.7499 | 118.9518 | -16.5371 | -81.1228 | -14.6921 | 159.827 | -17.7338 | -126.6206 | -12.4341 | -100.4006 | -43.7018 | -33.6346 | -35.5252 | -33.7018 | -49.9675 | -43.6073 | -43.5011 | -33.1018 | -38.4729 | -34.2081 | -47.9816 | -42.1917 | -47.2273 | 618 | -16.4856 | -25.6652 | -16.2824 | -36.6259 | -16.6049 | -28.3412 | -16.4418 | -29.6968 | 618 | -24.3086 | -29.6797 | -24.9086 | -41.1461 | -34.7859 | -33.3563 | -24.2804 | -28.3281 | -24.6844 | -39.8227 | -34.5899 | -34.4837 | -24.8414 | -26.732 | -25.4149 | -39.1602 | -33.3703 | -37.0825 | -24.8132 | -25.3804 | -25.1907 | -37.8368 | -33.1743 | -38.2099
619 | -8.8321 | 0 | -8.6842 | 0 | -10.2492 | 0 | -9.0922 | 0 | -32.5632 | -118.5528 | -17.3353 | -21.9544 | -37.3644 | -19.6618 | -27.2043 | 1.1358 | -44.2055 | 6.6394 | -43.3528 | 129.1991 | -32.4655 | -24.8844 | -17.6257 | 93.8019 | -38.9592 | 84.2226 | -31.8272 | 104.114 | -44.6813 | -104.9528 | -31.1414 | -169.3362 | -28.1189 | 19.2761 | -10.1778 | 48.3589 | -14.3529 | 81.7251 | -9.0659 | 109.4017 | -15.9039 | -86.1702 | -15.5361 | 139.4927 | -16.7071 | -138.2493 | -11.5204 | -114.2879 | -43.8576 | -33.7468 | -35.4352 | -34.0959 | -48.8068 | -41.239 | -43.2819 | -33.1907 | -38.0899 | -33.8131 | -48.5358 | -40.9992 | -44.3786 | 619 | -17.1652 | -26.028 | -16.8995 | -35.7244 | -17.4547 | -29.0052 | -17.2814 | -30.3152 | 619 | -24.3586 | -29.2578 | -25.2638 | -40.1226 | -32.5548 | -33.0327 | -24.5065 | -27.8407 | -25.0037 | -38.5576 | -32.1468 | -34.1897 | -24.9147 | -26.6031 | -24.981 | -39.8516 | -32.315 | -34.1294 | -25.0626 | -25.186 | -24.7209 | -38.2866 | -31.907 | -35.2864
620 | -8.8918 | 0 | -8.5665 | 0 | -10.2136 | 0 | -9.1387 | 0 | -33.955 | -121.0519 | -18.4135 | -27.9375 | -36.9173 | -38.725 | -27.7666 | -10.2353 | -43.1169 | -16.0001 | -35.6713 | 131.934 | -34.2311 | -34.435 | -18.7921 | 88.4539 | -37.5347 | 69.7081 | -32.613 | 91.1106 | -44.2651 | -113.2735 | -31.0256 | -164.1916 | -31.1364 | 101.9529 | -10.4869 | 43.0966 | -13.9205 | 74.3748 | -8.8067 | 99.4662 | -15.353 | -92.3544 | -17.0341 | 119.0736 | -16.5951 | -154.9942 | -11.1422 | -128.4757 | -43.5914 | -34.0549 | -35.5299 | -34.5914 | -48.2359 | -39.9689 | -42.3907 | -33.5183 | -37.5011 | -33.418 | -49.3516 | -40.4206 | -42.4485 | 620 | -18.2347 | -26.7296 | -17.8641 | -32.8143 | -18.6137 | -30.1645 | -18.3731 | -29.9847 | 620 | -24.6265 | -28.6093 | -25.6996 | -39.6694 | -31.4024 | -32.1771 | -24.9518 | -27.2875 | -25.4527 | -38.0223 | -30.8302 | -33.252 | -25.1631 | -26.6381 | -24.5262 | -40.7851 | -31.8541 | -32.2349 | -25.4884 | -25.3163 | -24.2793 | -39.138 | -31.2819 | -33.3098
621 | -8.9777 | 0 | -8.4816 | 0 | -10.0597 | 0 | -9.0909 | 0 | -34.7994 | -118.6248 | -19.427 | -27.9689 | -37.5723 | -58.8423 | -28.8965 | -19.8766 | -42.9011 | -38.4488 | -31.7894 | 115.3565 | -36.1422 | -36.9526 | -19.7872 | 90.5314 | -36.8512 | 51.3415 | -34.3519 | 79.086 | -44.1497 | -123.3275 | -30.1795 | -163.0226 | -22.2515 | 115.1423 | -10.8464 | 39.7573 | -13.9963 | 67.4192 | -8.863 | 89.3169 | -14.2645 | -100.6517 | -19.5604 | 102.668 | -16.4311 | -168.0346 | -11.2748 | -143.2436 | -42.9635 | -34.1861 | -35.7447 | -35.0025 | -48.2174 | -39.2174 | -41.4581 | -33.837 | -36.9894 | -33.13 | -50.2784 | -40.3292 | -41.5681 | 621 | -19.2385 | -27.7683 | -18.7413 | -30.5136 | -19.6052 | -31.8797 | -19.2706 | -29.1921 | 621 | -24.8593 | -28.0117 | -26.0248 | -39.7358 | -30.7358 | -31.3984 | -25.3554 | -26.9297 | -25.9116 | -38.1577 | -30.1265 | -32.3672 | -25.2084 | -26.767 | -24.1523 | -41.7968 | -31.8476 | -31.5084 | -25.7045 | -25.685 | -24.0391 | -40.2187 | -31.2383 | -32.4772
622 | -9.0639 | 0 | -8.451 | 0 | -9.85 | 0 | -8.9686 | 0 | -34.8329 | -116.9447 | -19.4908 | -23.1396 | -39.4386 | -78.0805 | -30.591 | -25.7245 | -43.7375 | -61.1902 | -29.7313 | 93.868 | -37.2816 | -33.4891 | -19.6904 | 95.9218 | -37.038 | 32.8241 | -37.3202 | 75.8215 | -44.7598 | -136.614 | -29.1478 | -167.3957 | -17.826 | 101.8829 | -11.0514 | 37.1519 | -14.2708 | 62.5647 | -9.1815 | 80.551 | -13.814 | -109.6427 | -23.9122 | 102.0979 | -17.1277 | 179.4939 | -11.9111 | -157.7219 | -42.2962 | -33.785 | -35.995 | -35.1712 | -48.7766 | -38.8554 | -40.8026 | -33.7563 | -36.6381 | -33.1346 | -50.7166 | -40.6235 | -41.9953 | 622 | -19.3232 | -29.0529 | -18.8007 | -29.1367 | -19.5375 | -33.9173 | -19.1574 | -28.3923 | 622 | -24.6924 | -27.5742 | -26.1073 | -40.3256 | -30.4044 | -30.9526 | -25.3053 | -26.7881 | -26.2026 | -38.9266 | -29.8868 | -31.834 | -24.7211 | -26.9311 | -24.0707 | -42.2656 | -32.1725 | -32.1453 | -25.334 | -26.145 | -24.166 | -40.8666 | -31.6549 | -33.0267
623 | -9.1249 | 0 | -8.5093 | 0 | -9.6409 | 0 | -8.7745 | 0 | -34.3532 | -119.7188 | -18.2894 | -23.175 | -42.4252 | -87.7263 | -31.9539 | -19.224 | -46.409 | -82.323 | -28.8764 | 72.5086 | -37.168 | -30.2989 | -18.4332 | 95.5186 | -38.2291 | 14.5392 | -38.6852 | 95.0483 | -46.2829 | -145.1547 | -28.2896 | -175.9562 | -15.8726 | 85.992 | -10.8357 | 35.9507 | -14.6048 | 61.3411 | -9.9464 | 73.6028 | -13.3548 | -119.4899 | -24.0811 | 129.378 | -18.2318 | 174.7127 | -13.5701 | -169.3614 | -42.0205 | -32.9485 | -36.3164 | -34.9625 | -50.0172 | -38.7754 | -40.5503 | -33.0308 | -36.5527 | -33.5209 | -50.1121 | -41.3454 | -43.6224 | 623 | -18.1669 | -29.8819 | -17.7572 | -28.6159 | -18.3308 | -34.5488 | -17.969 | -27.808 | 623 | -23.9059 | -27.4278 | -25.8376 | -41.5079 | -30.2661 | -30.9094 | -24.5215 | -26.9118 | -26.188 | -40.3763 | -30.0009 | -31.7758 | -23.8236 | -27.1915 | -24.396 | -41.6028 | -32.8361 | -33.9815 | -24.4392 | -26.6755 | -24.7464 | -40.4712 | -32.5709 | -34.8479
624 | -9.1479 | 0 | -8.6349 | 0 | -9.5195 | 0 | -8.6189 | 0 | -33.8824 | -125.0582 | -16.9724 | -28.4207 | -46.2403 | -81.1134 | -31.749 | -11.1969 | -51.6715 | -89.8083 | -28.8268 | 51.5143 | -36.4317 | -31.1878 | -17.173 | 90.0733 | -40.3398 | -1.912 | -36.8132 | 109.1228 | -47.8425 | -146.4088 | -27.7661 | 173.7839 | -14.9051 | 71.7576 | -10.481 | 33.0431 | -14.475 | 61.3104 | -10.6862 | 69.0433 | -13.5321 | -129.179 | -20.3575 | 137.3318 | -18.8263 | 173.3182 | -15.4136 | -178.3812 | -42.2939 | -32.1907 | -36.6206 | -34.6564 | -51.3167 | -38.8119 | -40.7494 | -32.1882 | -36.6631 | -34.0914 | -49.3586 | -42.1934 | -45.6473 | 624 | -16.8798 | -29.6484 | -16.5642 | -28.7266 | -17.1011 | -33.4472 | -16.7666 | -27.4921 | 624 | -23.0403 | -27.5152 | -25.5085 | -42.6818 | -30.177 | -31.2299 | -23.5533 | -27.1436 | -26.0375 | -41.7972 | -30.193 | -32.1305 | -23.0428 | -27.4727 | -24.9435 | -40.7237 | -33.5585 | -36.1278 | -23.5558 | -27.1011 | -25.4725 | -39.8391 | -33.5745 | -37.0284
625 | -9.1062 | 0 | -8.7312 | 0 | -9.4968 | 0 | -8.4695 | 0 | -33.5985 | -133.8112 | -15.9563 | -38.1056 | -47.9278 | -61.3594 | -30.2525 | -8.6338 | -59.492 | -33.2572 | -29.4825 | 31.712 | -35.465 | -37.5544 | -16.2562 | 80.1053 | -43.6217 | -14.5252 | -34.2033 | 106.0403 | -48.7117 | -142.0809 | -27.66 | 161.7493 | -14.8142 | 58.4634 | -10.0506 | 28.2505 | -13.918 | 60.5215 | -11.2976 | 67.262 | -14.108 | -138.5907 | -16.7523 | 125.6288 | -18.2546 | 175.3525 | -17.5765 | 178.978 | -43.1856 | -31.6583 | -36.92 | -34.3887 | -52.0645 | -39.0411 | -41.3874 | -31.5671 | -36.8484 | -34.4617 | -48.8874 | -42.7624 | -47.7791 | 625 | -15.8795 | -28.5971 | -15.6157 | -29.4165 | -16.1965 | -31.6911 | -15.8882 | -27.5182 | 625 | -22.4609 | -27.7422 | -25.2825 | -43.3333 | -30.3099 | -31.8906 | -22.8359 | -27.3516 | -25.9192 | -42.5677 | -30.5716 | -32.9179 | -22.5521 | -27.8138 | -25.3555 | -40.1562 | -34.0312 | -38.2823 | -22.9271 | -27.4232 | -25.9922 | -39.3906 | -34.2929 | -39.3096

## 19m_channel_Conn2
[62 empty] | Parameter | [8 empty] | Parameter
[62 empty] | Frequency | [8 empty] | Frequency
Parameter | Insertion loss Magnitude in dB | [7 empty] | NEXT loss near Magnitude in dB | [11 empty] | NEXT loss far Magnitude in dB | [11 empty] | Return loss nearMagnitude in dB | [7 empty] | Return loss farMagnitude in dB | [8 empty] | FEXT loss
Frequency | '45 | '45 | '12 | '12 | '36 | '36 | '78 | '78 | '12-45 | '12-45 | '36-45 | '36-45 | '45-78 | '45-78 | '12-36 | '12-36 | '12-78 | '12-78 | '36-78 | '36-78 | '12-45 | '12-45 | '36-45 | '36-45 | '45-78 | '45-78 | '12-36 | '12-36 | '12-78 | '12-78 | '36-78 | '36-78 | '45 | '45 | '12 | '12 | '36 | '36 | '78 | '78 | '45 | '45 | '12 | '12 | '36 | '36 | '78 | '78 |  | '12-45 | '36-45 | '45-78 | '12-36 | '12-78 | '36-78 | '45-12 | '45-36 | '78-45 | '36-12 | '78-12 | '78-36 |  | Pr1 PSNEXT | Pr2 PSNEXT | Pr3 PSNEXT | Pr4 PSNEXT | Pr1 PSNEXT | Pr2 PSNEXT | Pr3 PSNEXT | Pr4 PSNEXT |  | 12-1ELFEXT | 13-1ELFEXT | 14-1ELFEXT | 23-2ELFEXT | 24-2ELFEXT | 34-3ELFEXT | 12-2ELFEXT | 13-3ELFEXT | 14-4ELFEXT | 23-3ELFEXT | 24-4ELFEXT | 34-4ELFEXT | 21-1ELFEXT | 31-1ELFEXT | 41-1ELFEXT | 32-2ELFEXT | 42-2ELFEXT | 43-3ELFEXT | 21-2ELFEXT | 31-3ELFEXT | 41-4ELFEXT | 32-3ELFEXT | 42-4ELFEXT | 43-4ELFEXT
1 | -0.4683 | 0 | -0.4097 | 0 | -0.4292 | 0 | -0.4683 | 0 | -106.1069 | -79.457 | -87.3575 | -132.3129 | -90.5013 | -113.2995 | -101.466 | -116.7285 | -94.5847 | 53.8869 | -99.3741 | -130.8111 | -104.125 | -147.478 | -86.9511 | -144.7838 | -90.2287 | -123.6732 | -99.1391 | -177.9119 | -95.2953 | 56.2242 | -95.147 | 172.0679 | -30.6694 | 1.0286 | -30.1665 | -21.683 | -30.4552 | -4.3561 | -32.043 | -32.4836 | -30.5158 | -8.9341 | -31.537 | -32.6244 | -26.6046 | 8.8615 | -30.5673 | -18.6512 | -84.409 | -92.827 | -77.8465 | -84.0809 | -99.8348 | -79.9989 | -84.7769 | -91.6167 | -77.7573 | -84.1441 | -101.23 | -79.8355 | -81.4079 | 1 | -85.6018 | -93.5279 | -86.9369 | -88.6824 | -85.2212 | -93.4099 | -86.1164 | -88.0971 | 1 | -91.1484 | -77.289 | -83.6126 | -99.4251 | -79.5892 | -84.3477 | -91.207 | -77.3281 | -83.6126 | -99.4056 | -79.5306 | -84.3086 | -92.3587 | -77.3782 | -83.6758 | -100.8203 | -79.4258 | -80.9787 | -92.4173 | -77.4173 | -83.6758 | -100.8008 | -79.3672 | -80.9396
2 | -0.522 | 0 | -0.4752 | 0 | -0.4986 | 0 | -0.5455 | 0 | -94.9496 | -95.0125 | -87.8293 | -143.1262 | -85.8492 | -133.4186 | -99.6333 | -118.161 | -93.2604 | 27.8572 | -99.3899 | -63.6168 | -96.492 | -179.122 | -87.4514 | 175.3613 | -86.8654 | -163.3817 | -92.3312 | 132.0793 | -91.581 | 29.6486 | -90.9951 | 100.8505 | -24.1272 | -15.0539 | -25.1225 | -24.3753 | -23.6675 | -15.9072 | -26.4722 | -24.2546 | -24.142 | -18.3014 | -26.2459 | -24.0583 | -22.3016 | -20.5017 | -25.2966 | -27.7291 | -78.8351 | -84.3156 | -72.1554 | -79.1788 | -95.2062 | -74.7453 | -78.8111 | -84.3619 | -72.0377 | -79.2486 | -95.522 | -74.5806 | -74.6848 | 2 | -83.4018 | -90.454 | -87.2762 | -84.9652 | -83.8927 | -88.2282 | -84.9783 | -84.5 | 2 | -83.8399 | -71.5157 | -78.6568 | -94.731 | -74.2701 | -78.3125 | -83.8867 | -71.5391 | -78.6333 | -94.7076 | -74.1998 | -78.2656 | -83.7936 | -71.6334 | -78.7266 | -95.0468 | -74.1054 | -74.1862 | -83.8404 | -71.6568 | -78.7031 | -95.0234 | -74.0351 | -74.1393
3 | -0.5954 | 0 | -0.5602 | 0 | -0.5719 | 0 | -0.5954 | 0 | -92.3725 | -131.7024 | -87.9174 | -107.6213 | -90.7545 | -132.1348 | -93.4838 | -120.9079 | -97.9296 | -21.3116 | -89.4422 | -79.2933 | -94.0087 | 126.1808 | -96.1534 | 73.6235 | -92.0253 | 125.8268 | -90.0023 | 86.5995 | -95.2217 | 2.086 | -90.102 | 48.1815 | -25.1432 | -46.7753 | -26.5822 | -56.0521 | -24.6754 | -46.3487 | -27.801 | -57.062 | -24.7076 | -49.9782 | -27.4663 | -56.0151 | -23.7791 | -57.5833 | -26.7786 | -64.2804 | -75.6203 | -80.3351 | -68.8117 | -76.2101 | -92.4718 | -71.4718 | -75.486 | -80.2711 | -68.7243 | -76.111 | -91.525 | -71.3102 | -71.4422 | 3 | -85.1785 | -89.2499 | -84.9475 | -86.6986 | -88.972 | -87.7025 | -86.539 | -87.202 | 3 | -79.6757 | -68.1289 | -75.6147 | -91.9116 | -70.9116 | -74.9141 | -79.7109 | -68.1524 | -75.6147 | -91.8999 | -70.8764 | -74.8906 | -79.7397 | -68.2163 | -75.5156 | -90.9648 | -70.75 | -70.8703 | -79.7749 | -68.2398 | -75.5156 | -90.9531 | -70.7148 | -70.8468
4 | -0.6648 | 0 | -0.653 | 0 | -0.6648 | 0 | -0.6999 | 0 | -94.5528 | -151.3386 | -80.9404 | -93.1525 | -83.666 | -57.309 | -89.2289 | -153.166 | -97.2981 | 134.4263 | -86.7712 | -111.2486 | -94.0416 | 74.464 | -83.1498 | -49.7545 | -84.0825 | -30.4495 | -89.9838 | 54.136 | -100.9874 | 101.2496 | -93.5314 | 13.0105 | -29.2898 | -64.175 | -32.7477 | -77.6444 | -28.9561 | -62.6389 | -34.6382 | -81.4291 | -28.4651 | -72.7618 | -33.7569 | -79.2753 | -29.2605 | -84.2008 | -33.1975 | -98.5253 | -73.342 | -77.5413 | -66.428 | -74.2131 | -90.053 | -69.1897 | -73.2858 | -77.2858 | -66.5007 | -74.1218 | -89.6062 | -69.1452 | -69.051 | 4 | -78.961 | -87.6168 | -79.4498 | -81.8119 | -80.3894 | -88.3041 | -82.0141 | -83.5367 | 4 | -76.621 | -65.8359 | -73.5483 | -89.4 | -68.5367 | -72.621 | -76.6328 | -65.8359 | -73.5132 | -89.3882 | -68.4898 | -72.5859 | -76.8765 | -65.7632 | -73.457 | -88.9532 | -68.4922 | -68.3862 | -76.8883 | -65.7632 | -73.4219 | -88.9414 | -68.4453 | -68.3511
5 | -0.7459 | 0 | -0.7341 | 0 | -0.7459 | 0 | -0.7576 | 0 | -95.9908 | -112.6392 | -75.702 | -110.1282 | -75.672 | -77.314 | -87.7734 | 174.574 | -86.9417 | 100.625 | -88.0543 | -141.1792 | -99.2366 | -10.9501 | -76.6556 | -91.8547 | -76.2983 | -82.8051 | -89.7943 | 28.3337 | -87.056 | 93.138 | -98.0366 | -78.7048 | -33.0927 | -46.8636 | -39.2878 | -11.9914 | -32.4836 | -43.4249 | -40.0115 | 7.6951 | -33.7979 | -65.3067 | -40.7582 | -6.7423 | -37.5168 | -49.0294 | -48.2265 | 25.1963 | -71.5783 | -75.2737 | -64.594 | -72.5666 | -88.676 | -67.4885 | -71.4373 | -75.0505 | -64.6521 | -72.5544 | -87.3357 | -67.4998 | -67.0543 | 5 | -72.6565 | -84.0409 | -75.2089 | -75.1319 | -73.4515 | -85.0343 | -76.4197 | -75.9213 | 5 | -74.3046 | -63.9062 | -71.8207 | -87.9419 | -66.7544 | -70.6914 | -74.3164 | -63.9062 | -71.809 | -87.9301 | -66.7309 | -70.6797 | -74.5278 | -63.8481 | -71.8085 | -86.6016 | -66.7657 | -66.3084 | -74.5396 | -63.8481 | -71.7968 | -86.5898 | -66.7422 | -66.2967
6 | -0.8271 | 0 | -0.792 | 0 | -0.8271 | 0 | -0.8154 | 0 | -88.2387 | -105.4168 | -73.3781 | -134.2351 | -72.5274 | -105.3752 | -89.638 | 143.5004 | -82.2918 | 67.7782 | -92.2375 | -127.9007 | -90.0769 | -129.0013 | -73.7115 | -130.4667 | -72.3193 | -125.0925 | -93.8834 | -6.9671 | -82.19 | 63.5617 | -94.537 | 161.6194 | -30.827 | -35.5301 | -31.1566 | -4.7788 | -30.1172 | -34.2397 | -31.1644 | 0.1903 | -32.7706 | -40.5923 | -32.2426 | -2.6134 | -31.2678 | -24.7368 | -32.7675 | 6.6159 | -70.1108 | -73.2866 | -63.0444 | -71.146 | -87.5015 | -66.0444 | -70.0732 | -73.1201 | -63.1592 | -71.1435 | -85.5732 | -66.1474 | -65.4171 | 6 | -69.8581 | -80.7126 | -73.2217 | -72.0497 | -69.9076 | -81.2896 | -73.6345 | -71.8699 | 6 | -72.293 | -62.3321 | -70.3189 | -86.7095 | -65.2524 | -69.2461 | -72.3281 | -62.3321 | -70.3306 | -86.6744 | -65.229 | -69.2578 | -72.4595 | -62.2173 | -70.3164 | -84.7812 | -65.3554 | -64.59 | -72.4946 | -62.2173 | -70.3281 | -84.7461 | -65.332 | -64.6017
7 | -0.8735 | 0 | -0.8735 | 0 | -0.8853 | 0 | -0.8735 | 0 | -83.9883 | -127.1381 | -73.4072 | -158.5571 | -71.8922 | -133.9556 | -94.5923 | 138.4142 | -80.2525 | 35.6575 | -87.7724 | -82.8078 | -84.5015 | -177.3813 | -73.5928 | -168.9893 | -71.2701 | -166.8302 | -102.6218 | -57.6383 | -80.3273 | 31.6875 | -87.3063 | 124.6927 | -29.6116 | -48.7561 | -28.9486 | -29.1064 | -29.2452 | -48.8387 | -29.0741 | -27.6685 | -30.6222 | -48.3077 | -30.3743 | -27.2519 | -29.2083 | -45.8223 | -30.2659 | -24.5527 | -68.7954 | -71.6743 | -61.729 | -69.854 | -87.0102 | -64.8305 | -68.8501 | -71.5884 | -61.8774 | -69.9204 | -84.1938 | -64.936 | -64.1239 | 7 | -69.4193 | -78.6093 | -73.2193 | -71.2041 | -69.1395 | -78.9023 | -73.4067 | -70.6663 | 7 | -70.7149 | -61.0039 | -68.9805 | -86.1367 | -63.957 | -67.9648 | -70.7149 | -60.9921 | -68.9805 | -86.1249 | -63.957 | -67.9766 | -70.8008 | -60.8555 | -69.0469 | -83.3203 | -64.0625 | -63.2386 | -70.8008 | -60.8437 | -69.0469 | -83.3085 | -64.0625 | -63.2504
8 | -0.9435 | 0 | -0.9435 | 0 | -0.9553 | 0 | -0.9318 | 0 | -81.823 | -156.0124 | -75.9884 | -174.0971 | -74.37 | -155.1864 | -95.1454 | 178.8169 | -80.3481 | 8.8 | -82.7817 | -103.56 | -81.0248 | 143.1859 | -76.4113 | 148.3725 | -72.5697 | 148.4633 | -95.3474 | 135.5376 | -80.8433 | -2.8354 | -85.2741 | 86.8947 | -30.5343 | -62.1617 | -29.8774 | -54.9852 | -30.5389 | -62.4871 | -30.1502 | -56.0283 | -30.7333 | -62.0629 | -32.0219 | -51.0516 | -30.532 | -65.6803 | -31.4082 | -53.3521 | -67.7023 | -70.3937 | -60.6945 | -68.7492 | -85.6828 | -63.7609 | -67.7678 | -70.3185 | -60.842 | -68.8029 | -83.2912 | -63.842 | -63.1002 | 8 | -71.6547 | -77.9297 | -75.1198 | -72.9192 | -70.6507 | -77.8449 | -75.8319 | -71.769 | 8 | -69.375 | -59.8985 | -67.8057 | -84.7393 | -62.8174 | -66.8125 | -69.375 | -59.8867 | -67.8174 | -84.7275 | -62.8291 | -66.836 | -69.4502 | -59.751 | -67.8594 | -82.3477 | -62.8985 | -62.1449 | -69.4502 | -59.7392 | -67.8711 | -82.3359 | -62.9102 | -62.1684
9 | -1.0134 | 0 | -1.0016 | 0 | -1.0134 | 0 | -1.0016 | 0 | -81.8695 | 176.0811 | -79.9351 | -151.3275 | -80.3819 | -137.6708 | -88.8868 | 174.1373 | -82.9036 | -14.8408 | -81.3205 | -123.1721 | -80.2776 | 108.4084 | -85.5287 | 65.4005 | -77.295 | 87.9202 | -88.9948 | 97.9024 | -84.5055 | -38.7392 | -85.0477 | 56.3442 | -31.8242 | -61.9221 | -34.0789 | -73.4763 | -32.2368 | -62.0813 | -34.6473 | -77.2094 | -31.4626 | -66.2945 | -37.2978 | -58.0719 | -33.2287 | -66.4328 | -36.4893 | -72.4646 | -66.8431 | -69.3939 | -59.8353 | -67.8666 | -83.7884 | -62.8705 | -66.8727 | -69.1891 | -59.947 | -67.9313 | -82.3141 | -62.8766 | -62.1351 | 9 | -75.882 | -78.8879 | -77.2536 | -76.6433 | -75.1113 | -78.4817 | -81.4339 | -75.9664 | 9 | -68.1757 | -58.9336 | -66.8532 | -82.7868 | -61.8689 | -65.8593 | -68.1875 | -58.9336 | -66.865 | -82.775 | -61.8689 | -65.8711 | -68.3805 | -58.8219 | -66.9179 | -81.3125 | -61.875 | -61.1217 | -68.3923 | -58.8219 | -66.9297 | -81.3007 | -61.875 | -61.1335
10 | -1.0948 | 0 | -1.0713 | 0 | -1.0713 | 0 | -1.0479 | 0 | -83.8424 | 155.0334 | -74.3495 | -125.2321 | -74.268 | -90.739 | -86.4771 | 148.3997 | -87.8832 | -6.1083 | -81.9104 | -138.2847 | -81.6674 | 77.2444 | -77.2223 | -67.2533 | -78.8077 | -34.9208 | -86.5106 | 64.3436 | -103.3726 | -102.8405 | -87.0426 | 15.8846 | -30.2683 | -59.8883 | -40.4847 | -41.1456 | -31.168 | -60.9133 | -42.4462 | -41.0536 | -30.4342 | -69.0036 | -38.6848 | -11.4236 | -31.9133 | -56.9612 | -42.1604 | -20.0405 | -66.1048 | -68.5032 | -59.1048 | -67.3157 | -81.2025 | -62.0931 | -66.0635 | -68.2002 | -59.126 | -67.2627 | -82.0323 | -62.0752 | -61.2168 | 10 | -71.063 | -80.9654 | -73.4271 | -73.4201 | -74.0974 | -80.4139 | -76.3515 | -78.187 | 10 | -67.1054 | -58.0312 | -66.2209 | -80.1312 | -61.0218 | -64.9922 | -67.1289 | -58.0547 | -66.2678 | -80.1312 | -61.0452 | -65.0156 | -67.4084 | -58.01 | -66.1679 | -80.961 | -61.0039 | -60.1455 | -67.4319 | -58.0335 | -66.2148 | -80.961 | -61.0273 | -60.1689
11 | -1.1296 | 0 | -1.1178 | 0 | -1.1178 | 0 | -1.1061 | 0 | -88.7703 | 157.5803 | -69.8631 | -141.7067 | -68.8023 | -106.7346 | -87.8448 | 109.1132 | -84.7424 | 42.8112 | -83.6915 | -127.0422 | -88.2867 | 66.8762 | -70.9411 | -114.4506 | -71.6916 | -107.107 | -86.9215 | 34.6099 | -84.1305 | 89.0091 | -90.8222 | -80.4466 | -27.987 | -76.7673 | -34.5625 | -12.9293 | -29.5268 | -78.9501 | -35.3873 | -10.0291 | -28.6298 | -84.78 | -33.7375 | -10.7226 | -29.2663 | -72.6634 | -34.7042 | -7.0218 | -65.351 | -67.7494 | -58.3901 | -66.808 | -78.8979 | -61.4213 | -65.3327 | -67.2741 | -58.3014 | -66.7546 | -81.5124 | -61.4421 | -60.3611 | 11 | -66.2656 | -81.9891 | -69.621 | -68.5578 | -68.2466 | -81.3203 | -70.7896 | -71.4008 | 11 | -66.1445 | -57.1718 | -65.6784 | -77.7801 | -60.3035 | -64.2149 | -66.1563 | -57.1836 | -65.7019 | -77.7801 | -60.3152 | -64.2266 | -66.6198 | -57.2605 | -65.625 | -80.3946 | -60.3243 | -59.2433 | -66.6316 | -57.2723 | -65.6485 | -80.3946 | -60.336 | -59.255
12 | -1.1881 | 0 | -1.1412 | 0 | -1.1998 | 0 | -1.1529 | 0 | -86.656 | -157.9358 | -68.0949 | -166.7318 | -66.5356 | -131.6833 | -98.0169 | 61.7359 | -78.4546 | 27.6693 | -80.261 | -111.4765 | -87.2161 | 143.5064 | -68.6575 | -155.3887 | -68.4175 | -154.3239 | -92.0723 | 2.3771 | -77.8716 | 53.2152 | -82.6725 | -171.5382 | -27.063 | -104.9134 | -31.2004 | -31.4083 | -29.4876 | -110.3472 | -32.1038 | -30.7775 | -27.9466 | -112.9482 | -32.4437 | -30.8467 | -28.5635 | -103.5933 | -31.8753 | -30.2778 | -64.6091 | -66.9607 | -57.7653 | -66.2224 | -77.8278 | -60.8708 | -64.6373 | -66.4967 | -57.5592 | -66.1217 | -81.442 | -60.9459 | -59.7477 | 12 | -64.2105 | -77.8012 | -67.8347 | -66.0953 | -65.4962 | -77.2484 | -68.4695 | -67.807 | 12 | -65.3086 | -56.3711 | -65.0343 | -76.6866 | -59.7296 | -63.4375 | -65.3555 | -56.3594 | -65.0695 | -76.628 | -59.7179 | -63.4844 | -65.7726 | -56.5772 | -64.9336 | -80.3008 | -59.8047 | -58.5479 | -65.8195 | -56.5655 | -64.9688 | -80.2422 | -59.793 | -58.5948
13 | -1.2702 | 0 | -1.2234 | 0 | -1.2585 | 0 | -1.1999 | 0 | -80.4509 | -164.2323 | -68.467 | 167.3266 | -66.3526 | -154.3683 | -88.6918 | -132.5146 | -75.5903 | 0.5788 | -76.7721 | -130.0059 | -79.3344 | 128.2217 | -68.8617 | 165.371 | -67.3157 | 160.6306 | -93.7937 | 146.6542 | -75.2736 | 21.7012 | -78.6699 | 145.7587 | -27.9254 | -137.8019 | -30.8066 | -56.7498 | -31.6738 | -149.3084 | -32.0682 | -56.8622 | -29.231 | -147.4484 | -34.3707 | -49.9081 | -30.1671 | -141.1306 | -32.1944 | -57.4641 | -63.883 | -66.1291 | -57.1447 | -65.422 | -77.4376 | -60.3205 | -64.0632 | -65.8366 | -56.9265 | -65.4265 | -81.3835 | -60.4538 | -59.4197 | 13 | -64.1686 | -74.2057 | -67.8328 | -65.5248 | -64.8524 | -73.7918 | -68.4174 | -66.4052 | 13 | -64.5664 | -55.6563 | -64.1518 | -76.2142 | -59.0971 | -62.8047 | -64.6132 | -55.668 | -64.2221 | -76.1791 | -59.1206 | -62.8633 | -64.8589 | -55.8745 | -64.1563 | -80.1601 | -59.2304 | -58.1612 | -64.9057 | -55.8862 | -64.2266 | -80.125 | -59.2539 | -58.2198
14 | -1.2902 | 0 | -1.2667 | 0 | -1.3019 | 0 | -1.2667 | 0 | -76.7931 | 173.892 | -71.5239 | 146.7284 | -67.978 | -172.9694 | -81.8047 | -170.3957 | -74.7152 | -29.8077 | -75.3321 | -155.8959 | -75.8553 | 102.3571 | -71.9472 | 125.0541 | -68.7128 | 116.1409 | -82.598 | 109.1288 | -74.6999 | -8.8124 | -75.7354 | 108.4364 | -31.294 | -170.4001 | -32.7256 | -81.1671 | -37.7243 | 161.9098 | -34.9641 | -78.6582 | -33.7409 | 171.0411 | -39.481 | -43.4277 | -35.5972 | 176.4988 | -35.4495 | -79.6248 | -63.3055 | -65.3055 | -56.5477 | -64.6375 | -77.6063 | -59.7196 | -63.4855 | -65.2121 | -56.3332 | -64.6964 | -80.7355 | -59.8371 | -59.1816 | 14 | -66.0097 | -72.126 | -69.7346 | -66.5295 | -66.491 | -71.8473 | -70.1745 | -67.0978 | 14 | -63.9219 | -55.043 | -63.3473 | -76.3396 | -58.4529 | -62.1836 | -63.9454 | -55.0313 | -63.3708 | -76.3044 | -58.4529 | -62.2188 | -64.0153 | -55.2575 | -63.4062 | -79.4688 | -58.5704 | -57.8797 | -64.0388 | -55.2458 | -63.4297 | -79.4336 | -58.5704 | -57.9149
15 | -1.3646 | 0 | -1.3139 | 0 | -1.3373 | 0 | -1.3139 | 0 | -75.2984 | 148.6217 | -77.957 | 163.3813 | -70.9525 | -173.1508 | -79.0696 | 155.3015 | -75.9666 | -57.9701 | -77.6626 | 173.2049 | -74.825 | 73.7815 | -82.2751 | 61.3392 | -72.7068 | 55.8493 | -78.5493 | 71.0876 | -76.1452 | -39.3696 | -75.5473 | 69.4848 | -41.1548 | -179.5821 | -37.3701 | -96.5689 | -45.3406 | -2.3161 | -40.7695 | -73.3621 | -45.7671 | 41.8661 | -36.9408 | -1.5655 | -48.0685 | -5.6807 | -41.7639 | -62.3583 | -62.7786 | -64.5403 | -56.0169 | -64.0247 | -77.7591 | -59.1107 | -62.9779 | -64.4857 | -55.8881 | -64.1068 | -79.2279 | -59.1693 | -58.7599 | 15 | -69.002 | -71.7247 | -73.4175 | -69.1098 | -70.3402 | -71.4763 | -73.2087 | -69.7555 | 15 | -63.1211 | -54.5235 | -62.6601 | -76.4452 | -57.7968 | -61.6406 | -63.1718 | -54.5508 | -62.7108 | -76.4218 | -57.7968 | -61.664 | -63.1757 | -54.6523 | -62.7422 | -77.914 | -57.8554 | -57.4226 | -63.2264 | -54.6796 | -62.7929 | -77.8906 | -57.8554 | -57.446
16 | -1.3997 | 0 | -1.3646 | 0 | -1.3997 | 0 | -1.3411 | 0 | -74.8247 | 124.3435 | -72.5265 | -153.6397 | -71.2548 | -152.0049 | -77.9898 | 125.0658 | -79.9935 | -80.9157 | -86.6786 | 155.7304 | -75.5633 | 46.8506 | -75.347 | -98.3858 | -75.0485 | -46.0766 | -77.2781 | 32.5571 | -80.2952 | -62.7851 | -77.8438 | 26.0625 | -34.4959 | -98.5269 | -42.4058 | -70.7099 | -33.1336 | -81.0705 | -38.1772 | -38.496 | -31.8152 | -62.3114 | -32.2606 | -12.4174 | -32.3171 | -75.1925 | -36.9489 | -29.2878 | -62.4038 | -63.9663 | -55.4897 | -63.7085 | -77.064 | -58.6147 | -62.4622 | -63.7904 | -55.3958 | -63.6966 | -77.513 | -58.6029 | -58.1231 | 16 | -67.8589 | -72.3043 | -71.312 | -70.6013 | -70.5432 | -72.531 | -71.9153 | -72.4379 | 16 | -62.3907 | -53.9961 | -62.3088 | -75.6994 | -57.2501 | -61.0625 | -62.4258 | -53.9961 | -62.3674 | -75.6643 | -57.2736 | -61.1211 | -62.5666 | -54.09 | -62.2969 | -76.1484 | -57.2383 | -56.7234 | -62.6017 | -54.09 | -62.3555 | -76.1133 | -57.2618 | -56.782
17 | -1.4465 | 0 | -1.3996 | 0 | -1.4582 | 0 | -1.3996 | 0 | -75.4177 | 103.2656 | -67.5982 | -170.1449 | -67.8165 | -150.7836 | -78.9924 | 98.6554 | -88.0051 | -53.8783 | -82.3911 | -90.5864 | -78.5166 | 23.8787 | -68.613 | -145.1435 | -69.5717 | -126.7203 | -77.5751 | -6.1622 | -90.0106 | -21.5183 | -85.1357 | -37.3321 | -27.54 | -127.872 | -38.9101 | -52.4288 | -28.3845 | -129.3606 | -34.1861 | -55.7096 | -26.3989 | -106.9894 | -30.6097 | -37.9408 | -27.4964 | -120.2461 | -32.5041 | -50.0877 | -62.0367 | -63.6383 | -54.9938 | -63.5797 | -76.3258 | -58.2516 | -61.8957 | -63.2395 | -54.9465 | -63.509 | -76.3137 | -58.134 | -57.2988 | 17 | -64.3426 | -73.6737 | -67.1618 | -67.6276 | -65.816 | -74.8749 | -68.0088 | -69.4147 | 17 | -61.793 | -53.5 | -62.1332 | -74.9262 | -56.852 | -60.4375 | -61.8399 | -53.4883 | -62.1801 | -74.8676 | -56.852 | -60.4961 | -62.1918 | -53.5473 | -62.0625 | -74.9141 | -56.7344 | -55.8406 | -62.2387 | -53.5356 | -62.1094 | -74.8555 | -56.7344 | -55.8992
18 | -1.5168 | 0 | -1.4504 | 0 | -1.5168 | 0 | -1.4465 | 0 | -76.8326 | 88.0895 | -65.8081 | 164.3989 | -65.8467 | -167.7487 | -83.6293 | 82.8599 | -80.4444 | -3.2482 | -74.4257 | -113.3131 | -85.0542 | 21.0759 | -66.341 | 174.6841 | -66.4943 | -172.781 | -80.2779 | -53.7726 | -79.7344 | 19.431 | -81.6962 | 171.4964 | -24.3788 | -163.6477 | -36.7497 | -73.1533 | -25.9099 | -173.5903 | -32.834 | -91.5664 | -23.9113 | -148.6259 | -31.5681 | -67.0144 | -25.3854 | -163.5369 | -30.8304 | -83.5595 | -61.615 | -63.4275 | -54.6384 | -63.4509 | -75.3377 | -58.0525 | -61.466 | -62.8137 | -54.5597 | -63.2668 | -75.634 | -57.8879 | -56.6074 | 18 | -62.6481 | -74.6725 | -65.1861 | -65.1522 | -63.3771 | -76.3575 | -66.0491 | -66.1697 | 18 | -61.2969 | -53.0429 | -61.9341 | -73.8873 | -56.6021 | -59.9492 | -61.3633 | -53.0429 | -62.0044 | -73.8209 | -56.606 | -60.0195 | -61.9107 | -53.1216 | -61.75 | -74.1836 | -56.4375 | -55.0906 | -61.9771 | -53.1216 | -61.8203 | -74.1172 | -56.4414 | -55.1609
19 | -1.5637 | 0 | -1.509 | 0 | -1.5519 | 0 | -1.4816 | 0 | -77.6469 | 81.1191 | -66.4334 | 138.8932 | -65.9368 | 173.5379 | -85.4561 | 126.0624 | -74.7416 | -23.3887 | -71.9179 | -142.2855 | -85.0221 | 78.6687 | -66.6894 | 133.729 | -65.586 | 143.1622 | -83.9903 | -137.2864 | -74.3633 | -4.3342 | -75.7558 | 123.4316 | -23.3285 | 159.2046 | -37.7963 | -103.1904 | -25.2672 | 143.9475 | -33.4933 | -138.7893 | -23.366 | 170.4867 | -36.0084 | -96.7961 | -25.104 | 153.6172 | -30.9311 | -123.1748 | -61.205 | -63.0097 | -54.2988 | -63.0136 | -75.1035 | -57.9082 | -61.0676 | -62.4621 | -54.1965 | -62.8644 | -76.2355 | -57.7355 | -56.1582 | 19 | -63.0156 | -72.7084 | -65.3095 | -64.5256 | -63.0647 | -73.59 | -66.1105 | -64.6916 | 19 | -60.8984 | -52.6328 | -61.4499 | -73.5945 | -56.3992 | -59.5157 | -60.9531 | -52.6446 | -61.532 | -73.5516 | -56.4266 | -59.586 | -61.446 | -52.7351 | -61.3007 | -74.7265 | -56.2265 | -54.6063 | -61.5007 | -52.7469 | -61.3828 | -74.6836 | -56.2539 | -54.6766
20 | -1.5987 | 0 | -1.5557 | 0 | -1.6104 | 0 | -1.5401 | 0 | -77.894 | 75.111 | -69.8436 | 119.666 | -67.4206 | 158.484 | -78.5102 | 125.301 | -72.4782 | -50.1251 | -71.7609 | -171.8004 | -79.9615 | 77.9798 | -69.9927 | 89.1368 | -67.1696 | 101.3553 | -79.9965 | 130.2722 | -72.0984 | -31.3693 | -73.2168 | 83.8112 | -24.2387 | 122.9592 | -41.7559 | -140.0164 | -26.6759 | 103.1268 | -34.4524 | 160.6611 | -24.6516 | 129.82 | -56.799 | -98.3634 | -26.9776 | 110.2251 | -32.0964 | -167.9903 | -60.7794 | -62.4005 | -53.9903 | -62.3809 | -75.4435 | -57.7325 | -60.7471 | -62.0011 | -53.8643 | -62.2667 | -77.3878 | -57.5362 | -55.912 | 20 | -65.2141 | -70.6123 | -67.3418 | -65.1671 | -65.1979 | -70.8736 | -68.0174 | -65.2108 | 20 | -60.4024 | -52.2656 | -60.7822 | -73.8878 | -56.1768 | -59.1367 | -60.4454 | -52.2539 | -60.8408 | -73.8331 | -56.1924 | -59.207 | -60.8018 | -52.3916 | -60.668 | -75.8321 | -55.9805 | -54.3016 | -60.8448 | -52.3799 | -60.7266 | -75.7774 | -55.9961 | -54.3719
21 | -1.6386 | 0 | -1.58 | 0 | -1.6113 | 0 | -1.58 | 0 | -77.8269 | 65.8509 | -75.5043 | 146.8285 | -70.9881 | 161.0457 | -75.7783 | 99.6209 | -72.0115 | -75.2281 | -74.074 | 166.8052 | -78.5014 | 66.1093 | -77.9145 | 6.2375 | -71.8765 | 52.4345 | -76.429 | 74.3726 | -71.6627 | -60.3407 | -73.3769 | 44.9721 | -28.2039 | 88.4987 | -50.415 | 167.6787 | -32.077 | 62.4967 | -33.715 | 94.6004 | -29.1878 | 84.4145 | -37.552 | 11.8342 | -33.1111 | 59.1308 | -33.9861 | 141.7141 | -60.4166 | -61.6353 | -53.6197 | -61.7564 | -75.9361 | -57.3892 | -60.4355 | -61.4042 | -53.5292 | -61.7167 | -77.5566 | -57.205 | -55.6781 | 21 | -69.0553 | -69.7528 | -70.2813 | -67.406 | -70.2136 | -69.7853 | -70.7123 | -67.47 | 21 | -59.7656 | -51.8906 | -60.1178 | -74.3561 | -55.8092 | -58.8242 | -59.8242 | -51.9179 | -60.1764 | -74.3248 | -55.8092 | -58.8555 | -59.9967 | -51.9811 | -60.0781 | -75.9766 | -55.625 | -54.0668 | -60.0553 | -52.0084 | -60.1367 | -75.9453 | -55.625 | -54.0981
22 | -1.6584 | 0 | -1.6154 | 0 | -1.6584 | 0 | -1.5998 | 0 | -78.2657 | 54.9108 | -69.3063 | 177.0284 | -71.6204 | -171.2861 | -75.6075 | 72.7459 | -72.876 | -99.394 | -79.2965 | 176.0975 | -78.7588 | 60.3186 | -71.7442 | -114.4421 | -79.5546 | -66.495 | -75.1791 | 28.857 | -72.8054 | -89.4426 | -76.7325 | -2.763 | -46.7953 | 94.6755 | -55.4153 | 5.8765 | -42.2927 | -137.8396 | -32.3909 | 38.3904 | -40.2298 | -39.9034 | -32.61 | -19.5219 | -36.9754 | -103.5724 | -36.3621 | 87.0718 | -60.0653 | -61.0028 | -53.2059 | -61.3934 | -75.9286 | -57.0262 | -60.1271 | -60.8537 | -53.1779 | -61.3029 | -76.4396 | -56.881 | -55.4478 | 22 | -66.9662 | -70.2699 | -68.0528 | -68.7881 | -70.3947 | -70.1742 | -69.2632 | -70.7204 | 22 | -59.1953 | -51.5195 | -59.735 | -74.3132 | -55.4108 | -58.4687 | -59.2383 | -51.5195 | -59.7936 | -74.2702 | -55.4264 | -58.5273 | -59.3444 | -51.5475 | -59.6445 | -74.8242 | -55.2656 | -53.7894 | -59.3874 | -51.5475 | -59.7031 | -74.7812 | -55.2812 | -53.848
23 | -1.7055 | 0 | -1.6586 | 0 | -1.7289 | 0 | -1.6508 | 0 | -79.3898 | 46.9744 | -64.9083 | 157.7151 | -67.5035 | -167.8829 | -77.5316 | 48.2199 | -75.4454 | -113.6615 | -75.9435 | -139.8425 | -78.7054 | 66.2179 | -66.2543 | -164.4122 | -70.1128 | -162.5257 | -76.6575 | -15.4828 | -76.338 | -115.8987 | -81.0877 | -104.3904 | -28.3004 | -173.17 | -49.7783 | -77.6924 | -27.3176 | 174.4339 | -32.1236 | -10.1232 | -27.3914 | -141.3626 | -31.3805 | -54.3566 | -26.639 | -165.2041 | -39.9524 | 27.7783 | -59.7178 | -60.7295 | -52.8975 | -61.2725 | -75.0772 | -56.6749 | -59.7602 | -60.4281 | -52.8344 | -61.2172 | -75.0336 | -56.6312 | -55.2331 | 23 | -62.9059 | -72.388 | -64.3643 | -66.3512 | -64.5866 | -72.3433 | -65.7467 | -68.9124 | 23 | -58.7226 | -51.1289 | -59.567 | -73.4186 | -55.0163 | -58.0313 | -58.7695 | -51.1055 | -59.6217 | -73.3483 | -55.0241 | -58.1094 | -59.024 | -51.192 | -59.5117 | -73.375 | -54.9726 | -53.5042 | -59.0709 | -51.1686 | -59.5664 | -73.3047 | -54.9804 | -53.5823
24 | -1.7799 | 0 | -1.7096 | 0 | -1.7525 | 0 | -1.6861 | 0 | -80.8412 | 46.5044 | -63.31 | 130.7047 | -65.285 | 177.7093 | -83.5948 | 44.5403 | -78.2147 | -99.7818 | -70.7864 | -155.2746 | -76.3753 | 70.9165 | -64.2081 | 154.6165 | -65.7535 | 156.5021 | -80.5308 | -72.7184 | -86.6173 | -121.5961 | -74.4646 | 159.8138 | -22.5345 | 154.2516 | -45.7666 | -151.9809 | -22.894 | 138.1407 | -33.6424 | -58.9037 | -22.4127 | 176.3635 | -32.8259 | -90.7084 | -22.8228 | 154.2175 | -45.2698 | -56.66 | -59.4055 | -60.7532 | -52.6907 | -61.2766 | -73.9641 | -56.3938 | -59.4088 | -60.2174 | -52.5885 | -61.2447 | -74.2486 | -56.4439 | -54.9832 | 24 | -61.1292 | -75.5761 | -62.5612 | -64.0377 | -61.7498 | -74.6765 | -63.7253 | -65.174 | 24 | -58.4375 | -50.8086 | -59.4967 | -72.2545 | -54.6842 | -57.6563 | -58.5078 | -50.836 | -59.5905 | -72.2116 | -54.7077 | -57.7227 | -58.9733 | -50.9108 | -59.4648 | -72.539 | -54.7343 | -53.2307 | -59.0436 | -50.9382 | -59.5586 | -72.4961 | -54.7578 | -53.2971
25 | -1.8269 | 0 | -1.7449 | 0 | -1.8113 | 0 | -1.7097 | 0 | -80.5601 | 56.0674 | -63.9033 | 103.0665 | -64.5929 | 162.9353 | -81.8493 | 108.3632 | -75.5551 | -84.7421 | -68.9118 | 178.1615 | -73.7867 | 61.4008 | -64.5509 | 115.3841 | -64.3484 | 116.7633 | -81.2689 | -177.3459 | -80.5092 | -25.2085 | -71.2441 | 114.6446 | -20.3702 | 120.7658 | -41.4329 | 149.9056 | -21.5026 | 103.6724 | -37.341 | -117.5337 | -20.5404 | 139.1051 | -37.1504 | -135.3882 | -21.715 | 117.289 | -42.1813 | -163.3159 | -59.101 | -60.7182 | -52.515 | -61.101 | -73.2221 | -56.2494 | -59.1042 | -60.1238 | -52.3191 | -61.1745 | -74.366 | -56.3269 | -54.8075 | 25 | -61.1738 | -73.6501 | -62.6594 | -62.9791 | -61.1924 | -72.3526 | -63.6327 | -63.4544 | 25 | -58.2969 | -50.4922 | -59.2741 | -71.4772 | -54.5045 | -57.2929 | -58.3789 | -50.5078 | -59.3913 | -71.4108 | -54.5397 | -57.3945 | -58.8913 | -50.6881 | -59.3476 | -72.6211 | -54.582 | -52.9962 | -58.9733 | -50.7037 | -59.4648 | -72.5547 | -54.6172 | -53.0978
26 | -1.8388 | 0 | -1.7802 | 0 | -1.8388 | 0 | -1.7567 | 0 | -78.0599 | 58.6245 | -67.0948 | 77.661 | -65.2357 | 148.5787 | -74.843 | 93.6555 | -72.2026 | -96.1373 | -68.8762 | 146.1863 | -72.5084 | 45.2865 | -67.6689 | 74.4759 | -65.0849 | 78.5832 | -75.6387 | 111.1218 | -73.6096 | -48.3444 | -69.0417 | 76.5117 | -20.4973 | 87.7781 | -38.8669 | 108.1165 | -22.5307 | 70.737 | -39.6689 | 149.0215 | -20.8126 | 104.1022 | -45.0054 | 127.4448 | -22.9505 | 82.826 | -37.5048 | 139.2099 | -58.855 | -60.441 | -52.2574 | -60.6871 | -73.0816 | -56.1597 | -58.87 | -59.8934 | -52.038 | -60.8583 | -75.3075 | -56.163 | -54.6357 | 26 | -62.9211 | -69.6402 | -64.4668 | -63.1045 | -62.698 | -68.9627 | -64.9075 | -63.2025 | 26 | -58.0546 | -50.1992 | -58.8483 | -71.3014 | -54.3795 | -57.0312 | -58.1132 | -50.1992 | -58.9304 | -71.2428 | -54.403 | -57.1133 | -58.6022 | -50.4186 | -59.0195 | -73.5273 | -54.3828 | -52.7969 | -58.6608 | -50.4186 | -59.1016 | -73.4687 | -54.4063 | -52.879
27 | -1.8507 | 0 | -1.7921 | 0 | -1.8506 | 0 | -1.7921 | 0 | -75.9962 | 50.0363 | -75.373 | 80.1315 | -66.5016 | 136.9049 | -72.1822 | 65.0848 | -70.8049 | -115.7155 | -71.8135 | 112.5239 | -72.6502 | 29.2649 | -77.0176 | 14.0646 | -68.336 | 40.8669 | -72.7075 | 64.6616 | -71.013 | -77.4835 | -69.6903 | 42.095 | -23.2699 | 56.367 | -38.6639 | 76.8901 | -27.2376 | 42.6667 | -35.7341 | 72.1308 | -23.7547 | 71.6135 | -38.4711 | 25.8023 | -28.0681 | 53.0211 | -35.5552 | 99.9046 | -58.6443 | -59.8083 | -51.9294 | -60.2302 | -73.3044 | -55.9724 | -58.6944 | -59.4092 | -51.7335 | -60.421 | -76.9796 | -55.9405 | -54.4249 | 27 | -65.5603 | -67.7282 | -68.0858 | -64.286 | -66.5584 | -67.2786 | -67.4262 | -64.7719 | 27 | -57.5585 | -49.8828 | -58.3795 | -71.5123 | -54.1803 | -56.8438 | -57.6171 | -49.8829 | -58.4381 | -71.4538 | -54.1803 | -56.9023 | -57.9576 | -50.0787 | -58.5703 | -75.1875 | -54.1484 | -52.5743 | -58.0162 | -50.0788 | -58.6289 | -75.129 | -54.1484 | -52.6328
28 | -1.886 | 0 | -1.8508 | 0 | -1.886 | 0 | -1.8274 | 0 | -74.6378 | 37.4329 | -70.7296 | 148.5987 | -67.9818 | 135.9743 | -72.196 | 34.3409 | -70.5586 | -136.0838 | -84.4287 | 60.4675 | -73.4438 | 19.67 | -73.1443 | -145.3723 | -77.4417 | 0.3884 | -72.2578 | 23.5314 | -70.3684 | -107.5977 | -73.3816 | 8.2455 | -32.5676 | 36.8079 | -41.2044 | 60.7566 | -38.9072 | 113.4272 | -33.1629 | 21.2372 | -33.5398 | 53.8725 | -34.8173 | -22.7378 | -39.698 | 141.5262 | -35.9706 | 69.4646 | -58.4335 | -59.1288 | -51.5624 | -59.914 | -73.8046 | -55.7773 | -58.5188 | -58.8938 | -51.4485 | -60.1047 | -76.886 | -55.7063 | -54.2843 | 28 | -65.5586 | -67.3846 | -68.2841 | -66.0086 | -69.5174 | -67.0647 | -68.1292 | -68.0745 | 28 | -57.0078 | -49.5625 | -58.028 | -71.9538 | -53.9265 | -56.6328 | -57.043 | -49.5625 | -58.0866 | -71.9186 | -53.9499 | -56.6914 | -57.2428 | -49.6764 | -58.2187 | -75.0352 | -53.8555 | -52.3983 | -57.278 | -49.6764 | -58.2773 | -75 | -53.8789 | -52.4569
29 | -1.9331 | 0 | -1.8706 | 0 | -1.9448 | 0 | -1.8745 | 0 | -73.3754 | 22.2684 | -64.9331 | 129.1474 | -68.6688 | 142.9115 | -74.8961 | 4.8503 | -71.3287 | -155.3958 | -75.3011 | -126.419 | -73.8634 | 16.3679 | -66.3252 | 166.6078 | -76.4415 | 157.3814 | -74.6337 | -17.0059 | -71.4395 | -137.1018 | -93.8415 | -54.1489 | -29.2339 | 149.1233 | -43.5879 | 86.6134 | -24.9381 | 132.4798 | -32.655 | -23.7229 | -29.0432 | 161.0986 | -34.0569 | -65.9391 | -25.0108 | 145.6679 | -38.6271 | 52.8018 | -58.1564 | -58.8087 | -51.2931 | -59.84 | -73.9494 | -55.5509 | -58.2065 | -58.4839 | -51.2495 | -59.9253 | -75.0581 | -55.5307 | -54.1673 | 29 | -62.9845 | -68.1816 | -64.1677 | -66.2157 | -65.2748 | -68.3187 | -65.7205 | -70.2277 | 29 | -56.5508 | -49.3164 | -57.9069 | -72.0788 | -53.6803 | -56.2617 | -56.6133 | -49.3047 | -57.9655 | -72.0046 | -53.6764 | -56.332 | -56.8756 | -49.36 | -57.9922 | -73.1875 | -53.6601 | -52.2225 | -56.9381 | -49.3483 | -58.0508 | -73.1133 | -53.6562 | -52.2928
30 | -1.9919 | 0 | -1.906 | 0 | -1.9919 | 0 | -1.8864 | 0 | -72.9982 | 5.5988 | -63.0131 | 100.3127 | -68.2179 | 137.9423 | -85.0346 | -11.2591 | -74.2369 | -168.9641 | -69.0743 | -158.0846 | -73.6674 | 12.8185 | -64.0559 | 127.9705 | -67.9564 | 117.8425 | -83.4632 | -71.4024 | -74.5726 | -166.1048 | -74.6696 | 118.4935 | -21.5456 | 124.5276 | -38.1933 | 102.6485 | -20.4535 | 104.0675 | -33.8761 | -69.0895 | -21.6663 | 136.2325 | -35.2617 | -112.3759 | -20.6165 | 115.9651 | -41.2171 | 69.4905 | -57.8871 | -58.809 | -51.0941 | -59.9926 | -73.7972 | -55.3637 | -57.8669 | -58.3161 | -51.0857 | -59.8786 | -73.3669 | -55.4607 | -54.0385 | 30 | -61.5456 | -70.4108 | -62.0303 | -65.0558 | -62.2469 | -70.8419 | -63.6488 | -66.3997 | 30 | -56.3242 | -49.0938 | -58.0007 | -71.8912 | -53.4577 | -55.875 | -56.4101 | -49.0938 | -58.1062 | -71.8053 | -53.4773 | -55.9805 | -56.8171 | -49.1022 | -57.8867 | -71.4609 | -53.5547 | -52.0466 | -56.903 | -49.1022 | -57.9922 | -71.375 | -53.5743 | -52.1521
31 | -2.039 | 0 | -1.9296 | 0 | -2.0507 | 0 | -1.9452 | 0 | -73.3674 | -9.5314 | -63.416 | 70.558 | -68.3956 | 132.5364 | -78.4809 | 107.3714 | -77.4874 | -154.7267 | -66.8894 | 165.9741 | -73.0976 | 5.0892 | -64.336 | 90.2465 | -65.1692 | 79.006 | -79.3836 | 118.6969 | -84.8922 | 169.8382 | -69.2589 | 83.3957 | -18.8713 | 94.302 | -34.3163 | 87.2963 | -19.1488 | 74.1312 | -36.7792 | -121.326 | -19.0643 | 105.68 | -37.5952 | -169.8045 | -19.3389 | 85.4238 | -37.6198 | 81.3388 | -57.6061 | -58.9615 | -50.9772 | -60.0397 | -73.2311 | -55.2936 | -57.5507 | -58.2343 | -50.9804 | -59.8085 | -72.5195 | -55.4374 | -53.8862 | 31 | -61.8967 | -71.0749 | -61.7117 | -64.351 | -61.4169 | -71.9537 | -63.0225 | -63.706 | 31 | -56.1953 | -48.9414 | -58.0007 | -71.3015 | -53.364 | -55.5 | -56.3047 | -48.9297 | -58.0945 | -71.1804 | -53.3484 | -55.6055 | -56.9225 | -48.9382 | -57.7695 | -70.5899 | -53.5078 | -51.8355 | -57.0319 | -48.9265 | -57.8633 | -70.4688 | -53.4922 | -51.941
32 | -2.0559 | 0 | -1.9656 | 0 | -2.0526 | 0 | -1.9714 | 0 | -73.9981 | -21.6239 | -66.3372 | 41.7529 | -69.1976 | 129.4149 | -70.7783 | 78.5636 | -74.6538 | -130.3707 | -66.966 | 135.0046 | -73.0633 | -4.9801 | -67.4168 | 51.2078 | -64.4849 | 40.5753 | -71.4913 | 72.5385 | -80.1271 | -56.1255 | -67.678 | 49.4891 | -18.717 | 64.1902 | -32.7377 | 66.5066 | -20.2383 | 45.6657 | -40.1162 | 168.5137 | -18.9145 | 75.6181 | -38.6459 | 119.9373 | -20.414 | 56.4534 | -34.8233 | 66.3565 | -57.3959 | -58.858 | -50.8535 | -59.853 | -72.9389 | -55.2603 | -57.3523 | -58.0721 | -50.8332 | -59.6101 | -72.239 | -55.2987 | -53.6264 | 32 | -64.0611 | -68.0226 | -62.8642 | -64.49 | -62.3158 | -68.8592 | -63.7377 | -62.7047 | 32 | -56.0162 | -48.7773 | -57.7971 | -70.9733 | -53.2947 | -55.2997 | -56.1065 | -48.7806 | -57.8816 | -70.8863 | -53.2889 | -55.3809 | -56.8021 | -48.7976 | -57.5542 | -70.2734 | -53.3331 | -51.5738 | -56.8924 | -48.8009 | -57.6387 | -70.1864 | -53.3273 | -51.655
33 | -2.0723 | 0 | -1.9911 | 0 | -2.0759 | 0 | -1.9994 | 0 | -75.0605 | -27.8746 | -74.9226 | 26.0324 | -69.2911 | 131.5402 | -67.8839 | 47.3288 | -70.7006 | -138.5139 | -70.2189 | 105.1335 | -73.6495 | -15.4343 | -77.7169 | -1.2866 | -66.1412 | 0.9487 | -68.4694 | 34.5061 | -72.01 | -85.8088 | -68.1697 | 20.6695 | -21.1287 | 36.4612 | -33.1009 | 47.8433 | -24.653 | 24.2493 | -40.3996 | 92.1467 | -21.2744 | 48.5847 | -37.9144 | 57.5362 | -24.7332 | 34.7845 | -34.1845 | 44.1972 | -57.277 | -58.4321 | -50.6706 | -59.5113 | -72.648 | -55.2368 | -57.2138 | -57.7439 | -50.6504 | -59.3153 | -72.452 | -55.1345 | -53.4153 | 33 | -67.4206 | -65.5429 | -65.3751 | -65.259 | -65.1823 | -66.0492 | -65.0642 | -63.3864 | 33 | -55.6716 | -48.5781 | -57.439 | -70.6569 | -53.2457 | -55.1379 | -55.7528 | -48.5745 | -57.5119 | -70.5721 | -53.2374 | -55.2144 | -56.3598 | -48.5983 | -57.243 | -70.4609 | -53.1434 | -51.3394 | -56.441 | -48.5947 | -57.3159 | -70.3761 | -53.1351 | -51.4159
34 | -2.0948 | 0 | -2.0363 | 0 | -2.1099 | 0 | -2.0196 | 0 | -75.4651 | -22.2752 | -73.3688 | 126.4624 | -68.8806 | 125.8325 | -67.1107 | 16.626 | -68.5283 | -156.6861 | -83.2075 | 97.5969 | -74.429 | -16.4023 | -73.6336 | 179.6066 | -69.8184 | -44.4151 | -67.741 | -2.711 | -68.8083 | -115.9485 | -72.2647 | -11.6227 | -28.3236 | 23.8134 | -34.932 | 39.2965 | -32.1089 | 69.0051 | -39.7384 | 31.8594 | -27.8622 | 38.7309 | -37.819 | 5.6066 | -32.2715 | 77.3691 | -36.0163 | 23.6302 | -57.1933 | -57.8645 | -50.4548 | -59.205 | -72.3769 | -55.1496 | -57.177 | -57.3638 | -50.4698 | -59.091 | -72.3684 | -54.9302 | -53.2812 | 34 | -66.9069 | -64.3979 | -66.1027 | -65.6143 | -67.3601 | -64.7383 | -65.6718 | -65.2987 | 34 | -55.269 | -48.375 | -57.1102 | -70.3406 | -53.1133 | -55.0671 | -55.3275 | -48.3599 | -57.1854 | -70.267 | -53.13 | -55.1574 | -55.7697 | -48.36 | -56.9962 | -70.3321 | -52.8939 | -51.1713 | -55.8282 | -48.3449 | -57.0714 | -70.2585 | -52.9106 | -51.2616
35 | -2.1112 | 0 | -2.0702 | 0 | -2.1213 | 0 | -2.0529 | 0 | -73.2985 | -17.1611 | -66.0324 | 103.9945 | -68.0627 | 122.4165 | -68.4438 | -10.3428 | -67.4841 | -178.2975 | -73.7118 | -162.1756 | -73.3521 | -17.8547 | -66.6897 | 136.5189 | -77.6008 | -111.4082 | -69.2286 | -41.2471 | -67.5944 | -148.5385 | -90.5679 | -36.2413 | -28.4629 | 106.7814 | -35.9852 | 48.2905 | -23.361 | 95.946 | -41.0263 | -20.1549 | -28.0343 | 109.2876 | -39.0809 | -45.2213 | -23.5957 | 106.131 | -40.6761 | 19.6444 | -57.024 | -57.4774 | -50.2565 | -59.0474 | -71.8873 | -54.9462 | -57.0155 | -57.0431 | -50.287 | -58.9803 | -71.9022 | -54.7619 | -53.1519 | 35 | -63.4455 | -64.3372 | -63.6155 | -64.2338 | -65.5612 | -64.6896 | -64.7545 | -67.1612 | 35 | -54.9319 | -48.1758 | -56.9362 | -69.8171 | -52.876 | -54.8942 | -54.9729 | -48.1657 | -56.9945 | -69.766 | -52.8933 | -54.9626 | -55.3662 | -48.1453 | -56.8691 | -69.832 | -52.6917 | -51.0306 | -55.4072 | -48.1352 | -56.9274 | -69.7809 | -52.709 | -51.099
36 | -2.1675 | 0 | -2.0996 | 0 | -2.1927 | 0 | -2.0889 | 0 | -70.5422 | -29.247 | -63.8092 | 72.3632 | -69.194 | 106.3982 | -71.9354 | -24.6162 | -67.9064 | 160.7477 | -67.0842 | 176.1797 | -72.0126 | -32.5682 | -64.5408 | 99.4079 | -77.2025 | 113.8274 | -73.5399 | -89.6014 | -68.0159 | 178.815 | -74.2594 | 91.7969 | -20.7768 | 95.6359 | -33.9129 | 53.939 | -19.2545 | 73.5065 | -44.7623 | -78.7654 | -20.856 | 101.308 | -40.7931 | -105.9452 | -19.4014 | 84.3518 | -41.8307 | 57.441 | -56.7722 | -57.4082 | -50.1486 | -59.0651 | -71.319 | -54.7481 | -56.7871 | -56.9388 | -50.1518 | -59.0566 | -71.2871 | -54.7747 | -53.1061 | 36 | -62.0437 | -65.0273 | -61.7023 | -63.2054 | -63.6306 | -65.7662 | -63.6325 | -66.6866 | 36 | -54.7713 | -47.9843 | -56.8976 | -69.2194 | -52.6485 | -54.5944 | -54.8392 | -47.9591 | -56.9762 | -69.1263 | -52.6592 | -54.6982 | -55.2407 | -47.9811 | -56.8891 | -69.1875 | -52.6751 | -50.9134 | -55.3086 | -47.9559 | -56.9677 | -69.0944 | -52.6858 | -51.0172
37 | -2.203 | 0 | -2.1301 | 0 | -2.2485 | 0 | -2.1239 | 0 | -68.9824 | -48.8254 | -64.3565 | 40.2113 | -71.8577 | 90.8941 | -74.7617 | -1.6586 | -69.6285 | 142.8122 | -65.1204 | 145.8834 | -71.9281 | -56.1097 | -65.0483 | 63.2945 | -72.0856 | 54.599 | -78.0127 | 168.9556 | -70.4207 | 147.4147 | -68.7676 | 59.3013 | -17.9946 | 69.4396 | -31.8707 | 41.5806 | -18.2479 | 46.4999 | -47.9324 | -166.4739 | -18.1102 | 76.5794 | -40.0095 | -170.4939 | -18.2207 | 58.3143 | -37.2111 | 60.7636 | -56.5566 | -57.4993 | -50.0436 | -59.1074 | -70.8535 | -54.593 | -56.4895 | -56.854 | -50.035 | -59.0988 | -70.8098 | -54.8462 | -53.0447 | 37 | -62.5311 | -65.7067 | -61.5014 | -63.1721 | -63.5779 | -67.6772 | -63.3597 | -65.4448 | 37 | -54.651 | -47.832 | -56.9044 | -68.7234 | -52.4629 | -54.241 | -54.7239 | -47.7865 | -56.9835 | -68.605 | -52.4691 | -54.3656 | -55.2963 | -47.8406 | -56.8958 | -68.6797 | -52.7161 | -50.7962 | -55.3692 | -47.7951 | -56.9749 | -68.5613 | -52.7223 | -50.9208
38 | -2.2659 | 0 | -2.1516 | 0 | -2.2704 | 0 | -2.1555 | 0 | -68.5295 | -69.979 | -67.5532 | 9.2108 | -77.8841 | 89.9236 | -70.0331 | 9.5655 | -72.9532 | 137.0684 | -64.8191 | 117.0396 | -73.674 | -86.1467 | -68.4129 | 25.141 | -71.0672 | 5.6783 | -71.3653 | 85.4005 | -76.2931 | 118.8035 | -67.1132 | 26.1087 | -17.7677 | 41.8962 | -31.4671 | 20.7955 | -19.675 | 20.2232 | -46.111 | 116.7631 | -17.7815 | 50.1729 | -37.8832 | 144.1421 | -19.3535 | 34.0962 | -35.5739 | 40.6268 | -56.332 | -57.5036 | -49.9189 | -59.0234 | -70.5642 | -54.5446 | -56.218 | -56.7001 | -49.9397 | -58.9797 | -70.5207 | -54.8856 | -52.961 | 38 | -64.7855 | -65.373 | -62.1855 | -64.0163 | -65.7636 | -68.5568 | -63.856 | -65.2858 | 38 | -54.4342 | -47.6738 | -56.7575 | -68.4126 | -52.393 | -53.9476 | -54.5485 | -47.6693 | -56.8679 | -68.2938 | -52.3891 | -54.0625 | -55.2377 | -47.653 | -56.7138 | -68.3691 | -52.734 | -50.6906 | -55.352 | -47.6485 | -56.8242 | -68.2503 | -52.7301 | -50.8055
39 | -2.2766 | 0 | -2.1883 | 0 | -2.2847 | 0 | -2.1801 | 0 | -69.3279 | -91.2609 | -78.0002 | -13.7351 | -78.7572 | 149.6819 | -66.6192 | -10.8192 | -74.8864 | 159.5277 | -66.6582 | 86.309 | -78.419 | -124.5759 | -79.5916 | -32.0935 | -72.6824 | -47.0138 | -67.7863 | 42.1154 | -87.2899 | -136.7767 | -68.177 | -9.3615 | -19.9449 | 16.6556 | -33.0335 | -3.3358 | -24.6124 | 2.6781 | -46.7068 | 69.0416 | -19.7237 | 27.0259 | -36.2828 | 115.3278 | -23.2254 | 20.9289 | -37.0055 | 16.8751 | -56.1695 | -57.2307 | -49.7774 | -58.8727 | -70.3785 | -54.5471 | -56.0438 | -56.4038 | -49.7746 | -58.7996 | -70.4637 | -54.8999 | -52.8404 | 39 | -68.3595 | -64.3532 | -63.4725 | -65.823 | -71.0073 | -67.3816 | -64.8197 | -66.8205 | 39 | -54.1272 | -47.498 | -56.5961 | -68.1902 | -52.3588 | -53.7591 | -54.2155 | -47.4899 | -56.6926 | -68.0938 | -52.367 | -53.8637 | -54.9541 | -47.5008 | -56.523 | -68.2754 | -52.7116 | -50.5557 | -55.0424 | -47.4927 | -56.6195 | -68.179 | -52.7198 | -50.6603
40 | -2.3 | 0 | -2.2273 | 0 | -2.3006 | 0 | -2.1951 | 0 | -71.7365 | -108.009 | -73.7064 | 106.7588 | -73.7721 | 155.5078 | -65.4226 | -39.792 | -71.2886 | 174.1616 | -73.6502 | 65.0238 | -87.4196 | 120.1428 | -73.2363 | 154.5753 | -73.6833 | -121.9864 | -66.796 | 7.1553 | -72.8978 | -141.4046 | -71.9203 | -42.3552 | -26.0473 | 5.6137 | -37.8739 | -28.5751 | -30.4979 | 58.4275 | -54.7636 | 34.8975 | -24.6346 | 19.7807 | -35.2614 | 97.5015 | -26.7096 | 52.7855 | -43.6554 | -2.6644 | -56.0093 | -56.8092 | -49.6367 | -58.7007 | -70.1773 | -54.5631 | -55.9304 | -56.074 | -49.6516 | -58.6335 | -70.3562 | -54.8397 | -52.7684 | 40 | -68.1932 | -63.6828 | -64.287 | -67.9743 | -70.3575 | -65.8129 | -64.937 | -68.0025 | 40 | -53.774 | -47.3516 | -56.4007 | -67.95 | -52.3358 | -53.6298 | -53.8467 | -47.351 | -56.5056 | -67.8767 | -52.368 | -53.7353 | -54.5092 | -47.3367 | -56.3335 | -68.1289 | -52.6124 | -50.4678 | -54.5819 | -47.3361 | -56.4384 | -68.0556 | -52.6446 | -50.5733
41 | -2.2986 | 0 | -2.2437 | 0 | -2.347 | 0 | -2.2276 | 0 | -75.9095 | -102.917 | -66.684 | 77.0114 | -72.3454 | 139.5459 | -66.249 | -71.3776 | -67.9789 | 163.7782 | -78.6627 | 160.7798 | -76.6728 | 23.9616 | -67.2206 | 112.247 | -74.4718 | 148.8634 | -68.2332 | -22.9033 | -68.6249 | -174.7574 | -84.7463 | -133.8691 | -28.0084 | 72.1841 | -63.9885 | -54.9917 | -22.0264 | 74.0936 | -50.4672 | 168.8669 | -26.0676 | 64.1051 | -34.3447 | 84.9516 | -21.4909 | 68.6893 | -46.865 | 107.8334 | -55.8577 | -56.4454 | -49.483 | -58.6702 | -69.9827 | -54.5743 | -55.8296 | -55.886 | -49.4979 | -58.4859 | -69.9741 | -54.7805 | -52.803 | 41 | -65.2505 | -63.7458 | -63.3219 | -66.3613 | -66.0753 | -65.1009 | -64.6445 | -67.5371 | 41 | -53.5874 | -47.1993 | -56.3716 | -67.739 | -52.3306 | -53.4826 | -53.6423 | -47.1509 | -56.4426 | -67.6357 | -52.3467 | -53.602 | -54.1468 | -47.1844 | -56.1873 | -67.7304 | -52.5368 | -50.456 | -54.2017 | -47.136 | -56.2583 | -67.6271 | -52.5529 | -50.5754
42 | -2.349 | 0 | -2.2871 | 0 | -2.4016 | 0 | -2.2585 | 0 | -75.1575 | -72.0634 | -64.6475 | 42.2051 | -72.3007 | 117.5676 | -69.7216 | -102.6887 | -66.313 | 145.3732 | -68.3448 | 156.3842 | -72.7418 | -19.848 | -65.6636 | 76.7044 | -71.7927 | 78.6037 | -72.8898 | -43.075 | -66.776 | 151.0191 | -73.3413 | 94.7823 | -20.7323 | 71.5488 | -39.2247 | 101.0503 | -18.409 | 52.0146 | -41.8321 | 136.1396 | -20.479 | 67.4313 | -33.4944 | 73.5873 | -18.2404 | 51.2098 | -36.9749 | 96.2158 | -55.6785 | -56.2891 | -49.4397 | -58.702 | -69.7098 | -54.5703 | -55.6816 | -55.7766 | -49.4076 | -58.5527 | -69.6895 | -54.6945 | -52.7989 | 42 | -63.6418 | -64.3081 | -62.2477 | -63.5755 | -64.0806 | -65.0213 | -64.3279 | -64.9134 | 42 | -53.4276 | -47.0586 | -56.353 | -67.4227 | -52.2832 | -53.28 | -53.4895 | -47.006 | -56.4435 | -67.3082 | -52.3118 | -53.4231 | -53.9401 | -47.0907 | -56.2037 | -67.4024 | -52.4074 | -50.3973 | -54.002 | -47.0381 | -56.2942 | -67.2879 | -52.436 | -50.5404
43 | -2.4264 | 0 | -2.2987 | 0 | -2.4536 | 0 | -2.2987 | 0 | -71.2734 | -70.1401 | -65.2162 | 6.6749 | -80.2466 | 114.7695 | -80.5779 | -127.1779 | -65.7837 | 126.1002 | -65.2117 | 126.0693 | -72.0474 | -60.9497 | -66.6658 | 42.6573 | -70.348 | 19.258 | -79.8234 | 2.3452 | -66.7977 | 114.9073 | -68.7209 | 54.646 | -17.8813 | 48.7885 | -34.4933 | 77.8857 | -17.6758 | 26.4761 | -38.8445 | 105.018 | -17.8187 | 47.0968 | -33.0628 | 61.7213 | -17.4943 | 27.7942 | -34.1059 | 71.1643 | -55.5143 | -56.2943 | -49.3881 | -58.7721 | -69.3893 | -54.5286 | -55.494 | -55.77 | -49.4147 | -58.576 | -69.2518 | -54.6528 | -52.804 | 43 | -64.1465 | -64.5922 | -62.141 | -62.406 | -64.3157 | -65.4996 | -64.4352 | -63.6092 | 43 | -53.3436 | -46.9883 | -56.3457 | -67.0906 | -52.2299 | -53.0404 | -53.4713 | -46.9611 | -56.4734 | -66.9357 | -52.2299 | -53.1953 | -53.8679 | -46.9617 | -56.1496 | -66.9531 | -52.3541 | -50.3504 | -53.9956 | -46.9345 | -56.2773 | -66.7982 | -52.3541 | -50.5053
44 | -2.4757 | 0 | -2.3364 | 0 | -2.4847 | 0 | -2.3226 | 0 | -68.7115 | -83.5523 | -68.4306 | -30.5494 | -76.3559 | -143.3303 | -75.8061 | -0.4891 | -66.5 | 108.7228 | -65.0658 | 97.1913 | -74.0378 | -106.0095 | -70.8891 | 8.2532 | -68.9897 | -38.822 | -71.3099 | 29.4875 | -68.2602 | 74.8945 | -67.5653 | 22.5225 | -17.5513 | 23.9572 | -33.4157 | 57.7552 | -19.2947 | 2.782 | -38.7173 | 75.2 | -17.5336 | 23.2968 | -33.4094 | 51.7594 | -18.967 | 5.5477 | -34.2883 | 46.9074 | -55.3294 | -56.2785 | -49.2968 | -58.7747 | -69.1809 | -54.548 | -55.309 | -55.6449 | -49.2765 | -58.5903 | -68.9613 | -54.5785 | -52.7295 | 44 | -65.2113 | -64.149 | -63.1761 | -62.5299 | -66.0705 | -65.8054 | -64.8067 | -63.4617 | 44 | -53.1692 | -46.8008 | -56.299 | -66.8445 | -52.2116 | -52.8243 | -53.3085 | -46.7918 | -56.4521 | -66.6962 | -52.2254 | -52.9864 | -53.8028 | -46.8211 | -56.1146 | -66.6249 | -52.2421 | -50.2448 | -53.9421 | -46.8121 | -56.2677 | -66.4766 | -52.2559 | -50.4069
45 | -2.4988 | 0 | -2.3762 | 0 | -2.482 | 0 | -2.3618 | 0 | -67.5381 | -98.2079 | -77.5995 | -78.055 | -68.2159 | -152.2283 | -68.9123 | -31.2373 | -68.0308 | 99.144 | -66.7506 | 71.2895 | -79.3329 | 177.1363 | -89.8464 | -40.3008 | -68.3379 | -99.7406 | -67.1732 | 9.8794 | -72.0611 | 23.4068 | -68.6867 | -8.3761 | -19.4499 | 2.1594 | -34.6798 | 44.6647 | -23.9865 | -8.403 | -41.3584 | 51.1984 | -19.4455 | 1.5191 | -34.4935 | 48.7498 | -23.1481 | -4.5454 | -37.6998 | 30.4134 | -55.17 | -56.1 | -49.1677 | -58.6973 | -68.9747 | -54.5805 | -55.1262 | -55.4078 | -49.1707 | -58.5012 | -68.7082 | -54.525 | -52.6799 | 45 | -64.6286 | -63.3526 | -64.4714 | -62.8442 | -67.9772 | -65.7577 | -64.8403 | -64.6325 | 45 | -52.909 | -46.6719 | -56.1985 | -66.5985 | -52.2043 | -52.6442 | -53.0316 | -46.6887 | -56.3355 | -66.4927 | -52.2187 | -52.7644 | -53.6012 | -46.6689 | -56.0024 | -66.332 | -52.1488 | -50.1979 | -53.7238 | -46.6857 | -56.1394 | -66.2262 | -52.1632 | -50.3181
46 | -2.4981 | 0 | -2.3822 | 0 | -2.4906 | 0 | -2.3966 | 0 | -67.3186 | -110.1439 | -76.4323 | 96.0078 | -64.772 | -176.2453 | -66.7688 | -65.3782 | -69.2673 | 101.1906 | -72.6602 | 61.7549 | -74.6531 | 62.8105 | -73.0598 | 126.4847 | -67.4401 | -161.621 | -66.1215 | -13.846 | -74.9452 | -63.9918 | -73.7929 | -37.7297 | -24.1573 | -4.3543 | -37.4772 | 51.28 | -27.0851 | 35.625 | -48.9988 | 53.9173 | -24.2638 | -5.5877 | -34.7363 | 57.6441 | -26.0689 | 31.4771 | -42.888 | 61.5522 | -55.0705 | -55.886 | -49.0498 | -58.6799 | -68.6643 | -54.722 | -55.015 | -55.1703 | -49.088 | -58.4134 | -68.4095 | -54.5258 | -52.6884 | 46 | -62.6646 | -62.8885 | -65.4155 | -62.9598 | -65.7842 | -65.0789 | -64.7438 | -65.9503 | 46 | -52.6722 | -46.5899 | -56.1818 | -66.2821 | -52.3398 | -52.5244 | -52.7881 | -46.5974 | -56.2833 | -66.1737 | -52.3254 | -52.6184 | -53.3879 | -46.5517 | -55.9153 | -66.0273 | -52.1436 | -50.1978 | -53.5038 | -46.5592 | -56.0168 | -65.9189 | -52.1292 | -50.2918
47 | -2.4967 | 0 | -2.4074 | 0 | -2.5455 | 0 | -2.4295 | 0 | -66.9461 | -117.1175 | -68.9463 | 46.5879 | -63.3643 | 158.0005 | -67.3299 | -103.3726 | -68.1325 | 107.9163 | -74.6902 | 131.3639 | -68.5912 | 7.8318 | -68.142 | 92.5189 | -66.7213 | 138.1308 | -67.4447 | -33.829 | -70.6564 | -146.0753 | -87.5471 | 50.8558 | -25.8267 | 37.1668 | -36.4456 | 80.7131 | -21.0003 | 45.7951 | -45.213 | 116.1018 | -26.1543 | 37.8662 | -32.7698 | 65.3896 | -20.8193 | 43.2896 | -37.0449 | 91.1862 | -54.9317 | -55.6792 | -48.9663 | -58.7638 | -68.3224 | -54.7885 | -54.9582 | -55.0377 | -48.9811 | -58.4387 | -68.1028 | -54.6041 | -52.7549 | 47 | -61.0219 | -62.6706 | -64.6048 | -61.8806 | -62.9717 | -63.9319 | -64.7462 | -65.2218 | 47 | -52.541 | -46.4844 | -56.2671 | -65.915 | -52.3811 | -52.4127 | -52.6303 | -46.4356 | -56.3343 | -65.7769 | -52.359 | -52.5287 | -53.1825 | -46.4696 | -55.942 | -65.6954 | -52.1967 | -50.2094 | -53.2718 | -46.4208 | -56.0092 | -65.5573 | -52.1746 | -50.3254
48 | -2.5461 | 0 | -2.45 | 0 | -2.6154 | 0 | -2.4545 | 0 | -65.93 | -124.5771 | -66.5354 | 3.6363 | -63.9018 | 135.6361 | -71.1731 | -146.792 | -66.0635 | 100.7473 | -67.1443 | 129.3334 | -65.2849 | -34.9512 | -67.1887 | 63.7518 | -66.6122 | 80.5072 | -70.9411 | -35.5706 | -67.0643 | 164.9527 | -72.0325 | 59.2305 | -20.4912 | 42.6161 | -32.1556 | 86.0907 | -18.0178 | 26.1298 | -39.7932 | 102.3843 | -20.5977 | 43.9634 | -30.1027 | 60.1639 | -17.8626 | 25.3658 | -33.1279 | 74.5495 | -54.8454 | -55.5968 | -48.9454 | -58.9118 | -67.9665 | -54.7999 | -54.8719 | -54.9904 | -48.9484 | -58.5516 | -67.8641 | -54.7092 | -52.8247 | 48 | -60.5328 | -62.3722 | -63.0857 | -60.7173 | -61.5159 | -62.4165 | -64.7601 | -63.2113 | 48 | -52.4443 | -46.4023 | -56.3657 | -65.5165 | -52.3499 | -52.2565 | -52.5404 | -46.333 | -56.4573 | -65.3511 | -52.3454 | -52.4174 | -53.0507 | -46.3993 | -56.0055 | -65.4141 | -52.2592 | -50.2093 | -53.1468 | -46.33 | -56.0971 | -65.2487 | -52.2547 | -50.3702
49 | -2.6103 | 0 | -2.4934 | 0 | -2.6751 | 0 | -2.4742 | 0 | -64.8619 | -137.1257 | -66.2526 | -42.9876 | -66.8914 | 125.072 | -79.4083 | 113.7748 | -64.6451 | 84.4895 | -64.0532 | 106.1738 | -63.7629 | -74.5262 | -68.612 | 41.3781 | -67.6184 | 15.1563 | -70.9395 | -3.6424 | -65.3135 | 125.2071 | -68.019 | 29.7743 | -17.821 | 24.0263 | -29.0211 | 76.1879 | -17.5212 | 2.1924 | -38.3826 | 77.1719 | -17.8658 | 24.7773 | -28.2263 | 46.1348 | -17.3328 | 1.9385 | -32.3094 | 51.894 | -54.7013 | -55.5744 | -48.9745 | -58.9669 | -67.7521 | -54.7775 | -54.7629 | -54.9329 | -48.9424 | -58.6418 | -67.6613 | -54.7454 | -52.8491 | 49 | -61.1463 | -61.6682 | -61.9266 | -60.2641 | -61.3599 | -60.9952 | -64.2481 | -62.0409 | 49 | -52.3226 | -46.3321 | -56.3566 | -65.2587 | -52.2841 | -52.0878 | -52.4395 | -46.2673 | -56.4927 | -65.077 | -52.3033 | -52.2887 | -52.9641 | -46.3642 | -56.0315 | -65.1679 | -52.252 | -50.174 | -53.081 | -46.2994 | -56.1676 | -64.9862 | -52.2712 | -50.3749
50 | -2.6572 | 0 | -2.5112 | 0 | -2.6805 | 0 | -2.5033 | 0 | -64.4253 | -154.6894 | -67.1732 | -94.8553 | -69.6439 | 137.4383 | -71.0286 | 5.5633 | -64.4593 | 64.4345 | -63.582 | 80.1234 | -63.703 | -112.5512 | -71.5834 | 34.1619 | -67.6485 | -47.2196 | -66.0208 | -0.9235 | -65.1031 | 87.7841 | -67.2044 | -3.7879 | -17.3603 | 1.1454 | -27.2129 | 61.414 | -19.214 | -20.6411 | -39.8804 | 50.7616 | -17.4093 | 1.2942 | -27.3803 | 28.1404 | -18.9485 | -20.1999 | -34.217 | 31.4737 | -54.5043 | -55.4744 | -48.9042 | -58.9262 | -67.5472 | -54.7712 | -54.5581 | -54.8094 | -48.8838 | -58.6128 | -67.5268 | -54.7508 | -52.8193 | 50 | -61.7964 | -60.9798 | -61.4937 | -60.4334 | -61.7549 | -60.0653 | -62.9261 | -61.7327 | 50 | -52.1522 | -46.2266 | -56.269 | -65.036 | -52.26 | -51.8776 | -52.2982 | -46.2033 | -56.4229 | -64.8667 | -52.2679 | -52.0548 | -52.8172 | -46.247 | -55.9556 | -65.0156 | -52.2396 | -50.1388 | -52.9632 | -46.2237 | -56.1095 | -64.8463 | -52.2475 | -50.316
51 | -2.6762 | 0 | -2.538 | 0 | -2.6762 | 0 | -2.5253 | 0 | -65.1232 | -173.5662 | -68.3813 | -152.63 | -67.313 | 158.998 | -66.282 | -40.0442 | -65.6554 | 44.877 | -65.0904 | 58.5326 | -65.0875 | -150.506 | -72.692 | 50.728 | -66.7166 | -112.4771 | -63.1358 | -18.4175 | -66.3948 | 50.7 | -69.6553 | -33.4394 | -18.8373 | -19.9707 | -26.3888 | 45.6937 | -23.6686 | -31.348 | -44.9442 | 31.9301 | -19.0255 | -21.0986 | -27.7194 | 7.9601 | -23.3189 | -31.4276 | -39.514 | 31.9342 | -54.3319 | -55.2942 | -48.8177 | -58.8124 | -67.4686 | -54.8138 | -54.3623 | -54.6293 | -48.809 | -58.5107 | -67.4013 | -54.7582 | -52.8265 | 51 | -61.9504 | -60.89 | -61.6098 | -61.1504 | -62.3905 | -59.8926 | -61.8855 | -62.5916 | 51 | -51.9531 | -46.1328 | -56.1362 | -64.9306 | -52.2758 | -51.6861 | -52.0913 | -46.1328 | -56.2871 | -64.7924 | -52.2885 | -51.837 | -52.618 | -46.1415 | -55.8345 | -64.8633 | -52.2202 | -50.1503 | -52.7562 | -46.1415 | -55.9854 | -64.7251 | -52.2329 | -50.3012
52 | -2.6715 | 0 | -2.5676 | 0 | -2.6712 | 0 | -2.5525 | 0 | -67.4368 | 171.4731 | -69.5002 | 147.1862 | -63.701 | 154.4727 | -64.6704 | -79.2556 | -68.5939 | 31.6056 | -69.013 | 46.2351 | -68.977 | 171.4675 | -70.1572 | 51.4176 | -65.8795 | -172.2804 | -62.2187 | -40.0043 | -70.422 | 13.6245 | -77.3313 | -65.3044 | -22.4854 | -31.1179 | -26.3792 | 30.5204 | -27.0026 | 4.5257 | -53.3599 | 88.9843 | -23.2998 | -34.4602 | -29.5179 | -12.3731 | -26.9556 | 4.6953 | -38.5608 | 82.5968 | -54.1661 | -55.0588 | -48.7778 | -58.7404 | -67.1505 | -54.9416 | -54.1887 | -54.4251 | -48.7457 | -58.4348 | -67.3371 | -54.8587 | -52.9621 | 52 | -61.432 | -61.8057 | -62.3742 | -61.6101 | -63.1762 | -60.8763 | -61.4575 | -64.3476 | 52 | -51.7536 | -46.0742 | -56.0689 | -64.5829 | -52.374 | -51.5175 | -51.8575 | -46.0745 | -56.1879 | -64.4793 | -52.3891 | -51.6362 | -52.3873 | -46.1063 | -55.7633 | -64.7695 | -52.2911 | -50.2909 | -52.4912 | -46.1066 | -55.8823 | -64.6659 | -52.3062 | -50.4096
53 | -2.6824 | 0 | -2.5919 | 0 | -2.7216 | 0 | -2.6035 | 0 | -71.7712 | 176.077 | -71.4501 | 86.9443 | -62.2584 | 135.9949 | -65.4079 | -117.4665 | -72.596 | 45.736 | -72.2225 | 80.8285 | -80.0064 | 125.3915 | -68.9556 | 35.1885 | -65.9903 | 131.4815 | -63.0099 | -60.0826 | -82.9672 | -40.8171 | -79.84 | 81.398 | -25.859 | -9.6038 | -27.1096 | 17.7453 | -22.0018 | 17.1305 | -44.7836 | 111.4613 | -28.4202 | -1.1939 | -33.8228 | -30.0347 | -21.8104 | 20.0286 | -33.0958 | 77.4875 | -54.0616 | -54.906 | -48.7419 | -58.8467 | -66.6905 | -55.0584 | -54.1193 | -54.2841 | -48.6707 | -58.4943 | -67.1974 | -54.9637 | -53.1764 | 53 | -61.3511 | -63.8786 | -63.7733 | -61.4907 | -64.1014 | -62.8812 | -61.9545 | -65.732 | 53 | -51.6017 | -45.9883 | -56.1643 | -64.0986 | -52.4665 | -51.3977 | -51.6922 | -45.9491 | -56.2432 | -63.9689 | -52.4549 | -51.5158 | -52.2236 | -46.0595 | -55.8119 | -64.6055 | -52.3718 | -50.4548 | -52.3141 | -46.0203 | -55.8908 | -64.4758 | -52.3602 | -50.5729
54 | -2.6954 | 0 | -2.6141 | 0 | -2.767 | 0 | -2.6275 | 0 | -70.6789 | -148.4351 | -75.3674 | 11.2827 | -63.004 | 119.6964 | -68.8574 | -157.6221 | -70.0329 | 73.8601 | -67.2148 | 97.0179 | -74.7728 | -73.0962 | -70.0084 | 18.0398 | -69.0935 | 71.3155 | -65.5302 | -71.2151 | -73.9225 | 139.8685 | -70.2484 | 48.2152 | -22.5838 | 6.9378 | -28.2326 | 8.4986 | -19.3402 | -1.0105 | -42.975 | 84.2099 | -23.1407 | 24.2773 | -45.1422 | -12.102 | -18.9859 | 3.0954 | -31.3252 | 53.6617 | -53.9626 | -54.8343 | -48.6963 | -59.0329 | -66.1462 | -55.0804 | -54.0438 | -54.1967 | -48.6368 | -58.6883 | -67.0984 | -55.0443 | -53.3625 | 54 | -62.109 | -65.0187 | -64.5711 | -61.0244 | -65.9119 | -64.5132 | -63.241 | -65.8808 | 54 | -51.5013 | -45.9414 | -56.3375 | -63.5321 | -52.4663 | -51.2768 | -51.5826 | -45.8698 | -56.4054 | -63.3792 | -52.4529 | -51.4163 | -52.1389 | -46.0009 | -55.9929 | -64.4843 | -52.4302 | -50.5955 | -52.2202 | -45.9293 | -56.0608 | -64.3314 | -52.4168 | -50.735
55 | -2.7463 | 0 | -2.6542 | 0 | -2.8047 | 0 | -2.6541 | 0 | -66.1432 | -151.644 | -74.8929 | -92.8699 | -65.6111 | 121.5139 | -80.0183 | 134.2064 | -65.8993 | 65.7117 | -64.2094 | 81.8449 | -67.5855 | -114.8407 | -72.9747 | 12.7221 | -70.7651 | -6.7854 | -68.2871 | -59.0769 | -67.1871 | 99.208 | -67.4284 | 13.8793 | -19.978 | -6.9285 | -29.4811 | 3.304 | -19.2539 | -24.8546 | -47.0931 | 34.1215 | -19.7609 | 10.1807 | -36.9413 | 74.7525 | -18.6427 | -18.5632 | -32.6179 | 24.7076 | -53.8972 | -54.8134 | -48.6769 | -59.2957 | -65.7722 | -55.0595 | -54.0018 | -54.1289 | -48.6057 | -58.9315 | -66.8456 | -55.1172 | -53.3884 | 55 | -62.595 | -62.9236 | -63.7496 | -60.404 | -65.1058 | -62.8918 | -64.2074 | -63.4128 | 55 | -51.3826 | -45.8594 | -56.5494 | -63.118 | -52.4053 | -51.1971 | -51.4747 | -45.801 | -56.6416 | -62.9675 | -52.4054 | -51.3477 | -52.0671 | -45.9306 | -56.1852 | -64.1914 | -52.463 | -50.5837 | -52.1592 | -45.8722 | -56.2774 | -64.0409 | -52.4631 | -50.7343
56 | -2.785 | 0 | -2.6898 | 0 | -2.7941 | 0 | -2.6707 | 0 | -63.7089 | -171.2724 | -69.797 | -162.2376 | -66.2551 | 143.5106 | -72.245 | -22.2631 | -63.5502 | 44.7234 | -63.4019 | 62.6674 | -65.1867 | -152.7472 | -73.96 | 31.1885 | -68.2143 | -97.8399 | -66.0422 | -41.2312 | -64.4469 | 62.8739 | -67.9322 | -23.1929 | -19.669 | -29.2825 | -30.6007 | -1.9245 | -21.7421 | -47.4673 | -44.6206 | -93.1049 | -18.8896 | -9.73 | -30.9661 | 63.1927 | -20.4911 | -37.1906 | -39.6519 | -9.3855 | -53.7643 | -54.728 | -48.6057 | -59.3386 | -65.4323 | -55.0601 | -53.8304 | -54.0871 | -48.5624 | -59.0374 | -66.553 | -55.2042 | -53.2474 | 56 | -61.1501 | -60.3297 | -62.0669 | -59.4489 | -63.0631 | -60.4055 | -63.4686 | -61.7326 | 56 | -51.3021 | -45.7774 | -56.5536 | -62.7425 | -52.3703 | -51.0363 | -51.3973 | -45.7683 | -56.6679 | -62.6382 | -52.3894 | -51.1597 | -51.943 | -45.8207 | -56.2524 | -63.8632 | -52.5144 | -50.4533 | -52.0382 | -45.8116 | -56.3667 | -63.7589 | -52.5335 | -50.5767
57 | -2.7765 | 0 | -2.6726 | 0 | -2.7928 | 0 | -2.686 | 0 | -63.2999 | 164.9349 | -66.9005 | 150.8627 | -61.7643 | 149.965 | -66.172 | -66.8004 | -63.0241 | 20.3869 | -64.3153 | 47.6769 | -65.2417 | 169.1457 | -70.7203 | 30.9752 | -64.1062 | -160.6658 | -62.9214 | -48.19 | -63.5497 | 26.7997 | -72.965 | -71.4869 | -21.6948 | -52.4143 | -32.4001 | -9.763 | -28.191 | -50.7736 | -35.9204 | -141.4668 | -19.9497 | -27.5319 | -28.5942 | 47.2155 | -24.457 | -39.0357 | -40.0944 | 160.5987 | -53.5721 | -54.5517 | -48.5588 | -59.3221 | -65.1658 | -55.1962 | -53.5632 | -54.0115 | -48.5655 | -59.0202 | -66.1218 | -55.3865 | -53.1561 | 57 | -58.7353 | -59.1808 | -60.8841 | -58.1395 | -61.122 | -59.0273 | -61.9005 | -60.5521 | 57 | -51.235 | -45.789 | -56.5456 | -62.4932 | -52.5236 | -50.7704 | -51.3389 | -45.7727 | -56.6361 | -62.373 | -52.5102 | -50.8772 | -51.7752 | -45.7823 | -56.2437 | -63.4492 | -52.7139 | -50.3633 | -51.8791 | -45.766 | -56.3342 | -63.329 | -52.7005 | -50.4701
58 | -2.7804 | 0 | -2.7045 | 0 | -2.8192 | 0 | -2.714 | 0 | -65.0081 | 141.3995 | -66.5052 | 110.6926 | -58.6847 | 134.6038 | -64.219 | -106.9086 | -64.1087 | -5.0975 | -66.2957 | 43.9563 | -67.8646 | 127.9911 | -69.1253 | 6.806 | -62.2331 | 150.9927 | -61.7108 | -66.3455 | -64.2615 | -7.9865 | -77.3158 | 147.9859 | -27.4647 | -67.4232 | -37.0373 | -11.8332 | -27.8734 | 9.7009 | -31.447 | -173.2315 | -22.5158 | -34.5077 | -27.4985 | 34.747 | -24.9009 | -9.3709 | -29.9595 | 122.5878 | -53.4244 | -54.3047 | -48.5861 | -59.3033 | -65.0298 | -55.4922 | -53.3959 | -53.9325 | -48.5929 | -59.0287 | -66.0014 | -55.6864 | -53.346 | 58 | -57.2286 | -59.656 | -60.7738 | -57.0407 | -60.5364 | -59.1623 | -60.887 | -60.0376 | 58 | -51.1521 | -45.8125 | -56.5229 | -62.3253 | -52.7877 | -50.5767 | -51.228 | -45.7737 | -56.5893 | -62.2106 | -52.7782 | -50.6819 | -51.5243 | -45.8057 | -56.2483 | -63.2969 | -52.9819 | -50.5268 | -51.6002 | -45.7669 | -56.3147 | -63.1822 | -52.9724 | -50.632
59 | -2.8186 | 0 | -2.7209 | 0 | -2.852 | 0 | -2.743 | 0 | -70.3503 | 128.7825 | -69.0435 | 73.2419 | -57.2643 | 114.2683 | -64.6352 | -146.6539 | -67.3033 | -28.9654 | -66.7305 | 55.5354 | -75.7235 | 67.911 | -70.769 | -28.7261 | -61.8088 | 103.827 | -62.415 | -85.0392 | -66.9405 | -44.6908 | -68.3682 | 87.0414 | -32.9036 | 1.9835 | -40.8442 | 60.9326 | -21.7946 | 3.917 | -28.8375 | 160.2184 | -24.0833 | -21.6905 | -26.8117 | 27.1043 | -21.0045 | -8.255 | -25.8645 | 91.0321 | -53.3353 | -54.0875 | -48.5892 | -59.2963 | -64.9877 | -55.818 | -53.3186 | -53.7778 | -48.5607 | -59.0217 | -66.2053 | -55.8715 | -53.9641 | 59 | -56.7895 | -62.0603 | -61.6693 | -56.4286 | -61.1357 | -60.9555 | -60.9537 | -59.9687 | 59 | -50.9592 | -45.7421 | -56.4777 | -62.2668 | -53.0971 | -50.4666 | -51.0569 | -45.7087 | -56.5533 | -62.1357 | -53.075 | -50.5756 | -51.2689 | -45.7706 | -56.2031 | -63.4844 | -53.1506 | -51.1121 | -51.3666 | -45.7372 | -56.2787 | -63.3533 | -53.1285 | -51.2211
60 | -2.8358 | 0 | -2.7432 | 0 | -2.899 | 0 | -2.7686 | 0 | -73.2175 | -168.7728 | -79.5647 | 43.9373 | -57.3997 | 93.9402 | -67.5211 | 171.2661 | -75.1109 | -27.9169 | -64.8573 | 56.7532 | -73.2312 | -86.4613 | -77.5008 | -79.6055 | -63.5192 | 51.3826 | -64.936 | -94.5647 | -74.2183 | -86.9038 | -64.2606 | 51.6554 | -24.2587 | 10.6809 | -31.2201 | 76.9163 | -19.5825 | -20.0046 | -27.5052 | 136.7838 | -22.0351 | -13.2803 | -25.731 | 21.3027 | -19.0617 | -26.1735 | -24.1249 | 60.9247 | -53.3695 | -54.0525 | -48.548 | -59.3538 | -65.0687 | -55.9119 | -53.3761 | -53.5786 | -48.4139 | -59.0909 | -66.5089 | -55.8599 | -54.6707 | 60 | -57.2618 | -65.9267 | -62.8835 | -56.6205 | -62.9242 | -63.9115 | -61.4653 | -60.6677 | 60 | -50.7428 | -45.5781 | -56.518 | -62.3255 | -53.1687 | -50.4771 | -50.8354 | -45.5149 | -56.5852 | -62.1697 | -53.1433 | -50.6075 | -51.2167 | -45.7122 | -56.2551 | -63.7657 | -53.1167 | -51.7717 | -51.3093 | -45.649 | -56.3223 | -63.6099 | -53.0913 | -51.9021
61 | -2.8715 | 0 | -2.778 | 0 | -2.9271 | 0 | -2.7838 | 0 | -65.4288 | -164.6852 | -73.8264 | 173.7442 | -59.6099 | 78.676 | -74.4862 | 112.4728 | -72.6476 | 39.2105 | -63.3144 | 44.8048 | -65.7185 | -139.0128 | -78.9004 | 134.8113 | -66.1607 | -16.5131 | -67.4972 | -81.8879 | -77.7979 | 93.3797 | -63.4576 | 21.4152 | -20.9942 | -12.3879 | -26.3217 | 58.2341 | -19.8099 | -46.9085 | -27.034 | 115.8464 | -20.0895 | -24.1859 | -24.3356 | 11.8877 | -19.236 | -48.4852 | -24.0375 | 32.4253 | -53.3808 | -54.1276 | -48.5252 | -59.5293 | -65.1855 | -55.7526 | -53.3991 | -53.4076 | -48.3794 | -59.2663 | -66.485 | -55.7591 | -54.8624 | 61 | -58.4713 | -64.243 | -62.6503 | -57.9196 | -62.8154 | -63.3484 | -61.9254 | -61.489 | 61 | -50.5361 | -45.5079 | -56.6578 | -62.4075 | -52.9746 | -50.472 | -50.6296 | -45.4523 | -56.7455 | -62.2584 | -52.9688 | -50.6153 | -51.2561 | -45.6537 | -56.3948 | -63.707 | -52.9811 | -51.9353 | -51.3496 | -45.5981 | -56.4825 | -63.5579 | -52.9753 | -52.0786
62 | -2.9312 | 0 | -2.8094 | 0 | -2.9361 | 0 | -2.8045 | 0 | -61.9133 | 173.4511 | -66.538 | 144.3279 | -62.3196 | 85.3983 | -74.8753 | -26.6351 | -66.7615 | 28.203 | -63.7701 | 29.7506 | -62.7168 | -179.2211 | -71.0017 | 79.4062 | -65.331 | -107.6341 | -65.5527 | -64.0184 | -67.9416 | 41.5362 | -65.1755 | -3.1275 | -20.4896 | -39.5151 | -23.8461 | 34.1432 | -22.5849 | -72.6052 | -27.1802 | 97.8822 | -19.7056 | -41.7175 | -23.2515 | -2.6274 | -21.5206 | -68.218 | -25.5049 | 5.3458 | -53.2482 | -54.2343 | -48.5614 | -59.7131 | -65.0647 | -55.6093 | -53.243 | -53.3111 | -48.4273 | -59.3914 | -65.8953 | -55.9087 | -54.4607 | 62 | -58.381 | -60.5207 | -61.712 | -59.1481 | -60.4221 | -60.1143 | -61.7944 | -61.207 | 62 | -50.3799 | -45.4961 | -56.7819 | -62.2553 | -52.7999 | -50.3069 | -50.5017 | -45.4912 | -56.9086 | -62.1286 | -52.8048 | -50.4385 | -51.3031 | -45.6302 | -56.4602 | -63.0859 | -53.0993 | -51.5246 | -51.4249 | -45.6253 | -56.5869 | -62.9592 | -53.1042 | -51.6562
63 | -2.956 | 0 | -2.8426 | 0 | -2.9605 | 0 | -2.8246 | 0 | -60.5864 | 148.6656 | -64.0169 | 115.2459 | -61.0827 | 106.561 | -68.1816 | -89.1827 | -64.1861 | 5.0951 | -65.8162 | 24.5931 | -61.8125 | 142.3588 | -68.1289 | 38.8048 | -60.854 | -170.0435 | -62.6571 | -68.9214 | -64.3964 | 4.805 | -69.546 | 3.3204 | -22.2455 | -67.3991 | -23.0881 | 7.724 | -29.6581 | -83.5173 | -27.8335 | 81.4141 | -20.8478 | -59.6291 | -22.9693 | -20.6877 | -26.2004 | -71.8245 | -28.889 | -17.2221 | -52.9534 | -54.2471 | -48.6567 | -59.8675 | -64.4768 | -55.7393 | -52.9168 | -53.3121 | -48.6162 | -59.5926 | -65.1434 | -56.4293 | -53.8364 | 63 | -56.8833 | -58.5167 | -60.9119 | -58.4686 | -57.8671 | -58.0561 | -60.93 | -58.8743 | 63 | -50.3561 | -45.6602 | -56.9115 | -61.6342 | -52.8967 | -49.9563 | -50.4695 | -45.6557 | -57.0429 | -61.5163 | -52.9147 | -50.0922 | -51.2911 | -45.7007 | -56.6366 | -62.3008 | -53.5867 | -50.8759 | -51.4045 | -45.6962 | -56.768 | -62.1829 | -53.6047 | -51.0118
64 | -2.9654 | 0 | -2.8801 | 0 | -2.9825 | 0 | -2.8454 | 0 | -60.9364 | 123.3276 | -63.9492 | 87.3077 | -57.5142 | 101.1884 | -65.7614 | -134.5764 | -63.4889 | -22.4774 | -67.0568 | 37.3429 | -62.7299 | 102.5434 | -68.492 | -7.3607 | -58.62 | 145.5906 | -61.1957 | -84.9554 | -63.1244 | -33.3371 | -66.4634 | 35.6552 | -27.262 | -93.2987 | -24.0171 | -19.1992 | -31.0103 | -9.0797 | -28.9995 | 67.058 | -23.5922 | -70.5307 | -23.7457 | -38.9948 | -27.4373 | -37.0476 | -34.7852 | -20.1332 | -52.6238 | -54.0309 | -48.7834 | -59.9754 | -63.491 | -56.1481 | -52.6184 | -53.2989 | -48.7467 | -59.8293 | -64.8762 | -57.2872 | -53.7917 | 64 | -55.2559 | -58.1837 | -60.6293 | -56.1668 | -56.8848 | -57.4965 | -59.4823 | -56.8051 | 64 | -50.3335 | -45.7813 | -57.01 | -60.6109 | -53.268 | -49.6359 | -50.4188 | -45.7642 | -57.13 | -60.5085 | -53.3027 | -49.773 | -51.0655 | -45.818 | -56.8639 | -61.9961 | -54.4071 | -50.8092 | -51.1508 | -45.8009 | -56.9839 | -61.8937 | -54.4418 | -50.9463
65 | -2.9599 | 0 | -2.8934 | 0 | -3.0229 | 0 | -2.8664 | 0 | -63.6957 | 99.7702 | -66.5693 | 67.0247 | -55.5986 | 85.8309 | -65.9772 | 178.8751 | -65.2744 | -49.5639 | -65.3068 | 52.2234 | -66.1 | 52.0428 | -72.3747 | -75.6569 | -58.2378 | 110.0335 | -61.6102 | -103.2086 | -63.5747 | -72.6371 | -61.9549 | 24.019 | -43.9494 | -59.9944 | -27.2189 | -45.6759 | -24.0496 | -16.2682 | -31.0179 | 54.6633 | -26.6343 | -64.2391 | -25.8677 | -53.6494 | -23.3823 | -33.6634 | -36.5683 | 19.9612 | -52.4146 | -53.6144 | -48.86 | -59.9771 | -62.6802 | -56.7433 | -52.5614 | -53.187 | -48.667 | -59.995 | -65.4286 | -57.8432 | -54.7109 | 65 | -54.6821 | -60.1038 | -61.1492 | -54.7539 | -57.4381 | -58.6178 | -58.5835 | -55.8888 | 65 | -50.2271 | -45.7071 | -57.0172 | -59.7868 | -53.8499 | -49.5385 | -50.2936 | -45.6441 | -57.1107 | -59.6573 | -53.8769 | -49.695 | -50.6545 | -45.9001 | -57.0351 | -62.5352 | -54.9498 | -51.688 | -50.721 | -45.8371 | -57.1286 | -62.4057 | -54.9768 | -51.8445
66 | -2.9805 | 0 | -2.9285 | 0 | -3.0774 | 0 | -2.8976 | 0 | -69.5459 | 109.0627 | -71.4258 | 84.6522 | -55.0772 | 62.9335 | -68.5839 | 126.923 | -71.1688 | -64.5169 | -61.6399 | 49.0497 | -71.3689 | -44.8652 | -71.0137 | 171.1785 | -59.0522 | 79.4462 | -63.8912 | -112.8103 | -66.4778 | -121.2043 | -59.7386 | 2.1096 | -29.2093 | 10.1935 | -35.7247 | -61.121 | -21.8617 | -42.7186 | -34.415 | 48.5385 | -26.3116 | -50.7016 | -28.9062 | -55.6562 | -21.4707 | -52.9086 | -32.9966 | 19.1061 | -52.5553 | -53.2939 | -48.6971 | -60.0006 | -62.4381 | -56.9189 | -52.8934 | -52.9133 | -48.3125 | -60.0418 | -66.7098 | -57.3469 | -56.156 | 66 | -54.8286 | -64.8681 | -60.4766 | -54.1246 | -58.551 | -61.5108 | -58.0983 | -55.9672 | 66 | -49.9328 | -45.332 | -57.0201 | -59.5096 | -53.9904 | -49.816 | -49.9848 | -45.2351 | -57.103 | -59.3607 | -54.0213 | -49.9958 | -50.3134 | -45.7166 | -57.0613 | -63.7813 | -54.4184 | -53.0786 | -50.3654 | -45.6197 | -57.1442 | -63.6324 | -54.4493 | -53.2584
67 | -3.022 | 0 | -2.9384 | 0 | -3.0791 | 0 | -2.9276 | 0 | -66.016 | 142.006 | -66.5833 | 115.0395 | -57.152 | 38.3837 | -72.5101 | 54.6408 | -72.7906 | -8.9357 | -59.4785 | 29.8519 | -65.9558 | -142.3068 | -65.3224 | 109.849 | -62.8664 | 49.8534 | -65.8953 | -103.6162 | -72.5089 | 160.559 | -59.3966 | -22.9022 | -24.9652 | -14.3165 | -36.0443 | 44.0867 | -22.3294 | -72.6902 | -39.0862 | 69.7115 | -25.0463 | -55.9649 | -29.9007 | -39.9048 | -21.8503 | -76.7906 | -32.7107 | -4.2032 | -52.7918 | -53.2372 | -48.477 | -59.9871 | -62.8894 | -56.4481 | -53.1845 | -52.6455 | -48.0845 | -59.9579 | -66.5673 | -56.583 | -56.9313 | 67 | -56.2042 | -64.4495 | -58.5285 | -55.0768 | -59.7297 | -62.4627 | -57.6956 | -57.6396 | 67 | -49.6235 | -45.0625 | -56.9651 | -59.951 | -53.5097 | -50.1054 | -49.7071 | -45.0054 | -57.0595 | -59.8103 | -53.5205 | -50.2569 | -50.2152 | -45.455 | -56.9359 | -63.6289 | -53.6446 | -53.8522 | -50.2988 | -45.3979 | -57.0303 | -63.4882 | -53.6554 | -54.0037
68 | -3.0455 | 0 | -2.9592 | 0 | -3.0783 | 0 | -2.9542 | 0 | -62.2783 | 128.1942 | -62.098 | 100.0149 | -62.8002 | 35.8789 | -71.9916 | -35.1422 | -66.3409 | -10.4396 | -59.7656 | 12.4464 | -62.0667 | 169.1012 | -62.3186 | 68.3597 | -72.6971 | 78.2081 | -64.7818 | -90.8656 | -69.1785 | 54.6058 | -61.3775 | -47.8312 | -24.3457 | -39.5534 | -27.9787 | 27.9671 | -25.3643 | -101.8612 | -36.8114 | 107.119 | -25.51 | -70.8352 | -27.7418 | -35.7418 | -24.6201 | -98.7262 | -36.2863 | -33.0584 | -52.7423 | -53.424 | -48.4889 | -60.0197 | -63.254 | -55.9045 | -53.0177 | -52.4885 | -48.2018 | -60.0138 | -65.0099 | -56.3362 | -56.0987 | 68 | -57.6109 | -60.5196 | -57.6056 | -57.4173 | -58.9914 | -59.6872 | -57.8329 | -60.4443 | 68 | -49.443 | -45.1563 | -56.9742 | -60.2948 | -52.9453 | -49.9394 | -49.5293 | -45.1235 | -57.0655 | -60.1757 | -52.9503 | -50.0635 | -50.3785 | -45.4434 | -56.9683 | -62.0507 | -53.377 | -53.0204 | -50.4648 | -45.4106 | -57.0596 | -61.9316 | -53.382 | -53.1445
69 | -3.0614 | 0 | -2.9772 | 0 | -3.0937 | 0 | -2.9841 | 0 | -60.7109 | 105.5426 | -60.4593 | 75.7661 | -63.1132 | 81.4894 | -69.0423 | -100.7974 | -63.0331 | -30.5834 | -60.9044 | 3.0326 | -60.4037 | 130.4673 | -61.3334 | 30.7191 | -63.4436 | 119.7055 | -62.6331 | -92.6524 | -64.137 | 2.4618 | -68.0367 | -53.6222 | -26.2464 | -60.8822 | -25.4818 | 0.4967 | -33.5267 | -123.5638 | -32.4733 | 108.5343 | -28.3571 | -85.1234 | -26.2181 | -49.1411 | -30.4508 | -105.3036 | -50.9233 | -112.7539 | -52.4635 | -53.7324 | -48.6572 | -60.1901 | -63.0846 | -55.6738 | -52.5904 | -52.4335 | -48.4872 | -60.3365 | -63.6529 | -56.7851 | -54.794 | 69 | -56.5035 | -58.3237 | -57.3605 | -57.4529 | -56.7791 | -57.3463 | -58.4219 | -60.0199 | 69 | -49.3721 | -45.4258 | -57.1287 | -60.1074 | -52.6966 | -49.4967 | -49.4563 | -45.3935 | -57.206 | -59.9909 | -52.6897 | -49.6063 | -50.671 | -45.5958 | -57.2751 | -60.6757 | -53.8079 | -51.7003 | -50.7552 | -45.5635 | -57.3524 | -60.5592 | -53.801 | -51.8099
70 | -3.072 | 0 | -3.0204 | 0 | -3.1228 | 0 | -2.9997 | 0 | -60.6245 | 78.3182 | -60.9988 | 53.0314 | -58.2913 | 81.5899 | -67.7019 | -155.8254 | -61.2273 | -58.7898 | -61.249 | 1.7135 | -60.2125 | 92.9689 | -62.3686 | -7.3073 | -58.8159 | 93.6513 | -61.2022 | -104.6029 | -61.5371 | -36.6903 | -66.0138 | 5.8138 | -30.5631 | -65.477 | -25.6553 | -28.3841 | -36.6647 | -17.0413 | -30.1912 | 97.3525 | -34.5996 | -73.6324 | -26.5149 | -68.1326 | -33.1932 | -56.5595 | -36.4902 | 111.2478 | -52.1318 | -53.9296 | -48.8905 | -60.6591 | -62.3388 | -56.0663 | -52.1141 | -52.4744 | -48.8259 | -61.0399 | -62.9462 | -58.2635 | -54.5891 | 70 | -55.027 | -57.4723 | -57.659 | -55.2492 | -55.4587 | -56.1756 | -57.9909 | -56.4479 | 70 | -49.4024 | -45.7539 | -57.5871 | -59.3184 | -53.0459 | -48.9913 | -49.454 | -45.7031 | -57.6594 | -59.216 | -53.0666 | -49.1144 | -50.8576 | -45.8185 | -57.9679 | -59.9258 | -55.2431 | -51.4663 | -50.9092 | -45.7677 | -58.0402 | -59.8234 | -55.2638 | -51.5894
71 | -3.1028 | 0 | -3.0454 | 0 | -3.1544 | 0 | -3.0279 | 0 | -62.7173 | 41.7598 | -63.7836 | 39.2 | -55.6812 | 71.0307 | -67.8094 | 143.879 | -60.8737 | -93.8105 | -61.373 | 1.0154 | -61.8464 | 48.583 | -67.4746 | -50.6286 | -57.5679 | 67.5505 | -61.5051 | -121.6709 | -60.4818 | -75.7696 | -60.3 | -5.5794 | -31.7614 | -36.7245 | -28.44 | -55.8816 | -28.3286 | -35.5715 | -29.2402 | 84.1254 | -32.1641 | -22.4524 | -28.718 | -84.9746 | -27.9201 | -52.4337 | -31.0306 | 78.7729 | -51.8639 | -53.637 | -49.183 | -61.0826 | -61.1647 | -57.4261 | -51.8345 | -52.3849 | -48.9856 | -61.7603 | -63.2993 | -60.3341 | -55.9021 | 71 | -54.3693 | -58.1865 | -58.8174 | -53.7162 | -55.8784 | -56.467 | -57.4011 | -54.4625 | 71 | -49.2821 | -45.8828 | -57.9798 | -58.1193 | -54.3807 | -48.6801 | -49.3395 | -45.8312 | -58.0547 | -58.0103 | -54.3982 | -48.8066 | -50.5342 | -46.0802 | -58.6575 | -60.2539 | -57.2887 | -52.7477 | -50.5916 | -46.0286 | -58.7324 | -60.1449 | -57.3062 | -52.8742
72 | -3.1339 | 0 | -3.0479 | 0 | -3.1983 | 0 | -3.0289 | 0 | -72.9832 | -17.9414 | -67.1017 | 57.6067 | -53.8196 | 51.4956 | -68.0081 | 72.3659 | -64.2438 | -136.6332 | -60.1137 | 3.8497 | -68.0729 | -20.0436 | -79.3764 | 138.2536 | -57.2019 | 44.3896 | -64.0353 | -129.2275 | -62.3155 | -119.03 | -58.3288 | -26.7463 | -28.3858 | -35.4215 | -36.3166 | -69.7752 | -26.4501 | -67.0956 | -29.3315 | 71.6966 | -27.5002 | -28.2524 | -33.3526 | -84.3582 | -26.2069 | -73.5761 | -29.1086 | 51.5402 | -52.2414 | -53.0246 | -48.8665 | -61.2609 | -60.9563 | -59.0558 | -52.3877 | -52.1006 | -48.4269 | -61.7042 | -66.5245 | -60.167 | -58.6727 | 72 | -53.5703 | -62.3293 | -58.7704 | -52.596 | -56.8361 | -59.4406 | -57.2682 | -54.0223 | 72 | -48.9667 | -45.293 | -58.127 | -57.9084 | -56.0079 | -49.1894 | -49.0527 | -45.2286 | -58.232 | -57.758 | -56.0269 | -49.3588 | -49.8907 | -45.7326 | -58.5703 | -63.4766 | -57.1191 | -55.4744 | -49.9767 | -45.6682 | -58.6753 | -63.3262 | -57.1381 | -55.6438
73 | -3.1366 | 0 | -3.0783 | 0 | -3.2209 | 0 | -3.0548 | 0 | -68.9828 | 157.0954 | -63.2404 | 81.6212 | -54.8234 | 25.4708 | -67.1394 | 4.0329 | -73.7691 | -167.1552 | -58.2151 | -7.1947 | -69.9145 | -157.9483 | -64.3974 | 71.5379 | -58.7248 | 11.3979 | -65.0361 | -115.8569 | -68.6627 | -154.9095 | -57.7715 | -46.654 | -27.0975 | -55.2488 | -36.4142 | 17.5509 | -27.4442 | -101.3988 | -29.9165 | 62.094 | -26.0665 | -46.3112 | -33.7279 | -45.5988 | -27.2688 | -99.6793 | -29.3391 | 27.6391 | -52.8695 | -52.6254 | -48.4942 | -60.971 | -62.2288 | -59.0551 | -53.1681 | -51.8537 | -48.0898 | -61.0353 | -68.6095 | -58.5803 | -60.1289 | 73 | -54.0959 | -64.4177 | -56.624 | -53.1481 | -57.4315 | -62.5833 | -56.2941 | -55.0199 | 73 | -48.7171 | -44.9532 | -57.8344 | -59.1505 | -55.9768 | -49.9472 | -48.7754 | -44.8689 | -57.9162 | -59.0079 | -56.0003 | -50.1133 | -49.4888 | -45.3576 | -57.8987 | -65.5312 | -55.502 | -56.908 | -49.5471 | -45.2733 | -57.9805 | -65.3886 | -55.5255 | -57.0741
74 | -3.1722 | 0 | -3.1006 | 0 | -3.2173 | 0 | -3.0885 | 0 | -63.2536 | 120.2831 | -59.1229 | 69.7778 | -58.8388 | 20.2472 | -66.3498 | -48.937 | -78.2065 | -23.5821 | -57.9442 | -23.0586 | -64.2199 | 142.0761 | -59.8555 | 33.1746 | -67.223 | -7.4489 | -63.5035 | -110.5912 | -96.0517 | -62.0453 | -59.1139 | -66.9993 | -28.3386 | -80.383 | -28.9785 | 3.3862 | -31.3764 | -137.8797 | -30.7526 | 55.6265 | -26.7925 | -64.8514 | -28.967 | -42.8014 | -31.3291 | -124.4568 | -31.2956 | 11.6264 | -52.8566 | -52.6921 | -48.5884 | -60.298 | -63.1574 | -57.7351 | -53.1084 | -51.7212 | -48.266 | -60.4248 | -66.0772 | -57.6353 | -56.762 | 74 | -55.2243 | -61.429 | -55.1415 | -55.3357 | -57.9539 | -60.8353 | -55.6759 | -58.489 | 74 | -48.549 | -45.0938 | -57.1258 | -60.0568 | -54.6345 | -49.8911 | -48.6206 | -45.0487 | -57.2095 | -59.9401 | -54.6466 | -50.0199 | -49.5199 | -45.4162 | -57.2526 | -62.9766 | -54.5347 | -53.5447 | -49.5915 | -45.3711 | -57.3363 | -62.8599 | -54.5468 | -53.6735
75 | -3.1849 | 0 | -3.1469 | 0 | -3.2299 | 0 | -3.0998 | 0 | -61.2052 | 92.8121 | -57.2667 | 48.2767 | -59.6895 | 44.1065 | -66.439 | -92.0761 | -67.4902 | -43.1308 | -58.8356 | -35.611 | -61.8682 | 104.6473 | -58.0224 | -2.6508 | -66.8765 | 91.826 | -62.1534 | -114.3166 | -68.1938 | -37.5873 | -62.2159 | -71.5283 | -33.0809 | -105.72 | -26.6424 | -27.5356 | -40.9609 | 175.376 | -31.8459 | 51.8858 | -29.7478 | -76.4503 | -26.5782 | -61.0691 | -42.6241 | -134.3369 | -34.3152 | 12.6291 | -52.528 | -53.1265 | -48.8238 | -60.0397 | -63.3561 | -56.4664 | -52.6977 | -51.6986 | -48.5482 | -60.518 | -64.1391 | -57.8119 | -54.294 | 75 | -54.3084 | -59.3444 | -54.6712 | -55.9179 | -56.1396 | -58.5046 | -55.5499 | -60.1899 | 75 | -48.5137 | -45.3633 | -56.8548 | -60.2092 | -53.3195 | -49.4678 | -48.5517 | -45.3183 | -56.9399 | -60.1262 | -53.3666 | -49.5979 | -49.9416 | -45.6389 | -57.3331 | -60.9922 | -54.665 | -51.0641 | -49.9796 | -45.5939 | -57.4182 | -60.9092 | -54.7121 | -51.1942
76 | -3.1969 | 0 | -3.1818 | 0 | -3.2589 | 0 | -3.1167 | 0 | -60.53 | 64.7683 | -57.1411 | 26.74 | -56.2879 | 49.8183 | -68.1784 | -133.2405 | -62.9431 | -70.4429 | -59.296 | -41.8267 | -61.1847 | 71.1987 | -57.9112 | -40.2386 | -59.4533 | 71.5141 | -60.9525 | -123.1123 | -62.6405 | -65.0477 | -62.6737 | -43.6221 | -49.9714 | -82.7582 | -26.7988 | -63.3631 | -43.2326 | -1.66 | -33.1676 | 53.2526 | -33.4322 | -64.6241 | -26.0428 | -83.7674 | -38.904 | -23.5314 | -34.6425 | 31.4857 | -52.1137 | -53.722 | -49.1209 | -60.5238 | -62.6723 | -55.9798 | -52.2014 | -51.7862 | -48.9274 | -61.6936 | -62.7873 | -59.8409 | -54.276 | 76 | -52.8673 | -58.1106 | -54.8684 | -53.9421 | -54.5432 | -56.7597 | -55.2856 | -56.5387 | 76 | -48.5893 | -45.7305 | -57.3269 | -59.4905 | -52.798 | -48.9425 | -48.6044 | -45.6685 | -57.4071 | -59.4134 | -52.8631 | -49.0847 | -50.5251 | -45.924 | -58.4967 | -59.6055 | -56.6591 | -51.0171 | -50.5402 | -45.862 | -58.5769 | -59.5284 | -56.7242 | -51.1593
77 | -3.2194 | 0 | -3.1901 | 0 | -3.3022 | 0 | -3.1518 | 0 | -61.1927 | 31.7371 | -58.505 | 9.4674 | -54.592 | 38.1485 | -73.4338 | 163.4812 | -60.4837 | -104.7604 | -60.6881 | -50.1052 | -61.6158 | 32.5577 | -60.0378 | -83.182 | -56.9115 | 45.4542 | -60.9547 | -139.7798 | -59.5256 | -96.1337 | -59.0909 | -49.7312 | -36.1203 | -4.8718 | -29.1403 | -105.8812 | -37.1435 | -56.3761 | -33.7949 | 60.0589 | -32.3911 | -40.4708 | -27.1513 | -104.8577 | -33.2851 | -39.3894 | -32.1898 | 33.6586 | -51.6766 | -53.7008 | -49.6413 | -61.9652 | -60.9941 | -56.9441 | -51.6529 | -51.8647 | -49.3424 | -63.9232 | -62.2233 | -65.0307 | -55.9664 | 77 | -52.4837 | -57.696 | -56.3644 | -52.8218 | -54.2981 | -55.8379 | -55.1901 | -53.5807 | 77 | -48.6453 | -46.123 | -58.7458 | -57.804 | -53.754 | -48.3507 | -48.6746 | -46.0402 | -58.8134 | -57.6919 | -53.7923 | -48.5011 | -50.4814 | -46.4219 | -60.7038 | -59.0332 | -61.8406 | -52.6642 | -50.5107 | -46.3391 | -60.7714 | -58.9211 | -61.8789 | -52.8146
78 | -3.2602 | 0 | -3.1904 | 0 | -3.3471 | 0 | -3.1697 | 0 | -66.0464 | -19.6456 | -60.7194 | 2.4721 | -52.9173 | 26.6451 | -72.0041 | 22.2399 | -60.8465 | -149.2202 | -62.0896 | -36.7249 | -64.3708 | -29.4458 | -66.7692 | -136.3414 | -56.5581 | 27.5696 | -63.8094 | -149.7557 | -58.3404 | -137.3588 | -57.6868 | -66.0187 | -32.6636 | -32.591 | -33.4463 | -166.0043 | -37.0188 | -109.7783 | -33.1808 | 64.9941 | -30.215 | -42.1917 | -29.8015 | -119.8221 | -32.6206 | -60.9613 | -30.7857 | 22.4469 | -51.6827 | -52.9214 | -49.8932 | -63.335 | -59.1906 | -59.5756 | -51.6531 | -51.6225 | -48.9611 | -65.4111 | -64.4691 | -66.1602 | -59.0301 | 78 | -52.0732 | -59.4521 | -58.1575 | -51.8381 | -55.5519 | -56.4841 | -56.3268 | -52.694 | 78 | -48.3623 | -45.7009 | -60.0748 | -56.0002 | -56.3852 | -48.306 | -48.4321 | -45.614 | -60.1653 | -55.8435 | -56.4059 | -48.4834 | -49.6612 | -46.633 | -62.1509 | -61.2787 | -62.9698 | -55.683 | -49.731 | -46.5461 | -62.2414 | -61.122 | -62.9905 | -55.8604
79 | -3.2766 | 0 | -3.2008 | 0 | -3.3496 | 0 | -3.1859 | 0 | -75.4818 | 135.4756 | -62.3714 | 10.8405 | -52.8029 | 1.3451 | -65.0626 | -43.5846 | -66.3954 | -175.3518 | -59.2746 | -31.6877 | -69.7854 | -143.5484 | -73.1132 | 77.9208 | -56.3988 | 3.1104 | -64.8969 | -127.6131 | -61.2013 | -177.2051 | -57.7049 | -82.5501 | -34.0578 | -63.3278 | -34.6837 | 104.5073 | -38.9106 | 178.895 | -32.0509 | 62.4188 | -29.9701 | -51.8977 | -33.2658 | -119.2374 | -34.9046 | -77.246 | -30.9963 | 10.3663 | -52.7343 | -52.141 | -49.0835 | -63.8945 | -60.082 | -62.0667 | -52.8453 | -51.209 | -48.2297 | -64.4859 | -69.6383 | -61.6152 | -60.6946 | 79 | -52.3269 | -62.4463 | -56.8346 | -51.7681 | -56.1165 | -59.2546 | -56.8424 | -53.2366 | 79 | -47.9324 | -44.9531 | -60.6179 | -56.8812 | -58.8659 | -49.4957 | -48.0082 | -44.8801 | -60.7086 | -56.7324 | -58.8808 | -49.6594 | -48.8644 | -45.8069 | -61.2093 | -66.4375 | -58.4144 | -57.345 | -48.9402 | -45.7339 | -61.3 | -66.2887 | -58.4293 | -57.5087
80 | -3.3058 | 0 | -3.2092 | 0 | -3.3599 | 0 | -3.2207 | 0 | -65.6772 | 85.4989 | -60.993 | 19.2659 | -56.0602 | -12.8981 | -62.8696 | -86.2241 | -70.2057 | -166.7583 | -57.6696 | -46.1452 | -66.3605 | 132.6798 | -64.0994 | 9.3401 | -60.0249 | -18.3402 | -62.3317 | -125.7541 | -66.2641 | 157.8546 | -58.9051 | -99.4997 | -41.8663 | -103.3757 | -32.264 | 39.7416 | -37.6979 | 104.4656 | -31.7176 | 51.7959 | -31.0067 | -58.9228 | -33.9765 | -103.662 | -39.3954 | -73.882 | -32.1507 | 3.3373 | -52.86 | -51.9287 | -49.0308 | -62.5007 | -61.5163 | -61.1123 | -53.0413 | -51.0279 | -48.4816 | -62.7795 | -66.178 | -59.4381 | -56.2714 | 80 | -54.5057 | -60.5433 | -55.1967 | -53.6827 | -57.9195 | -59.7794 | -56.4582 | -55.9905 | 80 | -47.7221 | -45.1758 | -59.1949 | -58.3071 | -57.9031 | -49.6814 | -47.8187 | -45.1217 | -59.28 | -58.1564 | -57.8916 | -49.8206 | -48.6229 | -45.725 | -59.4737 | -62.9688 | -56.2289 | -52.9115 | -48.7195 | -45.6709 | -59.5588 | -62.8181 | -56.2174 | -53.0507
81 | -3.2976 | 0 | -3.2673 | 0 | -3.3711 | 0 | -3.261 | 0 | -63.2903 | 56.2495 | -59.4585 | 13.614 | -59.0231 | 4.1451 | -63.0448 | -118.9235 | -71.6046 | -142.5641 | -57.5014 | -56.4823 | -64.2226 | 91.235 | -61.0564 | -29.8597 | -65.4309 | 7.5144 | -61.2707 | -132.2346 | -77.9559 | 146.1723 | -63.1094 | -102.9594 | -41.3846 | 80.2924 | -32.3489 | -9.4459 | -36.9489 | 53.8946 | -33.2686 | 37.6429 | -32.2947 | -58.7513 | -32.5833 | -103.1136 | -41.0406 | -39.6756 | -32.709 | 5.6543 | -52.4964 | -52.272 | -49.2805 | -60.9846 | -62.3362 | -58.1743 | -52.7712 | -50.9453 | -48.782 | -62.1189 | -63.8259 | -59.0234 | -53.732 | 81 | -55.4457 | -59.8551 | -54.6769 | -55.0877 | -58.3904 | -59.4288 | -56.9484 | -61.0177 | 81 | -47.6477 | -45.4844 | -57.687 | -59.0689 | -54.907 | -49.4001 | -47.678 | -45.4109 | -57.7236 | -58.9651 | -54.9133 | -49.5102 | -48.9744 | -45.9829 | -58.8213 | -60.5586 | -55.7561 | -50.3609 | -49.0047 | -45.9094 | -58.8579 | -60.4548 | -55.7624 | -50.471
82 | -3.3205 | 0 | -3.288 | 0 | -3.4144 | 0 | -3.2616 | 0 | -62.6913 | 29.0194 | -58.8893 | 4.9136 | -56.3097 | 21.1769 | -64.3284 | -144.9926 | -67.3553 | -127.8451 | -56.64 | -67.9114 | -63.8101 | 59.8053 | -59.9375 | -67.6119 | -60.7225 | 27.0139 | -59.9864 | -138.8293 | -72.2926 | -89.0877 | -61.8417 | -61.1053 | -33.1947 | 43.8965 | -36.3334 | -63.7394 | -39.5399 | 25.9481 | -38.1318 | 37.0486 | -33.3302 | -56.1296 | -32.2293 | -112.759 | -38.1523 | -15.9103 | -31.8892 | 7.69 | -52.0914 | -53.2646 | -49.573 | -60.5835 | -62.5445 | -55.9717 | -52.3818 | -51.016 | -49.133 | -63.3974 | -62.2333 | -61.1019 | -53.928 | 82 | -53.8002 | -59.6215 | -54.17 | -53.2878 | -56.4261 | -58.3032 | -55.7316 | -58.0685 | 82 | -47.6955 | -45.8125 | -57.263 | -59.2565 | -52.6837 | -48.9674 | -47.728 | -45.7186 | -57.3219 | -59.1301 | -52.7101 | -49.1202 | -49.9441 | -46.2525 | -60.0769 | -58.9453 | -57.8139 | -50.5136 | -49.9766 | -46.1586 | -60.1358 | -58.8189 | -57.8403 | -50.6664
83 | -3.3503 | 0 | -3.294 | 0 | -3.4481 | 0 | -3.2842 | 0 | -63.0444 | 0.1072 | -58.8766 | -2.322 | -54.2277 | 12.3398 | -67.9586 | -175.6626 | -62.8924 | -141.074 | -57.2515 | -86.1848 | -64.0819 | 28.7361 | -60.7796 | -114.7971 | -57.1486 | 10.3914 | -59.3707 | -156.9213 | -64.761 | -106.3738 | -57.728 | -75.4535 | -30.9706 | 19.8003 | -40.0419 | 177.4179 | -44.9692 | 50.8113 | -39.0745 | 92.1854 | -35.1694 | -54.4287 | -32.8906 | -118.6827 | -34.8243 | -15.9178 | -30.5462 | 1.2666 | -51.7811 | -53.9468 | -49.9467 | -62.0584 | -61.5896 | -55.439 | -51.962 | -51.0848 | -49.6902 | -68.048 | -61.2276 | -68.4286 | -55.8799 | 83 | -52.5422 | -59.3187 | -54.7649 | -52.094 | -55.0107 | -57.2568 | -54.3428 | -54.0345 | 83 | -47.7345 | -46.3399 | -58.7081 | -58.2956 | -52.145 | -48.5139 | -47.7908 | -46.2421 | -58.7742 | -58.1415 | -52.1548 | -48.6778 | -50.5965 | -46.5964 | -64.6977 | -57.9336 | -65.1346 | -52.4318 | -50.6528 | -46.4986 | -64.7638 | -57.7795 | -65.1444 | -52.5957
84 | -3.3663 | 0 | -3.2902 | 0 | -3.4727 | 0 | -3.3093 | 0 | -64.3631 | -40.8061 | -58.8504 | -4.3712 | -53.354 | 4.5673 | -90.3802 | -83.796 | -59.5108 | -171.7173 | -60.3195 | -88.2318 | -65.4638 | -15.5754 | -64.6348 | 178.0932 | -56.6921 | -12.0875 | -61.8821 | -171.5852 | -60.6002 | -139.1637 | -57.437 | -93.4672 | -31.3924 | 7.3781 | -31.8157 | 102.07 | -37.2165 | 83.4921 | -32.4562 | 99.8946 | -38.8118 | -26.9851 | -32.904 | -118.3892 | -32.87 | -27.5027 | -29.7741 | -12.4609 | -51.4179 | -53.4676 | -50.4784 | -65.2343 | -59.6601 | -56.5692 | -51.4777 | -50.9805 | -50.3311 | -74.5246 | -60.8957 | -73.9454 | -58.7018 | 84 | -52.0143 | -58.2789 | -56.511 | -51.7601 | -55.5752 | -57.439 | -55.5338 | -53.1722 | 84 | -47.6142 | -46.9648 | -61.868 | -56.3699 | -53.279 | -48.005 | -47.6903 | -46.8584 | -61.925 | -56.1874 | -53.2599 | -48.1684 | -50.1013 | -47.1121 | -71.1583 | -57.6055 | -70.6552 | -55.2291 | -50.1774 | -47.0057 | -71.2153 | -57.423 | -70.6361 | -55.3925
85 | -3.3825 | 0 | -3.3305 | 0 | -3.4882 | 0 | -3.3117 | 0 | -71.4795 | -137.542 | -57.726 | -9.0039 | -51.5028 | -6.4193 | -66.1112 | -75.6369 | -60.1133 | 140.1554 | -58.7591 | -76.7957 | -70.313 | -117.1484 | -66.3742 | 74.3016 | -57.1257 | -25.2701 | -63.801 | -155.1013 | -60.8915 | 176.9878 | -57.8649 | -100.8268 | -31.4336 | 15.1724 | -28.0083 | 62.2821 | -32.1108 | 63.9483 | -28.9233 | 82.6139 | -34.1084 | 13.3619 | -31.3699 | -125.2879 | -32.2937 | -42.0784 | -29.9063 | -30.5429 | -52.0325 | -52.6159 | -49.9713 | -69.8607 | -58.8528 | -59.1433 | -52.0727 | -50.746 | -49.5818 | -69.1665 | -64.9126 | -64.5741 | -59.6121 | 85 | -50.5384 | -58.8934 | -54.8629 | -50.278 | -56.4554 | -58.7803 | -56.4165 | -53.5776 | 85 | -47.3635 | -46.1993 | -66.4782 | -55.5223 | -55.8128 | -48.5845 | -47.4155 | -46.0936 | -66.549 | -55.3646 | -55.8316 | -48.761 | -49.2334 | -46.5888 | -65.784 | -61.5821 | -61.2436 | -56.1239 | -49.2854 | -46.4831 | -65.8548 | -61.4244 | -61.2624 | -56.3004
86 | -3.4111 | 0 | -3.3629 | 0 | -3.4813 | 0 | -3.3267 | 0 | -69.8036 | 76.0879 | -57.3595 | -20.5145 | -52.3417 | -25.661 | -61.5987 | -112.7324 | -64.8598 | 117.0616 | -57.1905 | -87.6783 | -69.2182 | 120.1128 | -62.4264 | -0.6063 | -59.6007 | -54.4374 | -61.3175 | -151.8421 | -64.9366 | 160.9689 | -57.4514 | -107.4373 | -28.4788 | 16.6297 | -26.8129 | 29.5365 | -30.7306 | 36.14 | -27.4887 | 58.1401 | -28.4491 | 6.1155 | -30.1759 | -142.7791 | -32.9416 | -59.3795 | -30.6062 | -47.8669 | -52.9126 | -51.8435 | -49.4803 | -69.1392 | -60.8267 | -62.7107 | -52.9371 | -50.6688 | -49.2001 | -65.7809 | -67.566 | -61.4422 | -54.6915 | 86 | -51.0938 | -59.4952 | -53.5277 | -50.9321 | -57.4764 | -59.2851 | -55.0744 | -54.9276 | 86 | -47.2577 | -45.789 | -65.7281 | -57.4638 | -59.3478 | -49.4558 | -47.3059 | -45.7188 | -65.8125 | -57.3454 | -59.384 | -49.6104 | -48.4324 | -46.0692 | -62.3698 | -64.2031 | -58.0793 | -51.2102 | -48.4806 | -45.999 | -62.4542 | -64.0847 | -58.1155 | -51.3648
87 | -3.4382 | 0 | -3.3904 | 0 | -3.5027 | 0 | -3.3538 | 0 | -66.8511 | 25.1958 | -58.0419 | -28.6499 | -53.8182 | -26.8286 | -61.1707 | -142.9085 | -69.564 | 112.0997 | -57.7639 | -100.7105 | -67.7494 | 66.1986 | -60.7405 | -49.4535 | -69.1424 | -48.8038 | -60.5981 | -162.0368 | -68.0453 | 159.8789 | -59.2024 | -112.3899 | -26.0022 | 2.2351 | -27.7949 | 2.2353 | -32.1474 | 15.2205 | -28.0983 | 32.4465 | -25.724 | -12.9707 | -30.2151 | -169.9255 | -37.128 | -75.7999 | -32.0896 | -64.1883 | -52.6472 | -51.7009 | -49.7536 | -64.616 | -61.8777 | -61.9431 | -52.7771 | -50.5965 | -49.4734 | -64.2303 | -64.867 | -60.8855 | -52.0688 | 87 | -52.2713 | -59.6627 | -53.972 | -52.2656 | -59.4578 | -59.2224 | -55.3519 | -58.2966 | 87 | -47.1583 | -46.0352 | -61.1778 | -58.4873 | -58.5527 | -49.2744 | -47.2061 | -45.9707 | -61.2622 | -58.375 | -58.5893 | -49.4233 | -48.2627 | -46.3154 | -60.7921 | -61.4766 | -57.4951 | -48.5661 | -48.3105 | -46.2509 | -60.8765 | -61.3643 | -57.5317 | -48.715
88 | -3.4766 | 0 | -3.3879 | 0 | -3.5222 | 0 | -3.3777 | 0 | -66.5768 | -9.1207 | -58.5718 | -27.8228 | -53.1367 | -22.3466 | -61.8336 | -162.1469 | -73.4038 | 151.179 | -57.1057 | -104.5779 | -68.8532 | 31.8605 | -60.5427 | -89.8912 | -62.68 | 26.5024 | -60.1082 | -165.9921 | -70.2045 | 174.9756 | -58.2687 | -94.5312 | -25.2769 | -18.6581 | -30.8895 | -14.6264 | -35.0542 | 11.7216 | -30.9118 | 4.8105 | -25.3122 | -34.3576 | -31.8653 | 155.1625 | -46.4348 | -18.2371 | -33.8984 | -81.2139 | -52.1526 | -52.4392 | -50.1358 | -62.2736 | -62.5002 | -57.4353 | -52.4348 | -50.7214 | -49.7383 | -64.8996 | -62.8879 | -63.5182 | -52.2409 | 88 | -51.8937 | -60.3564 | -53.9878 | -51.6434 | -58.0903 | -59.2045 | -54.7525 | -56.727 | 88 | -47.2448 | -46.2617 | -58.797 | -59.1123 | -54.0474 | -48.9126 | -47.3335 | -46.2161 | -58.8959 | -58.978 | -54.0576 | -49.0571 | -48.9626 | -46.6592 | -61.423 | -59.5 | -60.1303 | -48.7187 | -49.0513 | -46.6136 | -61.5219 | -59.3657 | -60.1405 | -48.8632
89 | -3.501 | 0 | -3.4083 | 0 | -3.5598 | 0 | -3.4108 | 0 | -67.669 | -36.9512 | -57.7247 | -26.9708 | -52.054 | -29.9218 | -63.0816 | 174.4226 | -67.9004 | 178.4905 | -56.519 | -124.1145 | -70.5949 | 2.4982 | -61.131 | -140.1777 | -56.7332 | 9.1108 | -58.9377 | 178.5517 | -68.8812 | -156.1746 | -54.812 | -108.5048 | -26.7046 | -38.5554 | -34.1948 | -1.6202 | -34.919 | 29.8599 | -38.8303 | -23.5537 | -26.9665 | -52.5237 | -35.7748 | 106.3421 | -34.9263 | 13.499 | -35.5489 | -96.0156 | -51.8879 | -53.637 | -50.5001 | -62.5324 | -62.1769 | -54.9769 | -52.1622 | -50.9153 | -50.1846 | -68.9982 | -61.8263 | -69.3176 | -54.1577 | 89 | -50.9198 | -60.8351 | -53.5562 | -50.6436 | -55.2584 | -58.2574 | -52.7164 | -52.5545 | 89 | -47.4143 | -46.6836 | -59.0314 | -58.7686 | -51.5686 | -48.6024 | -47.507 | -46.6248 | -59.1216 | -58.6171 | -51.5661 | -48.7514 | -50.136 | -46.9991 | -65.4972 | -58.418 | -65.9093 | -50.5979 | -50.2287 | -46.9403 | -65.5874 | -58.2665 | -65.9068 | -50.7469
90 | -3.5321 | 0 | -3.4397 | 0 | -3.6151 | 0 | -3.4316 | 0 | -68.6459 | -60.5969 | -56.3976 | -31.1725 | -51.6424 | -42.5566 | -70.0871 | 161.3042 | -62.27 | 166.5045 | -60.1586 | -136.2063 | -72.3298 | -41.4064 | -62.8359 | 143.5059 | -54.3466 | -16.8233 | -60.905 | 157.2386 | -63.3561 | -154.6849 | -55.015 | -130.3608 | -30.6309 | -42.4734 | -31.6981 | 13.1002 | -31.9186 | 26.3277 | -42.7746 | 133.0368 | -31.0609 | -49.1105 | -38.7959 | 19.3257 | -30.4225 | -8.3705 | -37.5696 | -111.7017 | -51.7747 | -53.6454 | -50.9648 | -64.8763 | -61.0638 | -54.5751 | -51.9358 | -50.8651 | -50.7665 | -74.3108 | -61.3655 | -64.6346 | -57.1898 | 90 | -50.3246 | -60.8222 | -54.744 | -50.753 | -53.7113 | -58.7546 | -53.4836 | -51.3734 | 90 | -47.333 | -47.2344 | -61.3442 | -57.6241 | -51.1354 | -48.3207 | -47.4254 | -47.1514 | -61.4447 | -57.4487 | -51.1435 | -48.5042 | -50.1133 | -47.4327 | -70.7787 | -57.9258 | -61.1949 | -53.5747 | -50.2057 | -47.3497 | -70.8792 | -57.7504 | -61.203 | -53.7582
91 | -3.5408 | 0 | -3.4514 | 0 | -3.6263 | 0 | -3.4396 | 0 | -69.2777 | -99.9308 | -55.0515 | -41.8514 | -52.0719 | -51.9055 | -67.2995 | -125.7069 | -58.5979 | 134.813 | -60.9399 | -111.8178 | -70.7238 | -118.1881 | -61.3545 | 53.0026 | -54.7175 | -41.4544 | -65.526 | 166.5699 | -59.5189 | 179.1303 | -56.2732 | -134.5769 | -30.826 | -5.4639 | -29.3961 | -2.1173 | -30.4897 | 5.2792 | -32.8399 | 102.1967 | -30.1249 | -10.9824 | -35.1527 | -58.0927 | -29.2674 | -33.0702 | -38.3796 | -132.6622 | -51.6224 | -52.7036 | -51.5243 | -68.9193 | -59.0795 | -55.3833 | -51.6858 | -50.5911 | -51.2478 | -70.1467 | -61.635 | -60.7161 | -58.2363 | 91 | -50.2461 | -57.733 | -53.8546 | -50.7611 | -53.7763 | -58.2917 | -54.7225 | -51.6426 | 91 | -47.0503 | -47.707 | -65.3785 | -55.6281 | -51.9319 | -48.0595 | -47.1397 | -47.6215 | -65.4797 | -55.4532 | -51.9437 | -48.2462 | -49.1628 | -47.9835 | -66.6059 | -58.1836 | -57.2647 | -54.61 | -49.2522 | -47.898 | -66.7071 | -58.0087 | -57.2765 | -54.7967
92 | -3.5733 | 0 | -3.4781 | 0 | -3.6448 | 0 | -3.4527 | 0 | -78.9417 | 147.4542 | -54.5013 | -58.3428 | -52.2154 | -59.6864 | -61.1226 | -148.8666 | -59.1006 | 92.6958 | -57.3251 | -119.9795 | -67.1715 | 153.7281 | -58.6457 | -13.7864 | -55.6359 | -58.9666 | -62.7311 | -170.4682 | -60.3219 | 145.4302 | -56.0451 | -135.4059 | -25.3121 | -5.0079 | -29.7324 | -27.7101 | -31.7168 | -22.8869 | -29.7228 | 76.5968 | -24.7959 | -12.4108 | -32.774 | -103.8662 | -30.2035 | -54.9058 | -39.0789 | -155.7008 | -52.3914 | -51.7651 | -51.2756 | -77.8719 | -58.4226 | -57.2573 | -52.4781 | -50.2776 | -50.7022 | -67.0133 | -65.8727 | -59.0745 | -53.9347 | 92 | -50.1936 | -56.9571 | -52.0967 | -50.4164 | -53.6761 | -57.8158 | -53.5802 | -52.114 | 92 | -46.7043 | -47.1289 | -74.2986 | -54.9445 | -53.7792 | -48.8333 | -46.7995 | -47.0574 | -74.4192 | -54.7778 | -53.8046 | -49.0254 | -48.1918 | -47.7023 | -63.44 | -62.3946 | -55.5964 | -50.2899 | -48.287 | -47.6308 | -63.5606 | -62.2279 | -55.6218 | -50.482
93 | -3.6383 | 0 | -3.5004 | 0 | -3.6655 | 0 | -3.486 | 0 | -71.8351 | -28.4416 | -55.6173 | -75.4888 | -53.7332 | -67.6946 | -59.9986 | -178.9031 | -61.868 | 71.2193 | -57.0545 | -142.5218 | -69.7204 | 100.9264 | -58.0668 | -64.3748 | -58.6901 | -70.6111 | -60.5159 | 174.9799 | -62.0226 | 135.9417 | -55.8259 | -144.7663 | -22.2755 | -26.9298 | -33.1493 | -57.5519 | -36.8943 | -52.3965 | -29.1602 | 49.8713 | -22.0988 | -33.344 | -32.5507 | -138.2009 | -33.8189 | -70.5245 | -37.8346 | 177.4533 | -52.8004 | -51.0944 | -51.079 | -77.1168 | -59.9488 | -60.5827 | -52.8637 | -50.064 | -50.7204 | -66.1527 | -65.0121 | -59.4351 | -50.7368 | 93 | -51.523 | -57.6541 | -52.4306 | -51.6405 | -55.2008 | -57.8986 | -52.9556 | -53.3778 | 93 | -46.4257 | -47.0821 | -73.4785 | -56.4484 | -57.0823 | -49.1982 | -46.5636 | -47.0549 | -73.6308 | -56.2833 | -57.0967 | -49.3777 | -47.4561 | -47.4407 | -62.5144 | -61.5117 | -55.9347 | -47.0713 | -47.594 | -47.4135 | -62.6667 | -61.3466 | -55.9491 | -47.2508
94 | -3.668 | 0 | -3.5251 | 0 | -3.6632 | 0 | -3.5234 | 0 | -68.0216 | -85.1752 | -58.2193 | -77.8142 | -54.4964 | -62.1858 | -61.1073 | 162.7542 | -65.0454 | 56.7593 | -58.6893 | -152.0188 | -74.0432 | 106.9967 | -59.4326 | -103.0321 | -60.9407 | -49.9225 | -60.7362 | 165.2053 | -62.8365 | 127.3128 | -56.6414 | -144.1496 | -21.4706 | -53.2598 | -50.3971 | -128.1019 | -49.2524 | 60.4424 | -30.6012 | 28.9347 | -21.4182 | -58.3797 | -34.909 | -158.8452 | -38.0846 | -40.5474 | -36.7929 | 152.6991 | -52.2391 | -51.0921 | -51.3782 | -67.5126 | -61.1298 | -60.8499 | -52.5251 | -50.0499 | -50.9024 | -68.0836 | -62.9313 | -63.5265 | -50.3205 | 94 | -52.8269 | -59.0463 | -54.3961 | -52.8264 | -57.0241 | -58.5266 | -53.8188 | -54.5684 | 94 | -46.3819 | -47.2344 | -63.8446 | -57.6047 | -57.3248 | -48.8619 | -46.5248 | -47.2392 | -63.9892 | -57.4666 | -57.3265 | -49.0017 | -47.4241 | -47.7102 | -64.4156 | -59.4062 | -60.0014 | -46.6573 | -47.567 | -47.715 | -64.5602 | -59.2681 | -60.0031 | -46.7971
95 | -3.6825 | 0 | -3.5637 | 0 | -3.6905 | 0 | -3.5607 | 0 | -67.5089 | -131.8813 | -57.9601 | -65.0925 | -53.5134 | -61.8726 | -61.1705 | 147.4229 | -70.1875 | 61.4718 | -58.2567 | -160.809 | -70.172 | 114.1764 | -61.315 | -140.3808 | -57.7469 | -40.7461 | -59.3696 | 154.4152 | -64.4847 | 117.9307 | -54.2032 | -145.0092 | -22.5341 | -79.149 | -33.7981 | 75.5451 | -34.615 | 45.2783 | -33.7866 | 15.4949 | -22.9044 | -82.6818 | -38.0784 | -146.4421 | -32.6733 | -18.5541 | -35.0816 | 126.1206 | -51.7427 | -52.2601 | -51.6857 | -64.2193 | -61.6216 | -56.0218 | -52.1262 | -50.4288 | -51.1512 | -72.1145 | -61.6614 | -71.9718 | -51.43 | 95 | -52.0551 | -59.8423 | -54.1373 | -52.1876 | -55.9948 | -57.9361 | -52.4458 | -52.3395 | 95 | -46.7463 | -47.4687 | -60.5368 | -58.0579 | -52.4581 | -48.4357 | -46.8651 | -47.4607 | -60.6586 | -57.9311 | -52.4611 | -48.5655 | -48.5776 | -48.0032 | -68.432 | -58.0977 | -68.4081 | -47.7395 | -48.6964 | -47.9952 | -68.5538 | -57.9709 | -68.4111 | -47.8693
96 | -3.6801 | 0 | -3.577 | 0 | -3.7488 | 0 | -3.5596 | 0 | -69.3128 | -169.3466 | -56.0766 | -66.9735 | -52.5967 | -69.1533 | -63.8413 | 121.8296 | -70.3648 | 118.2426 | -60.768 | 170.8878 | -69.022 | 94.1289 | -65.5921 | 152.6431 | -55.0582 | -54.8794 | -60.1418 | 125.6679 | -66.8482 | 133.283 | -53.3696 | -167.6676 | -26.0506 | -97.6611 | -28.216 | 43.3685 | -31.6805 | 11.1896 | -37.1904 | 15.335 | -27.4944 | -99.7864 | -33.5126 | -130.7337 | -29.4462 | -37.5139 | -33.7181 | 97.6555 | -51.6388 | -53.4708 | -52.027 | -63.3068 | -61.2716 | -53.5997 | -51.9169 | -50.7137 | -51.727 | -67.8387 | -61.2528 | -61.3192 | -53.3126 | 96 | -50.9234 | -62.062 | -54.296 | -51.9183 | -54.5329 | -58.8614 | -52.3308 | -51.0074 | 96 | -47.0336 | -48.0469 | -59.6267 | -57.6946 | -50.0227 | -48.1681 | -47.1367 | -47.9782 | -59.7472 | -57.5228 | -50.0401 | -48.3573 | -49.7907 | -48.3469 | -64.1586 | -57.6758 | -57.7422 | -49.5638 | -49.8938 | -48.2782 | -64.2791 | -57.504 | -57.7596 | -49.753
97 | -3.697 | 0 | -3.6237 | 0 | -3.7845 | 0 | -3.5792 | 0 | -72.4765 | 173.4025 | -54.4975 | -77.0086 | -52.5392 | -78.5688 | -70.8405 | 140.1942 | -62.5002 | 117.5053 | -70.1862 | -168.3658 | -71.0871 | 88.1561 | -64.3237 | 30.2506 | -54.0336 | -77.5891 | -66.1704 | 101.8052 | -62.7328 | 149.6471 | -54.908 | 176.7469 | -30.7242 | -76.0955 | -26.0426 | 13.8594 | -31.7747 | -26.1982 | -38.3747 | 20.9494 | -34.045 | -52.2694 | -29.2018 | -149.9185 | -29.01 | -61.6395 | -33.1526 | 69.7697 | -51.6855 | -53.3893 | -52.4775 | -63.2714 | -60.1308 | -52.8698 | -51.8463 | -50.4994 | -52.4001 | -64.1549 | -61.0651 | -57.4408 | -54.4068 | 97 | -50.3718 | -61.5412 | -54.2848 | -52.0544 | -53.5677 | -60.6937 | -54.1555 | -51.1276 | 97 | -46.8024 | -48.7031 | -59.5744 | -56.5071 | -49.2461 | -48.0618 | -46.8757 | -48.6156 | -59.6922 | -56.3463 | -49.2906 | -48.2671 | -49.6923 | -48.7805 | -60.4579 | -57.4414 | -53.8171 | -50.6223 | -49.7656 | -48.693 | -60.5757 | -57.2806 | -53.8616 | -50.8276
98 | -3.7398 | 0 | -3.6321 | 0 | -3.7983 | 0 | -3.5972 | 0 | -73.1853 | 153.6486 | -53.558 | -92.8246 | -52.9519 | -85.3078 | -65.2728 | 165.7236 | -58.7752 | 86.624 | -61.6616 | -126.692 | -68.7673 | 110.2389 | -58.6138 | -39.3955 | -55.7703 | -98.8133 | -70.7218 | 168.2811 | -58.8675 | 127.0816 | -56.82 | 173.9484 | -25.9987 | -52.4705 | -26.0374 | -12.1253 | -34.8731 | -70.8782 | -39.9924 | 8.1883 | -25.6085 | -27.6035 | -27.1202 | -178.8309 | -30.6556 | -81.5067 | -33.0932 | 37.353 | -51.7916 | -52.532 | -53.0399 | -63.7838 | -58.0455 | -52.9812 | -51.9524 | -50.1069 | -52.857 | -62.7298 | -62.1243 | -55.8452 | -52.8033 | 98 | -50.2121 | -57.7707 | -52.6868 | -51.5024 | -53.812 | -58.1946 | -54.5095 | -52.1998 | 98 | -46.3671 | -49.1172 | -60.044 | -54.4134 | -49.3491 | -48.1541 | -46.4748 | -49.0587 | -60.1866 | -54.2472 | -49.384 | -48.3552 | -48.7922 | -49.3001 | -58.99 | -58.4922 | -52.2131 | -49.005 | -48.8999 | -49.2416 | -59.1326 | -58.326 | -52.248 | -49.2061
99 | -3.7844 | 0 | -3.6475 | 0 | -3.8132 | 0 | -3.6131 | 0 | -81.2363 | -73.6457 | -54.0207 | -113.416 | -53.5147 | -93.7087 | -63.1991 | 141.4918 | -59.4434 | 59.6309 | -59.0573 | -156.8982 | -66.0831 | 80.3631 | -56.4914 | -89.1598 | -58.7993 | -110.0229 | -65.1248 | 164.0449 | -59.2208 | 100.2749 | -57.4436 | 170.7147 | -21.9714 | -70.8861 | -27.7225 | -32.9161 | -40.864 | -151.9173 | -48.2731 | -48.8778 | -21.6106 | -48.263 | -26.6453 | 149.1526 | -34.9728 | -89.3552 | -34.1788 | 4.6196 | -52.6273 | -51.418 | -52.897 | -66.4086 | -58.014 | -54.0664 | -52.7022 | -49.7663 | -52.6984 | -63.2179 | -63.9796 | -55.5515 | -49.8492 | 99 | -50.7462 | -57.8968 | -52.454 | -51.6552 | -54.193 | -57.5691 | -53.6132 | -53.6487 | 99 | -45.9819 | -48.914 | -62.6242 | -54.3665 | -50.4189 | -48.889 | -46.1188 | -48.8852 | -62.7955 | -54.2008 | -50.4533 | -49.0891 | -47.6336 | -49.1126 | -59.4335 | -60.3321 | -51.904 | -46.036 | -47.7705 | -49.0838 | -59.6048 | -60.1664 | -51.9384 | -46.2361
100 | -3.8122 | 0 | -3.6492 | 0 | -3.8229 | 0 | -3.6416 | 0 | -66.5034 | -134.9718 | -56.8984 | -123.8627 | -54.147 | -93.4641 | -65.6651 | 120.6186 | -60.0555 | 46.2763 | -60.3455 | -173.3289 | -69.4984 | 74.5126 | -57.3102 | -130.0196 | -62.5363 | -98.8381 | -64.9897 | 155.7829 | -59.8715 | 82.4852 | -58.8317 | 170.9485 | -20.4743 | -98.2016 | -30.8118 | -40.8854 | -37.4108 | 97.2808 | -40.6036 | -179.7175 | -20.2141 | -73.643 | -27.9676 | 116.3814 | -37.0158 | -50.9734 | -35.32 | -34.2548 | -52.422 | -50.5409 | -53.1592 | -75.4767 | -59.0431 | -56.6542 | -52.5047 | -49.5299 | -52.7887 | -66.3797 | -62.7352 | -57.2174 | -48.8937 | 100 | -52.1362 | -58.2906 | -54.8981 | -52.3962 | -55.9729 | -58.3587 | -54.58 | -55.3815 | 100 | -45.7177 | -48.9765 | -71.6645 | -55.3939 | -53.005 | -48.6818 | -45.8807 | -48.9658 | -71.8351 | -55.2202 | -53.0126 | -48.8631 | -46.7287 | -49.347 | -62.5675 | -59.086 | -53.5682 | -45.0708 | -46.8917 | -49.3363 | -62.7381 | -58.9123 | -53.5758 | -45.2521
101 | -3.8272 | 0 | -3.6672 | 0 | -3.8368 | 0 | -3.6689 | 0 | -63.0205 | -179.0872 | -57.7429 | -108.6239 | -54.1109 | -94.2504 | -66.9389 | 127.1057 | -61.0056 | 33.4027 | -60.0257 | 175.4104 | -67.1146 | 89.9038 | -59.3726 | -161.2288 | -60.084 | -77.4999 | -62.78 | 154.1191 | -61.0814 | 61.4112 | -57.8225 | -173.1161 | -20.9252 | -126.8692 | -32.7991 | -27.8699 | -34.0211 | 31.7968 | -33.1197 | 142.4889 | -20.8948 | -99.0182 | -31.9536 | 83.8869 | -31.3953 | -42.6763 | -36.3697 | -73.5004 | -51.8032 | -50.8674 | -53.5727 | -71.9087 | -59.8931 | -57.1096 | -51.9953 | -49.8251 | -52.8507 | -84.8625 | -61.6593 | -59.9266 | -49.2512 | 101 | -52.1745 | -58.2551 | -55.4091 | -52.4656 | -56.3253 | -58.2358 | -54.7708 | -54.6706 | 101 | -45.9979 | -49.0235 | -68.0815 | -56.2259 | -53.4424 | -48.1585 | -46.1579 | -49.0139 | -68.2398 | -56.0563 | -53.4407 | -48.3264 | -47.0402 | -49.7455 | -81.0353 | -57.9921 | -56.2594 | -45.4144 | -47.2002 | -49.7359 | -81.1936 | -57.8225 | -56.2577 | -45.5823
102 | -3.8204 | 0 | -3.6973 | 0 | -3.8824 | 0 | -3.6853 | 0 | -62.7589 | 143.7052 | -55.5084 | -110.0656 | -53.6093 | -98.9009 | -68.3502 | 107.3405 | -62.6207 | 28.2036 | -61.4624 | 151.8539 | -64.7831 | 71.4833 | -62.692 | 157.425 | -56.8357 | -82.5601 | -61.9512 | 125.6657 | -64.868 | 38.8419 | -55.0799 | 173.8467 | -23.737 | -152.9795 | -30.8206 | -19.2274 | -33.2332 | -26.9678 | -29.7176 | 110.0917 | -23.9828 | -119.5276 | -45.281 | 69.2811 | -28.5237 | -62.0505 | -36.5022 | -110.4781 | -51.599 | -52.1825 | -53.9096 | -64.2045 | -60.3568 | -54.3466 | -51.7676 | -50.3785 | -53.1602 | -67.334 | -61.2325 | -57.6441 | -50.1872 | 102 | -51.1359 | -59.126 | -54.3495 | -52.5051 | -55.3126 | -58.8723 | -53.6848 | -52.5942 | 102 | -46.5581 | -49.3398 | -60.3841 | -56.6595 | -50.6493 | -47.8852 | -46.6812 | -49.2778 | -60.5192 | -56.4744 | -50.6613 | -48.0823 | -48.3621 | -50.0892 | -63.5136 | -57.5352 | -53.9468 | -46.3048 | -48.4852 | -50.0272 | -63.6487 | -57.3501 | -53.9588 | -46.5019
103 | -3.8121 | 0 | -3.7326 | 0 | -3.9089 | 0 | -3.7071 | 0 | -64.9146 | 114.8021 | -54.1098 | -122.0383 | -53.8551 | -105.9496 | -77.1459 | 159.8384 | -63.5909 | 36.8516 | -71.8655 | 136.5074 | -65.6384 | 49.4488 | -70.1127 | 50.8908 | -55.64 | -106.2743 | -66.2817 | 97.0095 | -77.883 | 61.5261 | -55.0855 | 151.9186 | -30.3305 | -157.0549 | -28.9724 | -29.019 | -33.2457 | -92.992 | -28.3968 | 78.9377 | -30.4174 | -108.7259 | -35.8853 | -178.1009 | -28.0715 | -82.8634 | -36.0737 | -136.479 | -51.7749 | -53.1739 | -54.206 | -61.2632 | -60.4859 | -52.5606 | -51.8146 | -50.4402 | -53.7886 | -62.1154 | -60.7638 | -54.612 | -51.2369 | 103 | -50.7986 | -61.0833 | -54.0164 | -53.3548 | -55.0872 | -62.8009 | -54.6427 | -52.3315 | 103 | -46.6281 | -49.9765 | -57.4511 | -56.7533 | -48.828 | -47.9057 | -46.7076 | -49.8797 | -57.5561 | -56.577 | -48.8535 | -48.1075 | -49.3618 | -50.3939 | -58.3033 | -57.0312 | -50.8794 | -47.328 | -49.4413 | -50.2971 | -58.4083 | -56.8549 | -50.9049 | -47.5298
104 | -3.839 | 0 | -3.7456 | 0 | -3.9327 | 0 | -3.7248 | 0 | -69.3786 | 105.1156 | -53.3698 | -138.8197 | -54.4281 | -111.8895 | -65.4493 | 171.9742 | -60.5023 | 42.7893 | -64.2509 | -136.8767 | -69.1412 | 38.4154 | -61.4302 | -60.1068 | -56.7582 | -130.6004 | -74.7305 | 142.5202 | -65.3332 | 128.3256 | -57.4705 | 140.2731 | -28.9169 | -101.2513 | -28.387 | -44.0838 | -32.1495 | -159.8608 | -28.7105 | 47.276 | -27.1582 | -61.5724 | -29.0506 | 152.2056 | -29.1683 | -99.8296 | -34.2953 | -154.285 | -52.0224 | -53.0806 | -54.5025 | -59.6786 | -59.7138 | -51.7759 | -51.9214 | -50.0147 | -54.671 | -59.9761 | -60.3393 | -52.7452 | -51.1551 | 104 | -50.7959 | -58.8897 | -52.7871 | -53.1212 | -55.3006 | -63.4835 | -55.9457 | -53.775 | 104 | -46.1757 | -50.832 | -55.8396 | -55.9682 | -48.0303 | -47.9887 | -46.2691 | -50.7383 | -55.9538 | -55.7811 | -48.0511 | -48.1966 | -49.2416 | -50.6635 | -56.1371 | -56.5937 | -48.9996 | -47.2224 | -49.335 | -50.5698 | -56.2513 | -56.4066 | -49.0204 | -47.4303
105 | -3.8985 | 0 | -3.7736 | 0 | -3.95 | 0 | -3.7469 | 0 | -71.8066 | 134.9298 | -53.7505 | -160.6888 | -54.9708 | -110.6662 | -63.0962 | 134.1359 | -58.106 | 22.0726 | -60.1547 | -169.9192 | -72.068 | 58.4263 | -57.3719 | -113.3985 | -61.6182 | -154.2202 | -67.4709 | 152.2932 | -60.3587 | 98.7981 | -59.4403 | 138.7232 | -22.8249 | -112.3656 | -28.4935 | -58.781 | -30.7276 | 143.1625 | -30.5414 | 11.7304 | -22.0146 | -71.5438 | -26.5007 | 118.0669 | -30.7336 | -102.6953 | -32.1135 | -170.7855 | -52.3316 | -51.8987 | -54.9409 | -59.4332 | -58.1871 | -51.6174 | -52.0783 | -49.3992 | -55.5781 | -59.5822 | -61.0978 | -51.7508 | -49.2347 | 105 | -51.2691 | -56.7719 | -52.4629 | -52.4448 | -55.8795 | -59.3484 | -55.0195 | -55.6111 | 105 | -45.5007 | -51.6796 | -55.5347 | -54.4135 | -47.8438 | -48.1283 | -45.6256 | -51.6281 | -55.6863 | -54.2371 | -47.8705 | -48.3314 | -48.0002 | -51.0424 | -55.6837 | -57.3242 | -47.9772 | -45.2847 | -48.1251 | -50.9909 | -55.8353 | -57.1478 | -48.0039 | -45.4878
106 | -3.9404 | 0 | -3.7897 | 0 | -3.9779 | 0 | -3.7806 | 0 | -66.183 | 158.4931 | -57.0446 | 176.7762 | -54.4152 | -109.424 | -66.8185 | 106.384 | -58.6175 | 1.6439 | -61.649 | 156.3527 | -72.1379 | 83.2905 | -57.5325 | -158.0683 | -71.2716 | -102.5528 | -69.3766 | 139.2538 | -59.5399 | 71.6907 | -61.2367 | 147.4175 | -20.3298 | -139.7785 | -28.6495 | -73.2579 | -30.8684 | 89.9979 | -33.5123 | -33.261 | -19.9048 | -93.6441 | -25.6537 | 84.7306 | -30.6004 | -97.2081 | -30.0659 | 168.6772 | -52.383 | -50.329 | -55.1939 | -61.7463 | -58.1096 | -52.4071 | -52.1765 | -48.8607 | -55.9756 | -61.4538 | -61.9147 | -51.849 | -47.7665 | 106 | -52.3405 | -57.3905 | -55.4257 | -52.4588 | -57.2107 | -58.8998 | -55.7961 | -57.1252 | 106 | -44.9203 | -52.0352 | -57.8059 | -54.3199 | -48.6174 | -48.1986 | -45.071 | -51.9977 | -57.9657 | -54.1317 | -48.6265 | -48.3959 | -46.3886 | -51.2535 | -57.5134 | -58.125 | -48.0593 | -43.7886 | -46.5393 | -51.216 | -57.6732 | -57.9368 | -48.0684 | -43.9859
107 | -3.9582 | 0 | -3.8191 | 0 | -3.9774 | 0 | -3.8222 | 0 | -61.3227 | 133.7408 | -62.9765 | -156.8459 | -53.0776 | -113.7817 | -69.4533 | 137.4291 | -59.8956 | -10.0037 | -65.2463 | 164.4046 | -66.5218 | 92.9954 | -60.552 | 172.3429 | -61.0219 | -69.4081 | -67.6969 | 161.6641 | -59.851 | 47.9962 | -60.5214 | 166.004 | -20.1134 | -170.1136 | -28.7495 | -92.6138 | -33.0388 | 25.3033 | -36.0381 | -96.9167 | -19.8089 | -116.217 | -26.0824 | 51.5003 | -28.4459 | -97.0313 | -28.4355 | 145.4847 | -51.7211 | -49.7621 | -55.657 | -68.4867 | -58.6468 | -53.4653 | -51.784 | -48.8133 | -55.8605 | -66.9051 | -61.3309 | -53.5047 | -47.4379 | 107 | -52.101 | -57.2695 | -60.3805 | -52.0438 | -57.2268 | -58.4539 | -57.1277 | -55.6669 | 107 | -44.8551 | -51.9023 | -64.5285 | -54.8277 | -49.6462 | -47.8066 | -44.9942 | -51.8831 | -64.6645 | -54.6694 | -49.6431 | -47.9618 | -45.8039 | -51.6988 | -62.9469 | -57.5118 | -49.6856 | -43.4605 | -45.943 | -51.6796 | -63.0829 | -57.3535 | -49.6825 | -43.6157
108 | -3.9725 | 0 | -3.8454 | 0 | -4.0132 | 0 | -3.8201 | 0 | -60.1959 | 100.6645 | -57.6967 | -134.4123 | -52.508 | -126.4903 | -67.0988 | 126.2633 | -61.1081 | -17.3623 | -63.9103 | 152.5255 | -63.8731 | 69.8559 | -64.2941 | 149.5624 | -56.7397 | -87.1305 | -65.4526 | 137.6782 | -62.1108 | 24.1793 | -57.0024 | 156.6776 | -22.2734 | 160.1274 | -29.0705 | -119.659 | -33.0498 | -67.8047 | -34.8988 | -150.6689 | -21.6011 | -134.1478 | -27.509 | 19.9139 | -26.1278 | -109.2841 | -27.9327 | 118.8554 | -51.3099 | -50.5402 | -56.1089 | -66.3646 | -59.0834 | -52.7746 | -51.529 | -49.3687 | -55.7811 | -66.4978 | -60.9704 | -54.8374 | -47.673 | 108 | -50.8257 | -57.154 | -56.3809 | -51.6786 | -55.3753 | -58.8276 | -55.7657 | -53.2535 | 108 | -45.3962 | -51.8086 | -62.3921 | -55.238 | -48.9292 | -47.5158 | -45.5233 | -51.7679 | -62.5445 | -55.0702 | -48.9545 | -47.7089 | -46.5677 | -52.1364 | -62.5253 | -57.125 | -50.992 | -43.6598 | -46.6948 | -52.0957 | -62.6777 | -56.9572 | -51.0173 | -43.8529
109 | -3.9668 | 0 | -3.8532 | 0 | -4.0507 | 0 | -3.8297 | 0 | -61.9406 | 71.0565 | -54.5537 | -149.1135 | -52.8076 | -141.5049 | -70.4427 | 133.5419 | -63.3057 | -15.1064 | -68.7101 | 136.4484 | -65.3722 | 48.0195 | -82.6119 | 81.3041 | -54.369 | -112.5772 | -70.627 | 116.335 | -68.2239 | 13.2441 | -56.7981 | 133.5615 | -28.9807 | 138.5212 | -29.9136 | -157.5034 | -28.4564 | -134.4834 | -33.3172 | -179.4573 | -24.7154 | -135.3242 | -29.742 | -6.6817 | -24.8151 | -129.2323 | -28.5418 | 91.5472 | -51.392 | -51.7887 | -56.5954 | -61.0326 | -59.5053 | -51.3902 | -51.572 | -49.746 | -56.1074 | -61.4978 | -60.5798 | -53.8163 | -48.2419 | 109 | -50.2765 | -59.2188 | -54.2836 | -52.3354 | -54.0313 | -62.7791 | -56.611 | -52.2933 | 109 | -45.7792 | -52.1406 | -57.0658 | -55.6521 | -47.537 | -47.5213 | -45.8928 | -52.0567 | -57.2029 | -55.4546 | -47.5605 | -47.7423 | -47.8219 | -52.6286 | -57.531 | -56.7266 | -49.9631 | -44.1912 | -47.9355 | -52.5447 | -57.6681 | -56.5291 | -49.9866 | -44.4122
110 | -4.0035 | 0 | -3.862 | 0 | -4.0711 | 0 | -3.8281 | 0 | -67.0761 | 52.9039 | -53.0533 | -168.2564 | -54.0804 | -156.7066 | -65.7479 | 155.3183 | -62.6128 | 3.7413 | -71.2527 | -143.8755 | -69.7116 | 52.3539 | -62.3116 | -96.2081 | -54.7088 | -138.7384 | -71.6614 | -173.7004 | -69.2352 | 86.2811 | -59.4881 | 114.6199 | -32.5204 | -122.1442 | -30.7326 | 152.4021 | -25.5165 | -177.7176 | -32.1323 | 168.5915 | -24.5281 | -114.3198 | -31.7281 | -24.929 | -24.581 | -150.0906 | -30.4932 | 59.2358 | -51.7641 | -52.7389 | -56.9252 | -58.2563 | -59.5259 | -50.2935 | -51.78 | -49.6141 | -56.777 | -58.7644 | -59.8933 | -52.0477 | -48.7666 | 110 | -50.4312 | -59.956 | -52.7639 | -53.4381 | -53.898 | -65.3116 | -57.4944 | -53.348 | 110 | -45.6106 | -52.7735 | -54.2528 | -55.6639 | -46.4315 | -47.7089 | -45.7521 | -52.7059 | -54.4282 | -55.4548 | -46.4654 | -47.9519 | -48.7354 | -52.9217 | -54.7609 | -56.0313 | -48.1857 | -44.6955 | -48.8769 | -52.8541 | -54.9363 | -55.8222 | -48.2196 | -44.9385
111 | -4.0487 | 0 | -3.9021 | 0 | -4.0979 | 0 | -3.8566 | 0 | -72.6589 | 110.1215 | -52.6843 | 168.4853 | -57.4908 | -166.4695 | -62.6569 | 129.3378 | -58.9799 | 3.259 | -63.2328 | -162.7243 | -68.0713 | 90.0329 | -56.3681 | -141.3051 | -56.6521 | -158.8283 | -64.9467 | 169.3985 | -60.9106 | 77.5525 | -63.7545 | 122.793 | -22.5268 | -134.1174 | -30.3194 | 95.5362 | -24.4332 | 150.1795 | -29.9267 | 163.3804 | -20.947 | -115.0757 | -31.7539 | -40.576 | -25.1486 | -168.9804 | -34.9552 | 13.3362 | -52.2496 | -52.5626 | -57.2205 | -56.7653 | -58.6715 | -49.5158 | -51.9373 | -49.1448 | -57.8456 | -57.3826 | -59.4763 | -50.555 | -48.5321 | 111 | -51.411 | -57.3017 | -51.9333 | -54.5323 | -53.3486 | -58.9046 | -55.1582 | -54.6932 | 111 | -45.0961 | -53.7969 | -52.7166 | -54.7694 | -45.6137 | -47.8394 | -45.2427 | -53.7477 | -52.9087 | -54.5736 | -45.6592 | -48.0807 | -48.5139 | -53.1718 | -53.3339 | -55.5742 | -46.6529 | -44.4342 | -48.6605 | -53.1226 | -53.526 | -55.3784 | -46.6984 | -44.6755
112 | -4.1058 | 0 | -3.938 | 0 | -4.1156 | 0 | -3.8809 | 0 | -63.7837 | 126.4674 | -54.2582 | 143.231 | -60.1991 | -150.6755 | -64.9899 | 101.33 | -56.7879 | -15.1257 | -63.0557 | 165.2963 | -63.3052 | 91.8877 | -55.0471 | 173.4136 | -61.1349 | -159.5038 | -66.2389 | 145.7727 | -57.6514 | 47.2192 | -62.4444 | 144.7585 | -18.9933 | -161.5348 | -28.8298 | 42.0742 | -25.2548 | 124.9896 | -27.546 | 152.1432 | -18.7467 | -133.1464 | -30.1177 | -63.3604 | -26.5575 | 174.0474 | -37.4489 | -73.6568 | -52.5004 | -50.9554 | -57.7308 | -56.934 | -57.7544 | -49.1937 | -51.8677 | -48.4906 | -59.1449 | -57.6411 | -60.145 | -49.6078 | -47.4682 | 112 | -52.9031 | -55.4813 | -53.4074 | -54.5037 | -53.5998 | -56.1578 | -54.05 | -55.1471 | 112 | -44.3848 | -55.0391 | -52.8282 | -53.8164 | -45.2557 | -47.7521 | -44.5526 | -55.0293 | -53.0531 | -53.6388 | -45.3128 | -47.9868 | -46.8496 | -53.625 | -53.5353 | -56.207 | -45.6698 | -43.3526 | -47.0174 | -53.6152 | -53.7602 | -56.0294 | -45.7269 | -43.5873
113 | -4.1275 | 0 | -3.9698 | 0 | -4.0899 | 0 | -3.9072 | 0 | -59.3855 | 104.0326 | -58.9049 | 132.725 | -58.6717 | -128.4242 | -69.1522 | 125.5308 | -56.5136 | -33.5219 | -67.959 | 162.2782 | -59.7857 | 77.6452 | -57.3718 | 133.9831 | -60.387 | -133.2802 | -67.03 | 165.3891 | -57.0795 | 17.1798 | -61.4591 | 149.3539 | -17.9516 | 170.9724 | -27.6698 | -4.2093 | -28.0206 | 115.8573 | -25.796 | 136.7648 | -18.2288 | -156.0467 | -28.2026 | -93.893 | -29.5922 | 163.7692 | -32.5586 | -139.8903 | -52.1535 | -49.6056 | -58.4401 | -59.3527 | -57.8331 | -49.6993 | -51.5362 | -48.1876 | -59.6314 | -59.9191 | -61.0362 | -49.6563 | -46.6618 | 113 | -54.2061 | -54.5528 | -58.0456 | -54.2603 | -54.2057 | -54.9379 | -55.6156 | -54.4509 | 113 | -44.0601 | -55.5039 | -55.2252 | -53.8633 | -45.7295 | -47.4463 | -44.2178 | -55.5415 | -55.4455 | -53.7432 | -45.7921 | -47.629 | -45.4781 | -54.3126 | -55.7916 | -57.0664 | -45.6865 | -42.5719 | -45.6358 | -54.3502 | -56.0119 | -56.9463 | -45.7491 | -42.7546
114 | -4.1217 | 0 | -4.0046 | 0 | -4.0861 | 0 | -3.9236 | 0 | -57.8829 | 75.3706 | -60.1059 | 161.7502 | -55.2524 | -133.1402 | -65.3517 | 132.8648 | -56.8385 | -48.6411 | -66.1797 | -169.232 | -57.9975 | 53.7547 | -62.0193 | 109.7186 | -56.5343 | -137.4113 | -64.1384 | 153.6419 | -57.6109 | -12.0649 | -59.2834 | 147.2782 | -18.938 | 145.7222 | -26.8142 | -44.6773 | -29.135 | 136.5435 | -25.2115 | 116.7302 | -19.4363 | -178.7693 | -26.7155 | -127.2692 | -32.4268 | -174.2899 | -29.356 | -174.9176 | -51.6375 | -49.6018 | -59.0905 | -62.1727 | -58.3641 | -50.2502 | -51.196 | -48.5939 | -59.5084 | -61.5905 | -61.2468 | -50.5001 | -46.4436 | 114 | -52.5276 | -53.9895 | -58.2144 | -52.7609 | -53.531 | -54.3123 | -56.5893 | -52.8955 | 114 | -44.4722 | -55.3867 | -58.051 | -54.3595 | -46.2456 | -47.1099 | -44.5893 | -55.4223 | -58.2491 | -54.278 | -46.3266 | -47.2724 | -45.4801 | -54.9688 | -57.4688 | -57.2422 | -46.4955 | -42.3575 | -45.5972 | -55.0044 | -57.6669 | -57.1607 | -46.5765 | -42.52
115 | -4.1068 | 0 | -3.9973 | 0 | -4.1272 | 0 | -3.956 | 0 | -58.5981 | 48.1835 | -56.6229 | 162.5289 | -54.5065 | -148.519 | -64.5604 | 126.5402 | -57.6724 | -61.9082 | -64.9859 | 175.9762 | -58.4849 | 28.8974 | -70.4509 | 88.3749 | -54.5089 | -159.4384 | -66.7853 | 137.4618 | -59.5828 | -44.2409 | -58.2275 | 127.4701 | -21.9019 | 131.1818 | -27.1134 | -82.6786 | -24.7968 | 143.3933 | -25.8722 | 99.1814 | -23.0738 | 164.4621 | -26.0905 | -160.2453 | -28.528 | -154.5515 | -28.5451 | 158.9722 | -51.4077 | -50.4399 | -59.5367 | -60.8139 | -59.0131 | -49.9907 | -51.1497 | -49.1507 | -59.7865 | -59.8411 | -61.0403 | -50.9358 | -46.7431 | 115 | -51.4874 | -54.6345 | -55.4616 | -52.5421 | -52.9684 | -55.6417 | -57.4382 | -52.1143 | 115 | -45.0439 | -55.6797 | -56.7071 | -55.0158 | -45.9934 | -47.0225 | -45.1534 | -55.6593 | -56.8579 | -54.8859 | -46.0347 | -47.1937 | -46.3331 | -55.4299 | -55.7343 | -57.043 | -46.9385 | -42.6159 | -46.4426 | -55.4095 | -55.8851 | -56.9131 | -46.9798 | -42.7871
116 | -4.1108 | 0 | -4.0111 | 0 | -4.18 | 0 | -3.9731 | 0 | -61.812 | 30.1685 | -54.5254 | 147.2784 | -54.4604 | -165.2074 | -62.715 | 125.8028 | -59.3122 | -69.4149 | -64.6011 | -171.4406 | -61.331 | 12.8034 | -68.3803 | -125.7631 | -54.2731 | -179.4565 | -68.4181 | 175.6355 | -64.3327 | -78.709 | -61.7488 | 101.0264 | -25.1617 | 148.7966 | -28.047 | -117.3085 | -21.9585 | 128.7302 | -28.432 | 86.2123 | -28.3287 | -173.9647 | -26.2249 | 168.4962 | -24.6972 | -165.9906 | -29.1447 | 144.345 | -51.5386 | -51.492 | -59.7576 | -57.9467 | -59.5348 | -49.2637 | -51.3489 | -49.3734 | -60.5673 | -57.6761 | -60.3074 | -50.4607 | -47.388 | 116 | -51.0975 | -56.2605 | -53.5563 | -52.9252 | -53.3539 | -59.0353 | -60.1878 | -53.2096 | 116 | -45.2626 | -56.4565 | -53.8359 | -55.5237 | -45.2526 | -47.1689 | -45.3623 | -56.3873 | -53.9736 | -55.3548 | -45.2906 | -47.3758 | -47.3812 | -55.6468 | -53.5653 | -56.2963 | -46.4496 | -43.208 | -47.4809 | -55.5776 | -53.703 | -56.1274 | -46.4876 | -43.4149
117 | -4.1372 | 0 | -4.0249 | 0 | -4.2315 | 0 | -3.9712 | 0 | -66.5661 | 46.2528 | -53.5144 | 125.1559 | -56.1918 | 177.8366 | -60.7072 | 108.1359 | -60.5136 | -64.9865 | -61.9086 | -179.395 | -64.9646 | 24.9661 | -58.6979 | -164.6699 | -55.4046 | 155.8817 | -62.4996 | 178.4522 | -77.16 | -170.4911 | -70.6171 | 143.6644 | -21.7213 | 167.3771 | -29.5267 | -145.9102 | -20.8923 | 109.9772 | -32.7722 | 94.4468 | -23.8496 | -141.2297 | -27.3766 | 139.6364 | -22.7101 | 174.1184 | -30.4844 | 142.863 | -51.9567 | -52.0307 | -59.657 | -55.7938 | -59.3883 | -48.4559 | -51.6381 | -49.1024 | -61.91 | -56.1113 | -59.3877 | -49.4295 | -47.7959 | 117 | -51.5022 | -57.0804 | -52.2576 | -54.0492 | -53.4204 | -60.4555 | -56.9924 | -55.2477 | 117 | -44.9652 | -57.7728 | -51.6566 | -55.3634 | -44.431 | -47.4066 | -45.0775 | -57.6785 | -51.8226 | -55.1568 | -44.4847 | -47.6669 | -47.8935 | -55.5198 | -51.9741 | -55.3628 | -45.4046 | -43.5644 | -48.0058 | -55.4255 | -52.1401 | -55.1562 | -45.4583 | -43.8247
118 | -4.1821 | 0 | -4.0288 | 0 | -4.2607 | 0 | -3.9862 | 0 | -62.7558 | 78.9249 | -54.0923 | 96.8154 | -60.1823 | 172.6272 | -61.8111 | 81.6552 | -59.051 | -60.8034 | -61.9684 | 156.0423 | -62.837 | 48.8893 | -55.6563 | 151.5156 | -58.0991 | 136.6982 | -60.6989 | 157.8614 | -66.5668 | 55.3509 | -61.4343 | 177.6854 | -18.2475 | 155.4793 | -31.0721 | -164.9122 | -21.2821 | 92.9192 | -31.5351 | 136.3693 | -19.6163 | -153.2561 | -29.8601 | 114.3474 | -22.1753 | 152.0952 | -29.5872 | 156.4267 | -52.4277 | -51.1127 | -59.4912 | -54.7207 | -58.4941 | -47.7963 | -51.8179 | -48.4247 | -63.6548 | -55.3569 | -58.9429 | -48.3192 | -47.1128 | 118 | -52.687 | -56.1378 | -52.8467 | -55.4688 | -53.1982 | -57.9801 | -53.6766 | -56.0409 | 118 | -44.2426 | -59.4727 | -50.5386 | -54.4653 | -43.7675 | -47.5572 | -44.3959 | -59.3941 | -50.7345 | -54.2334 | -43.8101 | -47.8317 | -46.9306 | -55.3091 | -51.1748 | -54.9141 | -44.2904 | -42.8521 | -47.0839 | -55.2305 | -51.3707 | -54.6822 | -44.333 | -43.1266
119 | -4.2379 | 0 | -4.0462 | 0 | -4.2555 | 0 | -4.0176 | 0 | -57.8755 | 67.0899 | -57.9341 | 67.4734 | -62.4932 | -168.6912 | -67.4928 | 80.3979 | -57.5639 | -71.5192 | -65.6528 | 157.8433 | -59.0578 | 44.0229 | -56.7112 | 106.8913 | -62.4832 | 149.419 | -61.176 | 149.0427 | -61.6667 | 14.1243 | -58.3849 | 160.193 | -16.9278 | 134.6895 | -31.5874 | -173.6162 | -23.2077 | 81.6731 | -26.7947 | 137.1391 | -17.8379 | -175.7451 | -34.0828 | 93.241 | -23.4208 | 131.3182 | -26.7174 | 155.3828 | -52.4334 | -49.4748 | -59.6876 | -55.16 | -57.7928 | -47.6974 | -51.6478 | -47.7516 | -63.7691 | -55.9056 | -59.3392 | -47.7008 | -46.0612 | 119 | -54.1984 | -54.4838 | -56.8627 | -55.871 | -54.0459 | -55.7084 | -53.6194 | -55.6923 | 119 | -43.5137 | -59.5312 | -50.9221 | -53.7466 | -43.6512 | -47.3923 | -43.7054 | -59.5136 | -51.1424 | -53.5373 | -43.6798 | -47.6302 | -45.2369 | -55.4497 | -51.6677 | -55.293 | -43.6546 | -41.8057 | -45.4286 | -55.4321 | -51.888 | -55.0837 | -43.6832 | -42.0436
120 | -4.2449 | 0 | -4.0553 | 0 | -4.2222 | 0 | -4.0259 | 0 | -55.5671 | 42.1053 | -68.0703 | 79.8755 | -60.3899 | -149.0232 | -65.3505 | 114.4446 | -57.4833 | -86.4915 | -63.5562 | -178.9217 | -56.8895 | 24.9507 | -61.9142 | 70.8497 | -60.4878 | 164.0532 | -60.5678 | 144.8004 | -60.6307 | -20.5073 | -56.9073 | 146.4489 | -17.4181 | 113.3409 | -30.4162 | 176.2953 | -25.6471 | 88.1991 | -24.0233 | 122.3614 | -17.9495 | 161.1856 | -42.8606 | 96.7891 | -26.637 | 125.2318 | -24.2421 | 143.9631 | -52.0051 | -48.7696 | -60.1283 | -56.7434 | -57.7785 | -48.0782 | -51.3639 | -47.7183 | -62.5183 | -56.9381 | -59.9928 | -47.9409 | -45.4658 | 120 | -54.1508 | -53.1408 | -60.513 | -55.0304 | -54.4563 | -54.2148 | -54.4864 | -54.2057 | 120 | -43.4734 | -58.2734 | -52.4985 | -53.7232 | -44.0229 | -47.1417 | -43.663 | -58.2961 | -52.7175 | -53.5563 | -44.0523 | -47.338 | -44.5247 | -55.8834 | -52.6932 | -55.9375 | -43.8856 | -41.2436 | -44.7143 | -55.9061 | -52.9122 | -55.7706 | -43.915 | -41.4399
121 | -4.2267 | 0 | -4.0717 | 0 | -4.241 | 0 | -4.0466 | 0 | -55.3775 | 15.6083 | -61.8379 | 138.1851 | -58.6111 | -159.1351 | -62.7259 | 105.9184 | -58.2541 | -96.8831 | -60.2724 | 173.7403 | -56.7049 | 0.7954 | -74.7052 | 63.0441 | -57.5884 | 156.2375 | -61.1393 | 137.5695 | -61.3576 | -53.7139 | -56.7568 | 127.7794 | -19.9129 | 99.1648 | -28.7317 | 159.4491 | -24.3578 | 108.5503 | -23.0461 | 105.039 | -20.0625 | 143.2415 | -42.3437 | -174.4456 | -27.4937 | 149.5095 | -23.1471 | 126.8336 | -51.6583 | -49.0151 | -60.4773 | -57.5372 | -58.1856 | -48.3081 | -51.2748 | -48.1473 | -61.9494 | -57.0248 | -60.4115 | -48.5106 | -45.4851 | 121 | -53.0708 | -53.0736 | -56.7203 | -54.1897 | -54.0762 | -54.3933 | -55.3562 | -53.3874 | 121 | -43.9206 | -57.7227 | -53.3105 | -54.1139 | -44.2364 | -47.0338 | -44.0756 | -57.7084 | -53.4906 | -53.9446 | -44.2615 | -47.2282 | -44.7884 | -56.2506 | -52.7981 | -56.3398 | -44.4389 | -41.2441 | -44.9434 | -56.2363 | -52.9782 | -56.1705 | -44.464 | -41.4385
122 | -4.2182 | 0 | -4.1093 | 0 | -4.2768 | 0 | -4.0605 | 0 | -57.0189 | -7.8417 | -57.0796 | 121.391 | -58.0277 | -171.8256 | -61.7673 | 98.013 | -59.4388 | -103.7875 | -58.8588 | 159.9026 | -58.8871 | -20.9613 | -68.3393 | -175.4955 | -56.4384 | 132.3996 | -61.6522 | 147.4299 | -64.6076 | -93.4943 | -58.8793 | 117.7801 | -23.6852 | 109.1257 | -28.0664 | 138.9058 | -21.432 | 107.0456 | -23.4926 | 87.3637 | -23.7319 | 145.9376 | -35.3255 | -172.3019 | -23.4518 | 152.5602 | -23.3199 | 109.6755 | -51.6334 | -49.8243 | -60.4064 | -56.4303 | -58.735 | -48.0509 | -51.4374 | -48.5697 | -62.3979 | -55.9062 | -60.1015 | -48.7104 | -46.0604 | 122 | -52.5803 | -54.2133 | -54.0613 | -53.965 | -54.307 | -56.3418 | -56.7273 | -54.0769 | 122 | -44.3515 | -58.1797 | -52.2121 | -54.6257 | -43.9416 | -47.1606 | -44.4604 | -58.1211 | -52.3698 | -54.4582 | -43.9904 | -47.3769 | -45.6061 | -56.1882 | -51.688 | -55.9922 | -44.6011 | -41.7836 | -45.715 | -56.1296 | -51.8457 | -55.8247 | -44.6499 | -41.9999
123 | -4.2559 | 0 | -4.1157 | 0 | -4.3473 | 0 | -4.072 | 0 | -60.8318 | -19.0426 | -55.1024 | 95.7963 | -59.0388 | 172.4657 | -60.9237 | 87.2067 | -60.4533 | -99.7706 | -57.9125 | 147.6692 | -64.0274 | -25.2859 | -60.4064 | 160.6832 | -56.5706 | 107.2333 | -58.7852 | 151.2572 | -73.1247 | -161.6642 | -60.8406 | 130.1898 | -21.4651 | 138.2846 | -28.5026 | 120.0084 | -19.801 | 95.8411 | -25.3033 | 75.3844 | -22.8167 | 172.2138 | -31.9555 | 176.2835 | -20.9627 | 134.5308 | -24.7675 | 95.9218 | -51.9329 | -50.6839 | -59.8699 | -54.636 | -58.9407 | -47.391 | -51.7368 | -48.6051 | -63.4004 | -54.5103 | -59.2876 | -48.3355 | -46.5689 | 123 | -52.8718 | -55.9602 | -52.5852 | -54.2415 | -54.5483 | -57.5275 | -55.1464 | -55.1211 | 123 | -44.3492 | -59.1445 | -50.3801 | -54.825 | -43.2753 | -47.3895 | -44.4894 | -59.0531 | -50.564 | -54.5934 | -43.319 | -47.6648 | -46.428 | -55.614 | -50.2544 | -55.1719 | -44.2198 | -42.2216 | -46.5682 | -55.5226 | -50.4383 | -54.9403 | -44.2635 | -42.4969
124 | -4.3258 | 0 | -4.1088 | 0 | -4.3792 | 0 | -4.1073 | 0 | -63.8752 | 5.8214 | -55.0261 | 64.792 | -62.0667 | 163.7114 | -61.7302 | 72.1008 | -59.2563 | -94.3358 | -57.3604 | 124.5718 | -65.1621 | 21.3305 | -57.365 | 123.2178 | -58.273 | 82.065 | -56.8018 | 137.454 | -68.0163 | 63.3983 | -57.4543 | 141.7179 | -17.5847 | 132.2137 | -30.3748 | 102.6879 | -19.5015 | 81.5236 | -28.094 | 75.4954 | -18.5918 | 168.9487 | -30.0705 | 163.7151 | -20.5293 | 112.2624 | -27.2469 | 92.9086 | -52.4573 | -50.7511 | -59.1273 | -53.3127 | -58.5471 | -46.587 | -51.9994 | -48.18 | -63.8727 | -53.4487 | -58.5619 | -47.3323 | -46.3396 | 124 | -53.7941 | -56.4438 | -52.4787 | -54.3836 | -54.404 | -55.9329 | -52.4261 | -54.6302 | 124 | -43.8542 | -59.5469 | -48.9869 | -54.4383 | -42.4782 | -47.6202 | -44.0712 | -59.4935 | -49.2054 | -54.1679 | -42.4797 | -47.8921 | -46.4253 | -54.8015 | -49.1229 | -54.4531 | -43.2235 | -41.9604 | -46.6423 | -54.7481 | -49.3414 | -54.1827 | -43.225 | -42.2323
125 | -4.382 | 0 | -4.1316 | 0 | -4.3803 | 0 | -4.108 | 0 | -59.7446 | 22.0221 | -57.3784 | 31.3576 | -64.1265 | 173.5078 | -64.5141 | 77.5778 | -57.2086 | -102.0811 | -60.4929 | 103.1215 | -59.5858 | 26.582 | -58.0262 | 79.6266 | -62.278 | 59.921 | -56.7477 | 124.5192 | -61.7286 | 14.8967 | -55.6142 | 121.0227 | -15.5404 | 114.9118 | -33.2054 | 106.3502 | -20.4022 | 72.6663 | -28.8941 | 94.7568 | -16.3315 | 148.9175 | -29.6488 | 152.0642 | -22.4131 | 91.1235 | -28.5167 | 107.5491 | -52.82 | -49.717 | -58.4102 | -52.9958 | -57.9801 | -46.0842 | -52.0691 | -47.6654 | -62.5148 | -53.1395 | -58.3856 | -46.4857 | -45.5679 | 125 | -54.8465 | -54.794 | -55.1213 | -54.9743 | -54.8582 | -54.1046 | -51.9144 | -53.9699 | 125 | -43.2834 | -58.1328 | -48.6138 | -53.8485 | -41.9526 | -47.6888 | -43.5338 | -58.1345 | -48.8878 | -53.5998 | -41.9762 | -47.9611 | -45.335 | -54.0282 | -48.7575 | -54.254 | -42.3541 | -41.1876 | -45.5854 | -54.0299 | -49.0315 | -54.0053 | -42.3777 | -41.4599
126 | -4.4301 | 0 | -4.1449 | 0 | -4.3498 | 0 | -4.1341 | 0 | -56.4003 | 7.1592 | -64.2868 | -3.4514 | -65.2915 | -164.588 | -62.0513 | 95.2078 | -56.1554 | -118.1582 | -64.6956 | 107.2032 | -56.5747 | 9.0257 | -63.3296 | 31.5514 | -66.4898 | 86.2978 | -56.8964 | 118.245 | -59.2327 | -22.4292 | -56.8717 | 105.2227 | -15.1937 | 96.2406 | -32.8105 | 132.5772 | -21.6753 | 75.4615 | -26.7278 | 102.9463 | -15.8576 | 124.7429 | -30.048 | 146.5703 | -27.6736 | 88.0546 | -26.608 | 116.4224 | -52.6692 | -48.7687 | -57.9739 | -53.5872 | -57.677 | -46.1242 | -51.9184 | -47.3967 | -60.8129 | -53.4848 | -58.727 | -46.2444 | -44.9482 | 126 | -55.2884 | -52.7263 | -58.7439 | -55.1449 | -55.3918 | -52.6462 | -53.4074 | -54.5933 | 126 | -42.9666 | -56.3828 | -49.1571 | -53.5321 | -41.9793 | -47.5686 | -43.2518 | -56.4631 | -49.4531 | -53.3272 | -41.9901 | -47.7843 | -44.3386 | -53.5438 | -49.0547 | -54.5821 | -42.0995 | -40.5984 | -44.6238 | -53.6241 | -49.3507 | -54.3772 | -42.1103 | -40.8141
127 | -4.4118 | 0 | -4.1654 | 0 | -4.3642 | 0 | -4.163 | 0 | -55.2713 | -15.3722 | -73.9739 | 151.4183 | -63.0909 | -166.048 | -59.0916 | 83.144 | -56.2865 | -136.7923 | -64.504 | 142.1777 | -55.6587 | -13.4553 | -74.3687 | -97.9423 | -63.4766 | 98.3316 | -56.8503 | 112.6004 | -58.5618 | -56.0976 | -58.819 | 98.5143 | -16.2089 | 79.4934 | -29.189 | 137.7415 | -20.7896 | 84.3025 | -25.1516 | 95.1445 | -17.2402 | 101.5314 | -29.7995 | 153.059 | -26.9485 | 140.9784 | -25.2233 | 110.5213 | -52.2522 | -48.4433 | -57.651 | -54.3108 | -57.7913 | -46.4198 | -51.7162 | -47.5986 | -59.8766 | -53.8568 | -59.0755 | -46.4814 | -44.7522 | 127 | -54.5573 | -51.8343 | -57.8856 | -54.9528 | -54.9445 | -52.0936 | -54.667 | -55.0111 | 127 | -43.1868 | -55.4648 | -49.899 | -53.6259 | -42.2544 | -47.352 | -43.4332 | -55.5124 | -50.1478 | -53.4271 | -42.2568 | -47.5532 | -44.0315 | -53.2392 | -49.445 | -54.9101 | -42.316 | -40.388 | -44.2779 | -53.2868 | -49.6938 | -54.7113 | -42.3184 | -40.5892
128 | -4.3733 | 0 | -4.1827 | 0 | -4.4196 | 0 | -4.1766 | 0 | -55.9713 | -36.2684 | -60.9544 | 117.2999 | -63.5676 | -165.895 | -58.2269 | 66.2802 | -57.5169 | -153.4033 | -60.8727 | 132.7969 | -56.8063 | -34.983 | -63.102 | 174.8871 | -59.7939 | 85.2981 | -57.0518 | 110.8977 | -59.3046 | -89.242 | -61.4482 | 111.4914 | -18.4926 | 73.3635 | -26.1478 | 131.4734 | -18.6523 | 83.0686 | -25.4054 | 87.3823 | -20.9451 | 84.4023 | -27.3796 | 154.7975 | -20.7713 | 134.8667 | -25.1101 | 99.875 | -51.9532 | -48.6159 | -57.1789 | -54.2344 | -58.1367 | -46.5924 | -51.6632 | -47.9509 | -59.3694 | -53.7686 | -59.1515 | -46.7985 | -44.9136 | 128 | -54.2354 | -52.3626 | -55.0517 | -55.1868 | -54.4076 | -52.8137 | -54.979 | -55.3185 | 128 | -43.5776 | -54.9961 | -49.8611 | -53.954 | -42.4097 | -47.2436 | -43.7682 | -54.9498 | -50.0578 | -53.7171 | -42.4158 | -47.4866 | -44.2426 | -52.8056 | -49.3953 | -54.9688 | -42.6158 | -40.494 | -44.4332 | -52.7593 | -49.592 | -54.7319 | -42.6219 | -40.737
129 | -4.3649 | 0 | -4.2011 | 0 | -4.4684 | 0 | -4.1729 | 0 | -58.4661 | -48.6655 | -57.269 | 85.095 | -64.9538 | -170.0197 | -58.5114 | 51.6027 | -60.3488 | -163.1702 | -59.8881 | 120.5697 | -60.4039 | -45.4608 | -58.8377 | 137.9785 | -58.8559 | 60.6433 | -56.219 | 110.9856 | -62.2632 | -121.5468 | -59.2031 | 129.6093 | -19.9718 | 82.6862 | -24.3239 | 117.946 | -17.1994 | 70.6576 | -26.6743 | 83.6231 | -26.5937 | 103.9075 | -24.8125 | 142.0801 | -18.0793 | 110.1607 | -26.4939 | 95.0442 | -51.995 | -49.0787 | -56.5221 | -53.2411 | -58.3466 | -46.3717 | -51.7871 | -48.1754 | -58.8883 | -53.0566 | -58.6777 | -46.7653 | -45.1271 | 129 | -54.4145 | -54.2536 | -53.6549 | -56.4425 | -54.5352 | -54.0967 | -53.101 | -55.0911 | 129 | -43.8105 | -54.5234 | -48.8762 | -54.1455 | -42.1706 | -47.3187 | -43.9743 | -54.4199 | -49.0682 | -53.8782 | -42.1988 | -47.6142 | -44.7138 | -52.1572 | -48.6917 | -54.4766 | -42.5642 | -40.6587 | -44.8776 | -52.0537 | -48.8837 | -54.2093 | -42.5924 | -40.9542
130 | -4.3847 | 0 | -4.2173 | 0 | -4.5005 | 0 | -4.2012 | 0 | -60.8313 | -36.5792 | -56.4672 | 51.4546 | -65.7369 | -159.1199 | -59.8099 | 38.9933 | -63.0097 | -152.8343 | -59.6717 | 96.6813 | -62.9853 | -16.6064 | -57.4163 | 102.4787 | -59.2214 | 35.8514 | -55.0411 | 104.1878 | -69.0237 | -143.5778 | -55.8146 | 125.7249 | -18.3973 | 91.4343 | -23.1778 | 103.202 | -16.974 | 55.1653 | -27.51 | 96.4765 | -21.951 | 139.0428 | -23.2782 | 124.2874 | -17.7621 | 85.2122 | -27.6936 | 108.8944 | -52.3706 | -49.4741 | -55.8036 | -52.0385 | -58.144 | -45.8999 | -52.061 | -48.0552 | -58.0761 | -52.1431 | -58.1782 | -46.0904 | -45.0542 | 130 | -54.7517 | -56.2514 | -53.5863 | -57.3389 | -54.5443 | -54.2474 | -51.2109 | -54.0417 | 130 | -43.6705 | -53.6914 | -47.6538 | -53.9267 | -41.6826 | -47.5605 | -43.8379 | -53.5756 | -47.8373 | -53.6435 | -41.6987 | -47.8598 | -45.0894 | -51.4189 | -47.7584 | -53.9609 | -41.8731 | -40.5537 | -45.2568 | -51.3031 | -47.9419 | -53.6777 | -41.8892 | -40.853
131 | -4.4494 | 0 | -4.2329 | 0 | -4.5066 | 0 | -4.1946 | 0 | -58.2028 | -22.4706 | -58.1088 | 17.7904 | -65.2754 | -151.5716 | -62.1607 | 42.4643 | -61.5843 | -136.7368 | -64.4738 | 75.1486 | -58.372 | -2.0655 | -58.8686 | 62.8608 | -61.0904 | 15.9331 | -54.919 | 95.7221 | -75.3094 | -59.6664 | -54.3669 | 102.5707 | -16.4286 | 85.147 | -22.7014 | 91.0818 | -18.1062 | 42.566 | -25.2925 | 108.2015 | -18.0111 | 124.2355 | -23.4783 | 100.952 | -19.8553 | 60.8201 | -25.4972 | 121.6404 | -52.7847 | -49.3786 | -55.2199 | -51.3979 | -57.7222 | -45.4021 | -52.3267 | -47.7566 | -57.0002 | -51.4908 | -57.9322 | -45.3816 | -44.7562 | 131 | -54.743 | -55.5053 | -56.0021 | -58.7028 | -54.5218 | -53.2734 | -50.8735 | -53.5008 | 131 | -43.3072 | -52.5508 | -46.9485 | -53.4893 | -41.1692 | -47.8201 | -43.5237 | -52.4936 | -47.2033 | -53.2156 | -41.2075 | -48.1321 | -44.9292 | -50.7705 | -47.0414 | -53.6993 | -41.1487 | -40.2496 | -45.1457 | -50.7133 | -47.2962 | -53.4256 | -41.187 | -40.5616
132 | -4.5012 | 0 | -4.2635 | 0 | -4.4838 | 0 | -4.228 | 0 | -55.1324 | -33.6466 | -63.2017 | -17.9713 | -65.5689 | -148.3134 | -60.6908 | 58.3347 | -59.2988 | -141.3696 | -70.3409 | 118.7686 | -54.9544 | -17.2413 | -65.1811 | 15.2757 | -64.6041 | 9.631 | -54.8694 | 92.8125 | -65.2296 | -61.3027 | -56.144 | 83.3432 | -15.6617 | 71.7657 | -22.7064 | 79.9675 | -20.2305 | 40.4659 | -22.7186 | 101.9461 | -16.7511 | 99.8085 | -25.5866 | 74.9118 | -25.2168 | 50.2736 | -22.7033 | 115.7239 | -52.8973 | -48.934 | -54.8146 | -51.4285 | -57.4129 | -45.1918 | -52.4627 | -47.519 | -56.1457 | -51.2752 | -58.0487 | -45.0385 | -44.476 | 132 | -54.1758 | -52.9281 | -58.4654 | -58.1105 | -54.1506 | -51.7041 | -52.2242 | -55.1197 | 132 | -43.0178 | -51.6445 | -46.9273 | -53.1494 | -40.9283 | -47.9789 | -43.2555 | -51.6619 | -47.2005 | -52.9291 | -40.9638 | -48.2347 | -44.4328 | -50.3134 | -46.774 | -53.7852 | -40.775 | -39.9922 | -44.6705 | -50.3308 | -47.0472 | -53.5649 | -40.8105 | -40.248
133 | -4.5207 | 0 | -4.3062 | 0 | -4.4707 | 0 | -4.2655 | 0 | -53.7812 | -54.263 | -79.1794 | -147.0049 | -64.0072 | -147.5887 | -57.6684 | 49.8481 | -57.8796 | -154.3205 | -63.8872 | 149.7174 | -53.6505 | -39.7457 | -69.8811 | -142.9586 | -63.156 | 26.0879 | -54.167 | 89.2906 | -61.5577 | -90.646 | -59.3251 | 78.7662 | -16.0811 | 57.9341 | -22.8554 | 70.982 | -20.5478 | 52.2145 | -21.3752 | 88.1925 | -17.7914 | 75.3115 | -32.9309 | 54.7204 | -27.0235 | 110.3567 | -21.4283 | 101.5827 | -52.7172 | -48.5419 | -54.3966 | -51.6821 | -57.2797 | -45.1669 | -52.4937 | -47.4472 | -55.5871 | -51.3296 | -58.3023 | -45.0371 | -44.3227 | 133 | -53.3759 | -51.2339 | -56.7135 | -56.1342 | -53.0972 | -50.5334 | -52.9228 | -56.2889 | 133 | -42.9265 | -51.0664 | -47.1614 | -52.9735 | -40.8607 | -48.023 | -43.141 | -51.1164 | -47.4166 | -52.809 | -40.9014 | -48.2282 | -44.0212 | -49.8759 | -46.8089 | -53.9961 | -40.7309 | -39.852 | -44.2357 | -49.9259 | -47.0641 | -53.8316 | -40.7716 | -40.0572
134 | -4.5059 | 0 | -4.3227 | 0 | -4.5132 | 0 | -4.284 | 0 | -54.1134 | -75.4907 | -62.3776 | 115.6549 | -64.4803 | -134.5262 | -56.3848 | 31.4237 | -57.5744 | -170.022 | -59.7678 | 131.3047 | -54.2414 | -63.1733 | -60.1086 | 158.7612 | -60.8215 | 18.4078 | -53.4246 | 82.4221 | -60.2408 | -121.3889 | -61.5197 | 101.8027 | -17.6151 | 50.6024 | -23.1333 | 65.682 | -18.5764 | 55.5044 | -21.6564 | 74.2748 | -21.6144 | 54.541 | -37.1835 | 178.679 | -20.1398 | 108.8632 | -21.7643 | 85.9958 | -52.4525 | -48.35 | -53.9638 | -51.7337 | -57.3431 | -45.2328 | -52.4399 | -47.6108 | -55.1504 | -51.3813 | -58.4243 | -45.1968 | -44.2953 | 134 | -53.1756 | -51.0098 | -54.0536 | -55.0039 | -52.5424 | -50.3353 | -52.0585 | -56.0582 | 134 | -43.1049 | -50.6445 | -47.2278 | -53.0204 | -40.9101 | -47.9267 | -43.2881 | -50.6372 | -47.4497 | -52.8299 | -40.9488 | -48.1559 | -43.8441 | -49.4579 | -46.8754 | -54.1016 | -40.8741 | -39.7821 | -44.0273 | -49.4506 | -47.0973 | -53.9111 | -40.9128 | -40.0113
135 | -4.4855 | 0 | -4.3261 | 0 | -4.5878 | 0 | -4.3028 | 0 | -56.2061 | -91.6955 | -57.5788 | 79.9801 | -62.0273 | -135.7026 | -56.6511 | 11.9485 | -58.359 | 175.7846 | -58.9776 | 109.2799 | -56.9958 | -80.7267 | -56.6477 | 122.8545 | -58.56 | 0.5271 | -52.9467 | 73.5867 | -60.5542 | -155.0713 | -58.1837 | 114.3031 | -18.8506 | 54.2689 | -23.0945 | 60.7426 | -17.0003 | 43.7358 | -23.2178 | 65.3857 | -30.0996 | 80.0538 | -26.2872 | 163.2299 | -17.3374 | 86.0985 | -23.7593 | 75.1854 | -52.4442 | -48.4597 | -53.3887 | -51.3153 | -57.3817 | -45.2136 | -52.4316 | -47.8612 | -54.6262 | -51.1621 | -58.1582 | -45.2597 | -44.1944 | 135 | -53.2159 | -52.2064 | -52.8618 | -54.7475 | -52.5538 | -50.9957 | -50.5765 | -54.2106 | 135 | -43.3757 | -50.1407 | -46.8298 | -53.0556 | -40.8875 | -47.8438 | -43.5351 | -50.0384 | -47.0125 | -52.7939 | -40.9108 | -48.1288 | -43.9742 | -48.9032 | -46.6766 | -53.8321 | -40.9336 | -39.6066 | -44.1336 | -48.8009 | -46.8593 | -53.5704 | -40.9569 | -39.8916
136 | -4.525 | 0 | -4.342 | 0 | -4.631 | 0 | -4.317 | 0 | -59.5477 | -87.5076 | -56.2768 | 46.4577 | -60.5033 | -139.8719 | -58.2955 | -4.0603 | -59.6551 | 165.8727 | -60.2236 | 93.0099 | -61.8151 | -71.2608 | -55.7765 | 89.6829 | -58.3737 | -20.2913 | -53.0616 | 63.3101 | -62.7389 | 172.3484 | -56.0294 | 104.2959 | -18.1275 | 60.0843 | -22.995 | 53.2502 | -16.8868 | 26.3827 | -25.0325 | 71.708 | -22.9001 | 128.7191 | -22.7306 | 138.0767 | -17.0323 | 60.5905 | -26.6901 | 86.3815 | -52.7529 | -48.749 | -52.8422 | -50.6592 | -57.374 | -45.0576 | -52.5295 | -47.9865 | -53.9821 | -50.7053 | -57.8303 | -45.0568 | -43.9645 | 136 | -53.608 | -54.3497 | -53.1991 | -55.3416 | -53.2265 | -52.124 | -49.9651 | -53.4859 | 136 | -43.4615 | -49.4571 | -46.1342 | -53.032 | -40.7156 | -47.8985 | -43.6445 | -49.3511 | -46.3422 | -52.743 | -40.7406 | -48.2125 | -44.224 | -48.3172 | -46.1803 | -53.4883 | -40.7148 | -39.3335 | -44.407 | -48.2112 | -46.3883 | -53.1993 | -40.7398 | -39.6475
137 | -4.5792 | 0 | -4.361 | 0 | -4.6191 | 0 | -4.3362 | 0 | -58.3047 | -63.3906 | -57.5586 | 15.8015 | -60.031 | -142.6064 | -61.3044 | -5.5046 | -60.8017 | 164.5573 | -65.3682 | 81.2434 | -59.2741 | -35.5012 | -57.3145 | 57.1251 | -60.053 | -40.21 | -54.0918 | 57.3632 | -68.1157 | 138.5479 | -55.3773 | 87.6535 | -16.6627 | 54.6375 | -23.5323 | 44.9685 | -18.5714 | 10.0215 | -23.7975 | 85.793 | -18.1765 | 111.072 | -21.9583 | 113.7636 | -18.8807 | 37.4675 | -24.8226 | 108.7979 | -53.2054 | -49.0182 | -52.4159 | -50.2211 | -57.2406 | -44.8073 | -52.7243 | -47.916 | -53.2355 | -50.2789 | -57.6618 | -44.7167 | -43.695 | 137 | -53.7419 | -55.1577 | -55.5509 | -56.7472 | -53.9516 | -52.8116 | -50.6284 | -53.9347 | 137 | -43.3368 | -48.6563 | -45.6419 | -52.8796 | -40.4463 | -48.1052 | -43.555 | -48.6164 | -45.8849 | -52.6215 | -40.4711 | -48.3881 | -44.439 | -47.8367 | -45.6997 | -53.3008 | -40.3557 | -39.0759 | -44.6572 | -47.7968 | -45.9427 | -53.0427 | -40.3805 | -39.3588
138 | -4.6217 | 0 | -4.3751 | 0 | -4.5749 | 0 | -4.3807 | 0 | -54.482 | -67.5187 | -62.2564 | -8.5144 | -60.3602 | -144.1536 | -60.8778 | 13.9863 | -61.3165 | 164.1911 | -65.5156 | 128.9944 | -54.6099 | -43.1719 | -62.7782 | 26.6939 | -61.2519 | -39.3065 | -54.7319 | 62.0242 | -87.3921 | 131.6216 | -57.0624 | 77.8738 | -16.0965 | 41.6134 | -25.0471 | 39.9777 | -22.3587 | 5.5844 | -21.1224 | 82.6982 | -16.6925 | 86.7562 | -23.3047 | 94.5965 | -23.4141 | 28.8029 | -21.4022 | 106.3436 | -53.4657 | -49.0678 | -52.1263 | -50.0672 | -57.1102 | -44.6225 | -52.8556 | -47.7546 | -52.6803 | -50.0119 | -57.6408 | -44.4968 | -43.4399 | 138 | -52.943 | -52.9087 | -57.7144 | -57.1226 | -53.2454 | -51.659 | -52.3226 | -55.6572 | 138 | -43.1329 | -48.0586 | -45.4455 | -52.7351 | -40.2474 | -48.2807 | -43.3795 | -48.1054 | -45.6865 | -52.5353 | -40.2418 | -48.4749 | -44.4461 | -47.5046 | -45.3902 | -53.2657 | -40.1217 | -38.865 | -44.6927 | -47.5514 | -45.6312 | -53.0659 | -40.1161 | -39.0592
139 | -4.6265 | 0 | -4.3786 | 0 | -4.5636 | 0 | -4.4307 | 0 | -52.3113 | -86.4041 | -71.5781 | 51.7735 | -61.2112 | -139.7035 | -57.3804 | 8.5062 | -61.3948 | 164.2042 | -59.5536 | 129.0833 | -52.3042 | -65.1196 | -77.022 | 154.828 | -60.5893 | -26.7278 | -53.408 | 66.1138 | -69.4845 | -115.0282 | -58.6956 | 84.6376 | -16.9842 | 26.6767 | -26.99 | 48.0368 | -24.5394 | 33.2355 | -19.6776 | 68.5534 | -17.3603 | 63.5294 | -26.3985 | 95.0682 | -25.5706 | 65.419 | -19.4052 | 90.3099 | -53.3636 | -48.8806 | -51.881 | -50.0003 | -56.9495 | -44.5173 | -52.8356 | -47.5909 | -52.3335 | -49.9216 | -57.7966 | -44.4386 | -43.2528 | 139 | -51.7397 | -50.7436 | -55.2205 | -55.8667 | -51.6905 | -49.7643 | -52.2675 | -56.3152 | 139 | -42.9644 | -47.707 | -45.3738 | -52.5709 | -40.1387 | -48.272 | -43.2123 | -47.7699 | -45.5696 | -52.3859 | -40.0866 | -48.4049 | -44.2541 | -47.2545 | -45.2951 | -53.418 | -40.06 | -38.6892 | -44.502 | -47.3174 | -45.4909 | -53.233 | -40.0079 | -38.8221
140 | -4.6011 | 0 | -4.4012 | 0 | -4.5943 | 0 | -4.4563 | 0 | -51.8906 | -109.1688 | -59.7761 | 76.3857 | -59.2904 | -129.8432 | -55.5525 | -14.6488 | -60.6989 | 160.5928 | -57.1506 | 106.4299 | -51.9542 | -90.343 | -59.8695 | 138.9373 | -57.3509 | -33.47 | -51.7135 | 60.2025 | -63.9483 | -148.7566 | -57.4755 | 94.4233 | -19.3507 | 18.1724 | -25.7612 | 67.1151 | -20.9212 | 44.6749 | -19.4213 | 50.2071 | -20.1609 | 48.2261 | -25.6267 | 119.2823 | -20.8432 | 71.5161 | -19.1442 | 71.0003 | -53.1009 | -48.6027 | -51.6329 | -49.8587 | -56.9603 | -44.4543 | -52.7058 | -47.5748 | -52.0815 | -49.9558 | -57.9754 | -44.4576 | -43.1077 | 140 | -50.6043 | -49.954 | -52.3922 | -54.0273 | -50.3398 | -48.6905 | -50.196 | -53.9452 | 140 | -42.9737 | -47.4804 | -45.2576 | -52.5591 | -40.0531 | -48.1115 | -43.1736 | -47.4872 | -45.4024 | -52.366 | -39.998 | -48.2495 | -44.0016 | -47.0318 | -45.3547 | -53.5742 | -40.0564 | -38.5134 | -44.2015 | -47.0386 | -45.4995 | -53.3811 | -40.0013 | -38.6514
141 | -4.5842 | 0 | -4.441 | 0 | -4.6462 | 0 | -4.4577 | 0 | -53.1815 | -129.3511 | -54.9133 | 50.5253 | -56.6954 | -131.0178 | -55.6364 | -43.5141 | -60.2504 | 154.965 | -56.9906 | 84.916 | -53.626 | -115.0081 | -55.3529 | 110.3121 | -55.3675 | -52.6554 | -50.7667 | 48.8176 | -61.9509 | 174.1181 | -55.6968 | 87.8945 | -22.078 | 29.8866 | -22.5376 | 68.2075 | -18.8277 | 31.5334 | -20.6003 | 33.1313 | -24.0019 | 62.6411 | -21.6442 | 118.0033 | -18.7314 | 52.6016 | -20.5703 | 53.0626 | -52.9533 | -48.4201 | -51.2644 | -49.5548 | -57.0001 | -44.3888 | -52.6403 | -47.7438 | -51.76 | -50.0309 | -57.9098 | -44.4391 | -42.9367 | 141 | -49.9255 | -50.715 | -50.9926 | -52.9381 | -49.9309 | -48.7423 | -48.5416 | -52.05 | 141 | -43.1596 | -47.1758 | -44.9706 | -52.5591 | -39.9478 | -47.9941 | -43.3028 | -47.1138 | -45.0971 | -52.3539 | -39.9311 | -48.1826 | -43.8359 | -46.6802 | -45.4467 | -53.4688 | -39.9981 | -38.2905 | -43.9791 | -46.6182 | -45.5732 | -53.2636 | -39.9814 | -38.479
142 | -4.6059 | 0 | -4.4796 | 0 | -4.6726 | 0 | -4.4396 | 0 | -56.3153 | -138.9391 | -53.0071 | 20.4799 | -54.6711 | -140.1502 | -57.6281 | -75.679 | -59.8181 | 148.6519 | -58.738 | 64.6077 | -58.2444 | -129.1917 | -53.6531 | 82.5437 | -54.6135 | -75.6611 | -50.7407 | 36.5385 | -61.8953 | 135.9684 | -55.3118 | 75.1468 | -20.4049 | 48.7172 | -20.2638 | 55.5636 | -19.1012 | 14.2213 | -23.2509 | 24.03 | -21.2151 | 86.0842 | -19.3553 | 99.5015 | -19.1543 | 30.9562 | -24.2493 | 43.3581 | -53.062 | -48.5051 | -50.8251 | -49.2183 | -57.0035 | -44.2863 | -52.7608 | -47.9695 | -51.3598 | -49.9522 | -57.6632 | -44.325 | -42.7129 | 142 | -49.6856 | -52.9197 | -50.9326 | -52.3724 | -50.3307 | -49.7566 | -48.0445 | -51.5205 | 142 | -43.3636 | -46.7539 | -44.6124 | -52.5239 | -39.8067 | -48.0882 | -43.4899 | -46.6872 | -44.7787 | -52.3309 | -39.8467 | -48.3212 | -43.8992 | -46.2192 | -45.3463 | -53.1836 | -39.8454 | -38.0403 | -44.0255 | -46.1525 | -45.5126 | -52.9906 | -39.8854 | -38.2733
143 | -4.6478 | 0 | -4.5186 | 0 | -4.6751 | 0 | -4.4351 | 0 | -58.5435 | -118.2747 | -53.0562 | -9.8413 | -54.4172 | -151.7323 | -63.0129 | -116.7839 | -59.4869 | 141.0107 | -63.5038 | 62.1585 | -62.7625 | -85.9767 | -53.7287 | 55.9806 | -56.321 | -97.593 | -51.5351 | 28.1242 | -63.7882 | 94.9142 | -56.9518 | 60.2512 | -17.7253 | 43.7346 | -19.4694 | 38.0965 | -21.8413 | 2.4151 | -25.8185 | 33.2698 | -17.7505 | 75.0052 | -18.8941 | 76.302 | -22.1424 | 16.804 | -28.5097 | 68.687 | -53.3628 | -48.8161 | -50.363 | -49.0112 | -56.855 | -44.1481 | -53.0694 | -48.1009 | -50.8236 | -49.7218 | -57.4093 | -44.1751 | -42.4691 | 143 | -50.0164 | -55.1948 | -52.2963 | -52.8499 | -51.4874 | -50.9855 | -48.7688 | -53.2162 | 143 | -43.4531 | -46.1758 | -44.3634 | -52.3364 | -39.6295 | -48.3943 | -43.5823 | -46.1485 | -44.5761 | -52.1799 | -39.713 | -48.6343 | -44.1683 | -45.7152 | -45.074 | -52.8907 | -39.6565 | -37.794 | -44.2975 | -45.6879 | -45.2867 | -52.7342 | -39.74 | -38.034
144 | -4.7039 | 0 | -4.5446 | 0 | -4.6711 | 0 | -4.4445 | 0 | -54.9232 | -105.15 | -55.0664 | -38.3485 | -55.2693 | -161.0606 | -72.2635 | 111.496 | -59.49 | 131.5224 | -64.042 | 97.6366 | -55.9619 | -69.1839 | -55.5926 | 32.0703 | -60.3428 | -106.4834 | -52.271 | 27.7021 | -67.4206 | 43.7283 | -60.3387 | 62.9635 | -16.543 | 26.865 | -20.1714 | 21.1277 | -25.5696 | 20.861 | -24.8823 | 45.6432 | -16.4511 | 53.9583 | -20.3694 | 54.347 | -25.7604 | 36.0267 | -24.6769 | 96.6948 | -53.6348 | -49.187 | -50.0089 | -48.9785 | -56.6075 | -44.0503 | -53.2985 | -48.0851 | -50.3992 | -49.4391 | -57.2829 | -44.0773 | -42.3007 | 144 | -50.3128 | -53.5628 | -54.4758 | -53.4765 | -52.0642 | -50.6333 | -50.172 | -56.9246 | 144 | -43.3812 | -45.6953 | -44.2746 | -52.0629 | -39.5057 | -48.6274 | -43.5405 | -45.7281 | -44.534 | -51.9364 | -39.6058 | -48.854 | -44.4831 | -45.305 | -44.7352 | -52.7383 | -39.5327 | -37.6296 | -44.6424 | -45.3378 | -44.9946 | -52.6118 | -39.6328 | -37.8562
145 | -4.7367 | 0 | -4.5237 | 0 | -4.7082 | 0 | -4.5067 | 0 | -51.7274 | -118.2451 | -60.0538 | -59.4422 | -56.1981 | -158.0408 | -61.1778 | 25.5569 | -59.6734 | 123.5444 | -59.5208 | 97.0081 | -52.1117 | -88.5842 | -60.0185 | 18.253 | -62.123 | -63.1086 | -51.6406 | 30.1901 | -70.9296 | -53.1209 | -60.1021 | 95.7427 | -17.1273 | 7.6199 | -22.4944 | 11.3652 | -22.4135 | 47.1285 | -23.1865 | 37.3334 | -17.1025 | 32.1421 | -24.6329 | 42.9928 | -22.2612 | 56.2885 | -21.2711 | 90.0562 | -53.7194 | -49.4117 | -49.7722 | -48.8756 | -56.3639 | -43.9664 | -53.4065 | -48.0051 | -50.057 | -49.2073 | -57.473 | -44.0442 | -42.1852 | 145 | -49.9543 | -50.6758 | -55.426 | -53.3775 | -51.1023 | -48.8326 | -50.5421 | -57.7707 | 145 | -43.2684 | -45.3203 | -44.1389 | -51.8402 | -39.4427 | -48.6983 | -43.4814 | -45.3488 | -44.3689 | -51.6557 | -39.4597 | -48.8998 | -44.675 | -45.0355 | -44.4706 | -52.9493 | -39.5205 | -37.477 | -44.888 | -45.064 | -44.7006 | -52.7648 | -39.5375 | -37.6785
146 | -4.7183 | 0 | -4.5246 | 0 | -4.7507 | 0 | -4.5255 | 0 | -50.3156 | -139.4843 | -68.3589 | -18.26 | -54.8554 | -145.5304 | -57.3964 | -17.808 | -59.8168 | 117.5108 | -57.7813 | 76.801 | -50.6232 | -114.6314 | -65.1307 | 54.8105 | -55.8708 | -56.0751 | -50.3784 | 25.0276 | -65.1395 | -135.2269 | -56.436 | 96.4131 | -19.6691 | -8.907 | -24.7711 | 22.538 | -18.9129 | 38.0711 | -23.0627 | 18.376 | -19.6883 | 14.4873 | -28.4353 | 79.578 | -19.2786 | 41.9487 | -20.0351 | 75.2283 | -53.7202 | -49.4307 | -49.5858 | -48.642 | -56.2944 | -43.9151 | -53.2316 | -47.9539 | -49.7925 | -49.0675 | -57.7355 | -44.0164 | -42.0749 | 146 | -48.9571 | -49.1495 | -54.3963 | -52.2336 | -49.3712 | -47.4148 | -49.3017 | -52.8685 | 146 | -43.2356 | -45.0742 | -43.9237 | -51.7698 | -39.3905 | -48.4809 | -43.4293 | -45.0418 | -44.1165 | -51.5437 | -39.3896 | -48.7061 | -44.7124 | -44.8675 | -44.3492 | -53.2109 | -39.4918 | -37.3242 | -44.9061 | -44.8351 | -44.542 | -52.9848 | -39.4909 | -37.5494
147 | -4.6754 | 0 | -4.5551 | 0 | -4.7932 | 0 | -4.521 | 0 | -50.5074 | -161.1351 | -60.2132 | 14.073 | -52.1614 | -148.5227 | -56.6577 | -59.6066 | -59.3168 | 111.5485 | -59.1244 | 52.7504 | -51.0328 | -143.023 | -59.4062 | 78.2749 | -51.9139 | -76.9927 | -49.6915 | 13.7672 | -61.2173 | 174.3857 | -54.2763 | 84.7117 | -24.724 | -8.9008 | -22.8942 | 38.9411 | -17.7961 | 19.601 | -25.4857 | -6.3553 | -23.6603 | 15.2609 | -22.7562 | 95.9874 | -18.6307 | 18.5762 | -20.1333 | 61.0367 | -53.6569 | -49.3755 | -49.4257 | -48.3288 | -56.4655 | -43.895 | -53.0004 | -47.9807 | -49.4762 | -49.016 | -57.8481 | -43.9612 | -41.9959 | 147 | -47.9782 | -49.1269 | -53.6308 | -50.7196 | -48.1062 | -47.1275 | -48.0636 | -49.6149 | 147 | -43.3053 | -44.8008 | -43.6534 | -51.9104 | -39.3399 | -48.2072 | -43.4256 | -44.683 | -43.8078 | -51.6723 | -39.374 | -48.4794 | -44.7001 | -44.7503 | -44.3406 | -53.293 | -39.4061 | -37.2027 | -44.8204 | -44.6325 | -44.495 | -53.0549 | -39.4402 | -37.4749
148 | -4.6815 | 0 | -4.6176 | 0 | -4.7979 | 0 | -4.5206 | 0 | -52.1637 | -178.4751 | -56.2768 | -7.5526 | -49.9106 | -162.5481 | -58.0114 | -106.8114 | -58.836 | 101.5133 | -63.7633 | 40.6971 | -53.6908 | -168.813 | -56.0865 | 64.1218 | -50.1835 | -103.0596 | -49.9957 | 2.1558 | -59.6226 | 134.2125 | -54.2227 | 71.2964 | -26.4918 | 32.526 | -20.0224 | 32.4062 | -18.7404 | 1.5415 | -32.4669 | -33.7018 | -24.4763 | 38.0413 | -19.4972 | 78.8655 | -20.7372 | -5.9505 | -21.5289 | 53.5581 | -53.6022 | -49.3567 | -49.2325 | -48.1335 | -56.7545 | -43.8528 | -53.0434 | -48.0909 | -49.1072 | -49.0551 | -57.602 | -43.9307 | -41.9416 | 148 | -47.2953 | -50.4748 | -53.6072 | -49.2315 | -47.8719 | -48.1317 | -47.8903 | -48.3986 | 148 | -43.4094 | -44.4257 | -43.452 | -52.1369 | -39.2352 | -48.2455 | -43.4733 | -44.3093 | -43.6129 | -51.9566 | -39.3322 | -48.5228 | -44.6752 | -44.551 | -44.3736 | -52.9844 | -39.3131 | -37.1437 | -44.7391 | -44.4346 | -44.5345 | -52.8041 | -39.4101 | -37.421
149 | -4.7128 | 0 | -4.6792 | 0 | -4.7817 | 0 | -4.5592 | 0 | -54.7854 | 177.5344 | -55.5468 | -34.9533 | -49.1909 | 178.9744 | -60.9185 | -171.5731 | -58.545 | 88.5285 | -66.9164 | 100.4205 | -59.962 | 179.5965 | -55.3146 | 45.6601 | -50.121 | -132.3102 | -51.0366 | -3.7052 | -59.6324 | 96.4776 | -55.217 | 63.2164 | -21.884 | 41.5755 | -18.5125 | 15.3731 | -21.314 | -5.1648 | -39.2404 | 114.6048 | -21.97 | 37.9231 | -18.4028 | 54.4048 | -26.7572 | -17.0568 | -22.6294 | 56.7478 | -53.652 | -49.4226 | -48.9943 | -48.1481 | -57.0036 | -43.8015 | -53.3393 | -48.1099 | -48.6581 | -49.0229 | -57.1127 | -43.9146 | -41.8664 | 149 | -47.4092 | -52.5729 | -54.2011 | -48.6489 | -48.6406 | -50.0114 | -48.593 | -48.5944 | 149 | -43.3971 | -43.9453 | -43.4353 | -52.3244 | -39.1223 | -48.5576 | -43.4307 | -43.8764 | -43.5889 | -52.2219 | -39.2423 | -48.7801 | -44.7098 | -44.2815 | -44.3101 | -52.4335 | -39.2354 | -37.0847 | -44.7434 | -44.2126 | -44.4637 | -52.331 | -39.3554 | -37.3072
150 | -4.7595 | 0 | -4.704 | 0 | -4.795 | 0 | -4.5773 | 0 | -55.2714 | -169.6832 | -57.6135 | -60.2384 | -49.8351 | 161.1475 | -60.818 | 100.9616 | -58.7964 | 74.1569 | -59.1881 | 110.087 | -62.8525 | -117.6314 | -56.408 | 31.6825 | -52.4271 | -157.9744 | -51.6945 | -1.6896 | -61.0716 | 62.6353 | -56.0653 | 71.1375 | -20.0763 | 28.8732 | -18.7457 | -4.8243 | -23.2685 | 9.9584 | -28.1509 | 89.8331 | -21.7662 | 20.4753 | -19.6295 | 28.9593 | -30.2352 | 48.9346 | -22.4595 | 62.2275 | -53.8293 | -49.5413 | -48.6895 | -48.2668 | -56.9347 | -43.7679 | -53.7978 | -48.0645 | -48.2556 | -48.8486 | -56.6103 | -43.9278 | -41.6917 | 150 | -48.2131 | -52.9087 | -54.2409 | -48.8901 | -50.6937 | -50.9317 | -49.3815 | -50.47 | 150 | -43.305 | -43.4961 | -43.5073 | -52.2307 | -39.0639 | -49.0028 | -43.3605 | -43.4606 | -43.6895 | -52.1397 | -39.1906 | -49.2205 | -44.7818 | -43.93 | -44.0891 | -51.9063 | -39.2238 | -36.8967 | -44.8373 | -43.8945 | -44.2713 | -51.8153 | -39.3505 | -37.1144
151 | -4.788 | 0 | -4.6698 | 0 | -4.8252 | 0 | -4.5862 | 0 | -52.8887 | -169.3651 | -63.5922 | -66.0289 | -52.2102 | 151.0056 | -57.3951 | 33.3145 | -59.5179 | 59.4669 | -55.1661 | 85.8201 | -55.671 | -114.7978 | -58.626 | 32.4454 | -58.1102 | -171.4888 | -50.8943 | 0.754 | -63.9929 | 25.7903 | -54.9334 | 75.5349 | -20.3219 | 15.7104 | -20.546 | -21.7632 | -20.8877 | 19.6052 | -25.6488 | 61.2249 | -24.3704 | 2.3356 | -23.3991 | 6.5853 | -22.6407 | 49.7347 | -21.3654 | 60.77 | -54.2208 | -49.5598 | -48.3508 | -48.2208 | -56.3575 | -43.6809 | -54.2244 | -48.001 | -48.0028 | -48.6033 | -56.4432 | -43.9228 | -41.366 | 151 | -49.3589 | -50.9253 | -52.7551 | -49.9257 | -52.4973 | -49.4895 | -48.9544 | -52.8776 | 151 | -43.213 | -43.2148 | -43.4328 | -51.6877 | -39.0111 | -49.3992 | -43.3312 | -43.1776 | -43.6346 | -51.5323 | -39.0947 | -49.6382 | -44.7718 | -43.5628 | -43.8153 | -51.7734 | -39.253 | -36.5408 | -44.89 | -43.5256 | -44.0171 | -51.618 | -39.3366 | -36.7798
152 | -4.7865 | 0 | -4.6337 | 0 | -4.8693 | 0 | -4.6016 | 0 | -51.1902 | 174.823 | -63.2844 | -9.4063 | -55.0456 | 165.8663 | -55.4142 | -17.8946 | -61.4526 | 45.9127 | -54.3583 | 57.3557 | -52.5902 | -138.6996 | -58.1747 | 51.1206 | -60.781 | -105.5589 | -49.5639 | -5.0413 | -72.3677 | -29.2623 | -53.13 | 69.0737 | -21.858 | 11.06 | -24.1337 | -27.7435 | -18.9137 | 7.8696 | -26.3549 | 32.2181 | -31.4226 | 13.268 | -31.9749 | 14.7031 | -20.0464 | 25.384 | -20.7722 | 54.3194 | -54.9699 | -49.4985 | -48.068 | -47.8918 | -55.6535 | -43.5492 | -54.5634 | -47.9864 | -47.8724 | -48.368 | -56.8329 | -43.8341 | -41.0816 | 152 | -49.5072 | -49.5104 | -51.5429 | -51.2432 | -51.0427 | -47.7931 | -47.5838 | -52.3977 | 152 | -43.1999 | -43.0859 | -43.1053 | -51.0198 | -38.9155 | -49.6941 | -43.3527 | -43.0031 | -43.2902 | -50.7842 | -38.9476 | -49.9618 | -44.712 | -43.2815 | -43.5815 | -52.1992 | -39.2004 | -36.2123 | -44.8648 | -43.1987 | -43.7664 | -51.9636 | -39.2325 | -36.48
153 | -4.8025 | 0 | -4.6429 | 0 | -4.8849 | 0 | -4.6441 | 0 | -51.1049 | 153.1115 | -57.074 | -16.1109 | -52.0235 | -174.2289 | -55.2914 | -66.3358 | -64.0604 | 49.7978 | -56.2523 | 21.6476 | -52.12 | -167.5043 | -54.7705 | 54.1283 | -52.5228 | -102.9503 | -48.9104 | -17.039 | -69.4706 | 162.4441 | -52.7527 | 57.1744 | -22.4571 | 19.1881 | -26.2586 | -5.4823 | -18.7418 | -9.6635 | -32.1638 | 3.8154 | -27.8938 | 75.5698 | -28.3393 | 82.1562 | -20.486 | -2.0981 | -21.0488 | 47.9935 | -55.7214 | -49.5376 | -47.8107 | -47.5026 | -55.405 | -43.4711 | -54.725 | -47.9552 | -47.7088 | -48.2445 | -57.7367 | -43.7208 | -40.8625 | 153 | -47.9613 | -49.5454 | -51.3735 | -50.4392 | -48.2202 | -47.1892 | -46.6774 | -49.5811 | 153 | -43.1527 | -42.9063 | -42.7001 | -50.7621 | -38.8282 | -49.8401 | -43.3123 | -42.8239 | -42.8585 | -50.5201 | -38.827 | -50.0809 | -44.7351 | -43.0082 | -43.442 | -53.0938 | -39.0779 | -35.9776 | -44.8947 | -42.9258 | -43.6004 | -52.8518 | -39.0767 | -36.2184
154 | -4.841 | 0 | -4.6728 | 0 | -4.8757 | 0 | -4.6525 | 0 | -52.8778 | 132.1857 | -54.5591 | -40.7887 | -48.3685 | 178.3472 | -56.9509 | -119.4941 | -62.8756 | 61.9333 | -63.548 | -14.5931 | -54.2116 | 164.6374 | -52.23 | 40.1416 | -48.7862 | -128.6375 | -49.4505 | -29.4907 | -62.0977 | 111.2816 | -53.4989 | 46.0016 | -21.0171 | 21.9619 | -23.6668 | 4.8201 | -20.4629 | -25.4625 | -39.1967 | 166.478 | -22.4329 | 64.6614 | -23.2663 | 68.9418 | -24.1133 | -28.2572 | -21.3433 | 44.8309 | -55.9857 | -49.8019 | -47.5093 | -47.3685 | -55.7044 | -43.4855 | -54.7548 | -48.0515 | -47.3019 | -48.2392 | -58.4345 | -43.7234 | -40.853 | 154 | -46.3424 | -51.1415 | -52.2476 | -48.0919 | -46.3826 | -48.0251 | -46.6153 | -47.3733 | 154 | -43.2105 | -42.4609 | -42.5275 | -51.0316 | -38.8127 | -49.8791 | -43.3787 | -42.4262 | -42.716 | -50.8287 | -38.833 | -50.1023 | -44.9609 | -42.6683 | -43.3982 | -53.7617 | -39.0506 | -35.9773 | -45.1291 | -42.6336 | -43.5867 | -53.5588 | -39.0709 | -36.2005
155 | -4.8638 | 0 | -4.7175 | 0 | -4.869 | 0 | -4.6743 | 0 | -57.0167 | 122.6617 | -54.451 | -68.3622 | -46.4994 | 157.6058 | -59.3854 | 169.8347 | -60.1996 | 52.5233 | -66.8864 | 161.6524 | -59.8277 | 146.3731 | -51.3533 | 22.1902 | -47.5031 | -157.8542 | -50.8784 | -35.4228 | -59.4328 | 72.0221 | -54.4985 | 44.6116 | -19.8808 | 12.2496 | -21.9329 | -5.9031 | -23.5702 | -27.6993 | -26.3841 | 131.9422 | -20.6703 | 42.2954 | -22.2592 | 45.8858 | -35.1207 | -26.5917 | -21.2125 | 41.8008 | -55.88 | -50.2227 | -47.1825 | -47.4855 | -56.331 | -43.5842 | -54.8659 | -48.0564 | -46.7227 | -48.2038 | -58.0998 | -43.867 | -41.1854 | 155 | -45.5336 | -53.8778 | -53.0581 | -46.2801 | -45.8281 | -49.8511 | -47.2031 | -46.4861 | 155 | -43.1926 | -41.8589 | -42.6217 | -51.6135 | -38.8667 | -49.9969 | -43.3389 | -41.8537 | -42.8112 | -51.462 | -38.9099 | -50.1916 | -45.3589 | -42.3187 | -43.34 | -53.3823 | -39.1495 | -36.3164 | -45.5052 | -42.3135 | -43.5295 | -53.2308 | -39.1927 | -36.5111
156 | -4.8781 | 0 | -4.7343 | 0 | -4.8847 | 0 | -4.6855 | 0 | -60.2099 | 152.649 | -56.8679 | -95.9387 | -46.2751 | 134.6583 | -58.4798 | 85.826 | -58.945 | 33.7022 | -56.3321 | 120.5263 | -66.7178 | -157.1693 | -51.8407 | 7.5667 | -48.2213 | 173.3891 | -51.8449 | -31.1189 | -58.9645 | 38.2161 | -54.5776 | 50.6831 | -20.1542 | -2.3212 | -22.2181 | -20.744 | -24.4153 | -11.5614 | -22.3012 | 104.5896 | -21.3643 | 20.0291 | -24.2263 | 25.2181 | -28.4958 | 62.2908 | -20.964 | 33.8094 | -55.891 | -50.5551 | -46.8512 | -47.6781 | -56.7269 | -43.6293 | -55.1716 | -47.9902 | -46.1983 | -48.0272 | -57.1808 | -44.0116 | -41.7029 | 156 | -45.7533 | -54.3807 | -52.3635 | -45.6577 | -46.6115 | -50.9576 | -47.8069 | -47.0298 | 156 | -43.1121 | -41.3202 | -42.8 | -51.9926 | -38.895 | -50.2869 | -43.2559 | -41.3136 | -42.9926 | -51.8422 | -38.9438 | -50.4861 | -45.677 | -41.9731 | -43.1491 | -52.4465 | -39.2773 | -36.8182 | -45.8208 | -41.9665 | -43.3417 | -52.2961 | -39.3261 | -37.0174
157 | -4.8604 | 0 | -4.7136 | 0 | -4.909 | 0 | -4.7105 | 0 | -55.8969 | 168.4132 | -64.7476 | -111.9862 | -47.9083 | 113.3006 | -55.4842 | 20.3713 | -58.7347 | 13.5207 | -52.8442 | 90.5814 | -58.08 | -134.6597 | -52.7689 | 1.1268 | -51.3926 | 148.6443 | -50.9226 | -24.843 | -59.6216 | 8.5157 | -53.5864 | 53.3486 | -22.1139 | -14.4325 | -24.4203 | -28.9497 | -22.5666 | -12.328 | -20.8676 | 79.7118 | -24.7616 | 3.6837 | -30.5932 | 25.1017 | -23.1007 | 43.2823 | -21.4644 | 21.2157 | -56.4095 | -50.6556 | -46.611 | -47.6634 | -56.6243 | -43.5541 | -55.6862 | -47.8972 | -45.919 | -47.6901 | -56.4245 | -44.0301 | -41.6978 | 157 | -47.1909 | -51.714 | -50.7786 | -46.4359 | -48.5083 | -49.6927 | -47.5078 | -48.9529 | 157 | -43.0368 | -41.0586 | -42.803 | -51.9107 | -38.8405 | -50.7772 | -43.1836 | -41.01 | -42.9529 | -51.7153 | -38.8436 | -50.9757 | -45.7952 | -41.7506 | -42.8297 | -51.7109 | -39.3165 | -36.7888 | -45.942 | -41.702 | -42.9796 | -51.5155 | -39.3196 | -36.9873
158 | -4.8493 | 0 | -4.7205 | 0 | -4.9357 | 0 | -4.7278 | 0 | -52.8804 | 153.9003 | -64.2965 | -14.8791 | -52.4193 | 103.6858 | -53.709 | -32.7428 | -58.8697 | -8.6799 | -51.5463 | 59.3574 | -54.0583 | -156.8431 | -52.9766 | -0.4518 | -58.6885 | 149.4439 | -49.1231 | -30.2835 | -60.9101 | -20.8458 | -52.322 | 44.3558 | -25.2037 | -12.7679 | -26.2491 | -14.7834 | -21.9215 | -29.2325 | -21.2158 | 58.7015 | -29.7388 | 23.4598 | -28.6865 | 86.9927 | -21.7459 | 19.2911 | -23.6082 | 6.9428 | -57.6313 | -50.366 | -46.471 | -47.3774 | -55.854 | -43.2879 | -56.4002 | -47.7951 | -45.943 | -47.3807 | -56.0916 | -43.8342 | -41.1345 | 158 | -49.4875 | -49.7037 | -49.343 | -48.5293 | -49.8634 | -47.7016 | -46.3573 | -50.9571 | 158 | -42.9458 | -41.0937 | -42.5281 | -51.1335 | -38.5674 | -51.4645 | -43.0746 | -41.0073 | -42.6496 | -50.9183 | -38.5601 | -51.6724 | -45.5167 | -41.6217 | -42.5314 | -51.3711 | -39.1137 | -36.1988 | -45.6455 | -41.5353 | -42.6529 | -51.1559 | -39.1064 | -36.4067
159 | -4.8643 | 0 | -4.7699 | 0 | -4.9461 | 0 | -4.7457 | 0 | -51.8433 | 132.1244 | -56.5864 | -32.0821 | -55.4363 | 142.4278 | -53.5336 | -85.966 | -60.6134 | -37.1207 | -53.4607 | 28.4683 | -52.8966 | 173.6653 | -52.6372 | -2.1547 | -55.791 | -143.0296 | -48.1841 | -44.5101 | -64.13 | -60.6602 | -52.2817 | 30.2502 | -25.8304 | 5.3869 | -23.7036 | -3.1304 | -23.7455 | -52.7946 | -22.8219 | 46.1276 | -26.5604 | 56.119 | -22.6617 | 81.1519 | -22.9578 | -1.2478 | -29.0225 | 1.2365 | -58.9151 | -50.0132 | -46.2985 | -47.0596 | -54.833 | -42.9702 | -57.1293 | -47.6649 | -46.0283 | -47.3597 | -56.7894 | -43.536 | -40.6526 | 159 | -49.3569 | -49.2657 | -49.5333 | -50.843 | -48.7887 | -46.8382 | -45.7589 | -50.4889 | 159 | -42.8006 | -41.164 | -42.1953 | -50.0631 | -38.2003 | -52.1832 | -42.895 | -41.0822 | -42.3139 | -49.8869 | -38.2245 | -52.3836 | -45.1489 | -41.4342 | -42.4954 | -52.0195 | -38.7661 | -35.7065 | -45.2433 | -41.3524 | -42.614 | -51.8433 | -38.7903 | -35.9069
160 | -4.8869 | 0 | -4.8067 | 0 | -4.9364 | 0 | -4.7593 | 0 | -52.721 | 107.2851 | -54.3699 | -58.4034 | -49.6624 | 158.7814 | -54.6274 | -143.5266 | -66.7545 | -51.3688 | -60.1681 | 9.9581 | -54.5661 | 143.4847 | -51.6043 | -6.4383 | -48.9545 | -157.8169 | -48.7915 | -60.1371 | -75.6022 | -141.8555 | -54.7421 | 20.9845 | -24.0523 | 7.4626 | -21.0683 | -14.7681 | -29.7964 | -73.8316 | -24.2682 | 46.5291 | -23.1825 | 48.6739 | -20.0296 | 60.0496 | -25.9978 | -7.076 | -33.32 | 64.7081 | -58.2918 | -50.109 | -45.7314 | -47.1082 | -54.6121 | -42.9957 | -57.0841 | -47.5849 | -45.6174 | -47.7013 | -58.67 | -43.5731 | -40.5842 | 160 | -47.0314 | -50.457 | -50.9347 | -49.2149 | -46.3586 | -47.7649 | -46.2938 | -47.9304 | 160 | -42.698 | -40.7305 | -42.2213 | -49.8054 | -38.189 | -52.1477 | -42.7782 | -40.681 | -42.3489 | -49.6757 | -38.2364 | -52.3248 | -45.2221 | -40.8445 | -42.8144 | -53.8633 | -38.7664 | -35.6478 | -45.3023 | -40.795 | -42.942 | -53.7336 | -38.8138 | -35.8249
161 | -4.9104 | 0 | -4.8309 | 0 | -4.9577 | 0 | -4.7755 | 0 | -56.1485 | 88.8628 | -54.7489 | -82.3318 | -45.7852 | 139.6731 | -55.5992 | 150.329 | -66.59 | -10.9336 | -60.5738 | 99.2929 | -59.429 | 122.8711 | -51.0106 | -17.9706 | -45.9943 | 170.69 | -50.5852 | -69.8975 | -68.1008 | 61.6044 | -57.1134 | 35.917 | -23.7136 | -3.3477 | -20.3057 | -35.3541 | -39.0049 | 28.4998 | -23.579 | 50.6512 | -22.4963 | 33.9823 | -19.6839 | 38.0958 | -27.1206 | 10.3972 | -25.4982 | 83.0771 | -57.2105 | -50.7319 | -44.9814 | -47.4644 | -55.5191 | -43.3217 | -56.5574 | -47.5944 | -44.7698 | -48.0184 | -59.284 | -43.9851 | -41.4258 | 161 | -44.9254 | -52.6749 | -51.5605 | -45.6086 | -44.6577 | -49.9849 | -47.3032 | -45.6462 | 161 | -42.684 | -39.8594 | -42.554 | -50.6882 | -38.4908 | -51.5997 | -42.7635 | -39.8121 | -42.6889 | -50.5614 | -38.5462 | -51.7819 | -45.8215 | -40.071 | -43.108 | -54.4531 | -39.1542 | -36.4681 | -45.901 | -40.0237 | -43.2429 | -54.3263 | -39.2096 | -36.6503
162 | -4.9202 | 0 | -4.8279 | 0 | -4.9966 | 0 | -4.809 | 0 | -61.3889 | 98.8792 | -57.3541 | -98.1666 | -44.6383 | 112.855 | -54.8708 | 83.4957 | -63.0245 | -22.8329 | -52.642 | 88.7489 | -67.4826 | 145.1352 | -51.584 | -27.1336 | -45.8401 | 136.7372 | -52.6895 | -68.2705 | -64.5652 | 17.6605 | -54.9133 | 58.5266 | -25.9541 | -14.9204 | -21.5665 | -58.357 | -27.6087 | 27.6804 | -22.1319 | 42.1706 | -23.9654 | 23.2474 | -21.3759 | 19.3198 | -25.1328 | 10.4541 | -22.2362 | 67.5029 | -57.1958 | -51.6029 | -44.6827 | -47.7427 | -56.3364 | -43.6185 | -56.5779 | -47.6333 | -44.428 | -48.0154 | -58.2927 | -44.3638 | -42.7146 | 162 | -44.3257 | -53.4849 | -49.7719 | -43.9459 | -44.7908 | -52.2831 | -48.0818 | -45.2817 | 162 | -42.7131 | -39.5078 | -42.8225 | -51.5085 | -38.7906 | -51.5813 | -42.8054 | -39.4314 | -42.9337 | -51.3398 | -38.8095 | -51.7689 | -46.6827 | -39.7625 | -43.0952 | -53.4648 | -39.5359 | -37.718 | -46.775 | -39.6861 | -43.2064 | -53.2961 | -39.5548 | -37.9056
163 | -4.9083 | 0 | -4.8076 | 0 | -5.0478 | 0 | -4.8149 | 0 | -60.1037 | 130.6528 | -61.2684 | -80.4244 | -45.9461 | 88.6979 | -53.4765 | 25.2424 | -62.125 | -42.4644 | -49.0589 | 65.6544 | -62.9823 | -161.0986 | -52.0893 | -27.8268 | -48.3161 | 103.9202 | -53.2152 | -54.3699 | -64.7567 | -7.3387 | -51.4825 | 56.1385 | -30.8764 | -3.2319 | -25.5209 | -78.1513 | -24.8925 | 1.89 | -21.8665 | 24.2068 | -25.6192 | 30.2476 | -24.6008 | 16.6026 | -24.324 | -2.5858 | -20.9874 | 48.6673 | -58.0232 | -52.2204 | -44.7177 | -47.5935 | -56.6365 | -43.5056 | -57.1084 | -47.6025 | -44.463 | -47.6084 | -57.3779 | -44.4267 | -42.9649 | 163 | -45.6614 | -52.1606 | -47.5307 | -44.1493 | -46.6917 | -52.5125 | -47.4331 | -46.5406 | 163 | -42.6942 | -39.5547 | -42.6852 | -51.8289 | -38.698 | -52.0606 | -42.7949 | -39.4152 | -42.7786 | -51.5887 | -38.6907 | -52.2935 | -47.3121 | -39.8094 | -42.7001 | -52.5703 | -39.6191 | -37.9171 | -47.4128 | -39.6699 | -42.7935 | -52.3301 | -39.6118 | -38.15
164 | -4.9207 | 0 | -4.8258 | 0 | -5.0747 | 0 | -4.8262 | 0 | -56.8738 | 128.2409 | -56.9537 | -54.404 | -49.713 | 73.5825 | -52.9578 | -28.6091 | -62.0373 | -58.1819 | -47.4195 | 38.3031 | -57.8553 | -170.7592 | -51.0966 | -30.0496 | -54.9939 | 76.2709 | -50.7798 | -48.166 | -65.075 | -17.3596 | -49.2183 | 43.7762 | -28.4269 | 37.8427 | -33.6622 | -51.2103 | -25.3549 | -23.4196 | -23.0347 | 4.6785 | -24.3515 | 42.0236 | -25.4217 | 39.4352 | -25.7684 | -17.724 | -21.8836 | 31.2164 | -59.7094 | -51.9778 | -44.8707 | -47.0453 | -56.5492 | -42.9465 | -58.0094 | -47.3598 | -44.5574 | -46.9547 | -56.4469 | -43.7856 | -42.0504 | 164 | -48.3109 | -51.1123 | -45.9872 | -45.313 | -49.0053 | -49.8692 | -45.5134 | -48.1108 | 164 | -42.4391 | -39.6367 | -42.1246 | -51.7234 | -38.1207 | -52.9347 | -42.534 | -39.4827 | -42.2191 | -51.4745 | -38.1203 | -53.1832 | -47.0571 | -39.95 | -42.034 | -51.6211 | -38.9598 | -36.9757 | -47.152 | -39.796 | -42.1285 | -51.3722 | -38.9594 | -37.2242
165 | -4.9584 | 0 | -4.8594 | 0 | -5.0775 | 0 | -4.8307 | 0 | -55.4134 | 113.6367 | -52.8193 | -69.0869 | -53.9509 | 96.9063 | -54.0022 | -86.9742 | -61.5579 | -78.7267 | -47.979 | 7.0475 | -55.6779 | 164.7352 | -50.606 | -40.1314 | -62.7808 | -165.1529 | -48.5595 | -61.6635 | -64.0249 | -28.0989 | -48.1224 | 20.9102 | -24.6291 | 33.4399 | -27.0858 | -7.3667 | -29.2818 | -48.9773 | -26.3885 | -13.2758 | -22.6808 | 35.553 | -22.4935 | 43.3231 | -29.2278 | -28.4514 | -24.9213 | 18.7604 | -62.0125 | -51.051 | -44.9944 | -46.5047 | -55.782 | -42.2424 | -59.6289 | -47.0072 | -44.642 | -46.6484 | -55.8672 | -42.9525 | -40.8775 | 165 | -49.1627 | -51.2189 | -45.9981 | -46.8507 | -49.2336 | -47.6868 | -44.1977 | -47.8698 | 165 | -42.0488 | -39.6836 | -41.5463 | -50.9226 | -37.383 | -54.5514 | -42.1478 | -39.5645 | -41.674 | -50.7045 | -37.4117 | -54.7982 | -46.0926 | -40.036 | -41.69 | -51.0078 | -38.0931 | -35.8 | -46.1916 | -39.9169 | -41.8177 | -50.7897 | -38.1218 | -36.0468
166 | -4.9733 | 0 | -4.8999 | 0 | -5.0656 | 0 | -4.8462 | 0 | -55.5358 | 92.7397 | -51.295 | -92.2319 | -50.4189 | 122.9363 | -56.0261 | -161.7215 | -63.4028 | -116.8166 | -52.424 | -20.9652 | -56.0189 | 131.281 | -50.6915 | -46.8214 | -50.6942 | -178.0778 | -48.529 | -81.561 | -64.8344 | -60.5857 | -50.2636 | -1.0938 | -23.6544 | 15.7765 | -22.5122 | -27.0323 | -40.3225 | -41.0949 | -31.5696 | -12.9354 | -22.4603 | 22.9059 | -20.3627 | 29.7729 | -33.1658 | -5.8042 | -29.2626 | 35.8664 | -61.6781 | -50.6133 | -44.9506 | -46.5921 | -54.5531 | -42.1485 | -62.1187 | -46.8195 | -44.5866 | -47.064 | -56.6031 | -42.882 | -40.4555 | 166 | -47.145 | -52.4042 | -48.0573 | -48.1645 | -47.0881 | -47.7312 | -44.9525 | -47.3844 | 166 | -41.8462 | -39.6133 | -41.6188 | -49.6532 | -37.2486 | -57.0531 | -41.9196 | -39.521 | -41.7459 | -49.4875 | -37.3023 | -57.2725 | -45.64 | -39.9773 | -42.0907 | -51.7032 | -37.9821 | -35.3899 | -45.7134 | -39.885 | -42.2178 | -51.5375 | -38.0358 | -35.6093
167 | -5.005 | 0 | -4.9154 | 0 | -5.0637 | 0 | -4.8617 | 0 | -60.0669 | 72.5075 | -51.9079 | -115.2141 | -45.8145 | 115.895 | -54.9941 | 114.3293 | -96.9004 | -156.5311 | -64.4537 | 20.2861 | -61.7471 | 88.3979 | -50.6691 | -56.1261 | -45.739 | 152.9284 | -50.416 | -97.4732 | -75.1917 | -38.8343 | -54.3405 | -3.1234 | -25.2889 | 1.2962 | -21.124 | -55.002 | -34.0419 | 38.9764 | -32.5902 | 13.0167 | -23.9532 | 14.6727 | -19.9912 | 11.5007 | -31.0373 | 14.6666 | -27.4285 | 70.4789 | -58.1662 | -50.8262 | -43.8418 | -47.3147 | -54.7443 | -42.6035 | -61.1224 | -46.6535 | -43.548 | -48.0443 | -59.8881 | -43.5598 | -41.6645 | 167 | -44.7309 | -53.818 | -50.013 | -45.7555 | -44.4472 | -50.0941 | -46.7081 | -45.1733 | 167 | -41.6485 | -38.543 | -42.3097 | -49.8289 | -37.6881 | -56.0587 | -41.7381 | -38.4843 | -42.453 | -49.6806 | -37.7418 | -56.2607 | -45.8212 | -38.8368 | -43.0393 | -54.9727 | -38.6444 | -36.6008 | -45.9108 | -38.7781 | -43.1826 | -54.8244 | -38.6981 | -36.8028
168 | -5.0076 | 0 | -4.9135 | 0 | -5.1107 | 0 | -4.8885 | 0 | -63.0464 | 123.2885 | -53.9457 | -125.6614 | -43.7087 | 88.4029 | -51.7958 | 54.9504 | -64.8659 | -37.3443 | -51.6572 | 70.5098 | -77.159 | -95.9903 | -51.7143 | -61.4508 | -44.2278 | 114.6112 | -53.4228 | -102.9085 | -65.1162 | -18.599 | -56.8265 | 31.6664 | -29.8367 | 3.8185 | -21.7749 | -85.9389 | -30.1594 | 22.4098 | -30.7616 | 0.7473 | -25.9701 | 21.8404 | -21.1212 | -4.5758 | -30.4439 | 8.9545 | -23.546 | 73.4226 | -57.6956 | -52.1076 | -43.0436 | -47.8636 | -56.4378 | -43.217 | -59.5659 | -46.5951 | -42.8826 | -48.3979 | -60.2846 | -44.267 | -44.3678 | 168 | -43.2698 | -51.287 | -47.5765 | -43.0341 | -43.5131 | -53.1211 | -48.7412 | -43.962 | 168 | -41.5875 | -37.875 | -42.856 | -51.5243 | -38.3035 | -54.4552 | -41.6816 | -37.7719 | -42.9751 | -51.3271 | -38.3285 | -54.6774 | -47.1 | -38.036 | -43.3903 | -55.3711 | -39.3535 | -39.2571 | -47.1941 | -37.9329 | -43.5094 | -55.1739 | -39.3785 | -39.4793
169 | -5.0069 | 0 | -4.9209 | 0 | -5.1697 | 0 | -4.9009 | 0 | -57.2735 | 126.3767 | -55.4031 | -122.531 | -44.6124 | 61.4571 | -49.4015 | 8.4267 | -62.0532 | -63.6669 | -46.1511 | 46.7054 | -61.4875 | -135.5785 | -51.8407 | -56.5049 | -45.4814 | 78.3973 | -56.9942 | -83.6184 | -63.3677 | -48.2653 | -51.3697 | 54.277 | -29.2335 | 47.53 | -24.9628 | -119.292 | -30.5528 | 6.927 | -30.7522 | -36.1866 | -24.9962 | 35.3125 | -23.339 | -13.6348 | -32.8111 | 11.4899 | -21.4591 | 63.8914 | -59.0077 | -54.1666 | -43.0429 | -47.4374 | -57.3592 | -43.0416 | -59.8584 | -46.4666 | -43.0812 | -47.6514 | -58.5381 | -43.9978 | -45.9777 | 169 | -44.0527 | -48.5467 | -44.1319 | -42.2579 | -44.4904 | -54.9916 | -48.0029 | -44.4297 | 169 | -41.4597 | -38.0743 | -42.4305 | -52.4383 | -38.1207 | -54.6887 | -41.5457 | -37.9115 | -42.5365 | -52.1895 | -38.1407 | -54.9575 | -49.1597 | -38.036 | -42.6445 | -53.6172 | -39.0769 | -40.808 | -49.2457 | -37.8732 | -42.7505 | -53.3684 | -39.0969 | -41.0768
170 | -5.0427 | 0 | -4.9346 | 0 | -5.2335 | 0 | -4.922 | 0 | -54.742 | 108.9954 | -54.3362 | -115.5723 | -48.1255 | 43.5381 | -48.5754 | -37.5863 | -60.0241 | -80.0176 | -43.2708 | 15.4756 | -56.6376 | -158.2629 | -49.894 | -59.5134 | -49.8742 | 44.9985 | -53.1553 | -55.9998 | -64.2238 | -61.8326 | -46.8357 | 39.058 | -24.6054 | 49.7169 | -33.0898 | -161.5193 | -33.6162 | 6.1479 | -30.8984 | -99.1673 | -23.1143 | 29.9263 | -25.1814 | -10.386 | -32.2276 | 37.8022 | -20.5112 | 53.1511 | -61.6425 | -54.4882 | -43.2193 | -46.205 | -57.5643 | -41.7656 | -60.9424 | -46.0616 | -43.2224 | -46.3369 | -56.7432 | -42.296 | -44.8697 | 170 | -46.4902 | -47.3915 | -41.8939 | -41.9736 | -46.4379 | -51.3178 | -44.4606 | -45.0315 | 170 | -41.0189 | -38.1797 | -41.1623 | -52.6297 | -36.831 | -55.7089 | -41.127 | -37.9889 | -41.283 | -52.3308 | -36.8436 | -56.0204 | -49.4455 | -38.1766 | -41.2942 | -51.8086 | -37.3614 | -39.6362 | -49.5536 | -37.9858 | -41.4149 | -51.5097 | -37.374 | -39.9477
171 | -5.0594 | 0 | -4.9453 | 0 | -5.2439 | 0 | -4.9335 | 0 | -53.9015 | 88.2022 | -52.4955 | -123.1113 | -52.6311 | 62.8407 | -50.0897 | -87.1254 | -58.1484 | -103.44 | -43.0785 | -21.819 | -54.3029 | 175.9292 | -49.275 | -76.3476 | -65.0826 | 25.1469 | -49.413 | -72.3556 | -63.335 | -69.3629 | -45.0364 | 11.9233 | -22.7023 | 37.0376 | -36.5793 | 28.5954 | -34.6534 | 38.9347 | -27.9181 | -164.696 | -23.2288 | 15.747 | -24.9632 | -6.2866 | -29.2004 | 39.925 | -20.2883 | 44.0791 | -66.3797 | -52.2526 | -43.4001 | -45.3914 | -56.7039 | -40.6119 | -62.9257 | -45.6346 | -42.9813 | -45.5937 | -55.7421 | -40.7439 | -43.3138 | 171 | -48.1936 | -48.1249 | -41.8946 | -42.502 | -48.0025 | -48.0621 | -42.6263 | -44.9305 | 171 | -40.5752 | -37.9219 | -40.332 | -51.7586 | -35.6666 | -57.6818 | -40.6893 | -37.7374 | -40.4579 | -51.46 | -35.6784 | -57.9922 | -47.1932 | -38.3407 | -40.5343 | -50.7968 | -35.7986 | -38.0699 | -47.3073 | -38.1562 | -40.6602 | -50.4982 | -35.8104 | -38.3803
172 | -5.0873 | 0 | -4.9568 | 0 | -5.2255 | 0 | -4.9476 | 0 | -54.2602 | 65.8428 | -51.4953 | -135.3536 | -49.2415 | 86.7219 | -54.9129 | -149.8714 | -57.564 | -132.9371 | -46.2028 | -58.0237 | -53.9987 | 147.4853 | -50.6104 | -86.7562 | -53.5009 | 151.2357 | -49.0864 | -96.5457 | -62.3408 | -90.9136 | -46.7422 | -15.3377 | -22.9757 | 27.4758 | -27.8783 | -20.9217 | -30.7224 | 49.115 | -24.8478 | 149.8105 | -26.5478 | 4.6377 | -24.3336 | -14.7129 | -27.998 | 30.3517 | -20.5459 | 35.8087 | -68.0162 | -51.0349 | -43.592 | -45.7076 | -55.4459 | -40.5818 | -66.4646 | -45.663 | -42.7865 | -45.9334 | -55.9178 | -40.6083 | -42.6744 | 172 | -46.4311 | -50.5908 | -44.6488 | -44.2443 | -47.6607 | -47.7194 | -43.7466 | -45.8133 | 172 | -40.5757 | -37.6992 | -40.6203 | -50.4891 | -35.625 | -61.2391 | -40.7062 | -37.561 | -40.76 | -50.2204 | -35.6342 | -61.517 | -45.9476 | -38.5047 | -40.8461 | -50.961 | -35.6515 | -37.4489 | -46.0781 | -38.3665 | -40.9858 | -50.6923 | -35.6607 | -37.7268
173 | -5.0915 | 0 | -4.9698 | 0 | -5.2082 | 0 | -4.982 | 0 | -56.152 | 38.4306 | -50.8191 | -150.6403 | -46.1299 | 78.9029 | -56.719 | 100.2124 | -59.4147 | -169.5424 | -55.2288 | -79.1726 | -56.2526 | 114.8564 | -51.1531 | -88.2608 | -47.8311 | 126.3203 | -51.0257 | -117.0693 | -63.4919 | -125.3552 | -51.0681 | -20.1992 | -23.6966 | 31.3168 | -25.5491 | -57.4435 | -29.4128 | 37.9898 | -23.8132 | 115.1793 | -31.4333 | 43.872 | -24.8886 | -29.631 | -29.0708 | 19.6204 | -20.943 | 28.8952 | -61.666 | -51.5802 | -43.7134 | -46.8847 | -54.2011 | -41.4435 | -70.8175 | -45.8801 | -42.779 | -47.126 | -57.8721 | -41.7082 | -44.2197 | 173 | -44.5487 | -52.4425 | -48.7258 | -45.4481 | -45.765 | -49.7005 | -46.3108 | -46.0652 | 173 | -40.7886 | -37.6875 | -41.7932 | -49.2313 | -36.4737 | -65.6093 | -40.9103 | -37.5708 | -41.9027 | -48.9929 | -36.4615 | -65.8355 | -46.4887 | -38.6219 | -42.0345 | -52.9023 | -36.7384 | -39.0115 | -46.6104 | -38.5052 | -42.144 | -52.6639 | -36.7262 | -39.2377
174 | -5.1394 | 0 | -4.9815 | 0 | -5.2405 | 0 | -5.0075 | 0 | -65.9268 | 16.4211 | -51.7335 | -169.0943 | -43.4266 | 61.2993 | -50.653 | 30.243 | -70.2332 | -178.7436 | -56.9238 | 46.1474 | -65.7924 | 112.2079 | -52.5282 | -90.0469 | -44.2562 | 97.1467 | -56.0893 | -130.5333 | -80.8356 | -175.224 | -53.2363 | 8.9665 | -22.1917 | 37.3216 | -25.8548 | -91.5116 | -30.5459 | 37.4168 | -25.1715 | 87.2759 | -24.6123 | 72.5762 | -27.1245 | -45.7844 | -32.3514 | 33.2356 | -21.9076 | 23.4077 | -57.8925 | -52.7765 | -42.4684 | -48.0487 | -54.8456 | -42.1242 | -62.9502 | -45.6897 | -41.7097 | -47.8877 | -63.126 | -42.9046 | -48.0256 | 174 | -42.8072 | -50.4797 | -47.6086 | -43.228 | -43.627 | -55.6344 | -48.9299 | -43.7382 | 174 | -40.5503 | -36.5703 | -42.9093 | -49.8641 | -37.1427 | -57.7097 | -40.7082 | -36.4692 | -43.0412 | -49.6051 | -37.1167 | -57.9427 | -47.6371 | -37.329 | -42.7483 | -58.1445 | -37.9231 | -42.7851 | -47.795 | -37.2279 | -42.8802 | -57.8855 | -37.8971 | -43.0181
175 | -5.173 | 0 | -4.9927 | 0 | -5.338 | 0 | -5.0201 | 0 | -63.4636 | 99.8367 | -53.207 | -175.6096 | -43.5623 | 31.0616 | -46.7211 | -14.0778 | -66.6543 | -122.998 | -45.9901 | 26.9805 | -65.1523 | 166.7101 | -51.5708 | -74.4956 | -43.8902 | 59.0107 | -62.2948 | -52.4836 | -68.3812 | -52.8166 | -48.1676 | 31.7485 | -19.9181 | 30.7492 | -28.4514 | -122.7996 | -29.4349 | 51.5882 | -29.5665 | 71.9719 | -20.3097 | 58.9451 | -31.0812 | -54.4656 | -28.3732 | 64.3327 | -22.9646 | 24.9403 | -58.7279 | -56.3701 | -42.0215 | -47.0365 | -57.0912 | -41.8349 | -62.6216 | -45.5645 | -41.8487 | -46.3833 | -59.1762 | -42.8849 | -51.5451 | 175 | -43.075 | -46.5871 | -42.9047 | -41.5849 | -43.1785 | -59.8295 | -46.42 | -42.5008 | 175 | -40.3915 | -36.6757 | -41.8635 | -52.0985 | -36.8422 | -57.2836 | -40.5718 | -36.5107 | -42.0164 | -51.7532 | -36.8148 | -57.6015 | -51.1971 | -36.8485 | -41.2103 | -54.1835 | -37.8922 | -46.2071 | -51.3774 | -36.6835 | -41.3632 | -53.8382 | -37.8648 | -46.525
176 | -5.1974 | 0 | -5.0023 | 0 | -5.4528 | 0 | -5.0395 | 0 | -58.9623 | 84.5449 | -53.822 | -178.4812 | -46.7084 | 7.7893 | -44.8287 | -58.1101 | -62.7529 | -113.0969 | -41.4746 | -7.8467 | -60.522 | -175.6032 | -48.0765 | -81.6315 | -46.3047 | 24.2346 | -50.7251 | -48.3766 | -64.6286 | -65.4845 | -43.339 | 14.3795 | -18.8307 | 14.4722 | -34.5261 | -147.752 | -26.754 | 49.0138 | -34.204 | 126.222 | -18.6227 | 38.8737 | -35.9824 | -36.6423 | -23.6392 | 52.406 | -22.7454 | 32.0747 | -61.2414 | -59.5396 | -42.0811 | -44.7297 | -58.2179 | -40.1373 | -64.6312 | -45.2927 | -42.3302 | -44.1116 | -55.9749 | -40.8356 | -49.6639 | 176 | -45.7258 | -44.5973 | -39.6556 | -40.3115 | -43.9929 | -50.1352 | -41.5249 | -41.5418 | 176 | -40.0953 | -37.1328 | -39.5323 | -53.2156 | -35.135 | -59.1784 | -40.2904 | -36.8774 | -39.6902 | -52.7651 | -35.0978 | -59.5917 | -54.3422 | -36.8837 | -38.9142 | -50.9726 | -35.8333 | -44.2111 | -54.5373 | -36.6283 | -39.0721 | -50.5221 | -35.7961 | -44.6244
177 | -5.1895 | 0 | -5.0031 | 0 | -5.4618 | 0 | -5.0654 | 0 | -57.6565 | 62.7444 | -54.1879 | 176.4104 | -52.8721 | 13.8053 | -45.567 | -103.9786 | -57.8947 | -127.4511 | -40.2995 | -48.1314 | -56.3081 | 171.4776 | -46.8204 | -104.9233 | -52.5202 | -5.0813 | -47.1102 | -81.4122 | -61.0144 | -88.4335 | -41.5459 | -16.0482 | -19.6088 | -4.3153 | -43.172 | -110.1015 | -25.3217 | 37.1876 | -25.8909 | 141.7172 | -19.1758 | 20.7392 | -36.4379 | -12.798 | -22.1217 | 30.8666 | -21.5592 | 30.9774 | -66.711 | -54.1658 | -42.0731 | -43.4962 | -57.418 | -38.8298 | -68.5344 | -44.997 | -42.2168 | -43.0773 | -54.6594 | -39.0907 | -47.298 | 177 | -49.7104 | -45.0736 | -39.0343 | -39.9947 | -45.4163 | -46.4619 | -39.5743 | -41.1668 | 177 | -39.8075 | -37.0273 | -38.3067 | -52.4149 | -33.8267 | -63.0726 | -39.9939 | -36.755 | -38.4308 | -51.9562 | -33.7644 | -63.469 | -48.9763 | -36.8836 | -37.8878 | -49.6563 | -34.0876 | -41.8362 | -49.1627 | -36.6113 | -38.0119 | -49.1976 | -34.0253 | -42.2326
178 | -5.1794 | 0 | -5.0155 | 0 | -5.3873 | 0 | -5.0958 | 0 | -58.2703 | 38.4988 | -54.8012 | 175.7423 | -50.7955 | 56.7412 | -49.4566 | -150.1862 | -55.8232 | -154.9273 | -42.2349 | -87.7978 | -54.8759 | 148.5848 | -48.127 | -124.0103 | -63.5615 | 88.8134 | -47.381 | -113.6255 | -59.5427 | -119.181 | -42.8244 | -45.3369 | -22.7433 | -14.9102 | -36.6763 | -90.7813 | -24.8805 | 20.7317 | -21.7942 | 121.782 | -21.6617 | 13.216 | -36.5798 | -4.9939 | -22.5835 | 10.772 | -20.5133 | 22.9473 | -81.3132 | -51.4194 | -42.1333 | -43.7937 | -56.2077 | -38.7788 | -78.1444 | -45.192 | -41.8434 | -43.4764 | -54.871 | -38.8287 | -46.4697 | 178 | -48.8187 | -48.114 | -41.2833 | -41.5048 | -47.1927 | -46.4509 | -40.6623 | -42.6972 | 178 | -40.0126 | -36.664 | -38.6143 | -51.1922 | -33.7633 | -72.7571 | -40.1765 | -36.4561 | -38.6979 | -50.8204 | -33.683 | -73.0486 | -46.24 | -36.9539 | -38.297 | -49.8555 | -33.8132 | -41.0824 | -46.4039 | -36.746 | -38.3806 | -49.4837 | -33.7329 | -41.3739
179 | -5.2053 | 0 | -5.0367 | 0 | -5.3312 | 0 | -5.1195 | 0 | -60.355 | 14.2491 | -53.5173 | 177.6698 | -46.5372 | 49.5376 | -57.6324 | 141.2194 | -55.4128 | 178.4187 | -47.8977 | -121.6449 | -55.4849 | 125.0785 | -49.9144 | -129.4522 | -51.1686 | 89.3756 | -49.9557 | -140.5283 | -59.9133 | -153.7838 | -46.7554 | -64.4042 | -26.2161 | 10.1712 | -33.3236 | -126.3981 | -26.855 | 1.7345 | -20.3706 | 98.867 | -23.0301 | 32.5453 | -37.3403 | 5.8422 | -24.9214 | -3.7147 | -20.4329 | 9.1753 | -68.354 | -51.0117 | -42.4405 | -45.0727 | -55.1469 | -39.6875 | -75.9547 | -45.7335 | -41.799 | -44.818 | -56.1383 | -39.7843 | -47.8588 | 179 | -45.5961 | -52.5791 | -46.4974 | -43.8407 | -46.847 | -48.554 | -43.8289 | -45.2623 | 179 | -40.5282 | -36.5937 | -39.8674 | -50.1102 | -34.6508 | -70.6235 | -40.6968 | -36.4678 | -39.9532 | -49.8157 | -34.568 | -70.8352 | -45.8064 | -37.2352 | -39.6127 | -51.1016 | -34.7476 | -42.5276 | -45.975 | -37.1093 | -39.6985 | -50.8071 | -34.6648 | -42.7393
180 | -5.2628 | 0 | -5.0487 | 0 | -5.3481 | 0 | -5.1408 | 0 | -63.4941 | -28.9709 | -51.8989 | 162.2195 | -44.7869 | 36.2337 | -53.6269 | 17.3792 | -56.4417 | 144.712 | -69.2447 | -163.6208 | -59.3694 | 104.2616 | -50.8531 | -132.4724 | -47.7045 | 70.1046 | -56.539 | -172.5879 | -61.8615 | 158.8192 | -53.1988 | -45.3618 | -21.7579 | 30.6627 | -33.1046 | -172.4836 | -32.2152 | 3.1413 | -21.0539 | 77.5572 | -19.7357 | 42.3815 | -35.9959 | 25.5823 | -28.6985 | 7.071 | -21.6343 | -6.7206 | -61.3581 | -52.099 | -42.5956 | -46.4363 | -53.7136 | -40.7865 | -65.4393 | -46.2349 | -41.8097 | -46.0643 | -59.869 | -41.3169 | -51.993 | 180 | -43.9665 | -51.5154 | -49.6196 | -44.4854 | -45.7942 | -53.9508 | -48.175 | -46.4968 | 180 | -40.9721 | -36.5469 | -41.1735 | -48.6649 | -35.7378 | -60.0912 | -41.1862 | -36.4616 | -41.2955 | -48.3655 | -35.6457 | -60.2985 | -46.8362 | -37.3328 | -40.8015 | -54.8203 | -36.2682 | -46.6449 | -47.0503 | -37.2475 | -40.9235 | -54.5209 | -36.1761 | -46.8522
181 | -5.3294 | 0 | -5.0594 | 0 | -5.4784 | 0 | -5.1434 | 0 | -68.069 | -167.5184 | -52.7488 | 145.4154 | -42.9281 | 12.287 | -46.7508 | -34.632 | -65.3336 | 130.396 | -47.9042 | 9.3913 | -62.5224 | 126.3286 | -52.4438 | -121.8746 | -44.7427 | 41.5352 | -58.5988 | -4.3662 | -69.2977 | 50.7653 | -48.9793 | 6.3117 | -18.4123 | 16.2237 | -33.9194 | 137.5447 | -31.2858 | 43.3959 | -23.5125 | 64.893 | -17.1247 | 30.5645 | -33.5665 | 21.7691 | -26.0738 | 31.5764 | -24.9604 | -15.6226 | -59.0876 | -54.5105 | -41.3068 | -45.8103 | -54.5368 | -40.6472 | -63.8055 | -45.8808 | -40.8177 | -44.9462 | -59.7352 | -41.4511 | -57.6038 | 181 | -42.4855 | -46.6595 | -43.7014 | -41.7101 | -44.0002 | -56.866 | -47.0494 | -43.3423 | 181 | -40.5514 | -35.4883 | -40.4809 | -49.4774 | -35.5878 | -58.3271 | -40.8214 | -35.3393 | -40.6669 | -49.0584 | -35.5038 | -58.6621 | -49.1811 | -35.9774 | -39.6168 | -54.6758 | -36.3917 | -52.1254 | -49.4511 | -35.8284 | -39.8028 | -54.2568 | -36.3077 | -52.4604
182 | -5.3553 | 0 | -5.0748 | 0 | -5.6127 | 0 | -5.1545 | 0 | -64.8513 | 116.8582 | -53.6354 | 135.0603 | -44.7796 | -15.7806 | -43.6863 | -80.5881 | -64.4752 | -165.2628 | -41.3904 | -30.9081 | -64.6229 | 144.946 | -48.7928 | -116.1265 | -45.5597 | 4.8492 | -48.0589 | -50.6811 | -64.7912 | -47.1132 | -42.2985 | -6.5862 | -17.3382 | -5.9908 | -35.4101 | 90.0698 | -28.355 | 38.2744 | -26.6811 | 72.3813 | -16.2648 | 12.8569 | -33.6303 | 4.5334 | -22.9838 | 16.9924 | -28.8357 | 2.68 | -61.8412 | -59.5002 | -41.1335 | -43.2982 | -56.435 | -39.0276 | -68.0435 | -45.64 | -41.0897 | -42.442 | -55.3912 | -39.6557 | -55.1755 | 182 | -44.2106 | -43.6174 | -39.2181 | -39.7375 | -43.8354 | -47.8749 | -40.5678 | -40.603 | 182 | -40.2847 | -35.7344 | -37.9429 | -51.3602 | -33.9528 | -62.4308 | -40.5652 | -35.477 | -38.1437 | -50.8223 | -33.8731 | -62.889 | -54.1449 | -35.7782 | -37.0867 | -50.3164 | -34.5809 | -49.5628 | -54.4254 | -35.5208 | -37.2875 | -49.7785 | -34.5012 | -50.021
183 | -5.3548 | 0 | -5.0834 | 0 | -5.6253 | 0 | -5.131 | 0 | -65.1376 | 94.9569 | -54.6976 | 126.5754 | -49.266 | -25.4504 | -43.817 | -125.9257 | -57.886 | -169.0651 | -39.4294 | -72.4824 | -60.5062 | 166.6078 | -46.8291 | -138.1406 | -49.4692 | -25.3732 | -45.2397 | -89.4609 | -59.9207 | -91.4776 | -39.6896 | -36.6916 | -18.45 | -29.3552 | -39.2974 | 53.7492 | -28.0067 | 30.0835 | -25.6466 | 95.1052 | -17.0553 | -3.3727 | -38.5931 | -11.2054 | -22.9308 | -5.7247 | -27.0062 | 26.9617 | -68.3889 | -55.4698 | -41.0978 | -41.9436 | -56.2991 | -37.6651 | -77.0483 | -45.1722 | -41.1595 | -41.228 | -54.0209 | -38.0472 | -51.4108 | 183 | -48.086 | -43.6194 | -37.9873 | -38.9446 | -44.8223 | -44.9712 | -38.011 | -39.2181 | 183 | -39.8174 | -35.8047 | -36.5888 | -51.2157 | -32.5817 | -71.423 | -40.0888 | -35.5342 | -36.8126 | -50.6738 | -32.5341 | -71.9173 | -50.115 | -35.743 | -35.8732 | -48.9375 | -32.9638 | -45.7855 | -50.3864 | -35.4725 | -36.097 | -48.3956 | -32.9162 | -46.2798
184 | -5.3039 | 0 | -5.0836 | 0 | -5.5299 | 0 | -5.1449 | 0 | -66.4624 | 96.583 | -56.2259 | 125.209 | -51.9972 | 4.4251 | -47.0655 | -167.2711 | -55.1758 | 166.6588 | -40.4545 | -111.3895 | -57.5621 | 156.8755 | -47.765 | -158.4781 | -60.2952 | -30.0629 | -45.5311 | -120.8658 | -58.2371 | -128.6226 | -39.9547 | -66.1384 | -22.3437 | -47.1351 | -47.9858 | 87.958 | -29.4899 | 22.4494 | -23.1214 | 93.616 | -19.3265 | -10.2605 | -44.3675 | 95.3167 | -25.6473 | -26.5822 | -24.4889 | 23.0339 | -84.1118 | -51.9526 | -41 | -42.0141 | -55.7953 | -37.476 | -76.9899 | -44.9831 | -40.8859 | -41.4196 | -53.8922 | -37.6315 | -50.1396 | 184 | -50.4944 | -46.3985 | -39.5039 | -40.0255 | -47.1181 | -45.0534 | -38.3636 | -39.8513 | 184 | -39.6792 | -35.582 | -36.7102 | -50.7117 | -32.3924 | -71.46 | -39.8995 | -35.356 | -36.8692 | -50.2654 | -32.3311 | -71.845 | -46.6487 | -35.6961 | -36.1157 | -48.8086 | -32.5479 | -44.6097 | -46.869 | -35.4701 | -36.2747 | -48.3623 | -32.4866 | -44.9947
185 | -5.2988 | 0 | -5.099 | 0 | -5.4609 | 0 | -5.1523 | 0 | -64.482 | 110.0562 | -55.3906 | 135.3498 | -47.8425 | 15.1414 | -54.664 | 150.2544 | -54.8107 | 142.9708 | -44.3416 | -145.1367 | -56.5114 | 142.3358 | -49.675 | -167.5541 | -54.7596 | 59.9463 | -47.5017 | -146.4174 | -58.4008 | -160.0839 | -42.2267 | -88.3333 | -28.5135 | -16.4407 | -37.2206 | 111.7514 | -31.8107 | 37.9308 | -22.258 | 81.7264 | -20.7053 | 3.0281 | -32.6571 | 94.0343 | -33.1184 | -21.667 | -24.1162 | 9.3767 | -66.9826 | -50.6375 | -41.0066 | -43.0294 | -55.4005 | -38.0789 | -68.5013 | -45.2304 | -40.7753 | -42.4662 | -54.3451 | -38.1758 | -51.801 | 185 | -47.0596 | -51.5021 | -43.6546 | -42.4767 | -47.8642 | -46.6849 | -40.5335 | -41.8927 | 185 | -39.9316 | -35.4765 | -37.7306 | -50.3015 | -32.9799 | -63.0404 | -40.1314 | -35.3144 | -37.8771 | -49.9396 | -32.9266 | -63.349 | -45.3387 | -35.7078 | -37.1674 | -49.2461 | -33.0768 | -46.3401 | -45.5385 | -35.5457 | -37.3139 | -48.8842 | -33.0235 | -46.6487
186 | -5.3416 | 0 | -5.1226 | 0 | -5.4681 | 0 | -5.1507 | 0 | -61.5826 | 99.7554 | -51.9884 | 124.9761 | -45.7083 | -0.5864 | -58.9715 | -8.3972 | -55.4655 | 122.7626 | -53.9862 | -174.7731 | -57.2722 | 123.6407 | -51.084 | -171.6331 | -48.9661 | 41.7908 | -52.066 | -175.2239 | -59.7142 | 171.7501 | -46.7057 | -97.0424 | -22.3236 | 15.0419 | -31.7877 | 80.645 | -28.0462 | 60.0703 | -23.2664 | 72.6992 | -18.5164 | 11.9653 | -28.1501 | 71.0937 | -29.0416 | 49.4526 | -26.0888 | -1.0023 | -62.1038 | -50.7266 | -41.2134 | -44.51 | -54.6702 | -39.0118 | -64.1499 | -45.8353 | -41.0057 | -43.7866 | -55.2749 | -39.4407 | -55.7926 | 186 | -44.6999 | -53.1852 | -49.3601 | -44.7239 | -46.5066 | -50.3827 | -44.5152 | -44.546 | 186 | -40.4937 | -35.6641 | -39.1684 | -49.5476 | -33.8892 | -58.6818 | -40.7127 | -35.5376 | -39.3593 | -49.2021 | -33.8611 | -58.9992 | -45.385 | -35.8718 | -38.445 | -50.1523 | -34.3181 | -50.3245 | -45.604 | -35.7453 | -38.6359 | -49.8068 | -34.29 | -50.6419
187 | -5.3882 | 0 | -5.1654 | 0 | -5.5922 | 0 | -5.1861 | 0 | -61.0613 | 89.1934 | -50.0564 | 93.7175 | -45.4136 | -13.2863 | -47.6856 | -63.7599 | -58.1568 | 97.0733 | -52.0524 | -20.6559 | -63.3149 | 124.7031 | -54.2186 | -168.7354 | -46.2722 | 22.1907 | -65.0796 | -3.2804 | -63.0858 | 122.9716 | -49.8101 | -57.8248 | -18.3419 | -3.5588 | -30.4593 | 43.7287 | -24.4028 | 43.746 | -25.0909 | 80.6472 | -16.3629 | 2.434 | -26.8005 | 47.072 | -22.6286 | 34.4181 | -30.0536 | 13.7807 | -59.4044 | -52.7648 | -41.0609 | -44.506 | -54.0411 | -39.2687 | -60.888 | -46.2563 | -41.146 | -43.5443 | -57.2318 | -40.3305 | -64.6549 | 187 | -44.0446 | -47.133 | -44.796 | -44.3756 | -45.5526 | -58.9688 | -48.3734 | -44.6179 | 187 | -40.8681 | -35.7578 | -39.1178 | -48.8757 | -34.1033 | -55.2958 | -41.0909 | -35.5538 | -39.3199 | -48.4489 | -34.0826 | -55.7019 | -47.3766 | -35.6727 | -38.1561 | -52.0664 | -35.1651 | -59.0627 | -47.5994 | -35.4687 | -38.3582 | -51.6396 | -35.1444 | -59.4688
188 | -5.4271 | 0 | -5.1788 | 0 | -5.7279 | 0 | -5.1989 | 0 | -59.5383 | 63.2868 | -50.9405 | 56.4978 | -45.0844 | -31.6662 | -43.4921 | -109.0319 | -65.9813 | 136.0444 | -42.3575 | -57.6474 | -60.5128 | 164.9349 | -50.8095 | -135.3526 | -44.5745 | -9.6444 | -47.8213 | -66.5301 | -67.7713 | -54.0407 | -43.4058 | -43.0461 | -17.2662 | -29.3029 | -31.1925 | 2.0211 | -24.0348 | 17.4854 | -23.5896 | 96.1774 | -15.7408 | -13.4268 | -27.4553 | 26.8969 | -20.5692 | 5.583 | -26.8842 | 46.1791 | -61.0311 | -58.1115 | -40.1935 | -42.3554 | -55.5858 | -38.1583 | -62.7491 | -46.3334 | -40.6341 | -41.4093 | -56.7882 | -38.9349 | -62.6031 | 188 | -43.96 | -43.3617 | -39.5502 | -40.4878 | -43.559 | -47.5522 | -41.5205 | -40.9317 | 188 | -40.9063 | -35.207 | -36.9283 | -50.407 | -32.9795 | -57.0212 | -41.1546 | -34.9062 | -37.1565 | -49.8579 | -32.9594 | -57.5502 | -52.6844 | -34.7664 | -35.9822 | -51.6094 | -33.7561 | -56.8752 | -52.9327 | -34.4656 | -36.2104 | -51.0603 | -33.736 | -57.4042
189 | -5.4128 | 0 | -5.1774 | 0 | -5.7401 | 0 | -5.2291 | 0 | -64.5194 | 29.8021 | -53.6505 | 20.1642 | -47.5951 | -45.1285 | -43.2029 | -152.1514 | -57.8435 | 159.112 | -39.2853 | -99.7623 | -56.4522 | 167.8594 | -46.7172 | -158.3938 | -46.2114 | -41.7526 | -44.5398 | -107.0209 | -58.977 | -117.8513 | -39.7305 | -67.0415 | -18.5072 | -55.2822 | -35.0696 | -49.3557 | -26.098 | -5.3793 | -20.6002 | 94.3919 | -16.6626 | -27.682 | -30.008 | 19.3185 | -21.312 | -21.7737 | -22.7379 | 38.2563 | -67.143 | -62.5807 | -40.1674 | -40.8617 | -56.0297 | -37.2995 | -67.9234 | -46.4276 | -40.6667 | -40.1461 | -54.7985 | -37.5253 | -57.3575 | 189 | -46.5629 | -43.0253 | -37.6946 | -38.6351 | -43.2345 | -44.1244 | -37.882 | -38.8077 | 189 | -41.0148 | -35.2539 | -35.4489 | -50.8523 | -32.1221 | -62.1833 | -41.2502 | -34.9266 | -35.6326 | -50.2896 | -32.0704 | -62.6943 | -57.1679 | -34.7546 | -34.7333 | -49.6211 | -32.3479 | -51.6174 | -57.4033 | -34.4273 | -34.917 | -49.0584 | -32.2962 | -52.1284
190 | -5.3785 | 0 | -5.1793 | 0 | -5.6522 | 0 | -5.2629 | 0 | -76.1353 | 128.0888 | -58.7909 | -21.9086 | -49.8442 | -36.4659 | -45.791 | 171.4964 | -54.0211 | 137.7759 | -39.4341 | -138.0524 | -53.815 | 154.8999 | -46.6271 | 174.0111 | -50.4525 | -65.7804 | -44.7158 | -139.2673 | -56.1326 | -155.8088 | -39.2039 | -94.2033 | -22.7186 | -76.0536 | -37.7173 | -154.1941 | -30.9673 | -26.1685 | -18.7949 | 81.8926 | -18.6797 | -33.68 | -31.3936 | 33.2816 | -24.3969 | -42.079 | -20.9385 | 15.8783 | -76.6215 | -55.6725 | -40.18 | -40.6176 | -56.4809 | -37.1998 | -68.9957 | -46.1053 | -40.4332 | -40.1364 | -54.4606 | -36.9803 | -55.7071 | 190 | -49.3142 | -45.1794 | -38.4895 | -38.9196 | -44.571 | -43.9413 | -37.5542 | -38.8086 | 190 | -40.7268 | -35.0547 | -35.2391 | -51.3016 | -32.0205 | -63.3435 | -40.926 | -34.781 | -35.3547 | -50.8287 | -31.9369 | -63.7328 | -50.294 | -34.8015 | -34.7579 | -49.2813 | -31.801 | -50.0549 | -50.4932 | -34.5278 | -34.8735 | -48.8084 | -31.7174 | -50.4442
191 | -5.3671 | 0 | -5.2026 | 0 | -5.5871 | 0 | -5.2813 | 0 | -61.6094 | 128.2191 | -68.5441 | -123.8585 | -48.2547 | -24.7129 | -51.1405 | 145.8878 | -52.7231 | 114.3312 | -41.8435 | -172.5195 | -52.6105 | 139.077 | -48.5688 | 155.3051 | -59.4686 | -54.2799 | -46.7703 | -165.5153 | -55.6811 | 172.0418 | -40.588 | -117.3142 | -30.73 | -40.8861 | -30.9851 | 127.8363 | -46.024 | 47.4515 | -18.3813 | 66.6018 | -19.8813 | -22.7615 | -28.5227 | 40.9262 | -29.9726 | -33.6774 | -21.2091 | -8.9898 | -67.426 | -52.4199 | -40.2273 | -41.1448 | -57.0667 | -37.5684 | -65.0425 | -46.0403 | -40.1835 | -40.8901 | -54.6011 | -37.1379 | -56.2163 | 191 | -48.0199 | -48.6256 | -41.3524 | -40.6702 | -46.8791 | -45.3429 | -39.1266 | -40.4014 | 191 | -40.6732 | -34.8164 | -35.7777 | -51.8641 | -32.3658 | -59.4554 | -40.8377 | -34.5964 | -35.8635 | -51.4796 | -32.2871 | -59.7612 | -47.0528 | -34.8602 | -35.523 | -49.3985 | -31.9353 | -50.6292 | -47.2173 | -34.6402 | -35.6088 | -49.014 | -31.8566 | -50.935
192 | -5.4168 | 0 | -5.2283 | 0 | -5.5545 | 0 | -5.2875 | 0 | -57.2943 | 95.7205 | -58.9268 | 117.6245 | -46.0489 | -33.6856 | -64.7369 | 137.5608 | -52.7561 | 94.0174 | -46.9609 | 158.2766 | -52.5224 | 120.6199 | -51.1264 | 148.1785 | -54.4423 | 5.9685 | -51.3722 | 171.8837 | -57.0874 | 144.8007 | -43.7798 | -132.2296 | -22.8199 | -5.7698 | -27.6256 | 87.0408 | -30.0102 | 77.5494 | -19.1039 | 54.5477 | -18.0958 | -15.9192 | -26.4608 | 25.3991 | -28.1397 | 3.0457 | -23.984 | -36.9799 | -62.9361 | -50.7545 | -40.3863 | -42.1822 | -56.5416 | -38.2077 | -62.3651 | -46.5702 | -40.1395 | -42.1502 | -55.1073 | -37.8319 | -61.09 | 192 | -45.5311 | -51.2483 | -46.6255 | -42.9867 | -47.7197 | -48.2854 | -42.4498 | -43.2393 | 192 | -41.1534 | -34.7227 | -36.7654 | -51.3133 | -32.9794 | -56.8106 | -41.3419 | -34.585 | -36.8947 | -50.9871 | -32.9202 | -57.0776 | -45.3377 | -34.9695 | -36.7334 | -49.879 | -32.6036 | -55.5355 | -45.5262 | -34.8318 | -36.8627 | -49.5528 | -32.5444 | -55.8025
193 | -5.4685 | 0 | -5.2481 | 0 | -5.6138 | 0 | -5.2631 | 0 | -56.6739 | 57.8044 | -53.5313 | 60.9311 | -45.6095 | -49.161 | -52.6032 | -93.128 | -53.4209 | 73.1309 | -66.3164 | 110.3369 | -54.7651 | 102.2323 | -54.1712 | 151.6177 | -49.4813 | -7.325 | -66.7137 | -113.7626 | -59.8215 | 126.3194 | -48.8682 | -116.2366 | -18.5766 | -27.282 | -26.5657 | 53.8177 | -26.3483 | 47.0944 | -20.3923 | 49.7834 | -16.1863 | -24.2056 | -26.4022 | 0.9377 | -23.7695 | -7.8123 | -32.316 | -70.6887 | -61.6746 | -50.6497 | -40.6372 | -42.6746 | -55.327 | -38.6068 | -61.3379 | -47.6997 | -40.32 | -42.7012 | -55.6231 | -38.7857 | -72.872 | 193 | -44.6766 | -49.1396 | -49.9312 | -44.9127 | -47.3438 | -53.3789 | -47.691 | -45.9709 | 193 | -42.2312 | -34.8515 | -37.2061 | -50.0789 | -33.3587 | -55.7241 | -42.4516 | -34.7062 | -37.4115 | -49.7132 | -33.3437 | -56.0748 | -45.1812 | -35.1687 | -37.2327 | -50.375 | -33.5376 | -67.2582 | -45.4016 | -35.0234 | -37.4381 | -50.0093 | -33.5226 | -67.6089
194 | -5.4969 | 0 | -5.249 | 0 | -5.6949 | 0 | -5.2779 | 0 | -60.0325 | 17.8503 | -51.5417 | 6.8663 | -46.115 | -59.4353 | -45.2394 | -133.0958 | -56.5537 | 49.6327 | -47.2894 | -83.3712 | -59.8339 | 121.0127 | -53.1837 | -179.9099 | -47.8725 | -27.0046 | -49.1238 | -94.7974 | -65.3988 | 123.4335 | -44.3539 | -82.7497 | -17.3133 | -55.2149 | -28.1028 | 26.2834 | -27.8162 | 14.8521 | -20.6827 | 52.111 | -15.6014 | -39.4707 | -28.8987 | -26.7204 | -22.6558 | -34.5666 | -33.4142 | 95.521 | -62.9405 | -53.3283 | -40.7769 | -41.3549 | -53.7831 | -37.9994 | -61.3212 | -48.8452 | -40.4167 | -41.2465 | -55.7584 | -38.5787 | -68.3059 | 194 | -44.8856 | -44.7977 | -42.5489 | -43.4352 | -46.5434 | -48.6765 | -42.6974 | -42.7323 | 194 | -43.3483 | -34.9198 | -35.858 | -48.5341 | -32.7504 | -55.6263 | -43.5962 | -34.7218 | -36.077 | -48.0882 | -32.7215 | -56.0433 | -47.8314 | -35.28 | -35.7496 | -50.5094 | -33.3297 | -62.611 | -48.0793 | -35.082 | -35.9686 | -50.0635 | -33.3008 | -63.028
195 | -5.4861 | 0 | -5.2441 | 0 | -5.7308 | 0 | -5.3089 | 0 | -67.5004 | -22.1168 | -51.7488 | -42.0224 | -46.0971 | -73.1224 | -43.7047 | -174.3149 | -63.4211 | 82.7807 | -41.7807 | -124.2831 | -55.663 | 144.6418 | -48.8324 | 171.6782 | -46.6339 | -49.7948 | -45.3011 | -129.2946 | -62.8682 | -174.2307 | -40.2023 | -100.3326 | -18.1981 | -82.4223 | -31.9275 | 15.8089 | -34.0275 | -6.4696 | -19.7221 | 49.1288 | -16.4897 | -54.4128 | -37.579 | -57.2322 | -24.4261 | -63.2166 | -24.2812 | 65.0271 | -67.7777 | -58.0822 | -39.9649 | -40.2757 | -53.6151 | -37.2841 | -63.8873 | -48.1675 | -39.7809 | -40.0894 | -55.876 | -37.5446 | -61.4687 | 195 | -45.027 | -43.6407 | -39.3681 | -40.3914 | -44.2589 | -44.8498 | -38.6 | -39.2932 | 195 | -42.6814 | -34.2948 | -34.7896 | -48.371 | -32.04 | -58.1565 | -42.9234 | -34.0501 | -34.9668 | -47.8843 | -31.9752 | -58.5784 | -52.5961 | -34.4788 | -34.6033 | -50.6319 | -32.3005 | -55.7379 | -52.8381 | -34.2341 | -34.7805 | -50.1452 | -32.2357 | -56.1598
196 | -5.4594 | 0 | -5.2489 | 0 | -5.686 | 0 | -5.3371 | 0 | -67.5597 | -169.456 | -52.6095 | -84.0701 | -48.2774 | -82.8854 | -45.1299 | 151.9602 | -57.1296 | 102.979 | -40.567 | -163.9839 | -52.7562 | 137.295 | -47.6342 | 144.3208 | -48.3893 | -77.0498 | -45.1253 | -159.2748 | -56.7605 | 162.2571 | -38.8562 | -125.0033 | -21.6138 | -105.2195 | -33.3047 | 47.8562 | -41.8258 | 95.7205 | -19.1198 | 38.0879 | -18.5702 | -61.4197 | -37.9871 | 96.4264 | -29.4958 | -83.9314 | -21.2774 | 35.8113 | -84.5466 | -60.3509 | -39.6165 | -39.9216 | -54.902 | -37.222 | -67.3348 | -47.4087 | -39.5844 | -39.7841 | -55.0341 | -37.061 | -59.3391 | 196 | -46.8767 | -44.8409 | -39.0681 | -39.8061 | -44.3141 | -44.187 | -37.4935 | -38.3348 | 196 | -41.9493 | -34.125 | -34.4622 | -49.6531 | -31.9731 | -61.6488 | -42.1598 | -33.8984 | -34.5845 | -49.216 | -31.8849 | -61.9977 | -54.8915 | -34.1571 | -34.3247 | -49.7852 | -31.8121 | -53.6531 | -55.102 | -33.9305 | -34.447 | -49.3481 | -31.7239 | -54.002
197 | -5.4333 | 0 | -5.2605 | 0 | -5.6443 | 0 | -5.3281 | 0 | -59.1877 | 135.5686 | -54.1773 | -126.2488 | -49.2655 | -76.4775 | -48.384 | 130.3831 | -54.2318 | 85.6873 | -41.9214 | 160.2719 | -51.1306 | 122.9604 | -49.2778 | 120.5433 | -52.8011 | -86.9842 | -46.7395 | 176.2681 | -55.0869 | 132.077 | -39.3662 | -149.209 | -27.9886 | -93.6058 | -28.3583 | 50.8857 | -30.7939 | 100.2368 | -19.552 | 21.6422 | -20.4357 | -52.4445 | -28.8906 | 66.3094 | -38.0726 | -46.1154 | -21.0129 | 9.7078 | -66.6129 | -56.8404 | -39.5435 | -40.0621 | -56.6558 | -37.5084 | -64.3933 | -46.9529 | -39.4529 | -40.0301 | -54.4246 | -37.0076 | -60.4733 | 197 | -47.7288 | -47.1024 | -40.8314 | -40.9764 | -46.0618 | -44.9494 | -38.2767 | -39.0637 | 197 | -41.5196 | -34.0196 | -34.6288 | -51.3953 | -32.2479 | -58.749 | -41.6924 | -33.8086 | -34.734 | -51.0115 | -32.1803 | -59.0652 | -51.4071 | -34.1102 | -34.5968 | -49.1641 | -31.7471 | -54.829 | -51.5799 | -33.8992 | -34.702 | -48.7803 | -31.6795 | -55.1452
198 | -5.4677 | 0 | -5.2984 | 0 | -5.6103 | 0 | -5.3207 | 0 | -56.2357 | 93.8672 | -58.1611 | -176.8158 | -48.2453 | -76.513 | -52.8448 | 120.0138 | -53.7415 | 64.9012 | -45.5456 | 127.3306 | -50.7631 | 104.696 | -52.2503 | 109.2618 | -55.5637 | -54.1968 | -50.3424 | 154.2548 | -55.8582 | 101.0134 | -41.4981 | -168.8576 | -24.1857 | -53.8553 | -25.2495 | 30.4569 | -27.212 | 79.6134 | -21.5501 | 7.5362 | -19.1757 | -40.1102 | -26.152 | 34.8539 | -31.306 | -14.8092 | -22.8317 | -13.2994 | -62.018 | -53.1853 | -39.6482 | -40.7485 | -57.2211 | -37.8493 | -61.5523 | -47.0009 | -39.4169 | -40.7281 | -53.9664 | -37.3368 | -62.3339 | 198 | -47.2388 | -49.2817 | -44.6079 | -43.2704 | -47.6644 | -46.941 | -40.6538 | -41.1806 | 198 | -41.5332 | -33.9492 | -35.2808 | -51.9227 | -32.5509 | -55.942 | -41.7025 | -33.8066 | -35.4278 | -51.6108 | -32.5286 | -56.2316 | -47.7176 | -34.1805 | -35.2604 | -48.668 | -32.0384 | -56.7236 | -47.8869 | -34.0379 | -35.4074 | -48.3561 | -32.0161 | -57.0132
199 | -5.5402 | 0 | -5.3152 | 0 | -5.6215 | 0 | -5.2837 | 0 | -56.6455 | 48.9578 | -65.4256 | 49.3546 | -47.4397 | -86.3979 | -60.6132 | 159.229 | -54.954 | 50.5003 | -53.3787 | 93.5132 | -52.5479 | 83.5854 | -55.1381 | 102.0484 | -50.6047 | -43.4642 | -62.6629 | 148.1803 | -59.7139 | 76.0177 | -45.2887 | -179.5319 | -19.2984 | -70.1826 | -24.3889 | 4.3465 | -27.6266 | 59.8452 | -25.2703 | 4.2389 | -16.9769 | -44.4725 | -26.2691 | 3.2875 | -28.6765 | -38.5955 | -27.8097 | -24.6806 | -60.5074 | -50.9504 | -39.8379 | -41.7066 | -55.4293 | -38.2395 | -60.4636 | -47.8949 | -39.5012 | -41.4597 | -54.0066 | -38.0394 | -69.4 | 199 | -46.886 | -52.0557 | -52.4045 | -45.8803 | -47.6132 | -51.4439 | -44.7894 | -44.0497 | 199 | -42.3547 | -33.961 | -36.1664 | -50.1141 | -32.9243 | -54.8421 | -42.5797 | -33.8797 | -36.4229 | -49.8078 | -32.9558 | -55.1799 | -45.4102 | -34.2977 | -35.9195 | -48.6914 | -32.7242 | -63.7785 | -45.6352 | -34.2164 | -36.176 | -48.3851 | -32.7557 | -64.1163
200 | -5.5807 | 0 | -5.3187 | 0 | -5.6718 | 0 | -5.2854 | 0 | -61.2546 | -12.3477 | -54.727 | -52.6802 | -47.5879 | -98.5036 | -50.3471 | -170.3868 | -57.154 | 45.806 | -56.3095 | -94.4137 | -58.9313 | 85.3637 | -61.9699 | 139.6107 | -47.5664 | -61.1031 | -51.9944 | -110.8457 | -67.1036 | 85.132 | -49.4323 | -151.2507 | -17.432 | -98.0247 | -25.526 | -20.1563 | -31.1888 | 67.9036 | -27.3693 | 27.3036 | -15.6353 | -57.3255 | -28.7632 | -31.9286 | -29.3708 | -72.7226 | -31.5982 | 16.699 | -62.132 | -51.282 | -40.0073 | -41.4367 | -53.8429 | -38.4187 | -61.5257 | -50.0624 | -39.6823 | -41.0179 | -54.1624 | -38.5858 | -72.509 | 200 | -46.6669 | -49.2421 | -48.257 | -46.6371 | -47.1159 | -51.0838 | -47.3638 | -45.3604 | 200 | -44.4817 | -34.1016 | -35.856 | -48.5242 | -33.1 | -55.8539 | -44.7437 | -34.0105 | -36.1513 | -48.1711 | -33.1333 | -56.2403 | -45.7013 | -34.4266 | -35.4372 | -48.8437 | -33.2671 | -66.8372 | -45.9633 | -34.3355 | -35.7325 | -48.4906 | -33.3004 | -67.2236
201 | -5.5852 | 0 | -5.3192 | 0 | -5.7356 | 0 | -5.2944 | 0 | -62.6263 | -130.1458 | -50.9614 | -99.8983 | -48.5895 | -107.5501 | -46.7754 | 156.7494 | -58.2135 | 63.0584 | -46.3646 | -144.0595 | -56.1344 | 141.6031 | -52.8962 | 159.1668 | -46.6963 | -82.9914 | -46.6858 | -144.3652 | -65.0717 | 143.1201 | -44.4293 | -131.6134 | -17.4953 | -127.7705 | -28.467 | -37.4927 | -28.1777 | 98.2006 | -24.6669 | 35.9393 | -15.5998 | -72.61 | -36.1221 | -78.4786 | -36.8717 | -130.325 | -26.0543 | 34.8505 | -67.2849 | -54.3341 | -40.1055 | -40.4294 | -53.0817 | -38.3419 | -64.6903 | -51.3958 | -39.7688 | -40.2176 | -54.6356 | -38.3099 | -64.8348 | 201 | -46.498 | -46.3701 | -42.8298 | -44.1519 | -45.3811 | -46.1626 | -42.031 | -42.3828 | 201 | -45.8106 | -34.1836 | -34.8442 | -47.7625 | -33.0227 | -58.9547 | -46.0766 | -34.0332 | -35.135 | -47.3461 | -33.0475 | -59.3959 | -48.7489 | -34.5203 | -34.6324 | -49.3164 | -32.9907 | -59.0992 | -49.0149 | -34.3699 | -34.9232 | -48.9 | -33.0155 | -59.5404
202 | -5.5715 | 0 | -5.2899 | 0 | -5.7615 | 0 | -5.3346 | 0 | -56.1237 | 168.0504 | -49.7009 | -136.1134 | -48.6582 | -113.2897 | -46.9358 | 127.97 | -54.9714 | 72.6504 | -44.0034 | 177.48 | -50.7718 | 131.0956 | -50.1454 | 129.6436 | -46.4031 | -103.2805 | -45.8348 | -175.4749 | -58.8812 | 149.1163 | -41.239 | -149.8728 | -19.5469 | -158.0426 | -32.2532 | -29.1375 | -23.6559 | 89.7328 | -23.0092 | 21.9516 | -16.5456 | -84.5669 | -39.1386 | 135.2212 | -35.3571 | 68.1671 | -22.937 | 18.2366 | -78.7087 | -58.9225 | -39.7169 | -39.904 | -53.5564 | -38.321 | -66.9774 | -50.2459 | -39.3215 | -39.9188 | -55.8524 | -37.8162 | -62.5796 | 202 | -45.7228 | -45.8713 | -41.5032 | -42.4732 | -43.8791 | -44.4662 | -39.549 | -40.0276 | 202 | -44.6744 | -33.75 | -34.3325 | -48.2665 | -33.0311 | -61.2159 | -44.956 | -33.56 | -34.5694 | -47.7949 | -32.9864 | -61.6428 | -53.351 | -34.1454 | -34.3473 | -50.5625 | -32.5263 | -56.8181 | -53.6326 | -33.9554 | -34.5842 | -50.0909 | -32.4816 | -57.245
203 | -5.5342 | 0 | -5.3021 | 0 | -5.7629 | 0 | -5.3631 | 0 | -52.4219 | 131.9859 | -49.9331 | -167.2068 | -49.7854 | -123.5485 | -48.6409 | 108.0023 | -51.9582 | 60.4214 | -44.1569 | 142.8306 | -48.6916 | 112.4515 | -50.8651 | 99.0032 | -47.9803 | -129.207 | -47.2898 | 155.9389 | -54.409 | 126.6171 | -40.4462 | -173.2511 | -24.7356 | -179.5612 | -30.3231 | -11.2916 | -21.6539 | 70.6797 | -23.328 | -0.6414 | -18.102 | -90.3539 | -30.9955 | 82.1776 | -27.7427 | 17.8974 | -22.2822 | -1.8185 | -69.7131 | -62.9903 | -39.2538 | -39.7288 | -55.1428 | -38.4864 | -66.9193 | -49.2473 | -39.0576 | -39.9428 | -55.6771 | -37.595 | -64.6749 | 203 | -45.7861 | -45.8888 | -42.0602 | -42.5747 | -44.2446 | -44.4607 | -39.3146 | -39.5948 | 203 | -43.7131 | -33.5234 | -34.1946 | -49.8407 | -33.1843 | -61.1564 | -43.9452 | -33.2947 | -34.3657 | -49.3799 | -33.1233 | -61.5562 | -57.4561 | -33.7196 | -34.4086 | -50.375 | -32.2929 | -58.912 | -57.6882 | -33.4909 | -34.5797 | -49.9142 | -32.2319 | -59.3118
204 | -5.5192 | 0 | -5.3152 | 0 | -5.737 | 0 | -5.3605 | 0 | -50.8725 | 98.4534 | -51.7883 | 163.1182 | -50.8589 | -126.6292 | -50.3927 | 93.34 | -50.3944 | 40.9305 | -46.4914 | 110.7206 | -48.0486 | 92.1501 | -54.9035 | 76.5985 | -52.012 | -142.1174 | -51.3 | 130.5404 | -52.78 | 98.0445 | -41.3137 | 163.1053 | -32.4223 | -126.4913 | -27.3874 | -23.4453 | -21.1958 | 50.7636 | -25.8651 | -25.5427 | -18.8968 | -87.2081 | -28.754 | 50.0022 | -25.3536 | -24.2749 | -23.6391 | -19.6416 | -63.9762 | -59.0972 | -39.145 | -39.9058 | -57.0738 | -38.7183 | -63.3308 | -48.9284 | -38.9957 | -40.2605 | -54.7487 | -37.7214 | -69.0788 | 204 | -46.3808 | -45.7762 | -44.1803 | -44.0045 | -45.9863 | -45.4732 | -40.7292 | -40.6823 | 204 | -43.4092 | -33.4765 | -34.3866 | -51.7586 | -33.4031 | -57.5938 | -43.6132 | -33.2587 | -34.5453 | -51.3368 | -33.3578 | -57.9703 | -53.578 | -33.6258 | -34.7413 | -49.4335 | -32.4062 | -63.3418 | -53.782 | -33.408 | -34.9 | -49.0117 | -32.3609 | -63.7183
205 | -5.5577 | 0 | -5.3355 | 0 | -5.7061 | 0 | -5.3479 | 0 | -51.5562 | 65.5634 | -58.2846 | 133.1834 | -51.3338 | -130.4939 | -53.3984 | 71.8846 | -50.3524 | 20.2014 | -51.374 | 80.6614 | -48.9106 | 71.2825 | -60.8416 | 86.7673 | -54.996 | -119.1968 | -63.1232 | 115.1711 | -53.2402 | 71.6258 | -43.9521 | 142.3521 | -23.1091 | -106.3486 | -26.5189 | -48.4231 | -22.3177 | 32.2403 | -33.0724 | -48.7514 | -17.9572 | -85.7828 | -29.6221 | 23.3263 | -25.2137 | -67.184 | -26.4021 | -28.1555 | -61.4809 | -53.5272 | -39.1953 | -40.4926 | -56.8833 | -38.9452 | -61.1676 | -49.3193 | -38.9874 | -40.9527 | -54.0387 | -38.124 | -74.8957 | 205 | -48.0056 | -46.8232 | -48.7469 | -46.2225 | -47.7365 | -47.4279 | -43.8129 | -43.1732 | 205 | -43.7616 | -33.4297 | -34.9349 | -51.5478 | -33.6097 | -55.4615 | -43.9838 | -33.2813 | -35.1447 | -51.1772 | -33.5973 | -55.8197 | -47.9695 | -33.6376 | -35.395 | -48.7032 | -32.7885 | -69.1896 | -48.1917 | -33.4892 | -35.6048 | -48.3326 | -32.7761 | -69.5478
206 | -5.606 | 0 | -5.3409 | 0 | -5.7032 | 0 | -5.3393 | 0 | -55.8804 | 37.9583 | -59.3593 | -106.1704 | -52.1099 | -135.564 | -68.8487 | 95.1699 | -51.2296 | 4.6499 | -64.8311 | 27.3002 | -52.5693 | 54.8448 | -62.9882 | 129.118 | -51.488 | -109.7126 | -54.9792 | -117.9468 | -55.2318 | 53.3445 | -49.8609 | 133.4863 | -18.954 | -129.9296 | -27.8298 | -76.0204 | -25.0484 | 22.1884 | -42.8957 | 65.7325 | -16.6741 | -93.1327 | -33.7508 | 10.3776 | -27.0332 | -113.1891 | -28.7001 | -12.7287 | -61.3339 | -50.5829 | -39.3295 | -41.0722 | -54.9355 | -39.247 | -61.2315 | -51.0704 | -38.9654 | -41.3917 | -53.9386 | -38.7344 | -70.6704 | 206 | -50.0468 | -49.8942 | -57.91 | -48.5341 | -48.8154 | -49.3145 | -48.537 | -46.8989 | 206 | -45.4644 | -33.3594 | -35.4662 | -49.5946 | -33.9061 | -55.5283 | -45.7295 | -33.2622 | -35.7329 | -49.2323 | -33.9077 | -55.8922 | -44.9769 | -33.7235 | -35.7857 | -48.5977 | -33.3935 | -64.9672 | -45.242 | -33.6263 | -36.0524 | -48.2354 | -33.3951 | -65.3311
207 | -5.6551 | 0 | -5.3604 | 0 | -5.7584 | 0 | -5.3636 | 0 | -65.0605 | 84.4003 | -50.0217 | -140.1818 | -52.7327 | -135.8392 | -53.347 | 152.1232 | -52.7551 | -7.5058 | -53.5137 | -147.7806 | -57.7501 | 87.2072 | -55.2512 | 147.3117 | -49.1845 | -126.9893 | -48.4289 | -151.4474 | -57.4929 | 46.7892 | -52.2258 | -166.5973 | -17.3796 | -157.4107 | -32.4963 | -98.0237 | -27.0834 | 36.0166 | -31.2776 | 53.1585 | -16.0286 | -108.0026 | -37.7507 | 51.296 | -30.0564 | -174.1585 | -26.8133 | -0.5348 | -64.1386 | -50.7319 | -39.4489 | -40.7753 | -53.7089 | -39.3609 | -63.6611 | -53.1842 | -39.0379 | -40.7549 | -54.1104 | -38.9303 | -63.4251 | 207 | -48.071 | -49.8964 | -47.2056 | -48.2144 | -47.7653 | -47.4913 | -46.3203 | -47.0253 | 207 | -47.5291 | -33.3828 | -35.1202 | -48.3485 | -34.0005 | -57.9027 | -47.8238 | -33.2795 | -35.4117 | -47.9505 | -33.9973 | -58.2975 | -45.0768 | -33.7938 | -35.0998 | -48.75 | -33.5699 | -57.6667 | -45.3715 | -33.6905 | -35.3913 | -48.352 | -33.5667 | -58.0615
208 | -5.6426 | 0 | -5.3783 | 0 | -5.7875 | 0 | -5.4005 | 0 | -55.0406 | 115.9988 | -47.5763 | -170.9052 | -52.2969 | -137.7061 | -49.9301 | 120.6367 | -54.5539 | -9.5839 | -47.8535 | 169.8867 | -52.184 | 112.3231 | -51.612 | 113.934 | -48.9122 | -149.1667 | -47.1465 | 175.1817 | -59.2797 | 49.6568 | -45.4309 | -165.7485 | -17.5345 | 177.3949 | -39.8195 | -52.8595 | -25.4424 | 38.6852 | -28.6526 | 16.398 | -16.4891 | -125.2451 | -31.2876 | 68.4743 | -31.9198 | 105.4856 | -24.5166 | -8.1356 | -68.7658 | -52.8665 | -39.4716 | -40.1916 | -53.3987 | -39.3665 | -66.9486 | -52.436 | -38.9433 | -40.1712 | -54.8587 | -38.6899 | -61.0286 | 208 | -45.7678 | -47.747 | -43.5627 | -45.8855 | -45.8849 | -45.7644 | -42.6101 | -43.6995 | 208 | -46.7934 | -33.3007 | -34.549 | -48.0204 | -33.9882 | -61.1611 | -47.0577 | -33.1558 | -34.7911 | -47.6112 | -33.966 | -61.5481 | -47.2239 | -33.829 | -34.5286 | -49.4804 | -33.3116 | -55.2411 | -47.4882 | -33.6841 | -34.7707 | -49.0712 | -33.2894 | -55.6281
209 | -5.6032 | 0 | -5.4013 | 0 | -5.7878 | 0 | -5.4429 | 0 | -50.4218 | 95.1259 | -46.9978 | 164.5292 | -51.5027 | -149.3494 | -49.4861 | 94.6424 | -54.7915 | -3.5997 | -46.5983 | 132.386 | -48.7057 | 98.7567 | -52.1441 | 75.2075 | -49.6185 | -173.0847 | -48.5432 | 145.852 | -58.6378 | 62.5151 | -42.823 | 170.4809 | -19.0416 | 155.8345 | -30.8704 | -28.0444 | -24.8772 | 24.275 | -29.489 | -29.4032 | -18.1164 | -142.2495 | -27.7035 | 52.8737 | -30.7253 | 37.5051 | -23.647 | -22.6124 | -70.5545 | -56.5465 | -39.1353 | -39.7811 | -54.1483 | -39.4176 | -69.0732 | -50.6589 | -38.6813 | -39.8896 | -55.4834 | -38.4557 | -62.6423 | 209 | -44.4235 | -46.262 | -42.7486 | -44.9108 | -45.1579 | -45.4022 | -41.4091 | -41.9051 | 209 | -45.0557 | -33.0781 | -34.1779 | -48.747 | -34.0163 | -63.2854 | -45.2576 | -32.8935 | -34.3382 | -48.3605 | -33.9747 | -63.6303 | -50.9433 | -33.5321 | -34.2864 | -50.0821 | -33.0544 | -56.8545 | -51.1452 | -33.3475 | -34.4467 | -49.6956 | -33.0128 | -57.1994
210 | -5.5747 | 0 | -5.4201 | 0 | -5.7721 | 0 | -5.4311 | 0 | -48.3737 | 69.3609 | -47.5429 | 142.7757 | -51.9842 | -164.9305 | -49.9875 | 70.0105 | -53.372 | -6.244 | -47.6043 | 97.1186 | -47.2789 | 80.8472 | -56.44 | 36.6493 | -53.0834 | 161.1518 | -52.4813 | 121.1342 | -55.9176 | 55.007 | -42.5936 | 144.2294 | -21.8256 | 146.8665 | -26.0626 | -53.9331 | -26.6591 | 2.7098 | -29.3241 | -89.5935 | -21.1952 | -152.4839 | -26.3391 | 29.9148 | -30.6494 | -16.8967 | -23.6896 | -39.3206 | -67.796 | -61.8237 | -38.8958 | -39.6241 | -55.839 | -39.4214 | -66.9905 | -49.4322 | -38.6176 | -39.8733 | -55.1701 | -38.4166 | -65.6112 | 210 | -44.1473 | -45.3504 | -43.4681 | -45.4831 | -45.8673 | -45.6994 | -42.0099 | -42.0404 | 210 | -43.8575 | -33.0429 | -34.0494 | -50.4189 | -34.0013 | -61.2184 | -44.0121 | -32.8455 | -34.193 | -50.0669 | -33.9903 | -61.5594 | -56.249 | -33.3211 | -34.2986 | -49.75 | -32.9965 | -59.8391 | -56.4036 | -33.1237 | -34.4422 | -49.398 | -32.9855 | -60.1801
211 | -5.5906 | 0 | -5.453 | 0 | -5.7314 | 0 | -5.4528 | 0 | -48.4137 | 41.5954 | -49.9289 | 126.4304 | -53.0547 | 177.6679 | -51.6917 | 39.4783 | -52.7876 | -19.1563 | -50.5115 | 62.6422 | -47.4093 | 61.2712 | -67.4609 | 2.8261 | -60.9642 | 168.7175 | -61.9699 | 109.0167 | -55.1392 | 34.0635 | -44.2704 | 117.9585 | -23.4886 | 157.1595 | -24.0107 | -83.9057 | -32.086 | -20.1602 | -27.0657 | -146.3453 | -24.7612 | -141.6841 | -26.7539 | 6.8733 | -32.1743 | -63.5093 | -24.3256 | -55.5114 | -65.4773 | -58.1268 | -38.8063 | -39.8796 | -56.4109 | -39.3925 | -64.8006 | -49.2041 | -38.6219 | -40.1405 | -54.4881 | -38.6103 | -65.3833 | 211 | -45.2984 | -45.7764 | -45.8791 | -47.1894 | -47.1809 | -46.6043 | -44.1768 | -43.8435 | 211 | -43.6135 | -33.0313 | -34.289 | -50.9579 | -33.9395 | -59.0692 | -43.7511 | -32.8905 | -34.4268 | -50.6795 | -33.9397 | -59.3478 | -52.5362 | -33.2157 | -34.5499 | -49.0351 | -33.1573 | -59.6519 | -52.6738 | -33.0749 | -34.6877 | -48.7567 | -33.1575 | -59.9305
212 | -5.5919 | 0 | -5.4543 | 0 | -5.725 | 0 | -5.4674 | 0 | -51.0108 | 17.5554 | -52.7903 | 141.3911 | -55.6916 | 157.5448 | -57.2565 | -2.0579 | -53.5179 | -30.176 | -55.8267 | 20.2244 | -49.5347 | 45.18 | -71.7613 | -119.4505 | -56.8845 | -147.4541 | -59.6207 | -128.6597 | -56.5027 | 16.9253 | -48.3235 | 94.6848 | -21.7744 | 162.8814 | -23.5589 | -113.977 | -55.6373 | 172.3214 | -24.857 | 174.6171 | -23.7437 | -120.4981 | -28.4045 | -17.2867 | -34.6569 | -100.5691 | -25.1575 | -72.7826 | -65.2911 | -52.8977 | -38.7138 | -40.5294 | -54.756 | -39.5071 | -65.259 | -50.7992 | -38.5294 | -40.5793 | -54.1692 | -39.0727 | -67.4474 | 212 | -47.9915 | -48.461 | -50.1078 | -50.1058 | -48.779 | -48.3985 | -47.9945 | -47.213 | 212 | -45.2073 | -32.9375 | -34.9375 | -49.3017 | -34.0528 | -59.534 | -45.3449 | -32.8044 | -35.062 | -49.031 | -34.0397 | -59.7916 | -47.3058 | -33.1219 | -34.9874 | -48.7149 | -33.6184 | -61.7224 | -47.4434 | -32.9888 | -35.1119 | -48.4442 | -33.6053 | -61.98
213 | -5.6159 | 0 | -5.4678 | 0 | -5.7578 | 0 | -5.4856 | 0 | -56.8314 | 18.398 | -49.1931 | 149.972 | -61.0354 | 149.4875 | -74.3907 | -157.4391 | -54.5367 | -35.1565 | -62.34 | -85.6219 | -53.4366 | 52.7527 | -57.4795 | -172.2872 | -53.4819 | -166.1707 | -51.6226 | -154.905 | -58.3261 | 9.9612 | -58.198 | 83.9202 | -20.301 | 153.7267 | -24.356 | -139.7236 | -31.9083 | 118.1531 | -23.6839 | 148.0185 | -21.2784 | -123.2145 | -31.8748 | -42.4113 | -36.4395 | -119.8907 | -26.4186 | -91.6861 | -68.7851 | -51.5555 | -38.6675 | -40.789 | -53.4413 | -39.9032 | -68.7647 | -54.2383 | -38.4831 | -40.6279 | -54.2764 | -39.5547 | -60.9882 | 213 | -48.267 | -52.4958 | -48.9751 | -53.1073 | -49.6639 | -48.8991 | -49.9211 | -51.2668 | 213 | -48.6224 | -32.8672 | -35.1731 | -47.9735 | -34.4354 | -63.0069 | -48.7705 | -32.7253 | -35.3034 | -47.6835 | -34.4176 | -63.2791 | -45.9396 | -33.0516 | -35.012 | -48.8086 | -34.0869 | -55.2304 | -46.0877 | -32.9097 | -35.1423 | -48.5186 | -34.0691 | -55.5026
214 | -5.62 | 0 | -5.4853 | 0 | -5.7935 | 0 | -5.4841 | 0 | -56.0074 | 66.0144 | -47.1635 | 134.7129 | -64.895 | -177.9711 | -59.9634 | 122.8164 | -55.1918 | -33.4212 | -55.6742 | -173.5601 | -51.811 | 79.8263 | -53.4949 | 138.491 | -53.2203 | 167.4018 | -50.2219 | 173.4539 | -60.1012 | 8.0864 | -55.2121 | -161.363 | -20.2639 | 140.9756 | -26.2051 | -156.5706 | -28.0739 | 98.88 | -23.6746 | 131.5486 | -20.5486 | -138.9725 | -38.8417 | -82.9629 | -35.3955 | -140.6463 | -28.4121 | -119.5567 | -77.4236 | -52.3803 | -38.6482 | -40.5096 | -52.8572 | -40.2905 | -71.3563 | -55.0748 | -38.4403 | -40.4657 | -54.7079 | -39.6607 | -56.8758 | 214 | -46.5665 | -51.8431 | -46.3957 | -52.1773 | -48.0062 | -47.6779 | -47.6992 | -50.5787 | 214 | -49.4548 | -32.8203 | -34.8896 | -47.3719 | -34.8052 | -65.5628 | -49.5895 | -32.6468 | -35.0255 | -47.0637 | -34.8064 | -65.8722 | -46.7603 | -33.0282 | -34.8457 | -49.2226 | -34.1754 | -51.0823 | -46.895 | -32.8547 | -34.9816 | -48.9144 | -34.1766 | -51.3917
215 | -5.6241 | 0 | -5.4927 | 0 | -5.8157 | 0 | -5.4874 | 0 | -50.6911 | 64.8984 | -46.7406 | 118.0731 | -61.1179 | -161.3385 | -57.4983 | 96.6632 | -54.6043 | -30.3397 | -52.8082 | 140.5757 | -48.1649 | 75.6137 | -54.4927 | 90.5576 | -55.7362 | 140.4675 | -52.5517 | 148.4958 | -61.9312 | 15.6737 | -47.8768 | 176.8944 | -21.5467 | 134.1158 | -27.5927 | -159.4712 | -27.0753 | 89.2229 | -23.7964 | 124.7569 | -21.8764 | -152.9444 | -40.3642 | 158.5191 | -31.7764 | -162.903 | -31.2425 | -159.9611 | -81.6967 | -54.1876 | -38.6054 | -40.1537 | -53.017 | -40.547 | -67.6372 | -53.3469 | -38.3624 | -40.3208 | -55.3833 | -39.6594 | -55.8396 | 215 | -45.1595 | -48.6101 | -45.4978 | -50.2341 | -46.6793 | -46.6844 | -45.9489 | -47.0741 | 215 | -47.7228 | -32.7383 | -34.5296 | -47.5243 | -35.0543 | -61.8215 | -47.8542 | -32.5467 | -34.6663 | -47.2013 | -35.0596 | -62.1498 | -48.5635 | -32.9813 | -34.6967 | -49.8906 | -34.1667 | -50.0239 | -48.6949 | -32.7897 | -34.8334 | -49.5676 | -34.172 | -50.3522
216 | -5.6398 | 0 | -5.5237 | 0 | -5.8361 | 0 | -5.5189 | 0 | -47.8644 | 47.2453 | -47.0087 | 104.3672 | -58.4506 | 177.6447 | -57.5003 | 73.5426 | -53.0412 | -33.9652 | -53.3839 | 102.9839 | -46.4749 | 59.0094 | -61.3494 | 29.6597 | -63.2953 | 122.3518 | -58.6034 | 150.3959 | -60.9468 | 36.4272 | -45.5869 | 147.4984 | -22.5057 | 141.8671 | -26.4808 | -160.0884 | -26.2574 | 87.1303 | -23.12 | 122.5275 | -24.8015 | -150.4793 | -32.7703 | 109.2708 | -28.8235 | 168.7968 | -36.135 | 136.0851 | -70.134 | -57.3604 | -38.5156 | -39.8801 | -54.0598 | -40.8526 | -64.1292 | -51.7541 | -38.2687 | -40.223 | -55.8519 | -39.6799 | -56.3994 | 216 | -44.2374 | -46.365 | -45.804 | -49.5935 | -46.2492 | -46.073 | -45.2669 | -45.3913 | 216 | -46.1143 | -32.6289 | -34.2403 | -48.5361 | -35.3289 | -58.2931 | -46.2304 | -32.4326 | -34.3612 | -48.2237 | -35.3337 | -58.6103 | -51.7206 | -32.8758 | -34.5832 | -50.3282 | -34.1562 | -50.5633 | -51.8367 | -32.6795 | -34.7041 | -50.0158 | -34.161 | -50.8805
217 | -5.6986 | 0 | -5.5647 | 0 | -5.8254 | 0 | -5.5596 | 0 | -46.9073 | 25.1657 | -47.7575 | 90.0184 | -57.7544 | 145.2768 | -59.2086 | 47.0714 | -51.668 | -45.6708 | -56.0732 | 68.1814 | -46.4241 | 40.2197 | -62.1291 | -125.9643 | -64.2985 | -123.8428 | -57.5239 | -161.2477 | -57.3591 | 33.2679 | -45.9748 | 115.7297 | -20.7623 | 150.678 | -24.6693 | -174.288 | -25.0465 | 82.1244 | -21.8427 | 117.4254 | -24.3018 | -125.8997 | -28.8648 | 81.4545 | -27.1804 | 137.6081 | -36.2389 | 40.364 | -65.6828 | -61.5607 | -38.4455 | -39.7453 | -55.2648 | -41.088 | -61.9241 | -50.7082 | -38.2572 | -40.2991 | -55.553 | -39.8098 | -56.3068 | 217 | -44.1095 | -45.4678 | -46.8976 | -49.6028 | -46.2404 | -45.786 | -45.5837 | -45.6108 | 217 | -45.0096 | -32.5586 | -34.0467 | -49.7001 | -35.5233 | -56.0987 | -45.1435 | -32.4318 | -34.1857 | -49.4394 | -35.5284 | -56.3645 | -55.8621 | -32.7469 | -34.6005 | -49.9883 | -34.2451 | -50.4814 | -55.996 | -32.6201 | -34.7395 | -49.7276 | -34.2502 | -50.7472
218 | -5.7636 | 0 | -5.5893 | 0 | -5.8108 | 0 | -5.6035 | 0 | -47.8023 | 4.2891 | -50.4597 | 79.5362 | -58.3936 | 102.9583 | -65.4687 | -14.0592 | -51.4082 | -62.0612 | -60.5589 | 18.7566 | -48.0071 | 24.1814 | -56.1937 | 178.4316 | -54.2805 | -145.2945 | -53.1352 | -162.2421 | -55.7581 | 17.0679 | -49.1836 | 81.7189 | -18.2441 | 145.1062 | -23.9056 | 162.7085 | -24.7215 | 73.2342 | -20.8289 | 109.06 | -20.3477 | -126.0203 | -27.0748 | 55.8683 | -27.405 | 108.7355 | -32.3879 | -28.0562 | -63.473 | -56.7725 | -38.4402 | -39.9691 | -55.4066 | -41.1553 | -61.1479 | -50.717 | -38.1698 | -40.5737 | -55.0464 | -40.1467 | -55.9759 | 218 | -45.6815 | -46.1795 | -49.9316 | -50.1966 | -46.5842 | -46.3195 | -47.138 | -47.3386 | 218 | -44.9534 | -32.4062 | -34.2055 | -49.8173 | -35.566 | -55.3371 | -45.1277 | -32.359 | -34.3656 | -49.5958 | -35.5518 | -55.5444 | -51.0089 | -32.6766 | -34.8101 | -49.4571 | -34.5574 | -50.1651 | -51.1832 | -32.6294 | -34.9702 | -49.2356 | -34.5432 | -50.3724
219 | -5.8067 | 0 | -5.5979 | 0 | -5.7941 | 0 | -5.6216 | 0 | -50.6104 | -5.2269 | -52.4457 | 102.1718 | -60.031 | 53.185 | -60.4584 | -160.598 | -51.9798 | -75.6427 | -60.0095 | -78.4038 | -51.3899 | 21.1393 | -55.1235 | 155.5062 | -50.9132 | 179.8704 | -51.1811 | -174.4747 | -55.5136 | 2.4027 | -57.7155 | 37.3853 | -16.7659 | 131.1732 | -24.8583 | 136.8207 | -26.0065 | 69.1161 | -20.4582 | 99.1798 | -17.8579 | -143.8075 | -26.7432 | 32.5602 | -30.0343 | 92.6655 | -29.8159 | -83.6445 | -63.6495 | -52.3809 | -38.4013 | -40.5518 | -54.1339 | -41.209 | -61.8987 | -52.4074 | -38.0489 | -40.9455 | -54.8205 | -40.6496 | -55.8422 | 219 | -48.1316 | -47.9785 | -51.1965 | -50.7937 | -47.3427 | -47.5228 | -49.0712 | -48.9944 | 219 | -46.6007 | -32.2422 | -34.7451 | -48.536 | -35.6111 | -56.1046 | -46.8095 | -32.2548 | -34.9302 | -48.3398 | -35.5874 | -56.2771 | -46.5742 | -32.5946 | -35.1388 | -49.2226 | -35.0517 | -50.0481 | -46.783 | -32.6072 | -35.3239 | -49.0264 | -35.028 | -50.2206
220 | -5.8176 | 0 | -5.6015 | 0 | -5.8346 | 0 | -5.6171 | 0 | -52.2008 | 11.3555 | -49.108 | 107.5831 | -61.7566 | 10.7778 | -54.4063 | 145.515 | -53.1072 | -86.9779 | -54.0645 | -144.9513 | -52.5878 | 48.0856 | -54.3006 | 133.2633 | -50.2997 | 146.3822 | -50.9511 | 170.5987 | -55.7138 | -9.7056 | -57.6166 | -117.3211 | -16.4924 | 115.403 | -28.2894 | 111.9091 | -27.0449 | 79.8281 | -20.4913 | 91.0824 | -17.1144 | -166.2254 | -27.6462 | 11.1842 | -32.0463 | 113.1369 | -27.829 | -134.0709 | -65.7898 | -51.5385 | -38.3653 | -40.8405 | -53.0788 | -41.5893 | -63.4882 | -53.8815 | -38.013 | -41.0194 | -54.871 | -40.9948 | -54.6367 | 220 | -47.2189 | -48.3745 | -47.0272 | -50.2322 | -47.3145 | -47.8976 | -48.7033 | -48.6178 | 220 | -48.0639 | -32.1954 | -35.0229 | -47.4773 | -35.9878 | -57.6536 | -48.28 | -32.1784 | -35.2234 | -47.2442 | -35.9722 | -57.8711 | -45.7209 | -32.5477 | -35.2018 | -49.2695 | -35.3933 | -48.8021 | -45.937 | -32.5307 | -35.4023 | -49.0364 | -35.3777 | -49.0196
221 | -5.8292 | 0 | -5.6085 | 0 | -5.8851 | 0 | -5.62 | 0 | -49.3534 | 20.7851 | -47.4803 | 95.9142 | -62.6927 | -21.115 | -52.6915 | 109.1159 | -54.7112 | -91.343 | -51.435 | 171.054 | -48.8245 | 56.3011 | -57.8964 | 105.0822 | -51.499 | 115.5483 | -52.7957 | 162.5994 | -56.5706 | -20.4688 | -49.4223 | -161.6532 | -17.3485 | 102.0151 | -38.5196 | 107.6297 | -25.3041 | 94.0986 | -20.6368 | 85.11 | -17.9583 | 171.5853 | -29.8568 | -3.6477 | -27.6117 | 121.7853 | -26.1874 | 178.1094 | -69.0077 | -52.6828 | -38.2909 | -40.621 | -52.6405 | -42.1125 | -64.3429 | -52.7445 | -38.0011 | -40.9093 | -55.2765 | -41.0336 | -54.156 | 221 | -45.2278 | -46.911 | -45.1669 | -49.5453 | -46.6129 | -46.8689 | -47.3757 | -46.8389 | 221 | -46.9153 | -32.1719 | -34.7918 | -47.032 | -36.504 | -58.4578 | -47.136 | -32.116 | -35.001 | -46.7554 | -36.4925 | -58.7229 | -46.8536 | -32.4617 | -35.0801 | -49.668 | -35.4251 | -48.2709 | -47.0743 | -32.4058 | -35.2893 | -49.3914 | -35.4136 | -48.536
222 | -5.8132 | 0 | -5.6274 | 0 | -5.9535 | 0 | -5.6247 | 0 | -46.7185 | 9.2878 | -46.8576 | 84.4865 | -64.6898 | -36.7446 | -52.9126 | 79.0611 | -55.4117 | -86.1546 | -51.0961 | 135.8258 | -46.2664 | 43.3823 | -66.5412 | -166.1929 | -54.6775 | 89.572 | -54.28 | 176.4454 | -57.9089 | -23.2294 | -46.3389 | 165.1934 | -19.1226 | 95.4406 | -33.2407 | -148.612 | -22.5948 | 91.088 | -20.5975 | 78.2214 | -20.7378 | 155.3553 | -31.6955 | -6.1657 | -24.4989 | 103.1183 | -25.4196 | 134.4402 | -71.2609 | -55.1847 | -38.2514 | -40.2414 | -52.9758 | -42.6378 | -63.3618 | -51.0394 | -37.985 | -40.7641 | -55.8852 | -41.1136 | -53.9314 | 222 | -43.7421 | -45.3345 | -44.7494 | -49.5919 | -45.646 | -45.3797 | -45.6563 | -45.4886 | 222 | -45.2262 | -32.1718 | -34.4282 | -47.3484 | -37.0104 | -57.4083 | -45.412 | -32.0315 | -34.6167 | -47.0223 | -37.0131 | -57.7371 | -49.3715 | -32.4382 | -34.9509 | -50.2578 | -35.4862 | -47.9779 | -49.5573 | -32.2979 | -35.1394 | -49.9317 | -35.4889 | -48.3067
223 | -5.8167 | 0 | -5.6575 | 0 | -5.9799 | 0 | -5.6571 | 0 | -45.6158 | -8.8529 | -46.8257 | 70.8681 | -64.4097 | -16.7045 | -54.8256 | 49.8378 | -54.2921 | -84.4657 | -52.2931 | 105.854 | -45.5656 | 24.8876 | -53.1442 | -170.9208 | -61.3021 | 83.9033 | -52.0476 | -172.899 | -57.8303 | -16.9987 | -45.9263 | 132.5416 | -20.4905 | 102.1215 | -26.421 | -166.5752 | -21.0414 | 78.8044 | -20.8449 | 69.6348 | -24.4853 | 163.2565 | -31.7451 | -8.4604 | -23.5474 | 79.5591 | -25.6924 | 93.1892 | -67.248 | -58.8673 | -38.1963 | -39.9551 | -53.9707 | -43.1252 | -61.3138 | -49.8198 | -37.9066 | -40.6653 | -56.2317 | -41.2221 | -52.5945 | 223 | -43.1359 | -44.6273 | -45.2347 | -50.0077 | -44.769 | -44.4794 | -44.3607 | -45.5381 | 223 | -44.0031 | -32.0899 | -34.1384 | -48.3132 | -37.4677 | -55.3339 | -44.1623 | -31.9267 | -34.298 | -47.9908 | -37.4681 | -55.6567 | -53.0506 | -32.3796 | -34.8486 | -50.5742 | -35.5646 | -46.6146 | -53.2098 | -32.2164 | -35.0082 | -50.2518 | -35.565 | -46.9374
224 | -5.8491 | 0 | -5.6592 | 0 | -5.9624 | 0 | -5.6946 | 0 | -45.991 | -27.6611 | -48.0803 | 57.6874 | -58.7795 | -19.0615 | -59.8962 | 13.8013 | -52.8489 | -91.9826 | -55.3276 | 74.7523 | -46.4266 | 9.2048 | -49.745 | 155.9003 | -60.3093 | 139.0209 | -50.1605 | -179.1821 | -55.8952 | -19.9837 | -48.2253 | 102.9807 | -19.6223 | 110.9491 | -23.8836 | 171.9888 | -21.4936 | 63.9072 | -21.7758 | 59.005 | -22.8443 | -173.0651 | -31.0243 | -28.6531 | -24.8082 | 56.873 | -27.2776 | 54.98 | -63.0739 | -58.2404 | -38.1583 | -39.8864 | -54.8786 | -43.3654 | -59.8194 | -49.3882 | -37.7514 | -40.6553 | -55.9522 | -41.4038 | -51.0144 | 224 | -43.7619 | -45.0329 | -47.0963 | -50.2474 | -44.6465 | -44.5619 | -44.5235 | -47.316 | 224 | -43.5391 | -31.9023 | -34.0373 | -49.2194 | -37.7062 | -53.857 | -43.729 | -31.789 | -34.1918 | -48.9162 | -37.6708 | -54.1248 | -52.3913 | -32.3092 | -34.8062 | -50.293 | -35.7446 | -45.052 | -52.5812 | -32.1959 | -34.9607 | -49.9898 | -35.7092 | -45.3198
225 | -5.8681 | 0 | -5.6631 | 0 | -5.9285 | 0 | -5.6806 | 0 | -48.007 | -41.1099 | -50.5688 | 58.6869 | -55.5159 | -42.9735 | -67.6592 | -143.7873 | -51.9793 | -104.5562 | -64.2562 | 26.2635 | -48.6356 | 2.1013 | -50.3907 | 131.2696 | -54.3192 | 122.9425 | -49.6998 | 175.5381 | -54.4856 | -32.9858 | -54.0328 | 83.1619 | -17.9381 | 108.4453 | -23.3405 | 154.8252 | -23.7355 | 60.5802 | -23.8774 | 49.2227 | -19.556 | 178.7032 | -30.7603 | -64.8461 | -28.8197 | 47.7351 | -30.4343 | 16.4021 | -61.691 | -53.3861 | -38.0718 | -40.2066 | -54.7301 | -43.3432 | -59.2842 | -50.3895 | -37.5361 | -40.8115 | -55.3662 | -41.8191 | -49.9452 | 225 | -45.6219 | -46.5102 | -50.3062 | -50.2122 | -45.7627 | -45.5336 | -46.2331 | -49.5039 | 225 | -44.5214 | -31.668 | -34.3385 | -49.067 | -37.6801 | -53.3557 | -44.7264 | -31.6076 | -34.526 | -48.8016 | -37.6626 | -53.6036 | -47.518 | -32.2037 | -34.9434 | -49.7031 | -36.156 | -44.0167 | -47.723 | -32.1433 | -35.1309 | -49.4377 | -36.1385 | -44.2646
226 | -5.8964 | 0 | -5.6604 | 0 | -5.9138 | 0 | -5.6544 | 0 | -50.5799 | -35.7091 | -50.3129 | 72.0229 | -54.7756 | -69.5067 | -55.3228 | 146.9337 | -51.6764 | -119.6958 | -61.1346 | -151.5614 | -50.2997 | 14.2096 | -52.0231 | 123.4088 | -52.7293 | 89.9702 | -48.9857 | 174.2015 | -53.8522 | -48.1675 | -65.0347 | 153.0399 | -17.0013 | 98.4508 | -23.5665 | 143.543 | -24.472 | 81.7684 | -28.094 | 50.7281 | -18.1234 | 158.1824 | -30.5061 | -118.2706 | -29.876 | 90.2649 | -36.888 | -29.2005 | -62.489 | -51.2034 | -37.9829 | -40.6531 | -53.9265 | -43.4886 | -59.3166 | -52.4646 | -37.4472 | -41.0315 | -54.9065 | -42.1638 | -49.6569 | 226 | -46.6989 | -47.3322 | -48.857 | -49.6266 | -46.7895 | -45.8364 | -47.1623 | -50.1025 | 226 | -46.5682 | -31.5508 | -34.7567 | -48.2661 | -37.8282 | -53.4028 | -46.8042 | -31.5334 | -34.9987 | -48.0127 | -37.8342 | -53.6622 | -45.307 | -32.0865 | -35.1351 | -49.2461 | -36.5034 | -43.7431 | -45.543 | -32.0691 | -35.3771 | -48.9927 | -36.5094 | -44.0025
227 | -5.893 | 0 | -5.6694 | 0 | -5.9885 | 0 | -5.6798 | 0 | -49.3452 | -19.7647 | -48.8521 | 73.1692 | -55.768 | -91.0423 | -51.6292 | 109.784 | -52.1147 | -135.3049 | -54.275 | 162.7159 | -48.0851 | 26.1002 | -54.0025 | 124.816 | -54.0925 | 58.2178 | -47.7078 | 171.2361 | -53.8777 | -66.7499 | -52.2075 | 179.8614 | -17.2294 | 87.1774 | -23.6833 | 140.1166 | -21.2243 | 90.5889 | -31.5061 | 86.856 | -18.7032 | 136.2855 | -29.2874 | -172.2118 | -24.2539 | 87.6662 | -44.1032 | -110.093 | -64.3887 | -51.1842 | -37.8974 | -40.791 | -53.291 | -44.0241 | -59.2671 | -53.4689 | -37.4438 | -41.1343 | -54.7749 | -42.3205 | -50.2821 | 227 | -45.638 | -46.0828 | -46.2646 | -49.0199 | -46.3046 | -44.3666 | -45.6951 | -48.5365 | 227 | -47.5759 | -31.5508 | -34.898 | -47.6216 | -38.3547 | -53.2786 | -47.7995 | -31.4553 | -35.1112 | -47.3025 | -38.3443 | -53.5873 | -45.2912 | -32.0044 | -35.2413 | -49.1055 | -36.6511 | -44.2936 | -45.5148 | -31.9089 | -35.4545 | -48.7864 | -36.6407 | -44.6023
228 | -5.8832 | 0 | -5.6889 | 0 | -6.042 | 0 | -5.6992 | 0 | -46.4795 | -24.079 | -47.3737 | 69.1133 | -58.5412 | -110.6581 | -50.6055 | 77.9614 | -53.1454 | -147.715 | -52.4958 | 127.0559 | -45.3816 | 17.7133 | -53.3865 | 150.1088 | -58.7081 | 36.5118 | -46.3589 | 164.0025 | -55.0853 | -85.9844 | -47.81 | 153.9189 | -18.5254 | 80.5444 | -22.9251 | 137.1543 | -18.667 | 80.6628 | -28.0478 | 117.3559 | -21.3538 | 120.2802 | -28.2388 | 139.8616 | -21.8416 | 62.6497 | -44.395 | -162.5671 | -65.5839 | -52.1792 | -37.8641 | -40.6229 | -53.0761 | -44.7221 | -58.6381 | -52.3936 | -37.4223 | -41.0483 | -55.0171 | -42.4561 | -51.2769 | 228 | -43.7469 | -44.4323 | -44.8632 | -49.2537 | -44.5725 | -42.5814 | -43.539 | -46.7768 | 228 | -46.5104 | -31.5391 | -34.7397 | -47.3872 | -39.0332 | -52.5961 | -46.7047 | -31.3803 | -34.9237 | -47.0341 | -39.0229 | -52.9389 | -46.296 | -31.9809 | -35.1651 | -49.3282 | -36.7672 | -45.2349 | -46.4903 | -31.8221 | -35.3491 | -48.9751 | -36.7569 | -45.5777
229 | -5.8764 | 0 | -5.7287 | 0 | -6.0859 | 0 | -5.7224 | 0 | -44.7781 | -40.6034 | -46.2221 | 58.7595 | -65.9111 | -108.1061 | -51.35 | 47.7196 | -54.3917 | -155.7365 | -53.4754 | 92.5001 | -44.1826 | 0.2996 | -48.6954 | 149.8192 | -65.2325 | 84.2048 | -45.5159 | 151.632 | -57.8333 | -98.8534 | -46.8249 | 122.6371 | -19.9565 | 85.4835 | -22.1576 | 129.8907 | -17.7498 | 65.5242 | -24.7682 | 120.3843 | -25.0817 | 129.0965 | -28.6414 | 97.4827 | -21.9396 | 32.9872 | -38.4771 | -148.3903 | -62.8619 | -53.3754 | -37.869 | -40.3815 | -53.3502 | -45.4848 | -57.5725 | -50.793 | -37.4272 | -40.924 | -55.6467 | -42.8086 | -51.0043 | 229 | -42.4106 | -43.5412 | -44.4749 | -50.7643 | -42.842 | -41.6813 | -42.0511 | -46.4359 | 229 | -44.9166 | -31.5508 | -34.5051 | -47.6215 | -39.7561 | -51.4866 | -45.0643 | -31.3413 | -34.6591 | -47.2643 | -39.7624 | -51.8501 | -47.499 | -31.9926 | -35.0476 | -49.918 | -37.0799 | -44.9184 | -47.6467 | -31.7831 | -35.2016 | -49.5608 | -37.0862 | -45.2819
230 | -5.9004 | 0 | -5.744 | 0 | -6.0689 | 0 | -5.7465 | 0 | -44.6299 | -59.6622 | -46.2756 | 46.2086 | -63.7564 | -31.3649 | -54.5515 | 15.4933 | -55.1424 | -160.5121 | -58.3251 | 53.9769 | -44.4815 | -18.0272 | -46.3396 | 129.0555 | -55.9878 | 103.7899 | -45.7461 | 138.4308 | -60.8717 | -90.4266 | -49.0297 | 91.0962 | -19.3488 | 96.976 | -21.9829 | 120.3845 | -18.2712 | 52.9496 | -22.7111 | 118.8253 | -22.959 | 150.9941 | -31.6586 | 56.8379 | -24.8834 | 1.2871 | -30.888 | -160.8012 | -60.0334 | -53.3349 | -37.846 | -40.2873 | -53.8693 | -45.9599 | -56.6151 | -50.0689 | -37.416 | -40.8221 | -56.1424 | -43.3775 | -49.4559 | 230 | -42.3335 | -43.8719 | -45.4437 | -53.0523 | -42.1196 | -42.0009 | -42.0507 | -48.0023 | 230 | -44.1685 | -31.5156 | -34.3869 | -48.1253 | -40.2159 | -50.5462 | -44.3249 | -31.3471 | -34.5408 | -47.8004 | -40.2134 | -50.8686 | -47.4345 | -31.9456 | -34.9217 | -50.3984 | -37.6335 | -43.387 | -47.5909 | -31.7771 | -35.0756 | -50.0735 | -37.631 | -43.7094
231 | -5.9471 | 0 | -5.7454 | 0 | -6.0268 | 0 | -5.7581 | 0 | -46.0762 | -75.5531 | -47.2249 | 37.5852 | -57.2369 | -36.1776 | -66.4448 | -17.5722 | -55.5322 | -166.0199 | -70.0739 | -89.1591 | -46.2766 | -31.0631 | -46.6 | 108.918 | -51.042 | 75.5752 | -47.3577 | 131.2483 | -59.4699 | -76.6141 | -55.5323 | 65.7758 | -17.3021 | 97.3982 | -22.5574 | 115.0553 | -19.46 | 49.9007 | -21.0429 | 115.5515 | -19.6211 | 140.1987 | -44.6673 | -14.3844 | -36.2422 | -42.0592 | -26.0362 | 173.8118 | -58.8825 | -51.6677 | -37.8107 | -40.4918 | -54.2379 | -46.0232 | -56.1321 | -50.7221 | -37.4393 | -40.929 | -56.097 | -43.8549 | -48.2497 | 231 | -43.4183 | -45.5742 | -47.151 | -53.201 | -42.7316 | -43.6579 | -43.6602 | -49.2833 | 231 | -44.775 | -31.4922 | -34.5447 | -48.4925 | -40.2778 | -50.1053 | -44.9767 | -31.4125 | -34.7337 | -48.2111 | -40.2651 | -50.374 | -45.7206 | -31.8636 | -34.9819 | -50.3516 | -38.1095 | -42.2229 | -45.9223 | -31.7839 | -35.1709 | -50.0702 | -38.0968 | -42.4916
232 | -6.01 | 0 | -5.7449 | 0 | -6.0135 | 0 | -5.7683 | 0 | -48.4896 | -78.8261 | -48.4861 | 36.0145 | -54.2629 | -48.0705 | -59.1021 | 129.6839 | -55.9124 | -172.5569 | -55.8371 | -169.1467 | -48.878 | -29.8628 | -48.1131 | 99.6594 | -49.2021 | 40.0971 | -48.1864 | 140.4399 | -57.1703 | -84.2626 | -66.5093 | -151.1175 | -15.8537 | 88.533 | -22.7893 | 116.6843 | -19.3158 | 54.3849 | -19.6566 | 109.3525 | -18.3582 | 116.6703 | -32.6799 | -174.8797 | -28.829 | 126.6299 | -23.4937 | 144.2267 | -59.2921 | -50.5021 | -37.7524 | -40.8428 | -54.2608 | -46.2482 | -56.0613 | -52.2596 | -37.4279 | -41.1746 | -55.5926 | -43.994 | -48.1777 | 232 | -44.938 | -47.4589 | -47.4453 | -50.4972 | -43.9355 | -45.2216 | -45.1077 | -48.4897 | 232 | -46.2496 | -31.4179 | -34.8328 | -48.5159 | -40.5033 | -50.0478 | -46.5147 | -31.4144 | -35.0745 | -48.2473 | -40.4799 | -50.293 | -44.4921 | -31.7424 | -35.1646 | -49.8477 | -38.2491 | -42.1642 | -44.7572 | -31.7389 | -35.4063 | -49.5791 | -38.2257 | -42.4094
233 | -6.0295 | 0 | -5.7841 | 0 | -6.0498 | 0 | -5.7974 | 0 | -49.0407 | -66.9243 | -49.1634 | 44.7895 | -52.5295 | -61.7294 | -52.2228 | 97.4962 | -56.4413 | -178.3084 | -51.3703 | 155.0185 | -48.5577 | -14.3232 | -49.6954 | 103.3758 | -49.7002 | 2.9249 | -46.2542 | 145.1729 | -55.8356 | -102.6672 | -51.3639 | -172.5198 | -15.4937 | 76.9842 | -21.728 | 117.9226 | -17.8604 | 51.1006 | -18.7686 | 101.7609 | -19.3755 | 90.7599 | -26.4846 | 146.1598 | -22.3683 | 88.7963 | -23.1089 | 115.2632 | -60.4101 | -50.0459 | -37.7309 | -40.9992 | -54.0498 | -46.8155 | -56.0243 | -53.6548 | -37.3537 | -41.3953 | -55.1471 | -43.9541 | -49.4763 | 233 | -45.2026 | -46.8329 | -45.9495 | -48.1963 | -44.5124 | -43.9536 | -43.7963 | -46.8554 | 233 | -47.6253 | -31.3242 | -34.9697 | -48.2657 | -41.0314 | -49.9745 | -47.8707 | -31.3039 | -35.2018 | -48 | -41.0181 | -50.2269 | -44.0164 | -31.7014 | -35.3658 | -49.363 | -38.17 | -43.4265 | -44.2618 | -31.6811 | -35.5979 | -49.0973 | -38.1567 | -43.6789
234 | -6.0072 | 0 | -5.8251 | 0 | -6.1002 | 0 | -5.8295 | 0 | -46.9347 | -63.5179 | -47.435 | 52.9087 | -51.695 | -72.486 | -49.6018 | 65.9921 | -56.9216 | 178.2502 | -49.5886 | 122.2385 | -45.9308 | -14.5718 | -48.8653 | 116.4799 | -52.7672 | -36.4181 | -44.2994 | 137.4333 | -55.8057 | -127.0499 | -47.2039 | 158.5972 | -16.0692 | 67.3484 | -20.4104 | 111.8 | -16.9517 | 39.0316 | -18.4513 | 94.458 | -22.7273 | 65.8963 | -24.0414 | 112.7771 | -20.0561 | 57.1197 | -24.6298 | 86.5276 | -60.3014 | -49.7858 | -37.732 | -40.9288 | -54.0089 | -47.7062 | -55.7897 | -53.9624 | -37.2259 | -41.4599 | -55.0185 | -44.0921 | -52.0483 | 234 | -43.4607 | -44.7825 | -43.9789 | -47.0347 | -43.5857 | -41.8504 | -41.6001 | -45.6941 | 234 | -47.9552 | -31.2187 | -34.9216 | -48.1838 | -41.8811 | -49.6895 | -48.1373 | -31.1257 | -35.0993 | -47.9087 | -41.8767 | -49.9602 | -43.7786 | -31.7248 | -35.4527 | -49.1934 | -38.267 | -45.9481 | -43.9607 | -31.6318 | -35.6304 | -48.9183 | -38.2626 | -46.2188
235 | -5.986 | 0 | -5.8487 | 0 | -6.1318 | 0 | -5.8256 | 0 | -45.0062 | -75.0006 | -45.0738 | 46.1091 | -51.1765 | -80.811 | -49.0215 | 34.6253 | -56.7357 | 176.4166 | -49.8947 | 90.4631 | -44.1827 | -28.8004 | -45.8857 | 115.9779 | -62.8851 | -87.5023 | -43.3224 | 123.3294 | -57.6054 | -155.1276 | -46.3161 | 129.8074 | -17.1483 | 63.4287 | -19.821 | 100.5955 | -17.3178 | 22.7607 | -18.5761 | 89.3375 | -32.3697 | 62.5726 | -23.7546 | 81.47 | -20.1025 | 28.1584 | -30.3381 | 61.6632 | -58.3138 | -49.5499 | -37.7635 | -40.7591 | -54.2942 | -48.7413 | -55.3917 | -52.8349 | -37.111 | -41.4073 | -55.2706 | -44.6161 | -54.1553 | 235 | -41.5308 | -43.3512 | -42.6871 | -46.9913 | -41.9062 | -40.6329 | -40.1919 | -45.9166 | 235 | -46.8489 | -31.125 | -34.7731 | -48.4455 | -42.8926 | -49.2599 | -46.9862 | -30.9792 | -34.9335 | -48.1624 | -42.9157 | -49.5661 | -43.5639 | -31.7775 | -35.4213 | -49.4219 | -38.7674 | -48.0235 | -43.7012 | -31.6317 | -35.5817 | -49.1388 | -38.7905 | -48.3297
236 | -5.9849 | 0 | -5.8405 | 0 | -6.1143 | 0 | -5.8359 | 0 | -44.5049 | -91.8278 | -44.1925 | 31.4384 | -50.5014 | -85.9082 | -50.4749 | 2.9466 | -55.7854 | 170.5732 | -52.7092 | 59.1727 | -43.9669 | -47.0318 | -43.9951 | 100.2763 | -57.6653 | 94.7003 | -43.5789 | 108.7047 | -63.3767 | 175.8676 | -48.1978 | 106.6081 | -17.6087 | 66.9484 | -20.4269 | 90.4574 | -19.4327 | 9.449 | -18.5266 | 88.5373 | -27.7463 | 147.6313 | -26.3161 | 52.4161 | -22.6435 | 3.6459 | -37.3573 | 167.7978 | -56.5047 | -49.3215 | -37.7507 | -40.7039 | -54.743 | -49.4387 | -55.1686 | -51.7588 | -37.0747 | -41.3522 | -55.7116 | -45.5986 | -52.3956 | 236 | -40.8389 | -43.2749 | -42.806 | -47.7192 | -40.8787 | -40.7346 | -40.0497 | -47.6159 | 236 | -45.7739 | -31.0898 | -34.719 | -48.9025 | -43.5982 | -49.0543 | -45.9183 | -30.9604 | -34.868 | -48.6287 | -43.6028 | -49.3327 | -43.3366 | -31.7658 | -35.3673 | -49.8711 | -39.7581 | -46.2813 | -43.481 | -31.6364 | -35.5163 | -49.5973 | -39.7627 | -46.5597
237 | -6.0127 | 0 | -5.8467 | 0 | -6.0748 | 0 | -5.8398 | 0 | -45.3548 | -107.9555 | -44.7224 | 17.4843 | -49.6424 | -92.365 | -54.9827 | -28.8499 | -55.0206 | 159.1581 | -59.9412 | 27.2095 | -45.0998 | -63.9801 | -43.9692 | 80.6405 | -49.7998 | 52.1449 | -44.9285 | 99.6453 | -76.3728 | -73.2717 | -51.9818 | 101.8392 | -16.8762 | 68.0151 | -21.7707 | 87.8718 | -23.0984 | 11.6966 | -17.9867 | 89.2392 | -21.6606 | 127.9424 | -34.8355 | 42.2963 | -28.1727 | 0.0421 | -25.0406 | 160.8154 | -55.8429 | -49.2702 | -37.6027 | -40.8859 | -54.8312 | -49.4226 | -55.46 | -51.6724 | -37.126 | -41.3819 | -55.9756 | -46.5357 | -50.2506 | 237 | -41.3247 | -44.5021 | -44.2138 | -48.2335 | -40.89 | -42.0014 | -41.047 | -47.7389 | 237 | -45.6597 | -31.1133 | -34.8732 | -48.9845 | -43.5759 | -49.3852 | -45.8257 | -31.0512 | -35.0461 | -48.7564 | -43.5828 | -49.6202 | -43.2575 | -31.59 | -35.3692 | -50.1289 | -40.689 | -44.1758 | -43.4235 | -31.5279 | -35.5421 | -49.9008 | -40.6959 | -44.4108
238 | -6.067 | 0 | -5.8623 | 0 | -6.0652 | 0 | -5.8635 | 0 | -47.382 | -116.575 | -46.3531 | 10.8207 | -49.0616 | -99.5293 | -72.8314 | -28.2449 | -54.7256 | 145.2514 | -66.7079 | -173.9923 | -47.599 | -72.4182 | -45.883 | 66.5883 | -46.5765 | 14.7993 | -46.0308 | 103.2369 | -61.264 | -79.4231 | -53.9739 | 127.8675 | -16.0497 | 62.1584 | -22.1034 | 97.3353 | -23.6116 | 36.5845 | -16.9446 | 85.3748 | -19.9877 | 99.6274 | -31.7762 | 134.1575 | -28.3099 | 42.0836 | -20.9182 | 133.4367 | -56.1632 | -49.3661 | -37.4577 | -41.2062 | -54.8351 | -49.3544 | -55.8389 | -52.1707 | -37.192 | -41.5264 | -56.0264 | -46.9715 | -49.3347 | 238 | -42.6888 | -46.6368 | -46.3036 | -47.9605 | -41.8586 | -43.6582 | -42.6161 | -45.7269 | 238 | -46.1037 | -31.125 | -35.1392 | -48.9728 | -43.4921 | -49.7737 | -46.3084 | -31.1268 | -35.3427 | -48.7699 | -43.4909 | -49.9754 | -43.2991 | -31.3907 | -35.4594 | -50.1641 | -41.1092 | -43.2695 | -43.5038 | -31.3925 | -35.6629 | -49.9612 | -41.108 | -43.4712
239 | -6.0913 | 0 | -5.8978 | 0 | -6.0896 | 0 | -5.9135 | 0 | -48.8801 | -110.0862 | -47.7911 | 20.8085 | -48.3943 | -106.9633 | -57.1364 | 73.8777 | -54.8378 | 132.5589 | -55.2971 | 153.8904 | -49.5843 | -62.4741 | -48.989 | 73.6732 | -45.6885 | -20.5597 | -44.9337 | 107.9539 | -56.9494 | -108.3771 | -50.3916 | 141.2585 | -15.9745 | 52.8927 | -20.1893 | 101.6491 | -20.7958 | 39.239 | -16.3227 | 77.2097 | -21.0532 | 70.8462 | -24.6558 | 113.152 | -23.7851 | 36.1959 | -19.8002 | 105.8258 | -56.7588 | -49.3845 | -37.3414 | -41.4115 | -55.0865 | -49.6143 | -55.6803 | -52.8033 | -37.1929 | -41.6244 | -55.8036 | -47.0837 | -49.8326 | 239 | -43.561 | -47.4094 | -46.6723 | -46.8384 | -42.9574 | -43.4551 | -42.6867 | -44.1858 | 239 | -46.712 | -31.1016 | -35.3202 | -49.1887 | -43.7165 | -49.5907 | -46.9055 | -31.1033 | -35.498 | -48.9969 | -43.7008 | -49.7668 | -43.2932 | -31.2501 | -35.5331 | -49.9058 | -41.1859 | -43.743 | -43.4867 | -31.2518 | -35.7109 | -49.714 | -41.1702 | -43.9191
240 | -6.085 | 0 | -5.9488 | 0 | -6.118 | 0 | -5.9388 | 0 | -47.8192 | -102.9594 | -45.8706 | 33.3518 | -48.1219 | -114.8396 | -51.83 | 43.5366 | -55.1113 | 119.9105 | -51.6115 | 124.837 | -47.9712 | -52.3266 | -47.8711 | 98.6623 | -46.6021 | -54.6435 | -43.2819 | 101.5142 | -55.268 | -140.5722 | -47.4058 | 131.2239 | -16.7509 | 45.0458 | -18.308 | 94.0553 | -19.5624 | 26.8319 | -16.4179 | 68.3385 | -25.0444 | 45.6972 | -22.1065 | 84.7031 | -22.2705 | 14.0352 | -20.6701 | 79.969 | -56.4341 | -48.9839 | -37.294 | -41.4489 | -55.8455 | -50.2174 | -55.1034 | -53.1062 | -37.1162 | -41.65 | -55.4426 | -47.2895 | -51.8447 | 240 | -42.3799 | -45.8226 | -44.0517 | -45.9529 | -42.6642 | -41.8114 | -40.8901 | -43.664 | 240 | -47.0212 | -31.0312 | -35.3639 | -49.8967 | -44.2686 | -48.9854 | -47.1574 | -30.9982 | -35.5101 | -49.7275 | -44.2786 | -49.1646 | -42.8989 | -31.209 | -35.565 | -49.4938 | -41.3407 | -45.7267 | -43.0351 | -31.176 | -35.7112 | -49.3246 | -41.3507 | -45.9059
241 | -6.0658 | 0 | -5.983 | 0 | -6.1126 | 0 | -5.9716 | 0 | -46.1017 | -109.4605 | -42.8941 | 27.4354 | -48.0255 | -123.7674 | -50.046 | 9.3826 | -55.559 | 109.0711 | -50.6365 | 97.6378 | -45.8675 | -60.4373 | -43.9309 | 98.6325 | -49.5843 | -86.3537 | -42.3787 | 87.6561 | -55.3809 | -173.3589 | -46.3834 | 112.8587 | -18.0053 | 43.1901 | -17.4306 | 81.4143 | -20.3623 | 12.2261 | -17.2499 | 62.5564 | -36.9936 | 57.5689 | -22.0276 | 52.5274 | -23.326 | -11.6238 | -24.4626 | 59.4277 | -55.4362 | -48.3548 | -37.2338 | -41.4049 | -56.6823 | -51.1908 | -54.6744 | -52.5813 | -36.9916 | -41.6236 | -55.2018 | -47.7962 | -55.6867 | 241 | -40.3787 | -44.2931 | -41.556 | -45.6586 | -41.1154 | -40.6238 | -39.1624 | -44.33 | 241 | -46.5155 | -30.9258 | -35.3391 | -50.6993 | -45.2078 | -48.5618 | -46.5983 | -30.879 | -35.4333 | -50.5697 | -45.2192 | -48.7028 | -42.289 | -31.168 | -35.5578 | -49.2188 | -41.8132 | -49.5741 | -42.3718 | -31.1212 | -35.652 | -49.0892 | -41.8246 | -49.7151
242 | -6.0821 | 0 | -5.9744 | 0 | -6.1189 | 0 | -5.9551 | 0 | -45.262 | -121.3368 | -41.4598 | 10.1732 | -48.2904 | -130.2497 | -50.6206 | -27.9017 | -55.6574 | 99.6176 | -52.0174 | 74.1424 | -45.0185 | -76.6616 | -41.628 | 82.0392 | -58.4481 | -112.0755 | -42.6999 | 72.7566 | -57.1614 | 155.6031 | -47.4714 | 95.5682 | -18.4729 | 47.9784 | -17.634 | 69.6489 | -23.0824 | 5.4474 | -18.0316 | 64.3719 | -27.7857 | 130.6894 | -24.8713 | 16.9282 | -27.6252 | -30.5026 | -32.6282 | 94.1303 | -54.8846 | -47.9744 | -37.1446 | -41.4549 | -56.4471 | -52.5134 | -54.8885 | -51.7165 | -36.8868 | -41.6267 | -55.2049 | -48.615 | -58.6539 | 242 | -39.3536 | -43.8555 | -40.6346 | -46.2294 | -39.9287 | -40.5991 | -38.5281 | -46.7259 | 242 | -45.6344 | -30.8047 | -35.3728 | -50.4727 | -46.539 | -48.7696 | -45.7421 | -30.7679 | -35.4998 | -50.3282 | -46.5583 | -48.9334 | -41.8923 | -31.0625 | -35.5446 | -49.2305 | -42.6406 | -52.535 | -42 | -31.0257 | -35.6716 | -49.086 | -42.6599 | -52.6988
243 | -6.1347 | 0 | -5.9466 | 0 | -6.1102 | 0 | -5.9555 | 0 | -45.4275 | -134.5711 | -41.6698 | -8.1073 | -48.7142 | -131.8712 | -53.6567 | -70.88 | -55.542 | 87.8103 | -55.5821 | 61.0904 | -45.5022 | -95.579 | -41.2325 | 62.3143 | -56.3864 | 11.5919 | -44.0876 | 62.9501 | -61.0422 | 126.5424 | -50.2717 | 90.0522 | -17.6692 | 49.5603 | -18.3457 | 63.5571 | -25.4269 | 23.1741 | -17.5424 | 68.8003 | -22.7265 | 106.6275 | -34.1065 | -43.3576 | -33.7167 | 3.0676 | -24.056 | 133.1214 | -54.8489 | -48.0945 | -37.0565 | -41.6458 | -55.6379 | -53.5281 | -55.513 | -51.2977 | -36.9042 | -41.7903 | -55.5247 | -49.286 | -56.6607 | 243 | -39.5788 | -44.4663 | -41.2405 | -47.2119 | -39.7568 | -41.6767 | -39.0762 | -49.0385 | 243 | -45.163 | -30.7695 | -35.5111 | -49.6913 | -47.5815 | -49.4028 | -45.3511 | -30.794 | -35.6903 | -49.5277 | -47.5726 | -49.5575 | -41.9598 | -30.9218 | -35.6556 | -49.5781 | -43.3394 | -50.5505 | -42.1479 | -30.9463 | -35.8348 | -49.4145 | -43.3305 | -50.7052
244 | -6.1567 | 0 | -5.9717 | 0 | -6.1376 | 0 | -5.9942 | 0 | -46.639 | -145.2852 | -43.4951 | -21.8876 | -48.3089 | -130.03 | -59.7266 | -141.5013 | -55.9106 | 72.6337 | -60.6226 | 87.3474 | -47.8018 | -112.5437 | -42.6871 | 45.7527 | -47.9501 | -18.9465 | -45.4742 | 63.3226 | -70.6004 | 107.3577 | -52.2193 | 106.9263 | -16.9359 | 43.3377 | -18.5289 | 63.1465 | -23.3873 | 37.8414 | -16.2724 | 66.3385 | -21.6052 | 77.7654 | -28.3952 | 170.631 | -28.2084 | 27.0465 | -19.3949 | 115.8206 | -55.2099 | -48.5477 | -36.9496 | -41.8779 | -55.081 | -54.0125 | -56.1084 | -51.3954 | -36.9145 | -42.0459 | -55.9678 | -49.6805 | -54.8873 | 244 | -40.9065 | -45.9669 | -43.3115 | -47.4013 | -40.6306 | -43.4652 | -40.5446 | -46.5525 | 244 | -45.2387 | -30.7578 | -35.7212 | -49.1093 | -48.0408 | -49.9708 | -45.4237 | -30.7769 | -35.8837 | -48.9434 | -48.0183 | -50.1142 | -42.391 | -30.7929 | -35.8892 | -49.9961 | -43.7088 | -48.7497 | -42.576 | -30.812 | -36.0517 | -49.8302 | -43.6863 | -48.8931
245 | -6.148 | 0 | -6.0065 | 0 | -6.1489 | 0 | -6.0492 | 0 | -48.2353 | -144.9832 | -46.4445 | -18.0079 | -46.9898 | -131.4123 | -57.6388 | 108.6348 | -57.1988 | 58.8608 | -55.5726 | 118.2895 | -52.2117 | -112.1765 | -45.521 | 46.0797 | -45.0828 | -52.8853 | -45.1922 | 68.4817 | -68.5803 | -136.7443 | -49.8832 | 122.4459 | -17.0753 | 33.4863 | -17.6895 | 59.9615 | -21.4802 | 31.2165 | -15.4645 | 56.9709 | -23.1797 | 46.9566 | -21.8719 | 128.7341 | -25.2787 | 7.1973 | -17.7473 | 91.8661 | -55.8931 | -48.934 | -36.8315 | -42.065 | -55.0454 | -54.3324 | -56.3776 | -51.688 | -36.8707 | -42.2916 | -56.319 | -49.9028 | -54.7696 | 245 | -42.3892 | -47.2952 | -45.6592 | -46.077 | -41.8653 | -44.3888 | -41.6384 | -43.8261 | 245 | -45.54 | -30.7227 | -35.917 | -49.0389 | -48.3259 | -50.2287 | -45.6815 | -30.7218 | -36.0158 | -48.8965 | -48.2832 | -50.3284 | -42.786 | -30.6835 | -36.1436 | -50.3125 | -43.8963 | -48.6207 | -42.9275 | -30.6826 | -36.2424 | -50.1701 | -43.8536 | -48.7204
246 | -6.1426 | 0 | -6.068 | 0 | -6.1677 | 0 | -6.0627 | 0 | -47.7269 | -137.2149 | -45.7714 | 4.6847 | -45.8828 | -140.5057 | -52.8443 | 53.5482 | -59.1593 | 56.029 | -51.2887 | 107.2765 | -52.5303 | -78.7932 | -45.3354 | 67.5816 | -44.8841 | -86.5151 | -44.0073 | 64.7374 | -60.3884 | -164.9859 | -47.1605 | 117.5998 | -18.2455 | 24.9564 | -16.9397 | 49.0306 | -21.5854 | 18.8558 | -15.7774 | 44.9813 | -28.3638 | 17.5642 | -19.3035 | 97.4655 | -25.6315 | -18.2967 | -17.9699 | 68.6586 | -56.0014 | -48.8356 | -36.7441 | -42.1147 | -55.7085 | -54.7145 | -56.2398 | -51.824 | -36.7833 | -42.3062 | -56.3102 | -50.1208 | -56.6712 | 246 | -41.6015 | -46.3291 | -44.0778 | -44.6279 | -41.7176 | -43.3496 | -40.5431 | -42.7884 | 246 | -45.6814 | -30.6407 | -35.9721 | -49.6405 | -48.6465 | -50.0721 | -45.756 | -30.6156 | -36.052 | -49.5408 | -48.6518 | -50.1771 | -42.693 | -30.6015 | -36.1636 | -50.2422 | -44.0528 | -50.5035 | -42.7676 | -30.5764 | -36.2435 | -50.1425 | -44.0581 | -50.6085
247 | -6.143 | 0 | -6.0871 | 0 | -6.1487 | 0 | -6.0565 | 0 | -45.6669 | -142.1992 | -42.1466 | 4.0837 | -45.4964 | -148.9265 | -50.8846 | 13.1359 | -59.0293 | 63.6983 | -49.267 | 85.9811 | -48.4891 | -77.5158 | -41.8667 | 69.6124 | -46.8365 | -115.5383 | -43.3345 | 54.2756 | -57.4385 | 157.9273 | -45.7162 | 104.585 | -20.0293 | 22.7156 | -17.2315 | 33.5168 | -23.4958 | 12.2495 | -17.2982 | 36.2125 | -54.9517 | 50.7994 | -18.9012 | 70.653 | -29.51 | -39.8321 | -20.2301 | 51.5392 | -54.5986 | -48.3439 | -36.7795 | -42.1221 | -57.2314 | -55.0236 | -55.8957 | -51.43 | -36.7367 | -42.2082 | -55.8254 | -50.4066 | -59.9217 | 247 | -39.3431 | -44.3736 | -40.9153 | -43.8409 | -40.0025 | -42.0504 | -38.5924 | -43.0683 | 247 | -45.287 | -30.5937 | -35.9791 | -51.1443 | -48.9365 | -49.747 | -45.3429 | -30.588 | -36.0656 | -51.0827 | -48.9671 | -49.8392 | -42.2009 | -30.6365 | -36.0652 | -49.7383 | -44.3195 | -53.773 | -42.2568 | -30.6308 | -36.1517 | -49.6767 | -44.3501 | -53.8652
248 | -6.159 | 0 | -6.0818 | 0 | -6.1653 | 0 | -6.0291 | 0 | -44.7176 | -157.4102 | -40.0675 | -12.2507 | -45.234 | -156.6928 | -51.0661 | -26.1906 | -57.2524 | 61.83 | -49.0344 | 62.0159 | -46.5243 | -94.3416 | -39.6371 | 54.4537 | -51.784 | -136.8392 | -43.6972 | 42.2896 | -57.0939 | 120.1306 | -45.5059 | 91.2532 | -21.3593 | 27.4378 | -19.1825 | 19.1003 | -25.3806 | 24.0517 | -19.4314 | 39.9701 | -30.2659 | 134.7197 | -20.2031 | 51.3008 | -38.3197 | -12.34 | -24.1826 | 56.6479 | -53.2535 | -48.0792 | -36.7017 | -42.105 | -57.1558 | -55.4659 | -55.8669 | -50.7552 | -36.6707 | -42.1091 | -55.1716 | -50.7161 | -61.0671 | 248 | -37.9003 | -43.6198 | -39.2529 | -43.5324 | -38.6135 | -41.7457 | -37.4582 | -44.3499 | 248 | -44.5962 | -30.5117 | -35.946 | -51.074 | -49.3841 | -49.7016 | -44.6734 | -30.5054 | -36.0759 | -50.9905 | -49.4368 | -49.8378 | -41.9202 | -30.5427 | -35.9501 | -49.0898 | -44.6343 | -54.9018 | -41.9974 | -30.5364 | -36.08 | -49.0063 | -44.687 | -55.038
249 | -6.1533 | 0 | -6.0658 | 0 | -6.1803 | 0 | -6.0439 | 0 | -45.0145 | -173.9102 | -39.7693 | -31.3594 | -45.4053 | -163.9449 | -53.6974 | -67.2338 | -55.4807 | 53.1084 | -50.7931 | 37.5443 | -46.3492 | -115.1473 | -39.1892 | 35.2443 | -59.8536 | -79.3807 | -44.9554 | 35.3647 | -58.1907 | 82.9498 | -46.3387 | 81.2687 | -21.8035 | 32.4162 | -23.5317 | 17.5124 | -24.012 | 38.8135 | -19.4037 | 55.5234 | -26.7716 | 110.698 | -22.575 | 47.1448 | -31.049 | 28.1372 | -23.109 | 85.2955 | -52.964 | -48.3051 | -36.4851 | -42.1476 | -55.3898 | -56.0317 | -56.3783 | -50.2155 | -36.583 | -42.1635 | -54.8158 | -51.0046 | -57.9296 | 249 | -37.8047 | -44.1323 | -39.2792 | -43.983 | -38.3942 | -42.4684 | -37.5521 | -45.8863 | 249 | -44.0622 | -30.4297 | -35.9943 | -49.324 | -49.9659 | -50.198 | -44.1497 | -30.4027 | -36.1037 | -49.2095 | -49.9878 | -50.3344 | -42.1518 | -30.3318 | -36.0102 | -48.75 | -44.9388 | -51.7493 | -42.2393 | -30.3048 | -36.1196 | -48.6355 | -44.9607 | -51.8857
250 | -6.1696 | 0 | -6.0976 | 0 | -6.2226 | 0 | -6.0762 | 0 | -46.3974 | 171.8775 | -41.1619 | -48.218 | -45.5053 | -166.4653 | -60.3246 | -118.7803 | -54.0015 | 38.0878 | -55.6231 | 18.5828 | -48.1339 | -134.6695 | -40.5345 | 18.6851 | -49.0626 | -59.937 | -45.9761 | 37.6805 | -61.0496 | 39.8909 | -47.3688 | 78.1246 | -22.3722 | 34.2597 | -25.113 | 58.8946 | -22.0587 | 34.6693 | -17.2385 | 58.9463 | -26.9509 | 95.2859 | -22.4893 | 59.4668 | -27.3471 | 4.3932 | -19.2545 | 81.705 | -53.5035 | -48.6559 | -36.3021 | -42.3082 | -54.2926 | -56.2497 | -56.8007 | -50.0117 | -36.5641 | -42.371 | -54.6484 | -51.2109 | -54.4913 | 250 | -38.9416 | -45.5549 | -40.9586 | -44.5756 | -39.3481 | -43.8289 | -38.7941 | -45.0138 | 250 | -43.8421 | -30.3945 | -36.1386 | -48.195 | -50.1521 | -50.5781 | -43.9141 | -30.3415 | -36.232 | -48.07 | -50.1735 | -50.7245 | -42.4863 | -30.1325 | -36.2014 | -48.5508 | -45.1133 | -48.2687 | -42.5583 | -30.0795 | -36.2948 | -48.4258 | -45.1347 | -48.4151
251 | -6.1728 | 0 | -6.1526 | 0 | -6.2234 | 0 | -6.1545 | 0 | -48.8816 | 165.8817 | -44.0835 | -51.9828 | -44.7185 | -169.0727 | -65.4975 | 104.1495 | -53.4458 | 18.6197 | -65.7516 | 64.1817 | -52.287 | -140.5625 | -43.3572 | 16.236 | -44.646 | -87.5931 | -45.4182 | 42.1671 | -65.8105 | -24.9457 | -47.6556 | 78.7831 | -23.6228 | 39.7704 | -19.8421 | 69.9337 | -21.6076 | 25.4254 | -15.6587 | 49.434 | -28.25 | 98.2387 | -19.624 | 56.1679 | -27.376 | -25.5035 | -17.4918 | 62.8297 | -54.6991 | -48.727 | -36.1295 | -42.5155 | -53.91 | -56.1098 | -56.7971 | -49.9539 | -36.5205 | -42.5783 | -54.6916 | -51.2351 | -51.3748 | 251 | -40.6687 | -47.5099 | -44.023 | -44.1421 | -40.6361 | -44.5732 | -40.3603 | -42.8628 | 251 | -43.7811 | -30.3477 | -36.3427 | -47.7574 | -49.9572 | -50.5737 | -43.8013 | -30.2971 | -36.361 | -47.6866 | -49.9553 | -50.6426 | -42.5542 | -29.9567 | -36.4055 | -48.539 | -45.0825 | -45.1514 | -42.5744 | -29.9061 | -36.4238 | -48.4682 | -45.0806 | -45.2203
252 | -6.2038 | 0 | -6.2175 | 0 | -6.2451 | 0 | -6.1969 | 0 | -50.4195 | 179.0244 | -45.0835 | -30.7248 | -43.782 | -177.882 | -58.1027 | 35.5768 | -54.0841 | 1.6346 | -55.8693 | 111.3739 | -54.1861 | -108.1915 | -43.8017 | 37.6435 | -43.3664 | -119.8121 | -44.2113 | 37.9413 | -65.0746 | -124.3255 | -47.5533 | 76.6247 | -23.8878 | 55.8092 | -16.6856 | 55.8554 | -22.4479 | 18.6423 | -15.3358 | 36.3797 | -26.572 | 109.1067 | -17.7948 | 37.429 | -30.9885 | -64.7013 | -17.6611 | 40.2033 | -56.2093 | -48.4284 | -36.0081 | -42.7328 | -53.9867 | -55.7096 | -56.5573 | -49.9053 | -36.446 | -42.6081 | -54.8503 | -51.0107 | -49.8105 | 252 | -40.864 | -48.3768 | -44.5399 | -43.1557 | -40.3835 | -43.7628 | -40.1253 | -41.9422 | 252 | -43.7015 | -30.2422 | -36.529 | -47.7692 | -49.4921 | -50.3122 | -43.6878 | -30.2009 | -36.5359 | -47.7416 | -49.5127 | -50.3604 | -42.2246 | -29.8043 | -36.4043 | -48.6328 | -44.7932 | -43.5654 | -42.2109 | -29.763 | -36.4112 | -48.6052 | -44.8138 | -43.6136
253 | -6.221 | 0 | -6.2445 | 0 | -6.2562 | 0 | -6.1741 | 0 | -48.1691 | -172.7194 | -41.6826 | -23.2992 | -43.7406 | 169.9201 | -55.7298 | -5.3804 | -55.4186 | -5.6666 | -50.7988 | 94.1504 | -49.7277 | -98.9151 | -40.3139 | 41.6158 | -44.5325 | -151.1219 | -43.4649 | 28.2648 | -59.964 | 174.3374 | -47.3884 | 73.3452 | -22.0032 | 67.3458 | -15.4832 | 37.1377 | -23.512 | 20.7127 | -16.2776 | 25.0346 | -24.1871 | 100.1866 | -17.5257 | 12.2308 | -41.8825 | -137.3862 | -19.9302 | 18.9709 | -56.8027 | -48.205 | -36.0605 | -42.8808 | -54.4042 | -54.662 | -56.557 | -49.8343 | -36.3929 | -42.4945 | -55.0179 | -50.5609 | -50.091 | 253 | -39.0176 | -46.8218 | -41.0307 | -42.7203 | -38.5733 | -42.4652 | -38.0603 | -42.6384 | 253 | -43.6133 | -30.1719 | -36.6598 | -48.1597 | -48.4175 | -50.3008 | -43.5898 | -30.1367 | -36.7067 | -48.148 | -48.4879 | -50.3829 | -41.984 | -29.8395 | -36.2735 | -48.7734 | -44.3164 | -43.8348 | -41.9605 | -29.8043 | -36.3204 | -48.7617 | -44.3868 | -43.9169
254 | -6.2575 | 0 | -6.2451 | 0 | -6.2812 | 0 | -6.1493 | 0 | -45.8401 | 174.6039 | -39.1235 | -37.0367 | -44.481 | 162.1009 | -56.206 | -49.0753 | -54.8677 | -3.393 | -48.8834 | 72.5702 | -46.8419 | -115.7896 | -38.0073 | 26.0964 | -48.8069 | -174.683 | -43.4569 | 17.8162 | -56.9832 | 129.2792 | -47.6445 | 69.3728 | -20.0705 | 66.8099 | -15.6529 | 19.9335 | -23.2326 | 27.1561 | -18.0739 | 22.6852 | -23.7323 | 81.0549 | -18.9612 | -15.6122 | -34.789 | 78.2568 | -25.3542 | 13.2007 | -55.3189 | -48.4175 | -36.2845 | -42.9165 | -55.3697 | -53.23 | -56.6201 | -49.8945 | -36.4177 | -42.413 | -54.9013 | -50.5508 | -51.952 | 254 | -37.3504 | -44.9871 | -38.611 | -42.8543 | -37.1652 | -41.6871 | -36.5652 | -44.8992 | 254 | -43.637 | -30.1602 | -36.659 | -49.1246 | -46.9849 | -50.3389 | -43.6494 | -30.1365 | -36.7672 | -49.0885 | -47.0807 | -50.4708 | -42.16 | -30.027 | -36.1555 | -48.6562 | -44.3057 | -45.6708 | -42.1724 | -30.0033 | -36.2637 | -48.6201 | -44.4015 | -45.8027
255 | -6.2785 | 0 | -6.1866 | 0 | -6.2975 | 0 | -6.1379 | 0 | -45.4399 | 153.1226 | -38.4751 | -56.8404 | -45.1108 | 159.7586 | -59.529 | -113.8654 | -53.3553 | -15.3626 | -48.9091 | 50.5091 | -46.0875 | -139.4187 | -37.5688 | 7.0271 | -57.0119 | -147.6431 | -43.963 | 9.8021 | -56.2996 | 89.3419 | -47.815 | 68.109 | -19.2864 | 61.443 | -16.8178 | 7.1364 | -22.4435 | 25.4004 | -18.9996 | 31.0391 | -26.317 | 62.7254 | -22.9237 | -46.4875 | -30.5456 | 33.3378 | -27.6452 | 63.305 | -53.8385 | -49.2463 | -36.3172 | -42.9986 | -55.7564 | -52.4455 | -56.1709 | -50.0397 | -36.3449 | -42.5655 | -54.1709 | -51.0866 | -51.8002 | 255 | -36.9579 | -44.6459 | -38.0678 | -43.1605 | -36.9542 | -41.7319 | -36.3503 | -46.8042 | 255 | -43.7612 | -30.0664 | -36.7201 | -49.5698 | -46.2589 | -49.8734 | -43.8531 | -30.0474 | -36.8607 | -49.4589 | -46.3076 | -50.033 | -42.9678 | -30.0387 | -36.287 | -47.9843 | -44.9 | -45.5027 | -43.0597 | -30.0197 | -36.4276 | -47.8734 | -44.9487 | -45.6623
256 | -6.2962 | 0 | -6.1625 | 0 | -6.3249 | 0 | -6.1777 | 0 | -46.7449 | 134.0258 | -39.5532 | -74.4063 | -44.9329 | 160.2077 | -59.2307 | 141.9898 | -53.0817 | -30.3137 | -50.9119 | 36.3579 | -47.2577 | -162.7272 | -38.7051 | -8.7611 | -49.6107 | -102.5932 | -44.5373 | 4.5664 | -57.5135 | 55.8933 | -47.6051 | 67.0877 | -19.0837 | 60.3543 | -18.1287 | 2.6819 | -22.3674 | 19.7449 | -17.7834 | 35.9926 | -33.7964 | 81.3911 | -33.7149 | -94.5077 | -31.1571 | -6.3923 | -21.7755 | 70.5317 | -53.7206 | -50.3674 | -36.1239 | -42.9511 | -54.6034 | -52.4026 | -55.8656 | -49.9148 | -36.1868 | -42.9438 | -53.4086 | -51.7234 | -48.6322 | 256 | -37.8486 | -45.6428 | -39.2033 | -43.4544 | -37.8389 | -42.5373 | -37.2752 | -45.2189 | 256 | -43.6186 | -29.8906 | -36.6549 | -48.4409 | -46.2401 | -49.5407 | -43.7523 | -29.8619 | -36.7734 | -48.2785 | -46.2249 | -49.6879 | -44.0712 | -29.8277 | -36.6476 | -47.2461 | -45.5609 | -42.3073 | -44.2049 | -29.799 | -36.7661 | -47.0837 | -45.5457 | -42.4545
257 | -6.3273 | 0 | -6.1867 | 0 | -6.3273 | 0 | -6.2453 | 0 | -49.4177 | 120.1155 | -42.1015 | -82.4202 | -44.0049 | 158.481 | -54.6181 | 74.8324 | -53.275 | -43.2352 | -53.904 | 39.3804 | -50.3321 | 178.6832 | -41.0501 | -14.4148 | -44.2591 | -123.3795 | -44.7129 | 1.2771 | -60.2344 | 30.1487 | -47.45 | 62.6623 | -18.5216 | 63.028 | -18.3344 | 2.3376 | -23.2395 | 17.0782 | -16.4109 | 30.0378 | -27.3782 | 137.1423 | -29.7245 | 99.0254 | -37.1739 | -59.873 | -19.3561 | 50.4579 | -54.4401 | -50.5338 | -35.9557 | -42.8815 | -53.9088 | -52.3463 | -55.8898 | -49.4796 | -36.0656 | -43.3312 | -53.1007 | -52.2921 | -45.2947 | 257 | -39.4754 | -47.0792 | -41.6014 | -43.139 | -39.0208 | -43.5659 | -38.8507 | -42.484 | 257 | -43.1523 | -29.7383 | -36.5542 | -47.7221 | -46.1596 | -49.5625 | -43.2929 | -29.7383 | -36.6362 | -47.5815 | -46.101 | -49.6445 | -44.2065 | -29.6284 | -37.0039 | -46.914 | -46.1054 | -38.9674 | -44.3471 | -29.6284 | -37.0859 | -46.7734 | -46.0468 | -39.0494
258 | -6.3774 | 0 | -6.2128 | 0 | -6.3416 | 0 | -6.2832 | 0 | -53.0143 | 123.7287 | -44.1922 | -68.4679 | -42.9566 | 149.8015 | -52.5943 | 31.0613 | -54.0165 | -54.7965 | -53.8917 | 60.7183 | -55.5647 | -179.2256 | -42.3904 | -1.191 | -42.2567 | -153.1613 | -44.6043 | -3.7489 | -65.4797 | 15.6586 | -47.9581 | 58.4416 | -17.2572 | 62.7156 | -17.7101 | -4.0838 | -23.7931 | 22.2407 | -15.9602 | 17.8944 | -21.743 | 120.1995 | -23.1462 | 62.8328 | -37.9518 | 151.1789 | -19.3776 | 26.5587 | -55.4896 | -49.4543 | -35.912 | -42.9896 | -53.6654 | -52.1614 | -55.9393 | -49.2361 | -35.9985 | -43.5565 | -53.2011 | -52.5291 | -43.3089 | 258 | -40.2824 | -48.3971 | -43.2174 | -42.3159 | -39.211 | -44.2367 | -39.6532 | -41.2056 | 258 | -42.8587 | -29.6211 | -36.6122 | -47.4526 | -45.9486 | -49.5977 | -43.0233 | -29.6569 | -36.7064 | -47.3238 | -45.8782 | -49.6561 | -43.0769 | -29.5346 | -37.1791 | -46.9883 | -46.3163 | -36.9673 | -43.2415 | -29.5704 | -37.2733 | -46.8595 | -46.2459 | -37.0257
259 | -6.421 | 0 | -6.2384 | 0 | -6.3859 | 0 | -6.2805 | 0 | -52.7296 | 144.3195 | -41.9064 | -53.7034 | -42.7473 | 137.4911 | -52.6689 | -5.4893 | -55.4138 | -59.1483 | -50.8045 | 67.8646 | -55.8937 | -140.7473 | -39.9927 | 7.9887 | -42.6418 | 175.8975 | -44.7799 | -11.2804 | -70.7661 | 85.3792 | -48.6208 | 59.8142 | -16.0853 | 58.1519 | -17.6555 | -17.6219 | -23.0255 | 27.2611 | -16.6062 | 6.5839 | -19.9352 | 94.0765 | -21.3272 | 34.2969 | -30.6015 | 95.2913 | -21.8761 | 0.7758 | -56.7496 | -48.4517 | -36.0025 | -43.3902 | -53.5621 | -51.4634 | -56.0119 | -49.4562 | -36.0304 | -43.6056 | -53.59 | -52.0695 | -43.4937 | 259 | -39.1036 | -48.659 | -41.0686 | -41.9175 | -38.0363 | -44.4461 | -38.3217 | -41.659 | 259 | -43.0352 | -29.6094 | -36.9692 | -47.3237 | -45.225 | -49.626 | -43.2178 | -29.6445 | -37.1097 | -47.1762 | -45.1829 | -49.7314 | -42.0307 | -29.5815 | -37.1846 | -47.3516 | -45.8311 | -37.1078 | -42.2133 | -29.6166 | -37.3251 | -47.2041 | -45.789 | -37.2132
260 | -6.4346 | 0 | -6.232 | 0 | -6.4221 | 0 | -6.2358 | 0 | -49.9777 | 138.7827 | -39.0282 | -62.0658 | -43.6124 | 128.2718 | -54.8988 | -42.494 | -55.3779 | -50.0461 | -48.4418 | 57.3341 | -51.7206 | -141.3974 | -37.6108 | -3.3971 | -45.713 | 149.7999 | -45.3346 | -16.8767 | -59.6092 | 92.8113 | -48.6205 | 63.5137 | -15.5225 | 50.5422 | -18.7956 | -34.085 | -22.1341 | 24.2425 | -17.9251 | -1.1454 | -20.7535 | 66.8881 | -21.8502 | 11.0635 | -28.6121 | 56.1538 | -29.411 | -23.2027 | -57.2471 | -48.4528 | -36.1919 | -43.7119 | -53.8838 | -50.1363 | -55.9117 | -49.9182 | -36.0909 | -43.6109 | -53.8766 | -51.6213 | -45.7877 | 260 | -37.4798 | -47.9083 | -38.4579 | -42.1651 | -36.8421 | -44.3062 | -36.6481 | -43.802 | 260 | -43.4836 | -29.6563 | -37.2773 | -47.6518 | -43.9043 | -49.4896 | -43.6862 | -29.6688 | -37.4761 | -47.4617 | -43.9005 | -49.6759 | -42.0182 | -29.7573 | -37.1763 | -47.6446 | -45.3893 | -39.3656 | -42.2208 | -29.7698 | -37.3751 | -47.4545 | -45.3855 | -39.5519
261 | -6.4452 | 0 | -6.1991 | 0 | -6.4569 | 0 | -6.2225 | 0 | -48.9456 | 116.0828 | -37.9403 | -80.0744 | -44.4111 | 127.9273 | -61.9754 | -92.744 | -52.563 | -54.4332 | -47.4318 | 42.2113 | -50.1298 | -160.9473 | -36.9865 | -20.3701 | -52.927 | 150.3995 | -45.7005 | -19.88 | -54.7389 | 59.8763 | -47.7406 | 67.8787 | -15.5424 | 44.8863 | -21.5764 | -47.3406 | -22.06 | 17.6219 | -19.1047 | -2.7538 | -25.5803 | 42.8594 | -24.3034 | -5.1668 | -30.9712 | 22.7686 | -34.0986 | 118.9643 | -56.7571 | -49.4641 | -36.3664 | -43.8782 | -55.1438 | -48.8899 | -54.8436 | -50.3983 | -36.0194 | -43.6718 | -52.9139 | -51.9022 | -47.3498 | 261 | -36.7851 | -47.2297 | -37.4622 | -42.2314 | -36.6766 | -43.982 | -36.1282 | -45.9723 | 261 | -43.9531 | -29.5742 | -37.433 | -48.9447 | -42.6908 | -48.3867 | -44.1992 | -29.5625 | -37.6557 | -48.6869 | -42.6674 | -48.6211 | -43.0189 | -29.9212 | -37.2266 | -46.7148 | -45.7031 | -40.8929 | -43.265 | -29.9095 | -37.4493 | -46.457 | -45.6797 | -41.1273
262 | -6.4771 | 0 | -6.1784 | 0 | -6.4825 | 0 | -6.2399 | 0 | -50.6248 | 87.3908 | -38.6081 | -96.4762 | -43.7477 | 129.2173 | -62.2823 | 107.6389 | -51.4157 | -72.9387 | -47.808 | 29.2555 | -50.91 | 177.8134 | -37.9985 | -35.8471 | -50.7385 | -149.759 | -45.6851 | -24.3838 | -53.6772 | 26.2677 | -46.1623 | 63.2212 | -15.5324 | 42.2309 | -25.7714 | -42.8562 | -22.658 | 16.2318 | -19.3618 | -4.4907 | -38.5122 | 136.025 | -27.6351 | -2.0385 | -44.6913 | -15.4856 | -24.3108 | 97.6323 | -56.6894 | -51.4663 | -36.1874 | -43.7988 | -55.0293 | -48.2788 | -53.5534 | -50.3771 | -35.7427 | -43.9088 | -51.3424 | -52.4005 | -44.4262 | 262 | -37.2438 | -47.8332 | -38.0984 | -41.8062 | -37.5674 | -44.0444 | -36.783 | -44.3271 | 262 | -43.9 | -29.2656 | -37.3217 | -48.8509 | -42.1004 | -47.0709 | -44.1987 | -29.2602 | -37.5589 | -48.5468 | -42.0389 | -47.3135 | -44.9892 | -29.7103 | -37.4317 | -45.164 | -46.2221 | -37.9437 | -45.2879 | -29.7049 | -37.6689 | -44.8599 | -46.1606 | -38.1863
263 | -6.5178 | 0 | -6.1812 | 0 | -6.4991 | 0 | -6.2751 | 0 | -55.4547 | 60.4791 | -40.4974 | -104.1509 | -42.7244 | 124.2555 | -54.4988 | 51.566 | -51.4862 | -87.0853 | -48.7882 | 23.4605 | -53.3963 | 161.499 | -40.0093 | -40.6861 | -44.4132 | -159.3198 | -45.852 | -29.9299 | -53.8871 | 3.4456 | -45.6926 | 51.1984 | -14.9725 | 41.0486 | -26.121 | -16.6123 | -22.7146 | 20.3115 | -19.6553 | -11.6259 | -22.6867 | 145.6079 | -27.3297 | 18.9986 | -32.5612 | 132.9939 | -21.1795 | 76.1009 | -57.325 | -53.8578 | -35.9429 | -43.4383 | -53.9969 | -48.4242 | -53.3335 | -49.4757 | -35.467 | -43.9976 | -50.7671 | -52.8976 | -41.0677 | 263 | -38.3735 | -48.697 | -39.7492 | -41.324 | -38.5214 | -44.6029 | -38.1606 | -41.7234 | 263 | -42.9579 | -28.9492 | -36.9205 | -47.8157 | -42.243 | -46.8344 | -43.2945 | -28.9679 | -37.1632 | -47.4978 | -42.1491 | -47.0584 | -47.34 | -29.4251 | -37.4798 | -44.5859 | -46.7164 | -34.5686 | -47.6766 | -29.4438 | -37.7225 | -44.268 | -46.6225 | -34.7926
264 | -6.5933 | 0 | -6.1957 | 0 | -6.5142 | 0 | -6.2957 | 0 | -72.488 | 43.4161 | -42.0108 | -97.3708 | -41.5368 | 115.1499 | -52.8612 | 13.0535 | -51.7656 | -100.5937 | -49.136 | 23.0895 | -58.0884 | 158.4776 | -41.1077 | -31.0576 | -41.5909 | 174.5472 | -46.0558 | -35.4867 | -53.986 | -18.5158 | -46.8469 | 42.0376 | -14.2033 | 34.8788 | -23.4676 | -16.3453 | -21.5754 | 20.6833 | -20.7947 | -23.9956 | -18.2068 | 121.3174 | -25.0876 | 19.2596 | -25.8733 | 102.9198 | -20.7475 | 58.856 | -57.7263 | -53.4745 | -35.9363 | -43.2536 | -53.6013 | -49.0057 | -53.5004 | -48.6822 | -35.2847 | -44.0004 | -50.8403 | -53.9361 | -39.45 | 264 | -38.7552 | -49.248 | -40.952 | -40.5033 | -38.2866 | -45.1791 | -39.1026 | -40.2692 | 264 | -42.0889 | -28.6914 | -36.6603 | -47.4056 | -42.81 | -46.9862 | -42.4865 | -28.7705 | -36.9579 | -47.0871 | -42.71 | -47.2047 | -46.8812 | -29.343 | -37.4071 | -44.6446 | -47.7404 | -32.9358 | -47.2788 | -29.4221 | -37.7047 | -44.3261 | -47.6404 | -33.1543
265 | -6.6449 | 0 | -6.1996 | 0 | -6.5394 | 0 | -6.305 | 0 | -58.8342 | 175.2633 | -40.7948 | -85.9161 | -41.0443 | 99.8931 | -54.8049 | -16.0084 | -52.5303 | -112.0412 | -49.3066 | 24.445 | -60.0979 | -163.7615 | -39.4948 | -22.798 | -41.0759 | 145.0544 | -46.4809 | -42.7265 | -55.3594 | -46.1181 | -48.2741 | 47.0933 | -14.074 | 24.9876 | -22.6656 | -32.5145 | -20.5752 | 12.236 | -23.7729 | -35.9202 | -16.8808 | 97.2529 | -24.2581 | 6.7536 | -23.6655 | 74.7551 | -21.7194 | 49.0452 | -58.3082 | -50.8512 | -36.0035 | -43.6324 | -53.0856 | -49.3238 | -53.68 | -48.8831 | -35.2425 | -44.18 | -51.2816 | -54.7621 | -39.6274 | 265 | -37.8725 | -49.9141 | -40.0738 | -40.1799 | -37.1812 | -45.7881 | -38.2477 | -40.1842 | 265 | -42.2382 | -28.5976 | -36.9875 | -46.886 | -43.1242 | -47.1406 | -42.6835 | -28.7031 | -37.3274 | -46.5462 | -43.0188 | -47.375 | -44.2063 | -29.3586 | -37.5351 | -45.082 | -48.5625 | -33.088 | -44.6516 | -29.4641 | -37.875 | -44.7422 | -48.4571 | -33.3224
266 | -6.6351 | 0 | -6.2042 | 0 | -6.5726 | 0 | -6.31 | 0 | -53.736 | 144.1883 | -38.2003 | -90.3739 | -41.7151 | 84.5526 | -60.6973 | -25.9242 | -54.2166 | -120.5449 | -48.3419 | 28.3715 | -55.8862 | -156.507 | -37.3112 | -30.2763 | -42.8307 | 116.9722 | -47.3539 | -47.3255 | -60.5543 | -73.2249 | -47.6948 | 57.4011 | -14.9992 | 16.76 | -24.1459 | -52.6383 | -20.9244 | -1.0191 | -29.6164 | -29.2954 | -17.7725 | 77.8737 | -25.0283 | -4.8609 | -23.9658 | 50.0797 | -22.9477 | 48.7737 | -59.6409 | -49.5679 | -36.0172 | -44.3558 | -52.2698 | -48.2984 | -54.1182 | -49.1859 | -35.3382 | -44.5479 | -52.0362 | -54.9007 | -41.8012 | 266 | -36.5179 | -50.5209 | -37.7768 | -40.6646 | -36.1903 | -46.6055 | -36.5537 | -41.5494 | 266 | -42.5508 | -28.7031 | -37.7207 | -46.0656 | -42.0942 | -47.5456 | -42.9817 | -28.7656 | -38.0458 | -45.6972 | -41.9884 | -47.8082 | -42.9328 | -29.3821 | -37.9128 | -45.832 | -48.6965 | -35.2286 | -43.3637 | -29.4446 | -38.2379 | -45.4636 | -48.5907 | -35.4912
267 | -6.5997 | 0 | -6.212 | 0 | -6.6052 | 0 | -6.3067 | 0 | -52.4635 | 109.7117 | -36.7604 | -105.8692 | -43.5589 | 75.2751 | -61.9332 | 53.1459 | -55.8288 | -112.8782 | -46.8023 | 24.3487 | -54.1012 | -172.5563 | -36.5311 | -46.4713 | -47.6521 | 98.8284 | -47.7496 | -47.5736 | -69.7569 | 18.9617 | -45.553 | 60.15 | -16.6534 | 16.9232 | -28.6348 | -67.4509 | -22.8246 | -10.6731 | -30.2841 | 23.2894 | -20.3263 | 75.7148 | -26.5411 | -9.2259 | -26.569 | 37.9571 | -22.6893 | 55.7355 | -61.1643 | -49.6943 | -36.0638 | -44.8206 | -51.8284 | -46.792 | -54.5752 | -48.6794 | -35.4318 | -44.919 | -52.8096 | -55.5466 | -44.08 | 267 | -35.8406 | -50.4942 | -36.3383 | -41.703 | -36.138 | -46.8226 | -35.7364 | -43.4565 | 267 | -42.0797 | -28.8321 | -38.2209 | -45.6164 | -40.58 | -47.97 | -42.4674 | -28.8266 | -38.5139 | -45.2232 | -40.4853 | -48.2685 | -43.0946 | -29.4641 | -38.3193 | -46.5976 | -49.3346 | -37.4748 | -43.4823 | -29.4586 | -38.6123 | -46.2044 | -49.2399 | -37.7733
268 | -6.6312 | 0 | -6.2167 | 0 | -6.6471 | 0 | -6.321 | 0 | -53.448 | 66.8803 | -36.9253 | -123.3872 | -45.0095 | 81.0034 | -52.6855 | 49.5123 | -53.735 | -104.61 | -45.8178 | 14.8334 | -54.6905 | 167.9225 | -37.3528 | -60.7923 | -52.6623 | 143.225 | -47.3518 | -53.2756 | -56.3686 | 12.8649 | -43.2866 | 50.1883 | -16.8272 | 29.9621 | -36.1783 | -31.2888 | -25.3103 | -4.8768 | -26.0067 | 24.4574 | -19.9626 | 96.796 | -27.4966 | -5.3943 | -28.1645 | 57.2258 | -21.7093 | 55.5962 | -61.2159 | -51.1268 | -36.1421 | -44.6495 | -52.3995 | -45.4588 | -54.2362 | -47.6627 | -35.3929 | -45.1112 | -52.5682 | -57.2682 | -41.4148 | 268 | -36.2149 | -48.4954 | -36.2973 | -42.0775 | -37.1496 | -46.1792 | -36.0332 | -42.6247 | 268 | -41.0315 | -28.7617 | -38.0183 | -46.1828 | -39.2421 | -47.5891 | -41.446 | -28.7458 | -38.3285 | -45.7524 | -39.1378 | -47.9152 | -44.4956 | -29.5109 | -38.48 | -46.3515 | -51.0515 | -34.7677 | -44.9101 | -29.495 | -38.7902 | -45.9211 | -50.9472 | -35.0938
269 | -6.7505 | 0 | -6.2465 | 0 | -6.6919 | 0 | -6.3637 | 0 | -56.608 | 2.8092 | -38.2554 | -134.2265 | -43.5969 | 84.6963 | -48.6389 | 21.907 | -51.8815 | -117.1233 | -45.6793 | 3.5519 | -57.5952 | 151.7144 | -38.8199 | -63.8071 | -45.6417 | 158.2426 | -48.0533 | -62.82 | -52.8544 | -18.2713 | -42.5586 | 28.5009 | -14.5613 | 34.6318 | -30.1811 | 8.2133 | -25.1171 | 10.2425 | -25.3109 | 10.3829 | -16.2203 | 97.3791 | -27.2666 | -5.832 | -25.2264 | 63.8142 | -21.5013 | 50.7935 | -59.1559 | -54.6051 | -36.0504 | -43.9606 | -53.4059 | -44.8668 | -53.1723 | -46.4028 | -35.2309 | -44.8481 | -51.3286 | -59.2661 | -37.9791 | 269 | -37.0929 | -46.5075 | -37.2088 | -41.1232 | -37.9522 | -46.4631 | -36.9388 | -40.558 | 269 | -39.6523 | -28.4804 | -37.2101 | -47.1594 | -38.6203 | -46.4804 | -40.1563 | -28.539 | -37.5969 | -46.714 | -38.5031 | -46.8086 | -47.8546 | -29.2999 | -38.0976 | -45.0821 | -53.0196 | -31.2872 | -48.3586 | -29.3585 | -38.4844 | -44.6367 | -52.9024 | -31.6154
270 | -6.8909 | 0 | -6.2687 | 0 | -6.6915 | 0 | -6.3634 | 0 | -57.4793 | -81.1805 | -39.6395 | -135.8599 | -42.0979 | 75.9249 | -47.6522 | -8.9201 | -51.5845 | -128.9004 | -46.685 | -5.2354 | -63.8025 | 159.9131 | -39.1703 | -61.3264 | -41.9698 | 137.2994 | -49.1934 | -63.6021 | -51.3885 | -43.0894 | -44.9081 | 7.13 | -12.6233 | 25.1494 | -26.9662 | -6.1741 | -23.6058 | 11.3506 | -27.8071 | -1.6131 | -13.7863 | 81.3789 | -27.4211 | -14.6682 | -23.3473 | 50.6997 | -21.9282 | 50.2557 | -57.1898 | -61.1634 | -36.0229 | -43.2562 | -53.7445 | -45.7376 | -52.7492 | -45.7306 | -35.1253 | -44.1671 | -50.9992 | -61.004 | -36.5335 | 270 | -37.6414 | -45.867 | -38.3186 | -40.4534 | -37.3282 | -47.0507 | -37.8149 | -39.8675 | 270 | -38.8397 | -28.2344 | -36.3653 | -47.4758 | -39.4689 | -46.0577 | -39.4619 | -28.4338 | -36.8928 | -47.053 | -39.3742 | -46.3858 | -54.2725 | -29.132 | -37.2762 | -44.7305 | -54.7353 | -29.842 | -54.8947 | -29.3314 | -37.8037 | -44.3077 | -54.6406 | -30.1701
271 | -6.9653 | 0 | -6.27 | 0 | -6.6598 | 0 | -6.3995 | 0 | -55.1589 | -140.851 | -39.9765 | -130.3771 | -41.4174 | 60.0128 | -49.7783 | -35.539 | -51.3018 | -140.7715 | -48.4353 | -0.555 | -61.3887 | -151.1432 | -38.8231 | -59.5058 | -40.7564 | 109.2878 | -48.9636 | -67.1109 | -50.7071 | -72.8856 | -49.9507 | 12.5191 | -11.9588 | 10.2856 | -27.129 | -25.4347 | -23.2349 | 2.926 | -33.6189 | 35.7104 | -13.0087 | 62.2656 | -29.1744 | -25.0755 | -23.5342 | 38.6405 | -21.5966 | 55.7747 | -56.566 | -54.4988 | -36.1715 | -43.4332 | -54.1793 | -47.7996 | -52.7739 | -46.4996 | -35.1645 | -44.0473 | -51.5395 | -60.3746 | -36.9119 | 271 | -37.5512 | -46.7814 | -39.0169 | -40.2733 | -36.6581 | -46.5918 | -38.1266 | -39.8874 | 271 | -39.5343 | -28.1992 | -36.4679 | -47.9093 | -41.5296 | -46.1141 | -40.2296 | -28.5047 | -37.0337 | -47.5195 | -41.4001 | -46.3744 | -47.5335 | -29.2062 | -37.082 | -45.2695 | -54.1046 | -30.2521 | -48.2288 | -29.5117 | -37.6478 | -44.8797 | -53.9751 | -30.5124
272 | -6.9193 | 0 | -6.272 | 0 | -6.6741 | 0 | -6.4244 | 0 | -54.6384 | -179.2744 | -38.4227 | -128.2402 | -42.1126 | 40.9096 | -54.5152 | -40.4406 | -51.8894 | -154.5469 | -46.9233 | 15.4239 | -57.6078 | -163.3296 | -37.441 | -61.7329 | -41.7457 | 81.3155 | -49.8408 | -75.95 | -52.0277 | -105.3106 | -49.8182 | 45.443 | -12.6959 | -4.239 | -30.0496 | -36.0897 | -24.9669 | -3.9014 | -26.9564 | 71.9673 | -13.8866 | 43.1315 | -32.2675 | -23.7342 | -25.1572 | 33.0161 | -20.072 | 54.5059 | -57.3624 | -50.3165 | -36.2017 | -44.5462 | -53.5309 | -47.556 | -53.2568 | -48.3641 | -35.3002 | -44.7538 | -52.5021 | -59.1092 | -38.9385 | 272 | -36.8046 | -48.7144 | -37.7564 | -40.5423 | -36.0398 | -47.3571 | -36.9667 | -40.7781 | 272 | -41.4448 | -28.3809 | -37.6269 | -47.2589 | -41.284 | -46.5827 | -42.0921 | -28.6261 | -38.1218 | -46.8568 | -41.1316 | -46.8324 | -43.3972 | -29.2824 | -37.8345 | -46.2301 | -52.8372 | -32.2644 | -44.0445 | -29.5276 | -38.3294 | -45.828 | -52.6848 | -32.5141
273 | -6.8086 | 0 | -6.293 | 0 | -6.746 | 0 | -6.4512 | 0 | -56.4901 | 153.2867 | -36.8759 | -138.2991 | -44.7907 | 24.5318 | -56.8563 | 3.8659 | -53.8697 | -162.8675 | -43.7139 | 13.3098 | -57.861 | 176.8918 | -36.4063 | -72.9853 | -45.2797 | 56.8221 | -50.8445 | -76.9204 | -56.0962 | -138.0624 | -46.2252 | 57.5859 | -14.6601 | -12.9497 | -33.9204 | -18.8824 | -27.1492 | 10.7018 | -22.5271 | 61.8214 | -16.2204 | 32.3273 | -33.7323 | 0.548 | -25.6489 | 48.5444 | -18.7832 | 46.3263 | -59.2394 | -48.6993 | -36.1378 | -45.7925 | -52.4598 | -45.5755 | -53.971 | -49.3003 | -35.4706 | -45.629 | -53.6685 | -58.4944 | -41.7724 | 273 | -36.1846 | -50.7528 | -36.0224 | -40.9795 | -35.8496 | -49.0917 | -35.8363 | -42.5215 | 273 | -42.4917 | -28.662 | -38.9839 | -46.1668 | -39.2825 | -47.225 | -43.0073 | -28.7246 | -39.3413 | -45.7138 | -39.1243 | -47.5198 | -41.8907 | -29.3292 | -38.8204 | -47.3755 | -52.2014 | -35.0264 | -42.4063 | -29.3918 | -39.1778 | -46.9225 | -52.0432 | -35.3212
274 | -6.7299 | 0 | -6.321 | 0 | -6.8777 | 0 | -6.4741 | 0 | -62.0968 | 145.151 | -36.5255 | -153.6535 | -49.5501 | 32.374 | -49.941 | 24.2561 | -55.7976 | -151.0595 | -41.6763 | -1.2812 | -61.063 | 164.648 | -36.7441 | -86.8978 | -53.8592 | 61.3558 | -50.6628 | -82.7524 | -71.7617 | -178.3657 | -42.9187 | 50.2323 | -16.8505 | -7.0566 | -31.2934 | 5.9877 | -24.6027 | 29.7977 | -20.7576 | 41.2796 | -18.7938 | 42.3321 | -31.6521 | 13.8152 | -22.3332 | 56.6637 | -18.3648 | 33.5591 | -61.6522 | -48.2869 | -36.0259 | -46.2577 | -51.5624 | -43.7713 | -54.4851 | -47.9987 | -35.5736 | -45.9695 | -54.5906 | -57.6745 | -40.6965 | 274 | -36.3028 | -48.7336 | -35.219 | -40.8777 | -36.6448 | -50.253 | -35.6657 | -42.5771 | 274 | -41.2688 | -28.8437 | -39.5278 | -45.2414 | -37.4503 | -47.6074 | -41.6777 | -28.6959 | -39.7836 | -44.6847 | -37.2972 | -48.011 | -41.557 | -29.296 | -39.2396 | -48.2696 | -51.3535 | -33.8188 | -41.9659 | -29.1482 | -39.4954 | -47.7129 | -51.2004 | -34.2224
275 | -6.7792 | 0 | -6.3622 | 0 | -7.0214 | 0 | -6.4825 | 0 | -62.5423 | -148.0488 | -37.3808 | -165.748 | -47.3844 | 66.7912 | -45.0083 | 3.8924 | -52.8613 | -139.0095 | -41.0887 | -18.4096 | -66.7271 | -179.1529 | -38.1295 | -92.2639 | -49.1134 | 129.2957 | -52.0381 | -100.1509 | -58.0723 | -20.8691 | -41.0963 | 32.4058 | -16.047 | 5.8569 | -29.084 | -2.9842 | -21.6584 | 21.5424 | -21.1401 | 22.0933 | -17.1793 | 56.5657 | -30.8514 | 7.9366 | -19.4417 | 42.0838 | -19.1869 | 19.9697 | -61.1035 | -48.962 | -35.9463 | -45.2871 | -51.3105 | -42.6456 | -54.0887 | -46.0839 | -35.5761 | -44.9872 | -54.0419 | -56.9511 | -37.5708 | 275 | -36.9552 | -44.2836 | -35.3437 | -39.9455 | -37.7908 | -50.9552 | -36.2383 | -40.3851 | 275 | -39.3047 | -28.7969 | -38.5079 | -44.9483 | -36.2834 | -47.0673 | -39.7217 | -28.5547 | -38.8046 | -44.2891 | -36.1631 | -47.6062 | -42.1828 | -29.1671 | -38.208 | -47.6797 | -50.5889 | -30.5494 | -42.5998 | -28.9249 | -38.5047 | -47.0205 | -50.4686 | -31.0883
276 | -6.8771 | 0 | -6.3747 | 0 | -7.1042 | 0 | -6.4765 | 0 | -54.5871 | -150.9341 | -38.622 | -171.0678 | -43.239 | 58.1801 | -42.9732 | -25.7469 | -50.3781 | -154.938 | -41.8077 | -33.2003 | -65.5347 | -116.8999 | -38.2211 | -88.5728 | -43.3681 | 113.3292 | -57.9413 | -106.7233 | -51.9711 | -59.0731 | -41.4992 | 10.528 | -14.1345 | 2.2131 | -29.2478 | -19.4542 | -20.7785 | 4.2847 | -23.5195 | 8.3363 | -14.8634 | 51.2592 | -32.3027 | 5.4019 | -18.5625 | 20.5353 | -21.4342 | 15.5484 | -57.5887 | -51.49 | -35.8802 | -43.6434 | -52.2137 | -42.3182 | -52.82 | -44.8503 | -35.4865 | -43.4489 | -52.1013 | -57.3503 | -36.3724 | 276 | -37.2526 | -42.0016 | -35.9564 | -39.1167 | -37.0565 | -50.8419 | -36.5162 | -39.0937 | 276 | -37.9732 | -28.6094 | -36.7663 | -45.839 | -35.9435 | -45.7158 | -38.4756 | -28.3823 | -37.1669 | -45.1095 | -35.8417 | -46.3435 | -44.6129 | -29.0031 | -36.5718 | -45.7266 | -50.9756 | -29.2682 | -45.1153 | -28.776 | -36.9724 | -44.9971 | -50.8738 | -29.8959
277 | -6.9249 | 0 | -6.3859 | 0 | -7.0265 | 0 | -6.5031 | 0 | -51.7252 | -178.1886 | -39.253 | -170.0251 | -41.5144 | 38.0386 | -43.8425 | -54.7093 | -50.2149 | -169.1871 | -43.6062 | -37.6753 | -58.3576 | -112.5757 | -37.318 | -93.5409 | -41.1519 | 88.0806 | -58.7551 | -53.8022 | -50.2358 | -92.4142 | -45.0781 | -0.9504 | -13.508 | -10.5168 | -33.3991 | -29.879 | -21.6519 | -9.3935 | -27.2048 | 17.5783 | -14.1247 | 36.5524 | -33.3316 | 20.4625 | -19.8014 | -0.1951 | -23.1436 | 25.3023 | -55.178 | -59.4436 | -35.9045 | -42.6077 | -52.6155 | -43.1116 | -52.3742 | -44.5617 | -35.3937 | -42.7531 | -51.5734 | -59.8468 | -36.5409 | 277 | -37.0763 | -42.4018 | -36.9114 | -39.0775 | -35.7905 | -49.114 | -36.6188 | -39.3095 | 277 | -37.6368 | -28.4688 | -35.6828 | -46.2296 | -36.7257 | -45.3477 | -38.1758 | -28.3672 | -36.1046 | -45.589 | -36.6085 | -45.8711 | -52.5187 | -28.9796 | -35.8282 | -45.1875 | -53.4609 | -29.5144 | -53.0577 | -28.878 | -36.25 | -44.5469 | -53.3437 | -30.0378
278 | -6.9013 | 0 | -6.3846 | 0 | -6.9227 | 0 | -6.524 | 0 | -52.1769 | 157.0165 | -38.7558 | -167.6253 | -41.5253 | 15.1443 | -47.7108 | -68.6826 | -49.9883 | 177.6002 | -44.2017 | -25.7042 | -55.7549 | -130.4908 | -37.119 | -100.8199 | -41.0604 | 62.3247 | -54.7713 | -59.7151 | -49.9653 | -123.43 | -47.2232 | 29.8546 | -14.5801 | -22.8685 | -38.2037 | 27.4786 | -23.5865 | -16.1476 | -26.4077 | 46.398 | -15.032 | 24.3455 | -30.542 | 38.8292 | -23.0364 | -6.2103 | -22.1733 | 35.6731 | -54.8837 | -58.2812 | -36.0098 | -42.8056 | -52.3798 | -43.9804 | -52.4667 | -45.575 | -35.37 | -43.2479 | -52.2049 | -59.7195 | -37.8707 | 278 | -36.7858 | -44.8116 | -37.2557 | -39.266 | -35.6047 | -47.9395 | -36.647 | -39.6912 | 278 | -38.6737 | -28.4687 | -35.9043 | -45.9952 | -37.5958 | -45.544 | -39.1904 | -28.4473 | -36.2816 | -45.4571 | -37.4564 | -45.9427 | -51.3799 | -29.1085 | -36.3466 | -45.8203 | -53.3349 | -30.948 | -51.8966 | -29.0871 | -36.7239 | -45.2822 | -53.1955 | -31.3467
279 | -6.847 | 0 | -6.3901 | 0 | -6.9534 | 0 | -6.5511 | 0 | -55.5648 | 144.6643 | -37.247 | -173.7801 | -43.4031 | -5.7803 | -50.3778 | -43.2246 | -50.8161 | 162.1623 | -41.376 | -18.4249 | -55.8973 | -137.8168 | -36.9696 | -108.8976 | -43.0186 | 40.4971 | -54.6121 | -71.6116 | -51.6454 | -155.046 | -42.7883 | 42.941 | -16.9643 | -24.2365 | -29.5844 | 42.8601 | -24.9826 | -7.5407 | -23.3949 | 46.311 | -16.9746 | 23.5296 | -27.1997 | 31.1569 | -24.4868 | 15.0989 | -20.6881 | 29.7883 | -56.3228 | -51.3275 | -36.0492 | -44.1041 | -51.5728 | -42.5892 | -52.9292 | -46.8167 | -35.386 | -44.7338 | -52.7182 | -53.0354 | -40.675 | 279 | -36.2535 | -46.94 | -35.6782 | -38.9685 | -35.9619 | -48.9022 | -35.9005 | -39.6109 | 279 | -39.9697 | -28.539 | -37.2571 | -45.1827 | -36.1991 | -45.9758 | -40.4266 | -28.4326 | -37.553 | -44.6194 | -36.0381 | -46.3781 | -44.4805 | -29.2022 | -37.8868 | -46.3281 | -46.6453 | -33.7216 | -44.9374 | -29.0958 | -38.1827 | -45.7648 | -46.4843 | -34.1239
280 | -6.8661 | 0 | -6.3962 | 0 | -7.1479 | 0 | -6.5636 | 0 | -58.3229 | 174.7822 | -36.5265 | 171.807 | -47.3673 | -11.9135 | -46.1038 | -26.6292 | -53.0102 | 154.506 | -38.3653 | -30.9067 | -54.5982 | -133.4653 | -37.5376 | -118.0966 | -46.8206 | 36.7421 | -55.5303 | -90.7902 | -55.9653 | 174.4726 | -39.1666 | 31.9034 | -17.388 | -6.302 | -25.8535 | 24.5382 | -23.179 | -1.2703 | -22.1407 | 34.0063 | -17.026 | 38.8751 | -25.8603 | 15.0033 | -21.1166 | 24.9588 | -21.2204 | 19.1933 | -58.8679 | -48.7564 | -36.0449 | -45.2976 | -50.4265 | -40.5142 | -53.443 | -46.4721 | -35.4521 | -45.3884 | -52.9001 | -49.0112 | -42.3423 | 280 | -36.1562 | -45.0868 | -34.059 | -37.7202 | -36.9776 | -50.5554 | -35.2252 | -38.4019 | 280 | -39.606 | -28.586 | -38.4315 | -44.0303 | -34.118 | -46.2951 | -40.0759 | -28.3042 | -38.734 | -43.2786 | -33.9506 | -46.8794 | -41.8903 | -29.1788 | -38.5223 | -46.5039 | -42.615 | -35.1944 | -42.3602 | -28.897 | -38.8248 | -45.7522 | -42.4476 | -35.7787
281 | -7.006 | 0 | -6.4083 | 0 | -7.3653 | 0 | -6.5489 | 0 | -53.5401 | -169.574 | -37.1445 | 156.7155 | -48.6004 | 15.6802 | -41.9846 | -38.6337 | -54.6809 | 167.4184 | -37.026 | -52.1906 | -52.6327 | -142.052 | -38.7511 | -119.4612 | -47.4533 | 61.6842 | -64.0196 | -146.2913 | -71.2923 | 124.2107 | -37.3539 | 9.8758 | -14.6538 | -2.012 | -24.9873 | 2.8151 | -21.7807 | -15.0856 | -22.7722 | 25.188 | -14.4645 | 40.9677 | -26.3218 | -4.7054 | -18.4247 | 9.865 | -23.4206 | 9.9265 | -59.3059 | -48.0012 | -36.091 | -44.5715 | -49.4152 | -39.134 | -53.4669 | -45.2989 | -35.4864 | -43.5294 | -53.0411 | -46.8653 | -39.3138 | 281 | -36.7525 | -41.4783 | -33.4232 | -36.6647 | -38.048 | -52.2733 | -34.9808 | -36.9473 | 281 | -38.2929 | -28.4804 | -37.5655 | -43.0069 | -32.7257 | -46.1016 | -38.8906 | -28.1211 | -38.0226 | -42.0499 | -32.5851 | -46.918 | -40.9952 | -29.085 | -36.5234 | -46.6328 | -40.457 | -31.9485 | -41.5929 | -28.7257 | -36.9805 | -45.6758 | -40.3164 | -32.7649
282 | -7.1487 | 0 | -6.4366 | 0 | -7.4419 | 0 | -6.5423 | 0 | -50.195 | 178.832 | -38.642 | 147.5592 | -44.488 | 18.3026 | -39.5806 | -63.269 | -51.7886 | 177.6227 | -37.5225 | -72.8106 | -52.229 | -153.5251 | -38.1882 | -115.363 | -43.6531 | 64.4728 | -55.571 | 41.3899 | -57.0422 | -59.2399 | -37.7739 | -14.3913 | -12.8082 | -14.1785 | -26.4004 | -15.6049 | -22.3675 | -34.0964 | -24.025 | 27.7928 | -12.6724 | 30.3498 | -29.5214 | -18.9557 | -17.9019 | -11.432 | -27.4668 | 30.8977 | -56.2521 | -48.9567 | -36.1752 | -42.3303 | -49.0685 | -38.9723 | -52.7647 | -44.3989 | -35.512 | -40.9952 | -53.8116 | -46.2778 | -37.6834 | 282 | -37.4029 | -38.9851 | -33.7288 | -36.5933 | -36.9708 | -49.6923 | -34.9282 | -36.7355 | 282 | -37.2502 | -28.3633 | -35.1816 | -42.6319 | -32.5357 | -45.3228 | -37.9623 | -28.0701 | -35.788 | -41.6266 | -32.43 | -46.2224 | -41.808 | -29.0265 | -33.8465 | -47.375 | -39.8412 | -30.2415 | -42.5201 | -28.7333 | -34.4529 | -46.3697 | -39.7355 | -31.1411
283 | -7.1961 | 0 | -6.4709 | 0 | -7.313 | 0 | -6.5785 | 0 | -48.7609 | 159.7663 | -40.0804 | 146.9525 | -42.3581 | -2.5191 | -39.5337 | -93.0814 | -49.0127 | 161.6608 | -39.5045 | -85.3576 | -52.3933 | -159.9555 | -37.0625 | -123.0058 | -41.115 | 47.5552 | -49.3443 | -10.8449 | -50.5382 | -100.8026 | -41.0973 | -30.2649 | -12.5733 | -31.5 | -29.3421 | -22.1827 | -24.9106 | -49.4618 | -23.146 | 35.4534 | -12.1953 | 15.3966 | -34.1027 | -7.0707 | -19.4129 | -30.5598 | -24.1703 | 61.2819 | -53.6536 | -52.6285 | -36.3202 | -40.5052 | -49.8177 | -40.3512 | -51.7053 | -44.2622 | -35.6414 | -39.7014 | -54.9982 | -46.9888 | -37.371 | 283 | -37.7065 | -38.6268 | -34.927 | -37.3817 | -35.5316 | -45.8124 | -35.4367 | -37.8552 | 283 | -37.0661 | -28.4453 | -33.3091 | -43.3468 | -33.8803 | -44.3923 | -37.7913 | -28.3284 | -33.9267 | -42.5047 | -33.7727 | -45.1268 | -45.4324 | -29.1241 | -32.5053 | -48.5273 | -40.5179 | -30.058 | -46.1576 | -29.0072 | -33.1229 | -47.6852 | -40.4103 | -30.7925
284 | -7.1288 | 0 | -6.4959 | 0 | -7.1433 | 0 | -6.6429 | 0 | -49.6334 | 139.6781 | -40.0982 | 151.0733 | -42.3393 | -27.5807 | -42.3799 | -114.8239 | -49.015 | 138.3022 | -41.8172 | -80.321 | -53.0043 | -166.4214 | -37.2449 | -133.7289 | -40.3114 | 24.3884 | -50.3587 | -49.722 | -48.9785 | -140.534 | -44.5633 | -7.9705 | -14.1441 | -47.1292 | -30.787 | -4.5761 | -28.9939 | -53.5154 | -21.1759 | 31.995 | -13.0872 | 4.2472 | -33.0159 | 31.5678 | -22.5324 | -33.1543 | -20.3787 | 59.5951 | -52.62 | -63.4979 | -36.5459 | -40.3895 | -50.8309 | -42.1932 | -51.5545 | -45.0183 | -35.8554 | -40.2537 | -54.8005 | -46.7957 | -37.9398 | 284 | -37.7729 | -40.9024 | -36.5486 | -38.6421 | -35.4261 | -45.708 | -36.3309 | -38.517 | 284 | -37.8895 | -28.7266 | -33.2607 | -44.335 | -35.6973 | -44.4112 | -38.5224 | -28.7121 | -33.7466 | -43.6876 | -35.5503 | -44.9116 | -56.3691 | -29.4171 | -33.1249 | -48.3046 | -40.2998 | -30.7965 | -57.002 | -29.4026 | -33.6108 | -47.6572 | -40.1528 | -31.2969
285 | -7.0399 | 0 | -6.5009 | 0 | -7.1181 | 0 | -6.7235 | 0 | -52.8055 | 136.6866 | -38.8172 | 148.6112 | -44.3458 | -52.8946 | -45.7729 | -114.4599 | -50.2828 | 124.3588 | -39.9056 | -63.9855 | -54.8902 | -158.7459 | -37.7924 | -140.3628 | -41.3065 | 1.2621 | -54.2869 | -56.8144 | -49.8425 | -173.1828 | -40.7017 | 12.4239 | -17.5989 | -48.9083 | -28.8395 | 1.2283 | -31.5651 | -27.4977 | -20.1697 | 16.7303 | -14.5495 | 2.3333 | -29.7628 | 35.1094 | -23.0727 | -15.4901 | -18.3858 | 42.6856 | -52.8828 | -60.332 | -36.8086 | -41.7461 | -50.625 | -41.25 | -51.9579 | -46.2626 | -36.1415 | -41.4462 | -56.1923 | -44.4306 | -40.3014 | 285 | -37.6118 | -43.8639 | -35.8508 | -38.2877 | -36.1348 | -47.6097 | -35.9336 | -37.7091 | 285 | -39.2227 | -29.1016 | -34.7062 | -44.1241 | -34.7491 | -44.8398 | -39.7617 | -29.0234 | -35.0226 | -43.5069 | -34.5265 | -45.2344 | -53.2921 | -29.7687 | -34.4063 | -49.6914 | -37.9297 | -33.1833 | -53.8311 | -29.6905 | -34.7227 | -49.0742 | -37.7071 | -33.5779
286 | -7.0572 | 0 | -6.5076 | 0 | -7.2948 | 0 | -6.7328 | 0 | -53.0093 | 162.9008 | -37.8378 | 135.1273 | -49.6694 | -69.2834 | -46.944 | -92.9145 | -52.1944 | 112.5937 | -36.3446 | -74.6225 | -52.6287 | -138.2246 | -38.3685 | -145.1176 | -44.0867 | -13.6534 | -56.7408 | -30.1277 | -52.467 | 158.1332 | -37.0092 | 1.9843 | -18.2186 | -20.8159 | -27.2756 | -11.9515 | -28.0039 | -23.5548 | -20.4063 | -2.4853 | -14.4853 | 10.0828 | -28.6893 | 27.2212 | -20.3333 | -13.9978 | -18.3299 | 27.3472 | -54.0888 | -53.29 | -37.025 | -43.8583 | -49.8544 | -38.4853 | -52.5076 | -46.5018 | -36.397 | -42.4061 | -56.5741 | -41.4666 | -45.5954 | 286 | -37.4397 | -45.052 | -33.8011 | -36.0406 | -37.2107 | -48.78 | -34.599 | -36.1298 | 286 | -39.4446 | -29.3398 | -36.8011 | -43.3468 | -31.9777 | -45.2128 | -39.9942 | -29.1022 | -37.1255 | -42.5596 | -31.7525 | -45.7748 | -46.2328 | -29.9678 | -35.3489 | -50.0665 | -34.959 | -38.3006 | -46.7824 | -29.7302 | -35.6733 | -49.2793 | -34.7338 | -38.8626
287 | -7.2032 | 0 | -6.5134 | 0 | -7.5232 | 0 | -6.7081 | 0 | -49.001 | 166.0563 | -38.2021 | 116.8402 | -55.1632 | -17.4297 | -42.9506 | -81.3867 | -56.0009 | 115.1433 | -34.9782 | -100.4301 | -48.9464 | -144.2963 | -39.047 | -145.013 | -47.1605 | -7.9426 | -52.3422 | -1.4868 | -58.5881 | 127.7166 | -35.1448 | -19.7842 | -14.419 | -16.1325 | -28.9474 | -33.9443 | -28.2051 | -51.9128 | -23.1145 | -21.495 | -12.6665 | 9.5085 | -29.5482 | 25.4305 | -18.6586 | -29.5882 | -19.7757 | 16.9223 | -55.2703 | -51.284 | -37.1828 | -45.0047 | -48.6844 | -36.5965 | -52.9118 | -45.6911 | -36.4493 | -41.7751 | -55.6384 | -39.5036 | -42.9021 | 287 | -37.775 | -41.8184 | -32.8417 | -34.9029 | -38.0545 | -46.9981 | -33.6029 | -34.8616 | 287 | -38.4879 | -29.2461 | -37.8015 | -42.171 | -30.0831 | -45.3886 | -39.1777 | -28.9261 | -38.2966 | -41.1612 | -29.8884 | -46.2037 | -44.0808 | -29.9796 | -34.5719 | -49.125 | -32.9902 | -35.3789 | -44.7706 | -29.6596 | -35.067 | -48.1152 | -32.7955 | -36.194
288 | -7.3782 | 0 | -6.5298 | 0 | -7.5733 | 0 | -6.6451 | 0 | -46.4794 | 151.4948 | -40.1593 | 101.0391 | -47.7324 | -2.8651 | -39.3712 | -99.866 | -54.8197 | 147.7371 | -36.0959 | -123.7328 | -47.1118 | -160.045 | -38.3243 | -144.6502 | -46.6753 | 8.2135 | -46.7457 | -12.5481 | -65.704 | -67.9529 | -35.3964 | -44.4707 | -11.991 | -30.8554 | -35.9371 | -49.0569 | -32.9832 | -87.1619 | -28.8792 | -29.9757 | -11.2299 | -1.8016 | -29.0821 | 34.9696 | -18.8702 | -50.6973 | -21.7282 | 17.7569 | -54.4976 | -52.213 | -37.264 | -42.9859 | -47.8921 | -36.2716 | -52.6352 | -45.21 | -36.4133 | -40.0532 | -55.4087 | -39.003 | -40.5539 | 288 | -38.6727 | -38.4965 | -33.3944 | -35.7535 | -37.2577 | -43.8859 | -33.4019 | -35.0806 | 288 | -37.8318 | -29.0351 | -35.6077 | -41.3623 | -29.7418 | -45.0619 | -38.6802 | -28.84 | -36.3408 | -40.3188 | -29.6265 | -45.9901 | -44.8348 | -29.8858 | -32.675 | -48.8789 | -32.4732 | -32.9806 | -45.6832 | -29.6907 | -33.4081 | -47.8354 | -32.3579 | -33.9088
289 | -7.437 | 0 | -6.5464 | 0 | -7.4097 | 0 | -6.6401 | 0 | -45.7824 | 131.8966 | -43.3065 | 97.9175 | -44.3192 | -24.512 | -38.4942 | -128.2782 | -50.5773 | 139.8522 | -38.9083 | -136.9344 | -46.5193 | -176.7872 | -37.4499 | -153.0873 | -44.2016 | 6.0104 | -44.3192 | -40.9705 | -52.552 | -114.0469 | -38.0637 | -62.0618 | -11.3549 | -50.0897 | -36.9742 | 64.4089 | -44.6048 | -166.754 | -33.776 | 31.6849 | -10.8525 | -17.2401 | -26.1364 | 38.7589 | -21.0961 | -65.7719 | -22.0083 | 27.3685 | -52.5767 | -56.4166 | -37.2642 | -40.6158 | -47.815 | -37.5689 | -51.769 | -45.4175 | -36.4604 | -38.9995 | -55.6128 | -39.937 | -39.8318 | 289 | -39.582 | -37.5299 | -34.9932 | -37.5864 | -36.1946 | -41.882 | -34.2822 | -36.9953 | 289 | -37.9805 | -29.0234 | -33.1788 | -41.2686 | -31.0225 | -44.3593 | -38.8711 | -29.0507 | -33.9757 | -40.4053 | -30.9288 | -45.1289 | -48.9796 | -29.8272 | -31.5625 | -49.0664 | -33.3906 | -32.4221 | -49.8702 | -29.8545 | -32.3594 | -48.2031 | -33.2969 | -33.1917
290 | -7.3418 | 0 | -6.5899 | 0 | -7.2427 | 0 | -6.6731 | 0 | -46.8077 | 113.0299 | -44.3517 | 113.5085 | -43.483 | -51.322 | -40.2507 | -153.1985 | -49.3962 | 118.462 | -42.012 | -133.618 | -47.3377 | 165.9649 | -37.5975 | -163.937 | -42.748 | -8.9114 | -45.1349 | -70.7947 | -48.6773 | -150.8915 | -41.9236 | -55.0606 | -12.1896 | -68.422 | -27.6052 | 49.8294 | -36.5263 | 93.3821 | -27.4241 | 46.0287 | -11.647 | -32.1127 | -23.4703 | 28.6343 | -24.0871 | -58.9394 | -20.6081 | 27.7996 | -51.2765 | -65.0817 | -37.2627 | -39.5655 | -48.3976 | -40.0934 | -50.836 | -46.4107 | -36.5996 | -39.0782 | -56.1875 | -41.649 | -39.7705 | 290 | -39.8964 | -38.9709 | -37.1214 | -39.2352 | -36.1003 | -42.029 | -35.7065 | -38.831 | 290 | -39.0689 | -29.2578 | -32.2237 | -41.8077 | -33.5035 | -43.5933 | -39.8208 | -29.3569 | -32.8924 | -41.1549 | -33.4203 | -44.1629 | -57.7399 | -29.9209 | -31.7364 | -49.5976 | -35.0591 | -32.5278 | -58.4918 | -30.02 | -32.4051 | -48.9448 | -34.9759 | -33.0974
291 | -7.1698 | 0 | -6.6005 | 0 | -7.1969 | 0 | -6.7279 | 0 | -50.5 | 107.1691 | -42.4023 | 114.0401 | -44.6132 | -77.8455 | -43.7341 | -158.7985 | -50.9394 | 103.6391 | -42.2526 | -104.5949 | -50.5039 | 158.8999 | -38.1693 | -171.8001 | -42.9546 | -26.7754 | -49.5546 | -79.649 | -47.8573 | 175.2771 | -40.739 | -27.8694 | -14.4922 | -80.2291 | -24.3479 | 25.222 | -31.5706 | 60.7356 | -25.894 | 30.7527 | -13.6577 | -40.4104 | -22.2153 | 13.0508 | -23.0409 | -42.7941 | -20.3373 | 20.8792 | -51.0293 | -58.1686 | -37.3368 | -40.0957 | -49.3965 | -41.1296 | -50.8935 | -47.8492 | -36.8846 | -40.3466 | -56.8193 | -42.0875 | -40.5686 | 291 | -39.957 | -42.2701 | -37.976 | -39.9074 | -36.7371 | -44.3934 | -36.0579 | -38.1994 | 291 | -40.6794 | -29.7148 | -32.9259 | -42.796 | -34.5291 | -43.6966 | -41.2487 | -29.6877 | -33.3678 | -42.1996 | -34.4017 | -44.1656 | -50.9988 | -30.167 | -33.1768 | -50.2188 | -35.487 | -33.3717 | -51.5681 | -30.1399 | -33.6187 | -49.6224 | -35.3596 | -33.8407
292 | -7.0526 | 0 | -6.5835 | 0 | -7.3559 | 0 | -6.7647 | 0 | -51.0416 | 136.3682 | -41.5592 | 98.995 | -48.3142 | -100.2145 | -44.7337 | -149.3572 | -51.4293 | 103.2106 | -36.9245 | -103.0421 | -51.6824 | -173.5074 | -38.9429 | -178.3548 | -44.6406 | -38.0925 | -50.1924 | -58.3474 | -49.0613 | 146.1489 | -36.5229 | -28.0289 | -16.8899 | -72.9464 | -23.6436 | 1.0959 | -31.3582 | 25.5174 | -27.1108 | 19.4056 | -15.6382 | -33.986 | -22.6218 | -2.4736 | -20.4022 | -49.3163 | -21.3596 | 15.0492 | -51.356 | -52.9057 | -37.4853 | -41.8756 | -50.6138 | -38.1948 | -51.3257 | -49.0317 | -37.119 | -41.9663 | -57.8609 | -39.8949 | -43.9739 | 292 | -40.3411 | -43.126 | -35.1359 | -36.4789 | -37.7289 | -45.4109 | -34.4391 | -35.6951 | 292 | -41.9791 | -30.0664 | -34.823 | -44.0303 | -31.6113 | -43.9698 | -42.4482 | -29.7631 | -35.1109 | -43.2579 | -31.4301 | -44.561 | -45.8531 | -30.4327 | -34.9137 | -51.2774 | -33.3114 | -36.618 | -46.3222 | -30.1294 | -35.2016 | -50.505 | -33.1302 | -37.2092
293 | -7.1073 | 0 | -6.5683 | 0 | -7.5995 | 0 | -6.7675 | 0 | -47.1241 | 140.0677 | -42.2373 | 80.3358 | -55.1354 | -89.4986 | -44.1157 | -140.5357 | -51.6643 | 97.0719 | -34.067 | -129.8703 | -47.6146 | -166.838 | -40.0532 | 179.4362 | -45.9603 | -35.042 | -48.3381 | -47.9278 | -52.0928 | 120.7897 | -33.7071 | -48.0563 | -15.5352 | -60.7355 | -25.3469 | -18.8389 | -42.8164 | 46.0343 | -30.5916 | 47.7002 | -14.6519 | -22.0296 | -24.0368 | -11.3521 | -19.1349 | -68.2444 | -23.6249 | 24.9502 | -52.208 | -51.0986 | -37.6103 | -44.0126 | -50.5283 | -35.3916 | -51.7089 | -48.494 | -37.1386 | -42.5956 | -56.6347 | -37.3729 | -46.8622 | 293 | -40.8515 | -41.8728 | -33.0935 | -33.9589 | -38.4939 | -44.1842 | -32.6815 | -33.397 | 293 | -41.3867 | -30.0313 | -36.9053 | -43.96 | -28.8233 | -44.1094 | -41.9257 | -29.5391 | -37.2451 | -42.9288 | -28.6241 | -44.9414 | -43.9913 | -30.503 | -35.4883 | -50.0664 | -30.8046 | -39.2627 | -44.5303 | -30.0108 | -35.8281 | -49.0352 | -30.6054 | -40.0947
294 | -7.2403 | 0 | -6.5737 | 0 | -7.6754 | 0 | -6.759 | 0 | -44.6737 | 125.3492 | -44.7136 | 61.8803 | -51.9059 | -46.5275 | -41.1987 | -142.9599 | -52.2875 | 100.6805 | -34.3893 | -159.8243 | -45.0715 | 179.3169 | -40.0661 | -177.9918 | -44.9832 | -31.5135 | -44.916 | -51.2836 | -60.9922 | 108.7367 | -33.1977 | -75.3714 | -13.2497 | -68.7974 | -29.7534 | -20.795 | -30.288 | 101.9313 | -25.0316 | 70.5955 | -12.5929 | -25.7484 | -25.7086 | -5.5704 | -20.0296 | -91.3388 | -21.8104 | 45.7931 | -52.8735 | -52.1745 | -37.7081 | -44.1938 | -49.229 | -34.3854 | -51.8901 | -47.5113 | -37.0606 | -41.4252 | -56.0424 | -36.3316 | -43.8328 | 294 | -41.2891 | -39.3601 | -33.2456 | -34.2443 | -37.9225 | -41.9285 | -32.1495 | -32.9122 | 294 | -40.271 | -29.8203 | -36.9535 | -42.6553 | -27.8117 | -44.2147 | -40.9376 | -29.3852 | -37.4348 | -41.5536 | -27.6264 | -45.1311 | -44.9342 | -30.4678 | -34.1849 | -49.4687 | -29.7579 | -36.1574 | -45.6008 | -30.0327 | -34.6662 | -48.367 | -29.5726 | -37.0738
295 | -7.3268 | 0 | -6.598 | 0 | -7.5685 | 0 | -6.7977 | 0 | -43.9576 | 105.6022 | -49.7004 | 55.1698 | -47.494 | -58.9455 | -39.4145 | -163.579 | -50.1648 | 102.2627 | -36.8976 | 179.5472 | -44.2317 | 161.8343 | -39.288 | 177.412 | -43.3725 | -38.6985 | -42.9544 | -71.773 | -56.9392 | -155.2062 | -35.0977 | -99.5925 | -12.3355 | -86.8221 | -30.0744 | 19.1868 | -25.7075 | 79.3891 | -20.8191 | 60.7704 | -11.6726 | -39.1608 | -24.9053 | 6.9481 | -23.3224 | -111.5596 | -18.684 | 46.3424 | -52.3549 | -56.3839 | -37.7829 | -42.222 | -48.2533 | -35.0168 | -51.3636 | -47.3107 | -37.0533 | -40.2269 | -56.4066 | -36.7286 | -42.7495 | 295 | -41.629 | -37.8446 | -34.8223 | -36.3503 | -36.956 | -40.4377 | -33.2088 | -34.4707 | 295 | -39.9839 | -29.7265 | -34.8952 | -41.6553 | -28.4188 | -43.7951 | -40.7127 | -29.4848 | -35.4243 | -40.6848 | -28.2191 | -44.5659 | -49.0571 | -30.4561 | -32.9001 | -49.8086 | -30.1306 | -35.181 | -49.7859 | -30.2144 | -33.4292 | -48.8381 | -29.9309 | -35.9518
296 | -7.2971 | 0 | -6.6399 | 0 | -7.3944 | 0 | -6.8676 | 0 | -44.9902 | 85.3435 | -52.6359 | 91.015 | -45.8837 | -83.9857 | -39.9222 | 173.5453 | -48.2439 | 86.1365 | -40.2054 | 172.5058 | -44.9375 | 145.1987 | -39.1591 | 168.3228 | -42.336 | -54.4527 | -43.4577 | -94.6223 | -49.7338 | -179.3974 | -39.4369 | -109.5731 | -12.8756 | -106.4658 | -24.5561 | 21.5622 | -24.3792 | 59.7191 | -18.5082 | 37.837 | -11.8419 | -53.463 | -22.3927 | 4.9835 | -28.5378 | -99.2468 | -16.5809 | 32.4355 | -51.1507 | -66.62 | -37.8586 | -40.6507 | -47.9554 | -36.8114 | -50.2766 | -48.0233 | -37.2463 | -39.7414 | -58.6125 | -38.0741 | -42.6264 | 296 | -42.0104 | -38.2832 | -36.9328 | -38.6594 | -36.7398 | -40.5641 | -35.5236 | -37.3785 | 296 | -40.7262 | -29.9492 | -33.3536 | -41.3155 | -30.1715 | -42.8822 | -41.3834 | -29.8519 | -33.7831 | -40.561 | -29.9438 | -43.409 | -59.3229 | -30.5615 | -32.4443 | -51.9726 | -31.4342 | -35.232 | -59.9801 | -30.4642 | -32.8738 | -51.2181 | -31.2065 | -35.7588
297 | -7.1641 | 0 | -6.6602 | 0 | -7.2891 | 0 | -6.9414 | 0 | -48.6788 | 73.05 | -48.2127 | 95.3758 | -46.4846 | -110.0066 | -42.3139 | 157.6232 | -48.4598 | 62.4587 | -43.7097 | -172.5363 | -47.5664 | 135.7721 | -39.4229 | 159.2698 | -42.5846 | -74.77 | -46.2074 | -106.926 | -47.4334 | 149.5172 | -42.7145 | -78.5658 | -14.6959 | -123.5933 | -22.1588 | 1.574 | -24.7166 | 44.7816 | -18.5523 | 14.5919 | -13.2447 | -66.1227 | -21.1057 | -8.5387 | -25.9976 | -69.0469 | -16.1916 | 15.3527 | -50.1007 | -58.3663 | -38.0069 | -40.0499 | -48.5147 | -38.671 | -49.2735 | -49.7383 | -37.7618 | -39.961 | -62.0313 | -39.3789 | -43.2401 | 297 | -42.9146 | -40.6294 | -39.3423 | -41.008 | -37.2845 | -42.2535 | -37.1742 | -38.9712 | 297 | -42.5742 | -30.5977 | -32.8858 | -41.8545 | -32.0108 | -41.9844 | -43.0781 | -30.4727 | -33.1085 | -41.2256 | -31.7296 | -42.3321 | -51.2022 | -30.8428 | -32.7969 | -55.3711 | -32.7187 | -35.951 | -51.7061 | -30.7178 | -33.0196 | -54.7422 | -32.4375 | -36.2987
298 | -7.0383 | 0 | -6.6696 | 0 | -7.3738 | 0 | -6.9616 | 0 | -52.5224 | 109.5439 | -47.0692 | 65.4096 | -48.7268 | -128.6104 | -44.7562 | 162.0038 | -52.0617 | 50.8177 | -40.2762 | -142.4739 | -49.8296 | 157.6638 | -40.051 | 148.1674 | -44.7155 | -92.1507 | -48.2415 | -95.0469 | -47.6843 | 121.0506 | -37.7169 | -59.3221 | -18.0676 | -127.1631 | -21.3301 | -20.0797 | -26.1177 | 32.0304 | -19.6802 | -7.4609 | -15.4056 | -68.5449 | -20.612 | -24.1916 | -22.4584 | -79.6254 | -17.2368 | -0.1041 | -49.946 | -51.9236 | -38.1975 | -40.7272 | -50.4655 | -37.6385 | -49.4 | -52.1863 | -38.4679 | -41.5446 | -57.3258 | -38.4754 | -45.5359 | 298 | -44.1298 | -43.4425 | -38.3291 | -39.4514 | -38.4467 | -43.7227 | -35.4823 | -36.5763 | 298 | -45.148 | -31.4296 | -33.6889 | -43.7959 | -30.9689 | -42.0262 | -45.5167 | -31.0941 | -33.7656 | -43.0917 | -30.6769 | -42.4384 | -44.8853 | -31.1592 | -34.5063 | -50.6562 | -31.8058 | -38.1621 | -45.254 | -30.8237 | -34.583 | -49.952 | -31.5138 | -38.5743
299 | -7.0094 | 0 | -6.6576 | 0 | -7.5871 | 0 | -6.9151 | 0 | -46.7966 | 123.1158 | -49.6689 | 29.4237 | -51.6563 | -137.9171 | -44.2042 | 166.4662 | -51.8529 | 62.8387 | -35.3821 | -162.866 | -45.9202 | 169.426 | -41.8958 | 139.6344 | -47.8279 | -92.4975 | -47.674 | -86.3047 | -48.8122 | 100.6667 | -33.6794 | -77.5007 | -19.2566 | -110.1378 | -22.3972 | -39.8085 | -28.1438 | 48.9083 | -22.6784 | -17.7143 | -16.3557 | -58.8476 | -21.5325 | -39.1568 | -21.0356 | -105.1329 | -19.8929 | -7.6148 | -50.2504 | -48.7581 | -38.2624 | -42.3637 | -51.9809 | -34.9768 | -49.6927 | -52.5989 | -38.6188 | -43.7318 | -56.3021 | -36.0754 | -53.519 | 299 | -44.1419 | -41.843 | -34.7061 | -35.1863 | -39.7183 | -42.5325 | -32.9216 | -33.389 | 299 | -45.5895 | -31.6094 | -35.3543 | -45.3233 | -28.3192 | -42.1056 | -45.9413 | -31.0317 | -35.4486 | -44.3938 | -28.0617 | -42.7776 | -41.7487 | -31.253 | -36.7224 | -49.6445 | -29.4178 | -45.9319 | -42.1005 | -30.6753 | -36.8167 | -48.715 | -29.1603 | -46.6039
300 | -7.0375 | 0 | -6.634 | 0 | -7.6903 | 0 | -6.8591 | 0 | -43.6998 | 107.788 | -54.7467 | -21.148 | -53.5428 | -131.2405 | -43.1309 | 165.595 | -51.6212 | 54.5211 | -34.7037 | 164.0444 | -43.2506 | 156.5188 | -43.6396 | 143.4936 | -48.2054 | -79.9091 | -45.2581 | -79.5919 | -51.3287 | 78.0573 | -32.4958 | -105.8994 | -16.6409 | -109.6345 | -25.3535 | -55.502 | -24.2801 | 61.1259 | -26.3297 | -4.9697 | -14.9715 | -53.6278 | -23.2313 | -46.8034 | -22.0487 | -134.3477 | -22.8919 | 7.1417 | -50.8284 | -48.2792 | -38.2905 | -43.7737 | -51.5823 | -33.7089 | -49.9895 | -50.2919 | -38.3383 | -43.4739 | -56.0793 | -34.6981 | -50.5169 | 300 | -42.9727 | -40.08 | -34.0834 | -34.561 | -39.76 | -40.7329 | -31.9658 | -32.3257 | 300 | -43.2544 | -31.3008 | -36.7362 | -44.9483 | -27.0749 | -42.2992 | -43.6579 | -30.648 | -36.9146 | -43.892 | -26.8498 | -43.1304 | -41.2417 | -31.253 | -36.4364 | -49.4453 | -28.0641 | -42.8266 | -41.6452 | -30.6002 | -36.6148 | -48.389 | -27.839 | -43.6578
301 | -7.0918 | 0 | -6.6347 | 0 | -7.6191 | 0 | -6.8457 | 0 | -42.7105 | 86.8201 | -56.0539 | -107.0491 | -52.5664 | -128.84 | -41.7184 | 153.1159 | -52.0169 | 54.683 | -36.7441 | 138.2823 | -42.3381 | 138.0834 | -43.2296 | 146.433 | -46.6136 | -79.2687 | -42.5592 | -93.6622 | -58.3013 | 74.1989 | -33.6372 | -132.6478 | -15.2661 | -125.2176 | -29.5962 | -43.4832 | -21.5869 | 45.4809 | -23.4894 | 12.1542 | -13.5988 | -61.2313 | -24.707 | -45.9216 | -25.9169 | -162.1845 | -21.0106 | 28.0858 | -51.0166 | -49.665 | -38.2627 | -43.2432 | -50.2549 | -33.79 | -50.0957 | -49.0801 | -38.1582 | -41.9472 | -56.1152 | -34.6855 | -47.2819 | 301 | -42.1047 | -38.9558 | -35.5061 | -36.508 | -38.9375 | -39.3809 | -32.7099 | -33.4096 | 301 | -41.9883 | -31.0664 | -36.1514 | -43.6202 | -27.1553 | -42.4766 | -42.4454 | -30.5391 | -36.3975 | -42.6358 | -26.9443 | -43.25 | -42.5732 | -31.1709 | -34.8554 | -49.4805 | -28.0508 | -39.6628 | -43.0303 | -30.6436 | -35.1015 | -48.4961 | -27.8398 | -40.4362
302 | -7.0933 | 0 | -6.6535 | 0 | -7.4756 | 0 | -6.8907 | 0 | -43.5759 | 67.2986 | -52.4133 | -164.8083 | -51.2067 | -142.9785 | -41.8249 | 133.3123 | -50.7753 | 50.5666 | -39.9731 | 123.6131 | -42.955 | 120.6589 | -42.9517 | 138.6965 | -45.147 | -88.8379 | -42.0325 | -114.7801 | -56.6258 | 134.9564 | -36.8979 | -153.0526 | -15.3774 | -147.0342 | -28.1197 | -15.6533 | -21.2525 | 28.9931 | -20.8717 | -1.3481 | -13.2298 | -74.3287 | -24.6948 | -43.3366 | -35.2685 | -157.1984 | -18.1664 | 25.5559 | -50.1994 | -52.2168 | -38.2759 | -41.7931 | -49.0705 | -34.7793 | -49.5949 | -49.1162 | -38.1597 | -40.9191 | -57.2746 | -35.4638 | -45.7675 | 302 | -42.4256 | -39.283 | -37.6435 | -39.3345 | -38.7979 | -39.3764 | -34.9815 | -36.2522 | 302 | -42.0229 | -31.0664 | -34.6998 | -42.417 | -28.1258 | -42.1193 | -42.4627 | -30.6841 | -34.9024 | -41.5949 | -27.8886 | -42.7042 | -45.1235 | -31.1826 | -33.8258 | -50.6211 | -28.8103 | -38.2919 | -45.5633 | -30.8003 | -34.0284 | -49.799 | -28.5731 | -38.8768
303 | -7.0527 | 0 | -6.6662 | 0 | -7.3371 | 0 | -6.9343 | 0 | -46.7402 | 55.0427 | -52.0908 | 158.898 | -51.2677 | -168.6728 | -43.9282 | 117.8646 | -50.7842 | 36.7546 | -44.4609 | 118.6691 | -45.4163 | 109.4051 | -43.5821 | 128.5044 | -44.6448 | -106.95 | -43.3017 | -132.9732 | -51.1877 | 122.402 | -42.7143 | -150.501 | -17.0652 | -167.8408 | -25.0943 | -19.685 | -21.9772 | 15.4593 | -20.0841 | -26.269 | -13.9521 | -86.7472 | -23.9957 | -47.861 | -30.1882 | -92.5818 | -16.8107 | 13.5742 | -48.884 | -54.1487 | -38.3877 | -40.7356 | -48.5676 | -36.3206 | -48.5373 | -50.3762 | -38.5683 | -40.5998 | -61.342 | -36.595 | -45.3676 | 303 | -44.5805 | -41.5487 | -40.8378 | -42.8719 | -39.711 | -40.8043 | -38.4129 | -40.2022 | 303 | -43.3235 | -31.5156 | -33.6829 | -41.9014 | -29.6544 | -41.2002 | -43.71 | -31.2312 | -33.8013 | -41.2305 | -29.3863 | -41.603 | -47.096 | -31.335 | -33.5471 | -54.6758 | -29.9288 | -38.0305 | -47.4825 | -31.0506 | -33.6655 | -54.0049 | -29.6607 | -38.4333
304 | -6.9918 | 0 | -6.6884 | 0 | -7.3284 | 0 | -6.9824 | 0 | -49.9568 | 78.0427 | -59.1021 | 147.4846 | -54.2871 | 163.751 | -46.1997 | 119.9547 | -52.5307 | 34.9128 | -48.4453 | 171.9833 | -48.3234 | 123.4173 | -45.0336 | 115.6135 | -46.1814 | -126.1254 | -45.2854 | -143.1979 | -49.52 | 102.0897 | -42.0256 | -101.697 | -20.5549 | 179.8292 | -24.0024 | -34.7224 | -23.7825 | 4.6641 | -21.1931 | -57.8789 | -15.5753 | -94.3057 | -24.0173 | -58.1742 | -25.0857 | -109.7015 | -16.6299 | 1.7573 | -47.871 | -51.0227 | -38.5142 | -40.3593 | -49.4843 | -37.136 | -47.6181 | -52.8714 | -39.2105 | -41.2235 | -58.9306 | -37.3128 | -45.7848 | 304 | -48.2229 | -44.015 | -44.0314 | -46.2682 | -41.5377 | -42.5577 | -39.0758 | -40.0884 | 304 | -45.8796 | -32.2187 | -33.3675 | -42.7959 | -30.4476 | -40.2897 | -46.183 | -31.8821 | -33.3769 | -42.1559 | -30.1536 | -40.6357 | -44.0309 | -31.5224 | -34.2317 | -52.2422 | -30.6244 | -38.4564 | -44.3343 | -31.1858 | -34.2411 | -51.6022 | -30.3304 | -38.8024
305 | -6.9607 | 0 | -6.7029 | 0 | -7.4724 | 0 | -6.9841 | 0 | -45.8172 | 98.6669 | -52.8179 | -133.522 | -59.6472 | 164.6321 | -46.0449 | 121.8639 | -51.2294 | 42.8129 | -39.7578 | 175.9971 | -45.8428 | 143.9353 | -49.0999 | 103.1323 | -49.4292 | -126.8684 | -48.7243 | -144.7863 | -48.6395 | 79.8493 | -36.1772 | -107.9633 | -24.3147 | -165.6325 | -24.6327 | -47.0614 | -26.5484 | 9.5898 | -24.522 | -96.1385 | -17.2256 | -91.6023 | -25.3717 | -70.3316 | -23.1865 | -137.1738 | -17.47 | -6.0171 | -47.7605 | -47.03 | -38.5417 | -40.9753 | -52.4285 | -35.5066 | -47.7419 | -52.3708 | -39.4372 | -43.1443 | -54.488 | -36.0935 | -47.6205 | 305 | -44.8799 | -42.3215 | -38.6703 | -39.4175 | -43.0319 | -42.746 | -35.7371 | -35.7474 | 305 | -45.4101 | -32.4765 | -34.0146 | -45.7256 | -28.8037 | -40.2695 | -45.6679 | -31.9648 | -33.9912 | -44.9561 | -28.5225 | -40.7578 | -40.0693 | -31.581 | -36.1836 | -47.7851 | -29.3906 | -40.1481 | -40.3271 | -31.0693 | -36.1602 | -47.0156 | -29.1094 | -40.6364
306 | -6.965 | 0 | -6.7098 | 0 | -7.5955 | 0 | -6.9353 | 0 | -42.2407 | 84.1284 | -46.3869 | -155.8796 | -59.708 | 175.3488 | -46.0346 | 120.2625 | -49.0882 | 30.9416 | -37.1309 | 142.5526 | -42.3758 | 135.4949 | -54.3204 | 146.9072 | -48.8777 | -116.0223 | -48.6047 | -117.0531 | -49.678 | 53.0839 | -34.0313 | -134.9537 | -22.1243 | -148.2793 | -25.6477 | -49.1013 | -25.3357 | 25.0761 | -30.8764 | -153.3299 | -17.2342 | -84.7995 | -28.9651 | -71.8868 | -23.3256 | -167.5722 | -18.4403 | -7.2764 | -48.6033 | -45.2195 | -38.6281 | -42.9822 | -53.5994 | -33.9539 | -48.5809 | -49.947 | -39.1603 | -44.4324 | -54.448 | -34.697 | -51.7751 | 306 | -40.7706 | -40.1345 | -36.1708 | -36.8401 | -41.2777 | -40.8395 | -33.8433 | -33.7782 | 306 | -42.982 | -32.1953 | -36.0172 | -46.8896 | -27.2441 | -40.9854 | -43.2372 | -31.5648 | -36.0469 | -46.0039 | -27.0186 | -41.6456 | -38.2545 | -31.6631 | -37.4674 | -47.7382 | -27.9872 | -44.1796 | -38.5097 | -31.0326 | -37.4971 | -46.8525 | -27.7617 | -44.8398
307 | -6.9773 | 0 | -6.7157 | 0 | -7.5727 | 0 | -6.9016 | 0 | -41.1508 | 62.2239 | -43.9943 | -175.8978 | -59.3161 | 168.9617 | -44.9107 | 114.5965 | -48.9371 | 14.0354 | -38.1029 | 112.3857 | -41.0188 | 117.1249 | -48.685 | 157.9816 | -47.58 | -122.2772 | -45.1858 | -121.7105 | -53.1496 | 26.3923 | -34.5714 | -163.5323 | -19.6337 | -159.3474 | -24.8542 | -43.2101 | -23.3344 | 15.8593 | -32.9168 | 89.4385 | -16.2364 | -85.4703 | -30.985 | -39.0411 | -26.164 | 164.4783 | -18.3582 | -5.3599 | -49.492 | -45.2085 | -38.6404 | -44.2108 | -52.4178 | -33.685 | -49.0242 | -48.3266 | -38.9265 | -43.5438 | -54.4422 | -34.4165 | -49.9283 | 307 | -39.2902 | -39.1444 | -36.4413 | -37.7283 | -39.5827 | -39.4222 | -34.0576 | -34.3024 | 307 | -41.3493 | -31.9492 | -37.2335 | -45.7021 | -26.9693 | -41.4515 | -41.6109 | -31.3538 | -37.3092 | -44.8451 | -26.7834 | -42.1226 | -38.2312 | -31.6631 | -36.5665 | -47.7265 | -27.7008 | -42.3556 | -38.4928 | -31.0677 | -36.6422 | -46.8695 | -27.5149 | -43.0267
308 | -6.987 | 0 | -6.7585 | 0 | -7.4573 | 0 | -6.8938 | 0 | -41.7883 | 40.9676 | -43.0474 | 167.0324 | -59.4454 | 157.5139 | -44.3235 | 96.9683 | -49.269 | 2.5863 | -40.7163 | 90.7135 | -41.2949 | 98.2255 | -47.6611 | 139.3803 | -47.2819 | -132.1193 | -44.3683 | -141.4834 | -64.0047 | 15.9947 | -37.1745 | 173.8627 | -19.4835 | -179.8755 | -22.5486 | -50.3716 | -23.789 | 1.7576 | -28.3537 | 22.1659 | -15.5614 | -94.0124 | -26.9262 | -24.8024 | -30.3788 | 161.2775 | -17.8927 | -8.0257 | -50.0505 | -46.2493 | -38.6149 | -43.7966 | -51.3903 | -34.1595 | -49.3132 | -47.6878 | -38.8659 | -42.3874 | -54.403 | -34.762 | -48.032 | 308 | -39.3197 | -39.3917 | -37.6619 | -40.0982 | -39.584 | -39.5394 | -36.1017 | -36.762 | 308 | -40.7008 | -31.8789 | -36.8096 | -44.6318 | -27.401 | -41.8559 | -40.9293 | -31.4086 | -36.9028 | -43.933 | -27.2657 | -42.4194 | -39.2623 | -31.6279 | -35.4004 | -47.6445 | -28.0035 | -40.5747 | -39.4908 | -31.1576 | -35.4936 | -46.9457 | -27.8682 | -41.1382
309 | -7.0052 | 0 | -6.7943 | 0 | -7.3529 | 0 | -6.9115 | 0 | -44.5742 | 24.8999 | -43.2508 | 153.6347 | -59.7714 | 144.54 | -45.9506 | 75.6937 | -49.3123 | -11.3924 | -44.6688 | 73.7772 | -43.4307 | 82.4505 | -50.0313 | 122.646 | -47.2484 | -143.275 | -46.155 | -158.5619 | -59.1853 | 122.3376 | -42.3574 | 162.9621 | -21.455 | 160.4671 | -20.5849 | -67.2756 | -26.1591 | -9.1162 | -26.1365 | -27.4499 | -15.7624 | -102.5464 | -22.9089 | -30.7114 | -32.7079 | -169.2994 | -17.544 | -15.4545 | -49.5238 | -47.9652 | -38.6214 | -42.6683 | -50.4769 | -35.0784 | -48.8451 | -48.2279 | -39.0951 | -41.6224 | -55.9467 | -35.4349 | -47.8575 | 309 | -40.7966 | -41.4265 | -39.7126 | -43.2884 | -41.2984 | -41.4977 | -40.349 | -41.0701 | 309 | -41.2227 | -32.0899 | -35.6631 | -43.6826 | -28.2841 | -41.4922 | -41.4336 | -31.7422 | -35.7568 | -43.124 | -28.1669 | -41.9336 | -40.96 | -31.6162 | -34.6172 | -49.1524 | -28.6406 | -40.5046 | -41.1709 | -31.2685 | -34.7109 | -48.5938 | -28.5234 | -40.946
310 | -7.011 | 0 | -6.833 | 0 | -7.3207 | 0 | -6.9388 | 0 | -49.1988 | 36.9352 | -44.3209 | 151.6227 | -62.7351 | 127.9011 | -49.2948 | 70.3079 | -51.104 | -28.3836 | -55.6784 | 71.7604 | -47.293 | 86.5787 | -56.3703 | 115.9386 | -48.2606 | -156.8565 | -48.6827 | -159.3045 | -53.4535 | 109.5713 | -47.045 | -152.2455 | -26.2171 | 160.7569 | -19.4048 | -89.5433 | -29.2116 | -11.4854 | -25.553 | -83.7604 | -16.4764 | -106.9719 | -20.4967 | -46.618 | -28.8756 | -163.2512 | -17.6031 | -22.9868 | -48.3515 | -49.2142 | -38.7092 | -41.7538 | -50.6444 | -36.0462 | -47.7548 | -49.805 | -39.7258 | -41.5556 | -57.1494 | -36.2582 | -48.8567 | 310 | -43.051 | -45.0108 | -42.8867 | -49.5888 | -44.4511 | -44.3522 | -44.4859 | -44.0685 | 310 | -42.794 | -32.7148 | -34.7428 | -43.8114 | -29.2132 | -40.4341 | -42.972 | -32.4051 | -34.815 | -43.3237 | -29.1074 | -40.816 | -42.2032 | -31.6982 | -34.5446 | -50.3164 | -29.4252 | -41.536 | -42.3812 | -31.3885 | -34.6168 | -49.8287 | -29.3194 | -41.9179
311 | -7.019 | 0 | -6.8426 | 0 | -7.3796 | 0 | -6.9451 | 0 | -46.6296 | 68.0047 | -43.2904 | 160.3154 | -62.8279 | 171.2747 | -49.5278 | 71.2992 | -53.425 | -26.1457 | -46.792 | 163.053 | -46.5998 | 115.1052 | -57.9906 | -144.6541 | -50.686 | -154.9838 | -50.1754 | -157.8472 | -49.8538 | 93.0874 | -39.9256 | -137.3549 | -26.6829 | -158.3927 | -19.4544 | -113.9399 | -32.0314 | 8.6888 | -25.5483 | -138.0824 | -16.7865 | -105.7655 | -19.2229 | -65.0145 | -26.9605 | -176.5895 | -18.0545 | -28.3304 | -47.3941 | -47.0492 | -38.7289 | -41.861 | -52.6096 | -35.6761 | -46.8867 | -49.7452 | -40.1381 | -42.6966 | -53.9638 | -36.129 | -51.9207 | 311 | -41.6035 | -44.2687 | -41.0261 | -45.8507 | -44.9477 | -43.7856 | -39.4723 | -39.1862 | 311 | -42.7262 | -33.1191 | -34.842 | -45.767 | -28.8335 | -39.5071 | -42.9026 | -32.7585 | -34.9159 | -45.23 | -28.731 | -39.9416 | -40.0302 | -31.7099 | -35.6776 | -47.1212 | -29.2864 | -44.5411 | -40.2066 | -31.3493 | -35.7515 | -46.5842 | -29.1839 | -44.9756
312 | -7.0654 | 0 | -6.855 | 0 | -7.468 | 0 | -6.9209 | 0 | -42.6102 | 63.4865 | -41.0048 | 155.6336 | -55.3775 | 162.6927 | -51.2624 | 51.9535 | -53.5197 | -27.4703 | -41.867 | 128.5175 | -42.8477 | 117.2595 | -47.8688 | -147.2384 | -49.0891 | -143.4234 | -52.2262 | -141.7564 | -48.1635 | 65.8872 | -36.8046 | -163.4558 | -21.0787 | -155.5161 | -20.0625 | -139.3878 | -30.0452 | 32.2853 | -25.0661 | 170.2524 | -15.8828 | -108.4436 | -18.7316 | -86.0853 | -25.5797 | 167.8671 | -18.7538 | -32.9803 | -47.1154 | -44.8591 | -38.8881 | -43.2059 | -55.068 | -34.5382 | -46.8229 | -47.7776 | -40.1142 | -44.5425 | -52.331 | -35.1826 | -56.9418 | 312 | -38.6306 | -41.7555 | -38.185 | -41.4024 | -40.9379 | -41.3573 | -36.3633 | -36.2653 | 312 | -40.7122 | -33.0488 | -36.1405 | -48.213 | -27.6832 | -39.3549 | -40.9226 | -32.6462 | -36.285 | -47.6 | -27.6173 | -39.902 | -37.7937 | -31.8227 | -37.4771 | -45.476 | -28.3276 | -49.4738 | -38.0041 | -31.4201 | -37.6216 | -44.863 | -28.2617 | -50.0209
313 | -7.107 | 0 | -6.8375 | 0 | -7.4899 | 0 | -6.8688 | 0 | -40.5759 | 44.5145 | -39.771 | 144.1766 | -51.847 | 130.1001 | -56.2456 | 52.0324 | -54.0573 | -32.8159 | -42.0022 | 93.8564 | -40.5625 | 102.0359 | -45.0512 | -177.401 | -46.5017 | -155.4595 | -49.3685 | -125.6549 | -49.1122 | 41.9362 | -36.9343 | 166.6503 | -17.9403 | -173.3867 | -21.0634 | -161.836 | -29.5656 | 33.5286 | -24.9212 | 130.9811 | -14.9524 | -116.8338 | -19.1195 | -105.9799 | -25.3913 | 157.9664 | -19.317 | -38.1666 | -47.3012 | -44.2738 | -39.2387 | -44.934 | -55.0824 | -34.0746 | -47.1109 | -46.2828 | -40.0211 | -45.4899 | -52.9078 | -34.7711 | -50.5351 | 313 | -36.9999 | -40.2741 | -37.6738 | -41.3354 | -38.493 | -39.5201 | -36.1015 | -36.2486 | 313 | -39.1758 | -32.9141 | -37.827 | -48.2449 | -27.2371 | -39.621 | -39.4453 | -32.5312 | -38.0652 | -47.5925 | -27.2058 | -40.2421 | -37.1668 | -32.1317 | -38.3829 | -46.0703 | -27.9336 | -43.0452 | -37.4363 | -31.7488 | -38.6211 | -45.4179 | -27.9023 | -43.6663
314 | -7.1486 | 0 | -6.8408 | 0 | -7.4502 | 0 | -6.8332 | 0 | -40.5248 | 24.2738 | -39.4056 | 134.8641 | -50.3864 | 100.5102 | -58.2047 | 65.4915 | -55.8662 | -37.3352 | -44.946 | 66.5436 | -40.2556 | 83.4021 | -46.3246 | 156.2428 | -45.8809 | -176.4555 | -47.5271 | -138.4366 | -51.2631 | 27.2307 | -39.4222 | 140.6144 | -16.7142 | 164.7257 | -22.7957 | 178.9631 | -29.2639 | 46.7038 | -26.7961 | 99.4141 | -14.7731 | -131.0146 | -20.473 | -124.7356 | -25.1462 | 145.5833 | -20.1994 | -40.4265 | -47.07 | -44.6443 | -39.4209 | -46.0075 | -53.8279 | -34.2576 | -46.915 | -45.5284 | -39.9104 | -44.8681 | -53.1572 | -34.919 | -48.1325 | 314 | -36.7278 | -40.3283 | -38.2916 | -43.5895 | -38.4342 | -39.2288 | -38.0907 | -38.3114 | 314 | -38.3798 | -32.7618 | -38.8589 | -46.9871 | -27.4168 | -39.4648 | -38.6876 | -32.4602 | -39.1743 | -46.3777 | -27.4244 | -40.0818 | -37.4957 | -32.2723 | -37.7195 | -46.3164 | -28.0782 | -40.6823 | -37.8035 | -31.9707 | -38.0349 | -45.707 | -28.0858 | -41.2993
315 | -7.1611 | 0 | -6.8438 | 0 | -7.4107 | 0 | -6.8143 | 0 | -42.1218 | 7.4249 | -39.2612 | 127.3749 | -49.8233 | 73.6562 | -62.651 | 77.0049 | -56.875 | -23.7364 | -51.5302 | 42.1978 | -41.4582 | 67.236 | -51.6718 | 150.0874 | -46.6874 | 162.9078 | -48.6816 | -148.0599 | -53.8817 | 29.2554 | -44.5031 | 121.3649 | -16.9197 | 145.1639 | -24.9137 | 166.1342 | -25.9838 | 53.8681 | -32.4452 | 95.2849 | -15.5885 | -146.6768 | -22.7868 | -137.79 | -23.8236 | 136.4173 | -21.2263 | -41.1779 | -46.6707 | -45.6399 | -39.4216 | -45.8348 | -52.866 | -34.7493 | -46.5431 | -45.4771 | -39.9345 | -43.9767 | -53.1251 | -35.3287 | -47.5386 | 315 | -37.2054 | -41.9418 | -38.9922 | -47.0998 | -40.0119 | -40.5004 | -42.5331 | -42.1475 | 315 | -38.316 | -32.7734 | -38.6737 | -46.0222 | -27.9055 | -39.1324 | -38.6333 | -32.5238 | -39.0205 | -45.4553 | -27.935 | -39.7288 | -38.4788 | -32.2605 | -36.8156 | -46.2813 | -28.4849 | -40.1279 | -38.7961 | -32.0109 | -37.1624 | -45.7144 | -28.5144 | -40.7243
316 | -7.1355 | 0 | -6.8364 | 0 | -7.3761 | 0 | -6.8381 | 0 | -45.162 | 5.6769 | -39.2269 | 121.9752 | -50.1517 | 48.1743 | -59.5085 | 140.572 | -55.3778 | -19.3589 | -65.8527 | -158.7439 | -43.9366 | 62.1769 | -52.9187 | -155.1571 | -48.5482 | 144.9586 | -49.5229 | -139.4351 | -53.6166 | 40.8472 | -53.936 | 140.6148 | -18.11 | 127.8424 | -26.134 | 159.949 | -23.1391 | 44.0326 | -30.6892 | 138.7609 | -17.5026 | -158.4085 | -25.7473 | -136.3413 | -23.1772 | 118.7258 | -21.6498 | -33.8538 | -46.171 | -46.992 | -39.4193 | -44.7921 | -52.1163 | -35.4412 | -45.9927 | -46.4269 | -40.2019 | -43.5122 | -53.8013 | -35.9386 | -48.1059 | 316 | -37.9695 | -44.6239 | -39.177 | -48.9227 | -42.2569 | -42.5254 | -46.9233 | -46.5056 | 316 | -39.2914 | -33.0664 | -37.6566 | -45.2799 | -28.6048 | -38.6166 | -39.5905 | -32.8258 | -37.954 | -44.7402 | -28.6031 | -39.1546 | -39.8565 | -32.2838 | -36.3767 | -46.9649 | -29.1022 | -40.7298 | -40.1556 | -32.0432 | -36.6741 | -46.4252 | -29.1005 | -41.2678
317 | -7.1121 | 0 | -6.8582 | 0 | -7.3699 | 0 | -6.8543 | 0 | -45.5796 | 26.5422 | -38.9385 | 119.8422 | -52.4634 | 26.579 | -53.1388 | 126.0156 | -54.1813 | -16.8511 | -47.8716 | 176.0072 | -45.1927 | 76.4782 | -47.0409 | -145.3064 | -53.1476 | 131.8148 | -48.0667 | -137.8686 | -51.7523 | 41.0959 | -48.4645 | -150.3194 | -19.819 | 127.1498 | -25.725 | 157.8827 | -22.7169 | 27.2314 | -24.2162 | 136.7081 | -20.0607 | -156.3212 | -26.0196 | -117.8529 | -24.1072 | 101.3154 | -20.5402 | -32.8263 | -45.8607 | -47.1654 | -39.3373 | -43.9545 | -52.4662 | -36.0482 | -45.3543 | -47.5379 | -40.7644 | -43.9558 | -53.5066 | -36.8035 | -49.4516 | 317 | -37.9309 | -44.3956 | -38.272 | -45.8815 | -42.6074 | -42.7953 | -43.0439 | -45.8896 | 317 | -40.4258 | -33.6523 | -36.8424 | -45.608 | -29.19 | -37.9844 | -40.6797 | -33.3945 | -37.1002 | -45.0963 | -29.1939 | -38.5 | -40.0533 | -32.2252 | -36.8437 | -46.6484 | -29.9453 | -42.0817 | -40.3072 | -31.9674 | -37.1015 | -46.1367 | -29.9492 | -42.5973
318 | -7.1093 | 0 | -6.8773 | 0 | -7.4252 | 0 | -6.9012 | 0 | -42.5189 | 29.4414 | -37.8181 | 114.7929 | -55.7975 | 39.4542 | -52.4007 | 97.3195 | -51.3549 | -22.9827 | -42.7527 | 140.9753 | -43.0813 | 84.3098 | -43.4355 | -154.7427 | -56.5883 | -167.4703 | -48.2483 | -142.2291 | -49.6522 | 27.9063 | -42.6621 | -170.5647 | -19.6475 | 133.9474 | -24.5831 | 151.7147 | -23.2482 | 13.6273 | -20.9096 | 111.8315 | -20.7591 | -143.0104 | -23.6809 | -116.6567 | -25.6547 | 88.1947 | -19.1722 | -36.2915 | -45.5712 | -44.9511 | -39.2289 | -44.0399 | -53.1649 | -35.7401 | -44.9984 | -46.101 | -40.9765 | -45.3382 | -52.2992 | -36.9994 | -51.058 | 318 | -36.4996 | -41.6075 | -36.496 | -42.0061 | -40.1449 | -41.2499 | -39.4127 | -41.7262 | 318 | -38.9917 | -33.8672 | -36.9306 | -46.2876 | -28.8628 | -37.5732 | -39.2237 | -33.5513 | -37.1387 | -45.7397 | -28.8389 | -38.0972 | -37.8418 | -32.1196 | -38.2289 | -45.4219 | -30.1221 | -43.6328 | -38.0738 | -31.8037 | -38.437 | -44.874 | -30.0982 | -44.1568
319 | -7.1397 | 0 | -6.9092 | 0 | -7.4547 | 0 | -6.9163 | 0 | -40.4359 | 16.6736 | -37.4528 | 104.0649 | -51.9529 | 52.246 | -55.5637 | 83.6294 | -50.0058 | -40.9461 | -41.9392 | 105.5184 | -41.0268 | 76.7984 | -41.7473 | -172.7491 | -48.2659 | -167.2183 | -47.5314 | -135.6215 | -49.4182 | 5.7341 | -42.0321 | 156.4982 | -17.8259 | 133.8644 | -23.9233 | 138.4074 | -25.4934 | 3.5348 | -20.237 | 87.0631 | -17.8161 | -142.1155 | -21.337 | -130.0388 | -27.6549 | 92.4182 | -18.156 | -50.2562 | -45.5093 | -43.2813 | -39.5093 | -44.771 | -52.8022 | -35.1446 | -45.2061 | -44.3922 | -40.878 | -46.1592 | -51.9444 | -36.4078 | -49.9472 | 319 | -35.5815 | -39.8626 | -36.0812 | -40.9501 | -37.9391 | -39.6645 | -38.3221 | -40.5075 | 319 | -37.2525 | -33.7383 | -37.6313 | -45.893 | -28.2354 | -37.7514 | -37.483 | -33.4233 | -37.8547 | -45.3475 | -28.2283 | -38.2898 | -36.1416 | -32.3696 | -39.0195 | -45.0352 | -29.4986 | -42.4925 | -36.3721 | -32.0546 | -39.2429 | -44.4897 | -29.4915 | -43.0309
320 | -7.2021 | 0 | -6.9378 | 0 | -7.4276 | 0 | -6.9019 | 0 | -39.798 | -1.1557 | -38.035 | 97.4728 | -48.9133 | 37.3207 | -58.3878 | 102.5541 | -49.8662 | -59.3612 | -43.5812 | 77.2128 | -40.1857 | 61.4638 | -42.5762 | 172.6939 | -44.9436 | 167.8258 | -45.836 | -142.9552 | -50.8185 | -12.6556 | -45.156 | 125.0391 | -16.2951 | 122.804 | -24.1644 | 123.7138 | -27.3948 | 13.6184 | -20.381 | 58.3806 | -16.5114 | -157.3917 | -20.8383 | -146.5017 | -27.5913 | 97.8141 | -17.8675 | -65.7067 | -45.6784 | -42.9611 | -39.8411 | -45.6198 | -51.7839 | -34.9885 | -45.5433 | -43.6229 | -40.831 | -45.8949 | -51.7503 | -36.1073 | -47.9478 | 320 | -35.6095 | -39.3359 | -36.9356 | -41.7395 | -37.373 | -38.8545 | -39.5137 | -41.4981 | 320 | -36.4208 | -33.6289 | -38.4177 | -44.8461 | -28.0507 | -38.1157 | -36.6851 | -33.4034 | -38.7179 | -44.3563 | -28.0866 | -38.6414 | -35.759 | -32.639 | -38.6928 | -44.8125 | -29.1695 | -40.5202 | -36.0233 | -32.4135 | -38.993 | -44.3227 | -29.2054 | -41.0459
321 | -7.2496 | 0 | -6.9488 | 0 | -7.4253 | 0 | -6.898 | 0 | -40.6391 | -16.8515 | -38.2407 | 97.2651 | -47.4296 | 17.6503 | -56.524 | 122.8212 | -50.7196 | -74.1141 | -47.2889 | 55.3384 | -40.8592 | 46.5986 | -44.2279 | 178.0814 | -43.7173 | 142.1126 | -46.3183 | -152.6747 | -53.6094 | -28.6867 | -53.5988 | 98.8063 | -15.5315 | 106.2306 | -25.4107 | 110.9916 | -26.3167 | 25.8751 | -23.0474 | 30.6608 | -16.2696 | -176.4965 | -21.2087 | -160.3655 | -26.2819 | 98.2435 | -18.2297 | -82.4588 | -45.5018 | -43.4979 | -40.0409 | -46.2674 | -51.2401 | -35.1971 | -45.4097 | -43.4332 | -40.8433 | -45.4097 | -51.1011 | -36.1753 | -47.8522 | 321 | -35.946 | -40.1316 | -37.6741 | -43.4472 | -37.8964 | -39.596 | -41.8385 | -42.9064 | 321 | -36.1836 | -33.5937 | -39.0178 | -44.2913 | -28.2483 | -37.9844 | -36.4844 | -33.418 | -39.3694 | -43.8148 | -28.2991 | -38.5117 | -36.2483 | -32.7913 | -38.1601 | -44.1523 | -29.2265 | -40.4269 | -36.5491 | -32.6156 | -38.5117 | -43.6758 | -29.2773 | -40.9542
322 | -7.2702 | 0 | -6.9689 | 0 | -7.403 | 0 | -6.8761 | 0 | -42.4987 | -24.7491 | -37.4835 | 96.3248 | -47.0797 | -3.3636 | -52.9894 | 124.5464 | -51.4207 | -84.3471 | -54.7904 | 50.6505 | -42.8191 | 39.1189 | -42.351 | -169.2719 | -43.5833 | 117.7286 | -47.0673 | -148.5761 | -59.1048 | -26.4363 | -58.2625 | -109.5159 | -16.0391 | 92.2713 | -28.7196 | 116.2063 | -25.3455 | 14.5361 | -29.4733 | -8.7326 | -17.6376 | 163.4614 | -22.0461 | -166.6915 | -25.2022 | 87.6957 | -19.3961 | -97.6246 | -45.2992 | -44.534 | -40.1942 | -46.1117 | -50.8617 | -35.6356 | -45.1135 | -43.7155 | -40.985 | -44.7619 | -50.9806 | -36.3327 | -48.5685 | 322 | -35.9458 | -41.644 | -37.2851 | -45.2117 | -38.1173 | -41.3593 | -41.0054 | -43.3217 | 322 | -36.4453 | -33.7148 | -38.8415 | -43.8928 | -28.6667 | -37.7105 | -36.7466 | -33.582 | -39.2356 | -43.4587 | -28.7595 | -38.2374 | -37.2638 | -32.924 | -37.4917 | -44.0117 | -29.3638 | -41.1655 | -37.5651 | -32.7912 | -37.8858 | -43.5776 | -29.4566 | -41.6924
323 | -7.254 | 0 | -6.979 | 0 | -7.3723 | 0 | -6.8813 | 0 | -43.8766 | -18.1378 | -36.6174 | 91.0969 | -48.2693 | -25.2364 | -50.4816 | 104.7458 | -52.3564 | -94.7257 | -56.2641 | 135.3329 | -44.5533 | 47.6229 | -39.4971 | -174.3835 | -44.5817 | 93.6288 | -45.6913 | -144.9463 | -59.2769 | 19.7659 | -48.0687 | -127.8925 | -17.1152 | 80.8403 | -28.5975 | 144.1475 | -25.9138 | -4.3336 | -34.9394 | -124.2508 | -20.8735 | 146.8886 | -21.7951 | -164.5808 | -25.1771 | 75.3652 | -20.3969 | -111.2689 | -45.2271 | -45.4564 | -40.2482 | -45.485 | -50.7428 | -36.2259 | -44.7017 | -44.5442 | -41.3673 | -44.5493 | -51.4868 | -36.6418 | -49.6789 | 323 | -35.6264 | -42.5398 | -36.3976 | -46.3691 | -37.3958 | -41.9929 | -38.101 | -42.8734 | 323 | -37.2902 | -34.1133 | -38.231 | -43.7638 | -29.2469 | -37.3294 | -37.5652 | -33.995 | -38.6037 | -43.3705 | -29.3446 | -37.8204 | -38.2024 | -32.9942 | -37.2953 | -44.5078 | -29.6628 | -42.3066 | -38.4774 | -32.8759 | -37.668 | -44.1145 | -29.7605 | -42.7976
324 | -7.231 | 0 | -7.0259 | 0 | -7.3913 | 0 | -6.8843 | 0 | -42.6426 | -11.9898 | -35.9843 | 83.0616 | -52.8689 | -38.2209 | -51.0838 | 75.2341 | -53.5494 | -99.1931 | -47.5088 | 129.2401 | -43.1871 | 59.3048 | -37.996 | 172.1607 | -47.3445 | 75.3433 | -44.5558 | -150.6851 | -54.0931 | 23.1821 | -44.4227 | -150.0821 | -18.9195 | 78.9338 | -24.0937 | 154.1722 | -30.1211 | -26.897 | -27.1836 | 177.9223 | -25.3663 | 156.2469 | -20.2184 | -169.4497 | -26.2031 | 69.5237 | -21.4887 | -125.6808 | -45.1333 | -44.7331 | -40.19 | -45.2622 | -50.9302 | -36.5729 | -44.1821 | -45.114 | -41.6724 | -45.311 | -51.522 | -37.0124 | -50.8858 | 324 | -35.0629 | -41.7636 | -35.5652 | -45.6338 | -36.4768 | -40.6083 | -36.3868 | -42.3324 | 324 | -37.883 | -34.4414 | -38.0312 | -43.9043 | -29.547 | -36.7908 | -38.0881 | -34.2811 | -38.3779 | -43.5389 | -29.6886 | -37.2978 | -37.5021 | -32.959 | -38.08 | -44.4961 | -29.9865 | -43.4945 | -37.7072 | -32.7987 | -38.4267 | -44.1307 | -30.1281 | -44.0015
325 | -7.2226 | 0 | -7.0703 | 0 | -7.414 | 0 | -6.9062 | 0 | -41.0375 | -19.1161 | -35.853 | 72.7884 | -55.521 | 14.6494 | -57.4368 | 48.6322 | -53.5448 | -103.453 | -45.058 | 96.647 | -40.9517 | 54.1036 | -37.7902 | 156.7504 | -50.7189 | 82.4497 | -43.9978 | -155.969 | -51.4924 | 3.3456 | -43.7226 | -173.3634 | -18.9858 | 82.5269 | -20.5174 | 143.4481 | -43.2858 | -11.7769 | -23.9958 | 149.8173 | -24.1169 | -176.0416 | -18.6294 | 178.1442 | -26.5362 | 66.7198 | -22.4034 | -140.8432 | -44.9549 | -43.0643 | -40.3221 | -45.8339 | -50.9862 | -36.2557 | -43.7578 | -44.6211 | -41.664 | -46.6523 | -51.2695 | -36.9414 | -50.8503 | 325 | -34.6675 | -40.7071 | -35.3336 | -44.1534 | -35.9324 | -38.9536 | -36.045 | -42.3655 | 325 | -37.3985 | -34.4414 | -38.6113 | -43.9159 | -29.1854 | -36.3438 | -37.5508 | -34.25 | -38.9277 | -43.5722 | -29.3495 | -36.8516 | -35.8417 | -33.0995 | -39.4297 | -44.1992 | -29.8711 | -43.4363 | -35.994 | -32.9081 | -39.7461 | -43.8555 | -30.0352 | -43.9441
326 | -7.2689 | 0 | -7.1112 | 0 | -7.4346 | 0 | -6.9085 | 0 | -40.3733 | -31.0701 | -36.8968 | 65.1909 | -48.4638 | 22.0887 | -62.5162 | 163.8748 | -54.104 | -110.6075 | -46.5358 | 66.1814 | -39.8233 | 41.2546 | -39.1103 | 147.8325 | -48.9971 | 96.7075 | -43.461 | -160.7989 | -51.2729 | -19.1291 | -45.1296 | 170.6268 | -17.8795 | 82.5753 | -18.4364 | 126.5333 | -32.9504 | 87.6823 | -22.487 | 138.9721 | -20.9643 | 175.5359 | -18.1419 | 159.7996 | -26.805 | 60.1055 | -24.416 | -161.9321 | -44.7575 | -42.2606 | -40.7902 | -46.6168 | -51.0856 | -36.0184 | -43.4823 | -43.876 | -41.64 | -47.2791 | -51.158 | -36.7393 | -49.883 | 326 | -35.0817 | -40.1678 | -36.4381 | -43.9433 | -36.2072 | -38.0498 | -37.0224 | -42.9456 | 326 | -36.6071 | -34.3711 | -39.3479 | -43.9744 | -28.9072 | -36.0477 | -36.7648 | -34.2054 | -39.7083 | -43.651 | -29.1099 | -36.5738 | -34.9917 | -33.5213 | -40.0102 | -44.0468 | -29.6281 | -42.4484 | -35.1494 | -33.3556 | -40.3706 | -43.7234 | -29.8308 | -42.9745
327 | -7.3103 | 0 | -7.1392 | 0 | -7.4303 | 0 | -6.93 | 0 | -40.5338 | -43.9795 | -37.5477 | 69.9643 | -44.8402 | 4.0848 | -51.5465 | 149.5497 | -54.3074 | -113.3078 | -50.9438 | 45.2151 | -39.9493 | 26.0175 | -40.2125 | 155.3575 | -46.3287 | 86.8078 | -42.9792 | -167.0006 | -53.0397 | -38.7623 | -47.2762 | 165.2649 | -17.0614 | 74.918 | -17.7055 | 110.7768 | -28.9281 | 78.6212 | -21.4478 | 131.6098 | -19.7551 | 155.8225 | -19.1636 | 140.1255 | -28.8336 | 48.725 | -28.2278 | 173.6771 | -44.469 | -42.4202 | -41.3119 | -46.8909 | -51.1018 | -36.0022 | -43.5337 | -43.1998 | -41.6228 | -47.4009 | -51.1509 | -36.606 | -49.9026 | 327 | -35.2706 | -40.0372 | -37.1911 | -43.5102 | -36.582 | -38.0549 | -37.8434 | -43.2811 | 327 | -35.8895 | -34.3125 | -39.5806 | -43.9626 | -28.863 | -36.1034 | -36.0606 | -34.1925 | -39.9609 | -43.6715 | -29.0722 | -36.6037 | -35.1099 | -34.0016 | -40.0906 | -44.0117 | -29.4668 | -42.4723 | -35.281 | -33.8816 | -40.4709 | -43.7206 | -29.676 | -42.9726
328 | -7.3478 | 0 | -7.1299 | 0 | -7.407 | 0 | -6.9263 | 0 | -41.5881 | -52.5623 | -36.2482 | 73.6817 | -43.1662 | -15.68 | -48.11 | 124.1331 | -54.294 | -116.0611 | -60.9954 | 52.4263 | -41.3846 | 15.695 | -38.3477 | 163.7894 | -44.935 | 68.1011 | -42.8599 | -174.3885 | -57.4612 | -43.9509 | -49.6224 | 171.1624 | -16.9985 | 62.3605 | -17.9948 | 98.5949 | -28.5322 | 70.3681 | -20.397 | 127.0612 | -20.4487 | 131.38 | -21.9552 | 124.7132 | -31.883 | 49.7245 | -36.8308 | 157.6324 | -44.0143 | -43.0218 | -41.7048 | -46.9987 | -51.0104 | -36.1664 | -43.6651 | -43.0945 | -41.8127 | -47.2745 | -50.7315 | -36.6414 | -50.2821 | 328 | -34.4996 | -40.5283 | -35.9605 | -42.7776 | -36.0016 | -38.9874 | -36.7993 | -43.487 | 328 | -35.7467 | -34.4649 | -39.6509 | -43.8805 | -29.0365 | -36.2581 | -35.9646 | -34.4057 | -40.0724 | -43.6034 | -29.2401 | -36.7388 | -35.674 | -34.357 | -39.9267 | -43.6016 | -29.5115 | -42.8751 | -35.8919 | -34.2978 | -40.3482 | -43.3245 | -29.7151 | -43.3558
329 | -7.3478 | 0 | -7.1369 | 0 | -7.3986 | 0 | -6.9377 | 0 | -42.7341 | -53.0596 | -34.7525 | 65.4693 | -42.6537 | -35.0129 | -47.119 | 99.9225 | -53.3869 | -120.8768 | -57.4617 | 142.2782 | -43.0717 | 17.7966 | -35.9162 | 155.8374 | -44.5905 | 46.1875 | -42.7283 | -179.2411 | -58.2603 | -5.5782 | -50.5733 | -165.3167 | -17.9035 | 49.4424 | -18.4341 | 92.9763 | -28.4935 | 81.2469 | -19.2579 | 122.2092 | -22.7808 | 104.8767 | -26.3805 | 136.3386 | -31.7564 | 87.1673 | -36.8618 | -99.7569 | -43.7594 | -43.7906 | -41.9156 | -46.9586 | -50.5914 | -36.4625 | -43.7658 | -43.758 | -42.2619 | -47.0119 | -50.5861 | -36.7736 | -49.532 | 329 | -33.5425 | -41.1193 | -34.4857 | -42.1712 | -34.6835 | -39.8236 | -34.973 | -43.4673 | 329 | -36.4102 | -34.9141 | -39.6108 | -43.4545 | -29.3256 | -36.3672 | -36.6211 | -34.8633 | -40.0209 | -43.1928 | -29.5248 | -36.8281 | -36.4428 | -34.5678 | -39.6641 | -43.4492 | -29.6367 | -42.1334 | -36.6537 | -34.517 | -40.0742 | -43.1875 | -29.8359 | -42.5943
330 | -7.3436 | 0 | -7.1658 | 0 | -7.4001 | 0 | -6.9584 | 0 | -42.4013 | -48.553 | -34.2889 | 53.5878 | -43.253 | -50.5656 | -48.2688 | 77.5117 | -52.4642 | -132.8731 | -50.7768 | 142.9391 | -42.542 | 27.5397 | -34.9043 | 140.4283 | -45.5688 | 21.9825 | -42.7093 | 175.0326 | -53.2597 | -3.5221 | -47.1032 | -148.0022 | -19.7427 | 40.2777 | -18.3485 | 94.8821 | -25.1138 | 95.0312 | -18.2589 | 117.0051 | -28.3401 | 83.9906 | -23.7928 | 172.9377 | -26.8328 | 97.1844 | -27.0308 | -119.4481 | -43.6944 | -44.3897 | -41.9347 | -46.9991 | -50.1631 | -36.8545 | -43.6892 | -45.2868 | -42.8318 | -47.2165 | -50.7556 | -37.0446 | -48.6628 | 330 | -33.2121 | -41.0738 | -34.0258 | -42.1244 | -33.9072 | -39.4309 | -34.0193 | -42.8445 | 330 | -37.9432 | -35.4882 | -39.6555 | -42.9973 | -29.6887 | -36.2891 | -38.121 | -35.4317 | -40.0407 | -42.763 | -29.8961 | -36.7308 | -37.0461 | -34.5911 | -39.8729 | -43.5898 | -29.8788 | -41.2627 | -37.2239 | -34.5346 | -40.2581 | -43.3555 | -30.0862 | -41.7044
331 | -7.3193 | 0 | -7.2419 | 0 | -7.4519 | 0 | -6.9881 | 0 | -40.9863 | -50.8775 | -34.8162 | 42.4306 | -44.3721 | -57.5955 | -52.0537 | 68.852 | -52.3974 | -146.926 | -47.0797 | 124.7295 | -40.5038 | 24.9269 | -35.5218 | 125.7673 | -48.7266 | -0.8008 | -42.9176 | 171.5415 | -50.465 | -23.234 | -43.572 | -155.9982 | -22.2432 | 39.0985 | -17.0268 | 92.9929 | -21.4477 | 86.3508 | -17.4435 | 110.6398 | -39.7303 | 102.2348 | -19.2321 | 165.7029 | -23.1859 | 78.7283 | -23.7633 | -153.3168 | -43.7118 | -44.1132 | -41.758 | -47.3603 | -49.9345 | -37.0937 | -43.4841 | -46.6668 | -42.9834 | -48.0935 | -50.9489 | -37.4128 | -48.5862 | 331 | -33.5054 | -40.3776 | -34.4889 | -42.0838 | -34.1694 | -38.2649 | -34.2546 | -41.7832 | 331 | -39.3475 | -35.6641 | -40.041 | -42.6926 | -29.8518 | -36.0322 | -39.4249 | -35.5315 | -40.3722 | -42.4826 | -30.1056 | -36.496 | -36.7939 | -34.4387 | -40.7742 | -43.707 | -30.1709 | -41.1343 | -36.8713 | -34.3061 | -41.1054 | -43.497 | -30.4247 | -41.5981
332 | -7.2988 | 0 | -7.321 | 0 | -7.5088 | 0 | -7.0297 | 0 | -39.7591 | -61.1301 | -36.2093 | 37.7886 | -44.3542 | -58.9213 | -53.528 | 102.6714 | -52.6004 | -158.4845 | -46.3282 | 102.0629 | -39.1521 | 11.289 | -37.2205 | 120.9042 | -55.9202 | -1.0329 | -42.7326 | 170.2521 | -49.3624 | -48.5864 | -41.999 | -172.9103 | -23.8226 | 49.0197 | -15.6581 | 83.1112 | -19.3707 | 69.1155 | -16.7325 | 103.8295 | -32.5876 | 179.0841 | -16.9502 | 147.945 | -21.8587 | 54.5403 | -21.9879 | 176.9814 | -43.6502 | -43.4982 | -41.714 | -47.8612 | -49.9549 | -37.045 | -43.2546 | -46.1494 | -42.7168 | -49.196 | -50.9929 | -37.4815 | -49.5497 | 332 | -34.182 | -39.369 | -35.7333 | -41.839 | -35.0339 | -37.2945 | -35.1419 | -41.121 | 332 | -38.8506 | -35.418 | -40.5624 | -42.6339 | -29.724 | -35.7458 | -38.8284 | -35.208 | -40.8315 | -42.4461 | -30.0153 | -36.2249 | -36.1994 | -34.4152 | -41.8972 | -43.6719 | -30.1605 | -42.0409 | -36.1772 | -34.2052 | -42.1663 | -43.4841 | -30.4518 | -42.52
333 | -7.3091 | 0 | -7.3481 | 0 | -7.5356 | 0 | -7.0747 | 0 | -39.2665 | -75.6228 | -37.0357 | 44.6856 | -43.9084 | -62.7431 | -48.5099 | 110.4614 | -52.5538 | -170.2076 | -47.7901 | 88.3269 | -39.2041 | -5.8974 | -38.0618 | 130.7851 | -54.8261 | 64.8928 | -42.0273 | 168.2395 | -49.8428 | -77.4608 | -42.1144 | 170.2572 | -25.2047 | 58.9713 | -15.2681 | 69.628 | -19.2113 | 51.2144 | -16.5618 | 98.9101 | -28.4814 | 166.6571 | -16.4754 | 127.9629 | -22.285 | 27.9969 | -22.1334 | 144.2774 | -43.1967 | -43.2436 | -41.8764 | -48.0405 | -50.1108 | -36.9663 | -43.0473 | -45.0591 | -42.7973 | -49.9145 | -50.727 | -37.4028 | -49.7058 | 333 | -34.4739 | -38.5997 | -36.4089 | -42.0171 | -35.5338 | -37.1403 | -35.5221 | -41.2427 | 333 | -37.75 | -35.4882 | -40.7314 | -42.7627 | -29.6182 | -35.5117 | -37.711 | -35.2617 | -40.9658 | -42.5752 | -29.8916 | -35.9726 | -35.9345 | -34.5673 | -42.6054 | -43.3789 | -30.0547 | -42.1702 | -35.8955 | -34.3408 | -42.8398 | -43.1914 | -30.3281 | -42.6311
334 | -7.3496 | 0 | -7.3326 | 0 | -7.5184 | 0 | -7.1043 | 0 | -39.795 | -90.8581 | -35.4261 | 50.2066 | -43.4273 | -67.6288 | -45.4218 | 92.5735 | -52.5468 | 176.5572 | -49.9482 | 89.8237 | -40.8117 | -20.2975 | -35.9279 | 138.8393 | -48.3349 | 58.9702 | -41.2363 | 163.0957 | -52.2854 | -107.581 | -43.9494 | 157.8851 | -24.6089 | 67.0811 | -15.9152 | 56.9384 | -19.8352 | 37.5005 | -16.2331 | 93.1714 | -27.5976 | 157.5653 | -17.424 | 111.1647 | -24.9962 | 3.3486 | -24.1525 | 115.1744 | -42.5092 | -43.0036 | -42.0301 | -47.8725 | -50.0952 | -36.984 | -42.9498 | -44.6199 | -43.2949 | -49.9224 | -50.3834 | -37.3621 | -47.7242 | 334 | -33.5959 | -38.567 | -34.8746 | -42.1392 | -34.522 | -37.8493 | -34.3075 | -42.1568 | 334 | -37.2703 | -35.9453 | -40.5229 | -42.7626 | -29.6514 | -35.4314 | -37.2873 | -35.7765 | -40.7682 | -42.5768 | -29.8797 | -35.8455 | -35.654 | -34.6805 | -42.5728 | -43.0508 | -30.0295 | -40.2058 | -35.671 | -34.5117 | -42.8181 | -42.865 | -30.2578 | -40.6199
335 | -7.3788 | 0 | -7.2788 | 0 | -7.4844 | 0 | -7.1171 | 0 | -41.5483 | -100.4245 | -33.7792 | 41.6701 | -42.6733 | -73.3828 | -44.7927 | 70.0984 | -52.8249 | 161.0971 | -49.6188 | 104.7787 | -43.1493 | -19.2318 | -33.5812 | 129.3246 | -45.9236 | 35.7627 | -40.7366 | 154.7171 | -57.5499 | -131.2734 | -46.3826 | 167.8968 | -24.8983 | 73.8816 | -17.6457 | 53.1584 | -21.4293 | 32.0006 | -16.2002 | 89.6671 | -27.1531 | 153.6014 | -19.3331 | 108.1223 | -31.7364 | -7.6148 | -30.568 | 118.3553 | -42.215 | -42.827 | -42.0533 | -47.7541 | -49.7852 | -37.1061 | -43.0131 | -44.9965 | -43.6323 | -49.722 | -50.2906 | -37.3868 | -45.9535 | 335 | -32.6527 | -39.6498 | -33.3446 | -41.5385 | -32.9039 | -38.7101 | -32.6296 | -42.9823 | 335 | -37.6177 | -36.2535 | -40.3753 | -42.5064 | -29.8273 | -35.5287 | -37.7177 | -36.1479 | -40.637 | -42.3008 | -29.989 | -35.896 | -35.4482 | -34.6745 | -42.3432 | -43.0118 | -30.108 | -38.4691 | -35.5482 | -34.5689 | -42.6049 | -42.8062 | -30.2697 | -38.8364
336 | -7.4053 | 0 | -7.2725 | 0 | -7.4631 | 0 | -7.1477 | 0 | -43.0979 | -98.2406 | -33.1341 | 29.7153 | -42.0359 | -83.1801 | -45.8695 | 49.9804 | -53.5991 | 145.8374 | -46.8803 | 111.3087 | -43.5835 | -8.0845 | -32.6143 | 113.7599 | -45.7581 | 12.3372 | -40.7051 | 145.8365 | -64.7723 | -96.8842 | -45.5352 | -173.6601 | -24.2401 | 84.4374 | -18.7699 | 61.0441 | -22.5099 | 33.9452 | -15.7225 | 87.9376 | -26.5861 | 148.7163 | -20.0942 | 117.5113 | -39.8138 | 50.2095 | -29.0457 | -179.4963 | -42.3399 | -43.0355 | -42.0034 | -47.8099 | -49.4594 | -37.2875 | -43.0361 | -45.746 | -43.7529 | -49.9003 | -50.3911 | -37.5232 | -45.3707 | 336 | -32.2364 | -41.0099 | -32.7381 | -40.5823 | -32.0893 | -38.8886 | -31.7999 | -42.6085 | 336 | -38.3407 | -36.3476 | -40.4046 | -42.1869 | -30.015 | -35.573 | -38.4735 | -36.2898 | -40.6622 | -41.9963 | -30.1398 | -35.8884 | -35.6302 | -34.5981 | -42.495 | -43.1186 | -30.2507 | -37.9076 | -35.763 | -34.5403 | -42.7526 | -42.928 | -30.3755 | -38.223
337 | -7.4192 | 0 | -7.3254 | 0 | -7.4426 | 0 | -7.2044 | 0 | -42.7465 | -90.1565 | -33.4263 | 17.4501 | -42.0437 | -94.6484 | -48.7789 | 38.5632 | -54.6836 | 133.1238 | -44.1895 | 101.2379 | -41.5517 | -2.7978 | -32.9482 | 98.452 | -47.7921 | -6.8537 | -41.0541 | 138.6028 | -62.9209 | -50.8078 | -42.1304 | -168.9047 | -22.8429 | 92.3546 | -17.5163 | 72.0408 | -22.2139 | 37.2433 | -15.3087 | 86.6799 | -25.4496 | 134.947 | -17.9904 | 122.2711 | -30.0617 | 74.5732 | -21.7698 | 171.8867 | -42.6736 | -43.4861 | -41.9822 | -47.99 | -49.2478 | -37.4549 | -42.884 | -46.4583 | -43.8372 | -50.6223 | -50.5989 | -37.759 | -45.9464 | 337 | -32.4418 | -41.5627 | -32.9612 | -39.8307 | -32.2637 | -38.2706 | -31.8918 | -41.0587 | 337 | -39.0391 | -36.418 | -40.5708 | -41.9224 | -30.1295 | -35.4414 | -39.1329 | -36.3946 | -40.7856 | -41.8052 | -30.2505 | -35.6796 | -36.0669 | -34.563 | -43.2031 | -43.2735 | -30.4336 | -38.5038 | -36.1607 | -34.5396 | -43.4179 | -43.1563 | -30.5546 | -38.742
338 | -7.4548 | 0 | -7.3998 | 0 | -7.4418 | 0 | -7.2974 | 0 | -40.915 | -96.7921 | -34.8062 | 11.1753 | -42.9419 | -102.2179 | -51.3641 | 56.9701 | -55.7865 | 123.1835 | -43.236 | 82.087 | -39.6002 | -15.719 | -34.5223 | 90.8688 | -51.5463 | 7.7109 | -41.3957 | 135.2781 | -59.3767 | -74.1816 | -39.9977 | 175.7991 | -20.4954 | 90.0711 | -15.2017 | 67.1667 | -21.5035 | 33.2614 | -13.9138 | 80.0897 | -25.9219 | 122.8374 | -15.9793 | 111.4656 | -29.0713 | 50.8372 | -18.4046 | 150.214 | -42.783 | -43.7079 | -41.9592 | -48.2635 | -49.2166 | -37.4657 | -42.4779 | -46.5512 | -44.1228 | -51.9545 | -50.6889 | -37.9848 | -47.0084 | 338 | -33.3493 | -40.4122 | -34.1405 | -39.9611 | -33.2823 | -37.3681 | -32.7937 | -39.6573 | 338 | -39.0964 | -36.668 | -40.8087 | -41.8168 | -30.0659 | -35.0361 | -39.1514 | -36.681 | -40.9661 | -41.7748 | -30.1683 | -35.1805 | -36.2531 | -34.5044 | -44.4997 | -43.2891 | -30.585 | -39.5666 | -36.3081 | -34.5174 | -44.6571 | -43.2471 | -30.6874 | -39.711
339 | -7.4781 | 0 | -7.4653 | 0 | -7.459 | 0 | -7.4043 | 0 | -40.1754 | -112.2062 | -35.7658 | 17.4687 | -43.5639 | -100.7449 | -48.345 | 72.3374 | -56.9873 | 114.7789 | -43.9345 | 64.4054 | -39.2338 | -35.6117 | -35.7384 | 96.4491 | -47.4641 | 32.2884 | -41.373 | 132.8687 | -60.4321 | -108.8763 | -39.6304 | 158.7721 | -19.3089 | 83.6756 | -14.0014 | 54.6857 | -22.368 | 25.4376 | -13.4789 | 71.1391 | -27.3427 | 107.5234 | -15.2608 | 94.6492 | -30.3065 | 28.6858 | -16.9311 | 122.8682 | -42.5203 | -43.514 | -41.9472 | -48.4695 | -49.3171 | -37.4242 | -42.0903 | -46.0176 | -44.3687 | -53.1098 | -50.7035 | -38.1074 | -46.272 | 339 | -33.9237 | -39.4815 | -34.9463 | -40.6332 | -33.9361 | -37.1423 | -33.4818 | -38.9375 | 339 | -38.5395 | -36.8906 | -40.9914 | -41.8518 | -29.9589 | -34.6313 | -38.5523 | -36.9097 | -41.0652 | -41.8581 | -30.0199 | -34.686 | -36.0359 | -34.4691 | -45.6317 | -43.2382 | -30.6421 | -38.813 | -36.0487 | -34.4882 | -45.7055 | -43.2445 | -30.7031 | -38.8677
340 | -7.5155 | 0 | -7.4362 | 0 | -7.4614 | 0 | -7.4462 | 0 | -40.8817 | -128.478 | -34.3043 | 23.8647 | -42.486 | -95.9657 | -45.3583 | 62.5056 | -58.6808 | 110.5541 | -45.9442 | 53.662 | -40.7375 | -54.8837 | -34.5425 | 104.504 | -43.2519 | 18.5292 | -40.9164 | 129.5065 | -66.7104 | -156.6141 | -40.7416 | 144.6955 | -19.9858 | 77.5246 | -14.1675 | 41.0932 | -24.7102 | 22.6111 | -13.5778 | 60.8478 | -30.5889 | 105.1696 | -15.994 | 78.2425 | -35.9602 | 19.9836 | -17.11 | 98.3633 | -42.3153 | -43.0358 | -42.09 | -48.4403 | -49.4403 | -37.4733 | -42.112 | -45.3403 | -44.4022 | -53.1628 | -50.7917 | -38.063 | -44.5676 | 340 | -32.931 | -39.504 | -33.7087 | -40.798 | -33.1602 | -37.8101 | -32.8681 | -38.8005 | 340 | -37.8248 | -36.8867 | -40.9248 | -42.0041 | -30.0371 | -34.6506 | -37.9041 | -36.9408 | -40.9941 | -41.9789 | -30.0271 | -34.6658 | -35.5203 | -34.5745 | -45.6473 | -43.3555 | -30.6268 | -37.1062 | -35.5996 | -34.6286 | -45.7166 | -43.3303 | -30.6168 | -37.1214
341 | -7.4988 | 0 | -7.3934 | 0 | -7.4519 | 0 | -7.4285 | 0 | -42.8223 | -138.3594 | -32.3917 | 17.0979 | -40.4083 | -103.8696 | -44.22 | 42.6503 | -59.4086 | 122.6595 | -48.4473 | 58.629 | -43.974 | -63.556 | -32.457 | 99.6071 | -41.3198 | -4.4854 | -40.3167 | 123.0786 | -68.0832 | 64.9233 | -42.7823 | 142.5217 | -20.6968 | 77.6574 | -15.5136 | 31.7359 | -26.6611 | 35.5664 | -14.3938 | 52.0309 | -31.1648 | 114.1253 | -18.3586 | 68.8639 | -38.4302 | 69.817 | -19.1805 | 79.1114 | -42.249 | -42.5654 | -42.5302 | -48.2333 | -49.456 | -37.6396 | -42.3895 | -45.198 | -44.4676 | -52.6785 | -50.9012 | -37.9441 | -43.3319 | 341 | -31.428 | -40.4 | -32.0157 | -39.7277 | -31.6636 | -38.7559 | -31.4655 | -38.9741 | 341 | -37.6992 | -36.9688 | -40.7345 | -42.0626 | -30.2462 | -34.9376 | -37.8046 | -37.0157 | -40.8048 | -42.0041 | -30.2111 | -34.961 | -35.0666 | -35.0314 | -45.1797 | -43.5078 | -30.5507 | -35.88 | -35.172 | -35.0783 | -45.25 | -43.4493 | -30.5156 | -35.9034
342 | -7.5172 | 0 | -7.3384 | 0 | -7.4541 | 0 | -7.3655 | 0 | -44.6651 | -133.577 | -31.4652 | 4.5573 | -39.256 | -119.4787 | -44.6891 | 24.5082 | -56.4899 | 127.396 | -47.522 | 77.2655 | -46.6953 | -46.9932 | -31.3664 | 85.5469 | -40.9441 | -26.4862 | -40.161 | 113.4915 | -59.6757 | 12.5749 | -43.2388 | 154.461 | -20.8731 | 87.0917 | -17.0185 | 34.9132 | -25.8092 | 50.9863 | -15.7599 | 48.9985 | -29.8947 | 116.7408 | -20.9424 | 80.1302 | -35.0052 | 83.4216 | -23.3022 | 79.0303 | -42.2994 | -42.4854 | -42.8805 | -48.0728 | -49.401 | -37.9229 | -42.5806 | -45.7744 | -44.9352 | -52.3853 | -51.0103 | -37.958 | -42.9358 | 342 | -30.6224 | -41.526 | -31.1617 | -38.5816 | -30.7991 | -39.2503 | -30.5856 | -38.8949 | 342 | -38.2572 | -37.418 | -40.5556 | -42.0626 | -30.5845 | -35.1265 | -38.436 | -37.4811 | -40.7073 | -41.9469 | -30.5574 | -35.2151 | -34.9682 | -35.3633 | -44.8681 | -43.6719 | -30.6196 | -35.4817 | -35.147 | -35.4264 | -45.0198 | -43.5562 | -30.5925 | -35.5703
343 | -7.5372 | 0 | -7.3741 | 0 | -7.4719 | 0 | -7.3493 | 0 | -43.8168 | -125.8884 | -31.7183 | -10.3234 | -39.5145 | -137.139 | -46.6095 | 10.1457 | -53.8369 | 112.9797 | -44.5291 | 72.1295 | -44.2883 | -31.9777 | -31.7129 | 69.5941 | -41.7863 | -44.8903 | -40.6108 | 104.4645 | -56.0897 | -22.2254 | -41.2966 | 157.4488 | -19.2375 | 95.3304 | -16.5912 | 43.8272 | -24.5625 | 56.1736 | -16.1266 | 54.0964 | -30.6016 | 94.2528 | -19.4058 | 97.3872 | -36.1253 | 82.5866 | -24.2771 | 115.1644 | -42.4053 | -42.7257 | -42.9825 | -48.0264 | -49.6123 | -38.1164 | -42.6866 | -46.9211 | -45.4591 | -52.7413 | -51.3272 | -38.1867 | -43.1999 | 343 | -30.8271 | -41.7077 | -31.3649 | -38.2043 | -31.0924 | -38.9759 | -30.7824 | -38.4488 | 343 | -39.3839 | -37.9219 | -40.4892 | -42.2382 | -30.7423 | -35.2147 | -39.547 | -37.9872 | -40.6771 | -42.1404 | -30.7671 | -35.3373 | -35.1885 | -35.4453 | -45.2041 | -43.9531 | -30.8126 | -35.728 | -35.3516 | -35.5106 | -45.392 | -43.8553 | -30.8374 | -35.8506
344 | -7.593 | 0 | -7.4461 | 0 | -7.4907 | 0 | -7.4049 | 0 | -42.1439 | -134.0518 | -33.142 | -18.5692 | -41.1119 | -150.5036 | -49.5769 | 11.4892 | -52.4046 | 93.0377 | -43.2267 | 54.0995 | -41.8236 | -42.4807 | -33.4078 | 61.6188 | -43.4061 | -55.5731 | -41.3925 | 99.4799 | -54.5823 | -50.9984 | -39.8809 | 148.0279 | -17.2976 | 93.9169 | -14.9904 | 42.0144 | -24.1283 | 60.9989 | -15.5251 | 56.0169 | -32.6056 | 45.4863 | -16.7154 | 93.3035 | -35.8248 | 124.7602 | -19.2384 | 117.6055 | -42.7351 | -43.2992 | -43.2609 | -48.1804 | -50.3796 | -38.2054 | -42.7821 | -47.9399 | -45.6906 | -53.8211 | -51.7078 | -38.5336 | -43.8087 | 344 | -32.0515 | -41.0896 | -32.6467 | -38.8362 | -32.4594 | -38.4844 | -31.9955 | -38.1842 | 344 | -40.3469 | -38.0976 | -40.5874 | -42.9335 | -30.7593 | -35.2914 | -40.4938 | -38.1999 | -40.7755 | -42.8889 | -30.8005 | -35.3772 | -35.7062 | -35.6679 | -46.2281 | -44.2617 | -31.0875 | -36.318 | -35.8531 | -35.7702 | -46.4162 | -44.2171 | -31.1287 | -36.4038
345 | -7.6496 | 0 | -7.4856 | 0 | -7.509 | 0 | -7.4856 | 0 | -41.9168 | -148.4708 | -34.6085 | -14.5004 | -43.279 | -151.0014 | -49.5929 | 30.6006 | -52.1115 | 70.56 | -43.9332 | 34.2394 | -41.2738 | -60.9347 | -35.0901 | 67.9603 | -44.5767 | -55.4358 | -41.9229 | 98.9197 | -54.6579 | -80.4372 | -39.6816 | 136.348 | -15.8033 | 86.4082 | -14.115 | 31.2102 | -22.9398 | 69.5033 | -14.7165 | 50.0702 | -31.274 | -57.5139 | -15.7125 | 79.341 | -29.3842 | 136.429 | -16.8845 | 101.8432 | -43.1416 | -43.8096 | -43.9971 | -48.3604 | -51.2432 | -38.212 | -43.0324 | -48.2199 | -45.677 | -54.7668 | -51.8996 | -38.8918 | -44.2725 | 345 | -33.3973 | -40.8912 | -34.007 | -40.2883 | -33.7761 | -38.4702 | -33.1734 | -38.3598 | 345 | -40.5703 | -38.0274 | -40.7108 | -43.7576 | -30.7264 | -35.5234 | -40.7343 | -38.168 | -40.8748 | -43.7342 | -30.7264 | -35.5468 | -36.16 | -36.3475 | -47.1172 | -44.414 | -31.4062 | -36.7635 | -36.324 | -36.4881 | -47.2812 | -44.3906 | -31.4062 | -36.7869
346 | -7.6753 | 0 | -7.4657 | 0 | -7.5526 | 0 | -7.5357 | 0 | -42.7892 | -162.1198 | -33.5827 | -5.8859 | -43.3445 | -139.185 | -46.7087 | 31.0655 | -53.0463 | 49.9888 | -46.4226 | 20.1163 | -42.2845 | -79.8009 | -33.8191 | 79.8549 | -43.9897 | -51.8259 | -41.661 | 99.9158 | -56.5846 | -107.3489 | -40.4828 | 127.4549 | -15.0675 | 77.7321 | -14.5643 | 19.0604 | -20.7492 | 71.5647 | -14.7005 | 39.4951 | -25.632 | -111.9526 | -15.7898 | 65.9161 | -25.5733 | 116.0756 | -15.9402 | 84.0453 | -43.2155 | -43.6891 | -44.9642 | -48.3874 | -51.5045 | -38.2907 | -43.2001 | -48.2167 | -45.8785 | -54.5477 | -51.8329 | -39.1386 | -43.9647 | 346 | -32.6989 | -41.0288 | -33.1661 | -41.305 | -32.89 | -38.877 | -32.4204 | -38.8081 | 346 | -40.5414 | -38.2032 | -40.7121 | -44.0388 | -30.825 | -35.6475 | -40.751 | -38.3259 | -40.8517 | -43.9519 | -30.755 | -35.6644 | -36.0138 | -37.2889 | -46.8724 | -44.3672 | -31.6729 | -36.4121 | -36.2234 | -37.4116 | -47.012 | -44.2803 | -31.6029 | -36.429
347 | -7.7123 | 0 | -7.4112 | 0 | -7.6066 | 0 | -7.5039 | 0 | -44.59 | -171.5802 | -31.4991 | -9.7872 | -41.2765 | -138.9892 | -45.0806 | 14.943 | -55.3297 | 37.8338 | -50.4408 | 22.6406 | -45.1402 | -92.9086 | -31.3187 | 75.3843 | -42.2641 | -56.7431 | -40.7212 | 96.6283 | -60.3079 | -120.0421 | -41.5907 | 126.2242 | -14.8181 | 69.8184 | -16.45 | 13.2882 | -19.1224 | 65.1556 | -16.0686 | 29.109 | -22.3887 | -150.1215 | -17.0604 | 59.337 | -23.2122 | 87.6199 | -16.8631 | 68.7071 | -43.1726 | -43.1454 | -45.9308 | -48.3562 | -51.2508 | -38.4774 | -43.1924 | -48.6457 | -46.435 | -53.9307 | -51.6339 | -39.2746 | -43.4524 | 347 | -30.8758 | -41.6288 | -31.26 | -40.6299 | -30.8191 | -39.3461 | -30.4956 | -38.8727 | 347 | -40.9334 | -38.7227 | -40.6439 | -43.8396 | -31.0662 | -35.5858 | -41.2345 | -38.8284 | -40.8523 | -43.6442 | -30.9735 | -35.6885 | -35.4331 | -38.2185 | -46.2184 | -44.2227 | -31.8634 | -35.8458 | -35.7342 | -38.3242 | -46.4268 | -44.0273 | -31.7707 | -35.9485
348 | -7.7278 | 0 | -7.4185 | 0 | -7.6288 | 0 | -7.4331 | 0 | -46.9509 | -168.6392 | -30.3184 | -23.1211 | -39.6208 | -149.3806 | -45.176 | -4.7378 | -57.3979 | 44.2224 | -51.0233 | 52.8695 | -49.4111 | -81.2776 | -29.9548 | 60.5833 | -40.9001 | -70.8741 | -39.9852 | 87.7161 | -62.1857 | -109.4389 | -41.5268 | 129.9408 | -15.5001 | 62.1585 | -18.3619 | 21.2812 | -18.4436 | 54.948 | -18.9665 | 24.4297 | -21.0454 | 179.5179 | -17.8852 | 65.7237 | -24.3832 | 61.8143 | -18.9721 | 61.8147 | -43.3439 | -42.6831 | -46.5712 | -48.34 | -50.9142 | -38.7456 | -43.1997 | -49.4803 | -47.5559 | -53.7583 | -51.4419 | -39.3553 | -43.0762 | 348 | -29.7526 | -42.8094 | -30.1431 | -39.2502 | -29.5735 | -39.4924 | -29.2769 | -38.1746 | 348 | -41.7525 | -39.8281 | -40.6122 | -43.4957 | -31.3271 | -35.5709 | -42.0618 | -39.9271 | -40.9069 | -43.2854 | -31.3125 | -35.7666 | -34.9553 | -38.8434 | -46.0305 | -44.0234 | -31.9368 | -35.4474 | -35.2646 | -38.9424 | -46.3252 | -43.8131 | -31.9222 | -35.6431
349 | -7.6957 | 0 | -7.4848 | 0 | -7.6371 | 0 | -7.4145 | 0 | -46.8613 | -153.8388 | -30.418 | -38.5543 | -39.0569 | -165.5614 | -47.1397 | -24.6351 | -55.9164 | 55.2541 | -47.6041 | 56.4697 | -47.1312 | -52.1536 | -30.0166 | 44.482 | -40.5139 | -89.1002 | -39.9224 | 76.4527 | -60.1126 | -113.699 | -40.621 | 127.9423 | -16.08 | 59.0583 | -16.7805 | 36.7308 | -18.3597 | 46.9809 | -21.2726 | 42.9294 | -21.6575 | 158.7205 | -16.5588 | 70.9798 | -29.431 | 40.7254 | -19.7066 | 71.5369 | -43.5977 | -42.6211 | -46.7852 | -48.4531 | -51.0781 | -39.0352 | -43.0668 | -50.2504 | -49.1918 | -54.2035 | -51.227 | -39.4926 | -42.8971 | 349 | -29.7753 | -43.718 | -30.246 | -38.4111 | -29.5688 | -39.1316 | -29.264 | -37.5328 | 349 | -42.5547 | -41.4961 | -40.7574 | -43.5933 | -31.5504 | -35.4297 | -42.7656 | -41.5547 | -41.0386 | -43.441 | -31.6207 | -35.6523 | -34.9254 | -39.0895 | -46.5078 | -43.7422 | -32.0078 | -35.26 | -35.1363 | -39.1481 | -46.789 | -43.5899 | -32.0781 | -35.4826
350 | -7.6943 | 0 | -7.6046 | 0 | -7.6537 | 0 | -7.4393 | 0 | -44.529 | -155.7548 | -31.872 | -50.1589 | -39.6878 | 178.7435 | -52.1304 | -35.5987 | -53.3185 | 49.7523 | -46.5259 | 43.1965 | -43.443 | -62.1828 | -31.4482 | 33.001 | -41.2772 | -105.4451 | -40.5157 | 67.4529 | -59.3868 | -138.1422 | -40.2556 | 121.2627 | -16.6197 | 61.2187 | -14.2261 | 33.1347 | -18.3623 | 44.0632 | -19.1316 | 60.9757 | -23.5538 | 152.7578 | -14.5775 | 63.9502 | -37.4349 | 117.6274 | -18.4033 | 75.6007 | -43.7408 | -42.9007 | -46.8596 | -48.7231 | -52.0433 | -39.2508 | -42.7409 | -50.4074 | -50.6975 | -54.9022 | -51.1593 | -39.7666 | -42.8962 | 350 | -31.0098 | -43.37 | -31.6864 | -38.7171 | -30.7768 | -38.6898 | -30.4599 | -37.6966 | 350 | -42.7131 | -43.0032 | -41.0288 | -44.4387 | -31.6462 | -35.0872 | -42.8028 | -43.0438 | -41.2838 | -44.3896 | -31.8115 | -35.3016 | -35.2064 | -39.1653 | -47.2079 | -43.5547 | -32.162 | -35.2425 | -35.2961 | -39.2059 | -47.4629 | -43.5056 | -32.3273 | -35.4569
351 | -7.7134 | 0 | -7.685 | 0 | -7.69 | 0 | -7.4904 | 0 | -43.4891 | -169.6766 | -33.9016 | -49.2083 | -41.3066 | 168.0524 | -57.1036 | 15.5001 | -51.6257 | 35.6508 | -47.4897 | 31.97 | -42.2369 | -84.5587 | -33.3583 | 34.5678 | -42.7758 | -117.7256 | -41.4494 | 61.8694 | -59.9211 | -162.2013 | -40.6186 | 113.4782 | -16.3896 | 66.2727 | -12.9151 | 20.331 | -18.0124 | 41.5607 | -17.0502 | 58.3754 | -23.382 | 168.8342 | -13.7853 | 49.4631 | -26.4044 | 136.0099 | -17.6619 | 67.52 | -43.8446 | -43.2284 | -47.4692 | -48.8212 | -53.2505 | -39.375 | -42.7219 | -50.2973 | -51.1683 | -54.9177 | -51.6147 | -40.0725 | -42.9911 | 351 | -32.7899 | -42.7078 | -33.6957 | -40.0559 | -32.4107 | -38.7815 | -32.0772 | -38.5227 | 351 | -42.5839 | -43.4549 | -41.1078 | -45.5655 | -31.69 | -35.0319 | -42.6123 | -43.4783 | -41.3308 | -45.5605 | -31.8846 | -35.2315 | -35.515 | -39.7558 | -47.2043 | -43.9297 | -32.3875 | -35.3011 | -35.5434 | -39.7792 | -47.4273 | -43.9247 | -32.5821 | -35.5007
352 | -7.7706 | 0 | -7.6735 | 0 | -7.7273 | 0 | -7.5198 | 0 | -43.797 | 175.3687 | -33.8897 | -36.9046 | -43.1971 | 168.2957 | -49.7329 | 41.4574 | -50.8381 | 19.0869 | -49.5544 | 36.215 | -43.0315 | -107.6274 | -33.0791 | 46.6837 | -44.6018 | -122.2497 | -41.9605 | 62.4036 | -60.0269 | 169.0538 | -41.4903 | 111.1141 | -15.425 | 67.6629 | -12.9256 | 5.4889 | -17.3252 | 36.9833 | -16.3145 | 49.9264 | -20.3836 | 167.9866 | -13.9656 | 33.7036 | -22.2007 | 114.4792 | -17.9863 | 57.02 | -43.7862 | -43.2424 | -48.4693 | -48.669 | -53.2784 | -39.4299 | -43.068 | -50.989 | -50.8917 | -53.9586 | -52.5211 | -40.3328 | -43.0109 | 352 | -33.0281 | -42.1756 | -33.6647 | -41.725 | -32.3916 | -39.4149 | -32.0289 | -39.7222 | 352 | -43.2184 | -43.1211 | -40.8984 | -45.6049 | -31.7564 | -35.3407 | -43.3155 | -43.1644 | -41.1492 | -45.5511 | -31.9101 | -35.5482 | -35.4718 | -40.6987 | -46.188 | -44.8476 | -32.6593 | -35.2836 | -35.5689 | -40.742 | -46.4388 | -44.7938 | -32.813 | -35.4911
353 | -7.8245 | 0 | -7.5784 | 0 | -7.7424 | 0 | -7.5198 | 0 | -45.1271 | 162.5038 | -31.6241 | -36.0966 | -43.2672 | 176.0715 | -45.7961 | 23.6209 | -50.9216 | 3.5593 | -48.6993 | 51.2965 | -45.7455 | -127.7884 | -30.6984 | 45.6895 | -45.3572 | -117.2824 | -41.2666 | 61.1875 | -60.9013 | 130.9112 | -41.8047 | 115.0359 | -14.3592 | 63.4049 | -14.2124 | -7.4217 | -17.2628 | 28.9969 | -16.9497 | 44.6504 | -17.9529 | 154.0806 | -15.4818 | 20.767 | -21.3322 | 92.6645 | -20.0571 | 54.8928 | -43.5973 | -42.9723 | -49.277 | -48.4411 | -52.195 | -39.4098 | -43.3948 | -52.6253 | -51.1096 | -52.9456 | -53.4495 | -40.469 | -42.862 | 353 | -31.1586 | -41.8625 | -31.3798 | -41.6299 | -30.4229 | -39.9076 | -30.0342 | -40.1802 | 353 | -44.8008 | -43.2851 | -40.6166 | -44.6166 | -31.8314 | -35.6524 | -45.0469 | -43.3672 | -40.9213 | -44.4526 | -31.89 | -35.875 | -35.1478 | -41.4525 | -45.1211 | -45.8711 | -32.8906 | -35.1196 | -35.3939 | -41.5346 | -45.4258 | -45.7071 | -32.9492 | -35.3422
354 | -7.856 | 0 | -7.4816 | 0 | -7.724 | 0 | -7.5314 | 0 | -47.4741 | 157.709 | -30.0012 | -48.642 | -41.9544 | 175.4147 | -44.5281 | -0.6162 | -51.542 | -8.0251 | -45.9593 | 50.386 | -51.511 | -131.089 | -29.1956 | 32.1528 | -44.1881 | -115.7562 | -40.5075 | 53.3479 | -63.5455 | 90.8131 | -40.923 | 118.0179 | -13.8033 | 56.9244 | -16.5417 | -10.2339 | -18.13 | 23.7351 | -17.5632 | 49.8433 | -17.2621 | 135.5714 | -18.0296 | 15.0131 | -23.2128 | 78.0734 | -21.9988 | 72.166 | -43.5356 | -42.7078 | -49.6835 | -48.2271 | -51.1919 | -39.3679 | -43.6613 | -54.3256 | -52.2349 | -52.1769 | -53.8448 | -40.5912 | -42.7849 | 354 | -29.6602 | -42.2074 | -29.7456 | -40.1715 | -29.0355 | -40.1559 | -28.6223 | -39.2293 | 354 | -46.4696 | -44.3789 | -40.3711 | -43.7103 | -31.8863 | -35.9373 | -46.844 | -44.5109 | -40.6957 | -43.4679 | -31.8365 | -36.1299 | -34.8518 | -41.8275 | -44.3209 | -46.3632 | -33.1096 | -35.0609 | -35.2262 | -41.9595 | -44.6455 | -46.1208 | -33.0598 | -35.2535
355 | -7.8538 | 0 | -7.4423 | 0 | -7.7203 | 0 | -7.5979 | 0 | -48.9307 | 169.5212 | -29.7178 | -65.1414 | -41.0221 | 167.0178 | -45.4215 | -23.5492 | -52.3616 | -13.1145 | -44.4687 | 36.0296 | -53.0024 | -80.2731 | -29.0775 | 16.324 | -42.9843 | -125.7189 | -40.5613 | 41.5864 | -71.4556 | 73.2842 | -40.0098 | 112.4702 | -14.3745 | 50.3748 | -17.7384 | 0.9629 | -19.52 | 23.8851 | -16.5475 | 55.8936 | -18.0725 | 120.7215 | -19.4727 | 26.601 | -25.2354 | 84.9479 | -18.6613 | 88.8524 | -43.5315 | -42.54 | -49.7984 | -48.1292 | -50.9143 | -39.4111 | -43.8134 | -54.8844 | -54.1624 | -51.7274 | -53.454 | -40.8922 | -42.5664 | 355 | -29.3593 | -43.2518 | -29.4632 | -39.1875 | -28.8875 | -40.3172 | -28.464 | -38.2349 | 355 | -47.0306 | -46.3086 | -40.2754 | -43.472 | -31.9688 | -36.0931 | -47.4421 | -46.4421 | -40.5313 | -43.194 | -31.8132 | -36.2155 | -34.6862 | -41.9446 | -43.8736 | -46.0117 | -33.4499 | -34.8461 | -35.0977 | -42.0781 | -44.1295 | -45.7337 | -33.2943 | -34.9685
356 | -7.8313 | 0 | -7.4657 | 0 | -7.7616 | 0 | -7.7274 | 0 | -47.1236 | 175.7166 | -30.8405 | -78.6664 | -40.9558 | 156.2865 | -48.735 | -39.4146 | -52.1661 | -13.4751 | -44.9749 | 18.4462 | -47.0772 | -78.2609 | -30.3064 | 3.1206 | -42.9678 | -140.2141 | -41.6325 | 32.0546 | -66.8275 | 136.125 | -39.8403 | 106.2027 | -15.2359 | 50.7456 | -16.4811 | 7.1373 | -19.4643 | 33.0198 | -14.702 | 52.0749 | -20.4628 | 120.2475 | -18.257 | 33.3078 | -23.3384 | 102.998 | -15.7209 | 81.4692 | -43.4142 | -42.5227 | -49.858 | -48.2111 | -51.4103 | -39.6398 | -43.5282 | -54.8671 | -55.843 | -51.4891 | -52.7469 | -41.4374 | -42.5725 | 356 | -30.3448 | -44.1064 | -30.6086 | -39.2766 | -29.9914 | -40.5317 | -29.5692 | -38.1123 | 356 | -47.0358 | -48.0117 | -40.3798 | -43.9446 | -32.1741 | -35.7666 | -47.4014 | -48.0814 | -40.4837 | -43.6487 | -31.9124 | -35.8008 | -34.6914 | -42.0267 | -43.6578 | -45.2812 | -33.9717 | -34.8109 | -35.057 | -42.0964 | -43.7617 | -44.9853 | -33.71 | -34.8451
357 | -7.8951 | 0 | -7.4967 | 0 | -7.8248 | 0 | -7.8013 | 0 | -45.284 | 164.8252 | -33.0069 | -82.889 | -41.4123 | 149.3057 | -54.0365 | -20.8051 | -51.2665 | -17.6401 | -47.4973 | 10.5412 | -44.4852 | -102.5372 | -32.3228 | 1.1736 | -43.9471 | -151.7966 | -42.8745 | 31.1775 | -60.1757 | 111.6379 | -40.0009 | 102.2426 | -15.0187 | 58.3343 | -15.337 | 1.3644 | -17.9704 | 33.9209 | -13.7342 | 40.1539 | -19.8658 | 134.8714 | -17.2429 | 26.2752 | -20.3545 | 99.4094 | -14.4492 | 67.0199 | -43.1522 | -42.3632 | -50.371 | -48.2655 | -52.1327 | -39.9765 | -42.9732 | -55.9302 | -56.399 | -51.4732 | -52.2506 | -42.1138 | -42.5653 | 357 | -32.2022 | -43.868 | -32.8222 | -40.1098 | -31.7936 | -40.5477 | -31.3234 | -38.5005 | 357 | -48.0351 | -48.5039 | -40.3704 | -44.636 | -32.4798 | -35.1484 | -48.4335 | -48.5742 | -40.4642 | -44.3079 | -32.1752 | -35.1719 | -34.4681 | -42.4759 | -43.5781 | -44.7539 | -34.6171 | -34.7405 | -34.8665 | -42.5462 | -43.6719 | -44.4258 | -34.3125 | -34.764
358 | -7.9994 | 0 | -7.4948 | 0 | -7.877 | 0 | -7.8114 | 0 | -45.1286 | 145.6237 | -33.9864 | -71.8774 | -41.9197 | 145.5422 | -50.3963 | 17.5639 | -50.4594 | -24.3523 | -49.8218 | 25.9394 | -44.7697 | -132.9044 | -32.6064 | 12.6771 | -45.2837 | -157.7346 | -42.5702 | 34.6151 | -57.284 | 87.7322 | -39.8055 | 101.0161 | -13.7661 | 60.0816 | -15.3339 | -9.4209 | -17 | 26.2002 | -13.9751 | 26.6723 | -16.9122 | 134.9211 | -17.6061 | 13.0816 | -19.0076 | 84.4043 | -14.6118 | 53.1181 | -43.1738 | -42.099 | -51.4987 | -48.3574 | -51.9785 | -40.181 | -42.8191 | -58.2403 | -56.1869 | -51.7214 | -52.2722 | -42.5528 | -42.3714 | 358 | -33.0598 | -43.1136 | -33.7789 | -40.7734 | -32.1346 | -40.4313 | -31.4957 | -38.6623 | 358 | -50.2409 | -48.1875 | -40.358 | -44.4837 | -32.6862 | -34.9421 | -50.7455 | -48.3099 | -40.546 | -44.1015 | -32.3696 | -35.0077 | -34.0996 | -43.4993 | -43.722 | -44.7774 | -35.058 | -34.4944 | -34.6042 | -43.6217 | -43.91 | -44.3952 | -34.7414 | -34.56
359 | -8.0842 | 0 | -7.4577 | 0 | -7.8959 | 0 | -7.7335 | 0 | -46.8379 | 127.2406 | -32.0378 | -65.3888 | -42.0003 | 144.5191 | -45.6814 | 8.6423 | -49.4733 | -33.2752 | -47.6944 | 42.3436 | -48.1404 | -161.6593 | -30.608 | 14.6136 | -46.5501 | -154.7119 | -41.6138 | 30.2352 | -54.5582 | 64.8457 | -39.324 | 96.9079 | -12.6345 | 54.9986 | -16.6367 | -16.9437 | -17.4225 | 15.6023 | -15.535 | 17.3599 | -15.4449 | 122.1209 | -19.402 | 3.9802 | -19.6749 | 68.4769 | -16.1936 | 42.2354 | -43.5234 | -42.071 | -52.2398 | -48.3789 | -50.625 | -40.071 | -43.3444 | -59.8217 | -56.2717 | -51.989 | -53.3054 | -42.2787 | -42.3668 | 359 | -31.4917 | -42.2891 | -31.7423 | -40.3912 | -30.4247 | -40.5646 | -29.7668 | -38.4627 | 359 | -51.7375 | -48.1875 | -40.2947 | -43.1673 | -32.6133 | -35.4485 | -52.364 | -48.3758 | -40.6454 | -42.7291 | -32.3375 | -35.6109 | -33.9868 | -44.1556 | -43.9048 | -45.8477 | -34.821 | -34.4709 | -34.6133 | -44.3439 | -44.2555 | -45.4095 | -34.5452 | -34.6333
360 | -8.0869 | 0 | -7.4355 | 0 | -7.8781 | 0 | -7.6784 | 0 | -50.1203 | 117.6045 | -30.0819 | -75.0178 | -41.3319 | 142.2994 | -43.6423 | -13.7339 | -48.905 | -45.6144 | -44.8225 | 38.256 | -56.1396 | -177.6288 | -29.0109 | 3.4715 | -45.5914 | -148.1551 | -40.8868 | 20.4945 | -53.127 | 34.302 | -38.9328 | 91.0915 | -12.3119 | 46.8398 | -18.062 | -16.301 | -18.8437 | 10.3713 | -17.6442 | 18.4703 | -14.9058 | 106.3601 | -22.28 | 9.0575 | -20.8896 | 68.9606 | -17.9927 | 49.8087 | -43.841 | -42.1704 | -52.2541 | -48.5129 | -49.3215 | -39.854 | -43.9003 | -57.7844 | -58.415 | -51.6933 | -54.1503 | -41.7922 | -42.3959 | 360 | -29.728 | -41.8162 | -29.7572 | -39.23 | -28.9083 | -40.5144 | -28.3412 | -37.9501 | 360 | -49.6975 | -50.3281 | -40.426 | -41.886 | -32.4185 | -36.0222 | -50.3489 | -50.5369 | -40.8345 | -41.4434 | -32.1756 | -36.2219 | -34.0835 | -44.1672 | -43.6064 | -46.7148 | -34.3567 | -34.5178 | -34.7349 | -44.376 | -44.0149 | -46.2722 | -34.1138 | -34.7175
361 | -8.0597 | 0 | -7.4386 | 0 | -7.8956 | 0 | -7.7198 | 0 | -53.6713 | 129.9439 | -29.4961 | -91.3847 | -40.5862 | 135.1633 | -43.8292 | -38.524 | -49.3053 | -56.9696 | -43.3947 | 23.618 | -59.0349 | -79.0209 | -28.6231 | -11.6711 | -43.7292 | -155.3317 | -40.8702 | 6.4652 | -54.2979 | 4.9227 | -39.058 | 83.614 | -12.7139 | 42.8836 | -18.6398 | -5.3247 | -19.789 | 21.6817 | -17.5743 | 31.5792 | -16.8096 | 96.2026 | -22.7199 | 24.9099 | -22.6033 | 79.9187 | -17.3216 | 62.1418 | -44.0082 | -42.5863 | -51.9339 | -48.8558 | -48.9144 | -39.7894 | -44.1964 | -55.1651 | -63.4933 | -51.2745 | -53.4151 | -41.63 | -42.3195 | 361 | -29.1553 | -42.4081 | -29.1714 | -38.3901 | -28.4873 | -40.6144 | -28.0158 | -37.6876 | 361 | -47.1054 | -55.4336 | -40.7961 | -41.4758 | -32.3508 | -36.3008 | -47.7265 | -55.5977 | -41.136 | -41.0188 | -32.0696 | -36.4766 | -34.5266 | -43.8742 | -43.2148 | -45.9765 | -34.1914 | -34.4239 | -35.1477 | -44.0383 | -43.5547 | -45.5195 | -33.9102 | -34.5997
362 | -8.0708 | 0 | -7.455 | 0 | -7.9501 | 0 | -7.8092 | 0 | -52.1366 | 148.6814 | -30.4124 | -107.0376 | -40.2733 | 125.346 | -46.3277 | -60.6284 | -49.617 | -61.4082 | -43.7157 | 6.2112 | -50.5988 | -89.4096 | -29.5127 | -26.4141 | -43.1314 | -172.0143 | -41.9362 | -7.4055 | -58.3932 | -5.0253 | -39.6436 | 79.4454 | -13.2552 | 45.0404 | -17.5901 | -4.741 | -18.453 | 27.8177 | -15.6635 | 31.2729 | -19.093 | 108.0823 | -21.1307 | 28.9547 | -19.6794 | 88.4055 | -15.0213 | 62.3477 | -43.966 | -43.4298 | -51.6521 | -49.3527 | -49.4699 | -39.9962 | -44.1659 | -54.5868 | -70.9692 | -51.2558 | -52.1972 | -41.829 | -42.6786 | 362 | -29.9593 | -43.9438 | -30.109 | -38.3172 | -29.2956 | -41.2966 | -28.8896 | -37.9963 | 362 | -46.516 | -62.8984 | -41.2819 | -42.0149 | -32.5412 | -36.2158 | -47.1318 | -63.0191 | -41.5435 | -41.5198 | -32.187 | -36.3567 | -35.359 | -43.5813 | -43.185 | -44.7422 | -34.374 | -34.7285 | -35.9748 | -43.702 | -43.4466 | -44.2471 | -34.0198 | -34.8694
363 | -8.2192 | 0 | -7.4666 | 0 | -7.9942 | 0 | -7.8817 | 0 | -49.8115 | 139.7931 | -32.6869 | -114.3164 | -40.4281 | 116.474 | -52.0546 | -65.3411 | -49.2686 | -65.2948 | -46.0542 | -4.3857 | -47.9434 | -118.1062 | -31.4562 | -32.4415 | -44.1883 | 172.8501 | -43.9944 | -14.1311 | -58.715 | 23.8755 | -40.1298 | 78.9867 | -12.3932 | 50.0018 | -17.2541 | -10.6038 | -16.8651 | 22.6598 | -14.5165 | 17.473 | -16.9122 | 123.5271 | -20.3816 | 19.9922 | -17.8308 | 78.6973 | -13.6044 | 51.8372 | -43.8018 | -44.0833 | -51.7771 | -49.4346 | -50.4932 | -40.3333 | -44.0017 | -56.8418 | -69.8247 | -51.8103 | -51.5134 | -42.4121 | -43.3359 | 363 | -31.9402 | -45.4502 | -32.4436 | -38.9533 | -31.139 | -42.4212 | -30.6954 | -38.648 | 363 | -48.6226 | -61.6055 | -41.2154 | -43.0266 | -32.8667 | -36.0075 | -49.3752 | -61.8305 | -41.5529 | -42.499 | -32.4516 | -36.12 | -35.8641 | -43.5579 | -43.5911 | -44.0468 | -34.9455 | -35.3417 | -36.6167 | -43.7829 | -43.9286 | -43.5192 | -34.5304 | -35.4542
364 | -8.4265 | 0 | -7.4657 | 0 | -8.0099 | 0 | -7.8741 | 0 | -49.3777 | 119.5392 | -34.3947 | -103.4105 | -40.5459 | 110.3005 | -53.8849 | -9.9207 | -48.8394 | -72.0881 | -49.0348 | 9.6003 | -47.9853 | -151.4066 | -32.8173 | -24.7671 | -46.2996 | 168.488 | -45.3402 | -8.9435 | -54.7093 | 23.1451 | -40.0428 | 81.2126 | -10.806 | 47.5162 | -18.004 | -15.5353 | -16.5206 | 7.4847 | -14.9137 | 0.3676 | -13.6332 | 117.0539 | -21.407 | 15.4197 | -17.2885 | 64.1471 | -13.2851 | 38.7492 | -43.672 | -43.4779 | -52.6054 | -48.8595 | -51.1759 | -40.8294 | -43.7977 | -60.0685 | -67.1726 | -52.3016 | -51.079 | -43.252 | -43.1641 | 364 | -33.3418 | -45.4224 | -34.201 | -39.4409 | -32.5021 | -43.1404 | -31.8643 | -39.0016 | 364 | -51.642 | -58.7461 | -40.433 | -43.7102 | -33.3637 | -35.7878 | -52.6028 | -59.1627 | -40.9854 | -43.166 | -32.9553 | -35.9236 | -35.0514 | -44.1789 | -43.8751 | -43.6133 | -35.7863 | -35.1542 | -36.0122 | -44.5955 | -44.4275 | -43.0691 | -35.3779 | -35.29
365 | -8.5681 | 0 | -7.4861 | 0 | -8.0369 | 0 | -7.8025 | 0 | -51.0086 | 92.5215 | -32.6478 | -92.6234 | -40.6257 | 103.841 | -47.5365 | -5.0926 | -48.4189 | -75.9391 | -46.8368 | 30.6791 | -50.6657 | 167.7957 | -31.5605 | -17.4794 | -47.2193 | 177.2742 | -44.7933 | -6.4131 | -52.6534 | 9.7293 | -39.1184 | 79.7137 | -9.8195 | 38.363 | -19.3367 | -11.2536 | -17.922 | -2.2296 | -17.1026 | -18.2454 | -12.0747 | 100.8845 | -23.2562 | 23.1833 | -17.827 | 55.0367 | -13.9319 | 29.2278 | -43.7978 | -42.2588 | -54.3213 | -48.4892 | -50.9228 | -41.165 | -43.9275 | -55.7087 | -63.5525 | -51.6736 | -51.1462 | -43.6306 | -42.648 | 365 | -31.9516 | -43.9845 | -32.3517 | -39.1474 | -31.3924 | -43.2632 | -30.6863 | -38.3296 | 365 | -47.1406 | -54.9844 | -39.9211 | -43.4367 | -33.6789 | -35.8906 | -48.2226 | -55.5156 | -40.6867 | -42.8859 | -33.3625 | -36.125 | -33.6907 | -45.7532 | -43.1055 | -43.6601 | -36.1445 | -34.6111 | -34.7727 | -46.2844 | -43.8711 | -43.1093 | -35.8281 | -34.8455
366 | -8.5472 | 0 | -7.529 | 0 | -8.0691 | 0 | -7.7408 | 0 | -55.9253 | 65.7759 | -30.4731 | -100.2074 | -40.6354 | 98.7079 | -44.928 | -26.221 | -47.0697 | -84.5205 | -43.5801 | 28.2994 | -57.1061 | 107.3711 | -29.781 | -23.7404 | -45.9496 | -175.2412 | -44.1507 | -12.1633 | -50.9667 | -3.7615 | -38.233 | 72.6546 | -9.756 | 27.7835 | -18.8015 | -2.602 | -20.349 | 0.7467 | -22.0263 | -28.2748 | -12.0555 | 84.0726 | -22.5716 | 39.2677 | -19.2998 | 55.2308 | -15.0581 | 23.9127 | -44.3837 | -41.5722 | -55.605 | -48.6415 | -49.4149 | -41.0917 | -44.5094 | -51.7409 | -61.8245 | -51.0368 | -52.529 | -43.1237 | -42.2114 | 366 | -30.0624 | -42.6487 | -30.1198 | -38.2427 | -29.6695 | -43.1511 | -29.0644 | -37.3606 | 366 | -43.1937 | -53.2773 | -40.0943 | -41.8859 | -33.5627 | -36.4403 | -44.2119 | -53.7554 | -40.9007 | -41.3458 | -33.3509 | -36.7686 | -33.025 | -47.0578 | -42.4896 | -45 | -35.5947 | -34.1423 | -34.0432 | -47.5359 | -43.296 | -44.4599 | -35.3829 | -34.4706
367 | -8.4181 | 0 | -7.5798 | 0 | -8.1093 | 0 | -7.7228 | 0 | -67.2684 | 60.1206 | -29.5541 | -115.3796 | -40.0648 | 93.0699 | -45.0691 | -49.1741 | -46.7641 | -101.2849 | -41.6743 | 12.8036 | -58.1565 | -0.2548 | -29.0433 | -37.4558 | -43.494 | 179.9408 | -43.7806 | -22.108 | -50.1727 | -27.2291 | -38.2242 | 62.4573 | -10.5732 | 19.969 | -17.0591 | -3.2512 | -20.4012 | 14.0695 | -27.5245 | 12.6371 | -13.5561 | 72.6401 | -20.0154 | 41.8315 | -18.7339 | 64.7394 | -15.9306 | 26.5287 | -44.8915 | -41.5773 | -56.2415 | -49.2548 | -48.1024 | -40.7648 | -44.7477 | -49.6445 | -58.3087 | -50.9001 | -52.4626 | -42.4804 | -42.1578 | 367 | -29.1835 | -42.8085 | -29.182 | -37.2678 | -28.885 | -42.7562 | -28.4199 | -36.8855 | 367 | -41.2264 | -49.8906 | -40.8367 | -40.5226 | -33.185 | -36.6384 | -42.0647 | -50.1994 | -41.532 | -39.9931 | -33.042 | -37.0249 | -33.1592 | -47.8234 | -42.482 | -44.8828 | -34.9006 | -34.0485 | -33.9975 | -48.1322 | -43.1773 | -44.3533 | -34.7576 | -34.435
368 | -8.3509 | 0 | -7.5969 | 0 | -8.139 | 0 | -7.7412 | 0 | -67.0838 | 149.3773 | -30.0851 | -131.4156 | -39.5334 | 83.2091 | -47.928 | -68.0742 | -48.1256 | -112.9219 | -41.4986 | -5.5946 | -53.5949 | -54.4168 | -29.6132 | -52.2158 | -41.9081 | 163.5965 | -44.0575 | -35.0516 | -52.394 | -50.0752 | -38.9491 | 56.1231 | -11.5 | 21.0063 | -16.0663 | -11.5427 | -18.2728 | 18.2004 | -22.0233 | 42.6087 | -15.8942 | 77.9006 | -18.473 | 29.5705 | -17.14 | 62.1384 | -15.7807 | 24.9038 | -45.1196 | -42.478 | -56.6314 | -50.2251 | -48.0258 | -40.5484 | -44.6594 | -49.4944 | -55.0892 | -51.2805 | -50.843 | -42.1116 | -43.0233 | 368 | -29.6172 | -44.9885 | -29.7162 | -37.0431 | -29.3481 | -43.061 | -28.9969 | -37.0425 | 368 | -41.1435 | -46.7383 | -41.8742 | -40.4289 | -32.9515 | -36.5204 | -41.8975 | -46.9502 | -42.4839 | -39.8868 | -32.8072 | -36.9182 | -34.1271 | -48.2805 | -42.9296 | -43.2461 | -34.5147 | -34.8843 | -34.8811 | -48.4924 | -43.5393 | -42.704 | -34.3704 | -35.2821
369 | -8.4752 | 0 | -7.6041 | 0 | -8.1198 | 0 | -7.7448 | 0 | -65.7226 | 127.4655 | -32.0177 | -142.1067 | -39.6414 | 69.5783 | -54.8744 | -61.3766 | -49.4634 | -113.4078 | -43.3262 | -22.2924 | -52.2172 | -89.0023 | -31.3325 | -59.6925 | -41.9143 | 143.9393 | -45.4238 | -49.7086 | -56.5588 | -43.7086 | -39.5106 | 53.4437 | -11.0481 | 26.9391 | -16.0932 | -24.6631 | -16.9669 | 7.375 | -19.4665 | 27.9237 | -14.7808 | 94.0634 | -18.3683 | 15.008 | -16.089 | 53.3097 | -15.7503 | 21.3156 | -45.244 | -44.0096 | -57.0409 | -50.6659 | -48.7596 | -40.5877 | -44.4205 | -51.5807 | -53.6158 | -52.3463 | -50.0299 | -42.0455 | -45.4493 | 369 | -31.3238 | -48.2863 | -31.6868 | -37.7881 | -30.9359 | -44.3305 | -30.573 | -37.4839 | 369 | -43.1055 | -45.1406 | -42.1907 | -41.1555 | -32.9836 | -36.3007 | -43.9766 | -45.496 | -42.9211 | -40.6398 | -32.8429 | -36.6757 | -35.5344 | -48.5657 | -43.8711 | -42.4258 | -34.4414 | -37.3295 | -36.4055 | -48.9211 | -44.6015 | -41.9101 | -34.3007 | -37.7045
370 | -8.7236 | 0 | -7.6045 | 0 | -8.1083 | 0 | -7.7087 | 0 | -74.7673 | 28.8087 | -34.2282 | -136.4503 | -40.3264 | 60.3911 | -52.4346 | 6.2461 | -49.4097 | -107.8207 | -47.7737 | -19.1645 | -53.7453 | -117.3842 | -32.8867 | -55.5354 | -43.6483 | 127.5089 | -48.1375 | -58.185 | -55.353 | -19.4624 | -39.8721 | 51.5006 | -9.5826 | 24.1171 | -17.1074 | -36.6815 | -17.1252 | -7.9963 | -19.8677 | 10.576 | -11.9442 | 90.7805 | -19.4835 | -1.2664 | -16.3814 | 41.7655 | -16.1881 | 15.5955 | -45.1857 | -44.2091 | -58.4064 | -49.5373 | -49.6779 | -41.295 | -44.1865 | -55.8622 | -53.0752 | -54.3584 | -49.9365 | -42.5849 | -48.7073 | 370 | -33.2742 | -47.6452 | -33.9779 | -39.1753 | -32.504 | -46.4797 | -31.9875 | -38.266 | 370 | -47.1386 | -44.3516 | -40.8137 | -42.0734 | -33.6905 | -36.0782 | -48.2577 | -44.9669 | -41.8286 | -41.5696 | -33.5863 | -36.4778 | -35.4855 | -49.6828 | -45.6348 | -42.332 | -34.9804 | -40.599 | -36.6046 | -50.2981 | -46.6497 | -41.8282 | -34.8762 | -40.9986
371 | -8.9133 | 0 | -7.5983 | 0 | -8.1401 | 0 | -7.6906 | 0 | -61.2864 | -64.1256 | -33.4732 | -123.1391 | -40.794 | 52.6707 | -45.6979 | 2.3724 | -47.9816 | -106.7854 | -46.8651 | 20.1103 | -60.0591 | -136.6244 | -32.2756 | -47.4005 | -46.1382 | 125.827 | -50.7207 | -51.428 | -52.5178 | -20.2391 | -39.9546 | 51.4032 | -8.6968 | 15.1084 | -19.2521 | -42.9429 | -19.3781 | -16.3757 | -23.664 | 4.1477 | -10.3593 | 76.7531 | -22.1328 | -10.0229 | -17.4209 | 35.7195 | -17.035 | 15.1881 | -44.9921 | -42.5144 | -62.2407 | -48.1327 | -50.3671 | -42.6667 | -43.8991 | -53.8472 | -52.5618 | -55.0905 | -49.739 | -43.5347 | -48.739 | 371 | -32.7288 | -43.6063 | -33.0368 | -39.2158 | -32.0938 | -48.2224 | -31.5386 | -38.8278 | 371 | -44.9339 | -43.6485 | -39.2194 | -42.7688 | -35.0684 | -35.759 | -46.2489 | -44.4217 | -40.4421 | -42.227 | -34.9761 | -36.2085 | -33.6011 | -53.3274 | -46.1772 | -42.1407 | -35.9364 | -40.5989 | -34.9161 | -54.1006 | -47.3999 | -41.5989 | -35.8441 | -41.0484
372 | -8.8916 | 0 | -7.612 | 0 | -8.2395 | 0 | -7.7141 | 0 | -54.3841 | -92.3776 | -31.2087 | -125.3815 | -41.1202 | 46.5832 | -42.6251 | -17.5858 | -46.1961 | -111.0863 | -42.199 | 21.3043 | -62.0284 | -31.8551 | -30.6558 | -50.8482 | -47.0696 | 136.4616 | -50.7624 | -41.1228 | -50.7736 | -24.9272 | -39.7194 | 47.3592 | -8.6897 | 3.4525 | -21.401 | -41.1994 | -21.51 | -9.6278 | -27.4402 | 35.6291 | -10.1841 | 61.6717 | -26.2446 | -2.6513 | -18.2332 | 38.5256 | -17.36 | 18.5251 | -45.0877 | -41.0708 | -74.719 | -47.701 | -50.0995 | -43.7622 | -43.901 | -49.3333 | -51.9854 | -53.0963 | -49.7174 | -43.6653 | -45.9281 | 372 | -30.7677 | -40.8465 | -30.595 | -37.9171 | -30.5546 | -47.5982 | -30.1104 | -38.707 | 372 | -40.4417 | -43.0938 | -38.8094 | -42.4875 | -36.1502 | -35.6615 | -41.7213 | -43.7459 | -39.9869 | -41.86 | -36.0481 | -36.1869 | -32.1792 | -65.8274 | -44.2047 | -42.1054 | -36.0533 | -37.6886 | -33.4588 | -66.4795 | -45.3822 | -41.4779 | -35.9512 | -38.214
373 | -8.7106 | 0 | -7.6403 | 0 | -8.3356 | 0 | -7.7692 | 0 | -51.1715 | -119.943 | -29.8394 | -138.7525 | -41.272 | 41.3075 | -41.8815 | -38.7238 | -44.5142 | -125.1438 | -39.5268 | 6.4126 | -53.1982 | -50.3492 | -29.7407 | -62.2547 | -45.1481 | 146.7948 | -49.5601 | -41.101 | -48.3197 | -36.4499 | -40.1506 | 43.6946 | -9.6912 | -5.6291 | -22.5866 | -38.5099 | -20.9389 | 6.1719 | -22.1066 | 65.9336 | -11.3692 | 50.3852 | -28.0811 | 23.2636 | -17.4676 | 44.2055 | -16.9383 | 19.9119 | -45.6356 | -40.5067 | -69.1981 | -48.0927 | -48.3505 | -43.4364 | -44.2341 | -47.0895 | -51.8513 | -51.3473 | -50.0192 | -42.527 | -44.0514 | 373 | -29.5081 | -39.6721 | -29.1577 | -36.5465 | -29.5984 | -45.1459 | -29.3212 | -38.4808 | 373 | -38.3789 | -43.1407 | -39.3821 | -40.7102 | -35.7961 | -35.8985 | -39.4492 | -43.5157 | -40.3235 | -40.0149 | -35.6672 | -36.4649 | -31.7961 | -60.4875 | -42.6367 | -42.3789 | -34.8867 | -35.7158 | -32.8664 | -60.8625 | -43.5781 | -41.6836 | -34.7578 | -36.2822
374 | -8.5828 | 0 | -7.6524 | 0 | -8.37 | 0 | -7.828 | 0 | -50.6588 | -140.0042 | -29.8226 | -155.4505 | -40.8561 | 33.2669 | -42.8993 | -55.479 | -44.3579 | -142.4164 | -38.4372 | -11.495 | -51.292 | -71.8767 | -29.9957 | -74.8761 | -42.2479 | 137.4189 | -48.4234 | -55.0903 | -47.9608 | -56.8356 | -40.4808 | 45.3527 | -11.1536 | -5.2143 | -24.6547 | -39.0154 | -19.3155 | 3.2687 | -18.9236 | 54.2672 | -13.3432 | 50.2866 | -26.7228 | 47.4558 | -16.5128 | 38.531 | -16.4366 | 14.1023 | -45.9641 | -41.0723 | -61.875 | -48.8938 | -47.5852 | -42.0098 | -44.4688 | -46.8544 | -50.9148 | -50.5352 | -48.961 | -41.245 | -44.9529 | 374 | -29.46 | -40.1525 | -29.0788 | -35.8156 | -29.7142 | -44.2255 | -29.5668 | -37.8223 | 374 | -38.2716 | -42.332 | -40.311 | -39.9328 | -34.3574 | -36.0988 | -39.202 | -42.5448 | -41.0658 | -39.2152 | -34.1818 | -36.6408 | -32.4895 | -53.2922 | -41.9524 | -41.3086 | -33.5926 | -36.5829 | -33.4199 | -53.505 | -42.7072 | -40.591 | -33.417 | -37.1249
375 | -8.6741 | 0 | -7.6733 | 0 | -8.3179 | 0 | -7.8313 | 0 | -51.294 | -147.5812 | -31.294 | -168.8143 | -40.6931 | 21.1094 | -45.2719 | -59.9107 | -45.2148 | -153.8568 | -38.9355 | -29.838 | -51.3104 | -85.9014 | -31.2836 | -84.4286 | -41.1047 | 117.1028 | -49.0582 | -80.4064 | -48.9502 | -65.674 | -39.6318 | 43.7536 | -11.0293 | 2.9562 | -28.1532 | -26.5102 | -19.3001 | -6.8291 | -18.1284 | 39.4151 | -12.9758 | 63.5836 | -24.1198 | 57.9949 | -16.5851 | 30.083 | -16.8709 | 6.5007 | -46.1725 | -43.2429 | -58.7906 | -49.1491 | -48.278 | -40.8991 | -44.5248 | -48.9311 | -49.721 | -51.1459 | -48.3451 | -40.4858 | -47.76 | 375 | -30.7831 | -41.7248 | -30.4585 | -36.1418 | -30.8142 | -44.8743 | -30.6279 | -37.0088 | 375 | -40.257 | -41.0469 | -40.475 | -40.6047 | -33.2258 | -36.2069 | -41.2578 | -41.4031 | -41.3178 | -39.9601 | -33.0678 | -36.6935 | -34.5688 | -50.1165 | -42.4718 | -40.6718 | -32.8125 | -39.4421 | -35.5696 | -50.4727 | -43.3146 | -40.0272 | -32.6545 | -39.9287
376 | -8.95 | 0 | -7.7191 | 0 | -8.2577 | 0 | -7.8043 | 0 | -50.8808 | -144.0456 | -33.594 | -170.4659 | -41.4431 | 6.5935 | -46.5587 | -41.153 | -45.896 | -157.931 | -41.1666 | -38.4384 | -52.5148 | -90.7807 | -32.8993 | -85.8893 | -41.9754 | 97.5942 | -52.624 | -108.2497 | -48.9021 | -70.1308 | -39.7139 | 33.5982 | -9.4874 | 1.8548 | -28.352 | 24.5475 | -20.9328 | -15.2379 | -19.3193 | 30.1586 | -10.7031 | 62.8609 | -21.7569 | 59.6495 | -17.7231 | 23.5571 | -18.7544 | 4.147 | -46.2652 | -45.757 | -57.7617 | -48.1597 | -49.5113 | -40.9835 | -44.1605 | -54.3749 | -48.8718 | -54.0159 | -48.6527 | -40.8515 | -53.5201 | 376 | -32.865 | -42.5198 | -32.7112 | -37.597 | -32.3508 | -46.2077 | -32.0397 | -37.3722 | 376 | -45.4249 | -39.9218 | -39.2097 | -41.7922 | -33.2644 | -35.9028 | -46.6558 | -40.6141 | -40.3554 | -41.2536 | -33.1792 | -36.3562 | -36.807 | -48.8117 | -45.0659 | -40.9336 | -33.1324 | -45.2624 | -38.0379 | -49.504 | -46.2116 | -40.395 | -33.0472 | -45.7158
377 | -9.1688 | 0 | -7.747 | 0 | -8.2782 | 0 | -7.7938 | 0 | -49.5246 | -144.2035 | -34.0019 | -158.8503 | -42.5344 | -1.3297 | -42.9156 | -28.6694 | -45.534 | -159.9681 | -42.6632 | -26.5091 | -53.14 | -83.5311 | -33.4219 | -78.1762 | -44.0899 | 90.0445 | -57.972 | -127.9939 | -48.793 | -75.0401 | -41.2525 | 32.0341 | -8.4022 | -9.4236 | -22.9694 | 33.0302 | -23.0715 | -7.5322 | -21.1011 | 36.5798 | -9.1881 | 51.0981 | -19.8442 | 55.0127 | -18.0895 | 30.5342 | -20.2828 | 14.7752 | -46.0821 | -44.754 | -58.1251 | -47.1056 | -50.129 | -42.3204 | -43.3055 | -54.4774 | -48.3954 | -57.0165 | -48.5985 | -42.4696 | -54.5638 | 377 | -33.3266 | -40.4468 | -32.9826 | -38.6039 | -33.0222 | -47.066 | -32.7464 | -38.957 | 377 | -45.3086 | -39.2266 | -37.9368 | -42.382 | -34.5734 | -35.0273 | -46.7304 | -40.1172 | -39.3118 | -41.8508 | -34.5266 | -35.5117 | -35.5852 | -48.9563 | -47.8477 | -40.8515 | -34.7226 | -46.2856 | -37.007 | -49.8469 | -49.2227 | -40.3203 | -34.6758 | -46.77
378 | -9.1795 | 0 | -7.7769 | 0 | -8.4366 | 0 | -7.8576 | 0 | -48.1329 | -146.3105 | -32.2886 | -156.8462 | -43.2418 | -7.2907 | -39.6155 | -41.043 | -44.8568 | -166.82 | -40.7004 | -16.6277 | -52.2711 | -75.2938 | -32.0785 | -74.6877 | -44.8863 | 95.7449 | -62.337 | -173.6909 | -48.1261 | -81.0565 | -41.5983 | 37.9271 | -8.3787 | -22.5427 | -20.1307 | 21.5182 | -21.6103 | 8.4313 | -19.7845 | 51.0677 | -8.8374 | 37.1137 | -19.1444 | 41.9283 | -17.2446 | 34.2673 | -18.9186 | 26.448 | -45.6316 | -42.4319 | -57.0421 | -46.5613 | -49.7801 | -43.7601 | -42.5699 | -48.3429 | -48.0077 | -53.5191 | -47.523 | -43.9444 | -48.3588 | 378 | -31.8498 | -38.0324 | -31.0527 | -37.8201 | -31.8174 | -46.5942 | -31.615 | -39.3156 | 378 | -39.1634 | -38.8282 | -37.3818 | -42.0032 | -35.9832 | -34.1333 | -40.566 | -39.5711 | -38.7037 | -41.3435 | -35.9025 | -34.7123 | -33.2524 | -47.8626 | -44.3396 | -39.7461 | -36.1675 | -39.9222 | -34.655 | -48.6055 | -45.6615 | -39.0864 | -36.0868 | -40.5012
379 | -8.9536 | 0 | -7.7782 | 0 | -8.6011 | 0 | -7.9236 | 0 | -46.4478 | -150.6889 | -30.7569 | -166.0122 | -43.8211 | -11.056 | -38.2261 | -60.8378 | -44.5534 | -173.4709 | -38.3504 | -21.535 | -50.1524 | -70.1013 | -30.7759 | -83.4037 | -43.9935 | 97.3651 | -60.5191 | 90.3074 | -48.1801 | -91.6709 | -41.3831 | 42.0499 | -9.3616 | -34.6071 | -19.7402 | 9.827 | -19.163 | 1.6083 | -17.2707 | 47.8205 | -9.6085 | 24.4781 | -19.2728 | 35.7731 | -15.7645 | 31.8009 | -16.9623 | 25.096 | -45.4454 | -40.8699 | -53.8747 | -46.4454 | -49.4181 | -43.4206 | -42.4775 | -45.0894 | -47.6411 | -49.6298 | -46.7704 | -43.23 | -45.5622 | 379 | -30.4373 | -36.8161 | -29.4435 | -36.5221 | -30.5261 | -45.8926 | -30.4096 | -38.9346 | 379 | -36.1358 | -38.6875 | -37.4918 | -41.6399 | -35.6424 | -33.8764 | -37.3112 | -39.04 | -38.5218 | -40.817 | -35.497 | -34.5539 | -31.9163 | -44.9211 | -40.6762 | -38.9922 | -35.4518 | -36.9611 | -33.0917 | -45.2736 | -41.7062 | -38.1693 | -35.3064 | -37.6386
380 | -8.6935 | 0 | -7.8066 | 0 | -8.7092 | 0 | -7.9994 | 0 | -45.4784 | -160.7095 | -30.2129 | 179.3478 | -43.4867 | -13.6289 | -38.6842 | -80.8621 | -43.3652 | 177.5191 | -36.6759 | -32.8222 | -48.1718 | -76.6663 | -30.6664 | -96.1604 | -42.5222 | 94.2816 | -58.7407 | 21.8843 | -48.2061 | -97.1475 | -40.5516 | 49.2966 | -11.4459 | -38.9775 | -20.8402 | 3.1976 | -18.598 | -13.8496 | -15.9001 | 34.8448 | -11.2739 | 19.1521 | -20.7011 | 33.5033 | -14.8261 | 20.0738 | -16.0044 | 14.1153 | -46.048 | -40.3178 | -51.7083 | -46.9191 | -48.048 | -41.2592 | -42.9316 | -43.6897 | -47.8028 | -47.6464 | -47.1386 | -41.3264 | -45.2366 | 380 | -29.8915 | -36.7822 | -28.8521 | -35.1447 | -30.3202 | -44.9915 | -30.2358 | -37.9824 | 380 | -34.9962 | -39.1093 | -38.2256 | -40.2414 | -33.4526 | -34.2224 | -35.8831 | -39.0936 | -38.9197 | -39.3388 | -33.2598 | -34.9322 | -31.6243 | -43.0148 | -38.9529 | -39.332 | -33.5198 | -36.5274 | -32.5112 | -42.9991 | -39.647 | -38.4294 | -33.327 | -37.2372
381 | -8.6075 | 0 | -7.8302 | 0 | -8.7247 | 0 | -8.0177 | 0 | -45.219 | -165.1564 | -30.984 | 163.0536 | -42.446 | -25.6405 | -40.5083 | -92.8379 | -43.1673 | 158.4586 | -35.8367 | -50.1025 | -47.1207 | -80.8676 | -31.6606 | -105.7474 | -40.9064 | 81.1456 | -64.2492 | -83.83 | -48.7681 | -108.2482 | -38.0078 | 47.3697 | -12.4041 | -30.7903 | -22.0089 | 16.6188 | -19.6479 | -29.1517 | -15.9746 | 19.5923 | -12.3218 | 26.5549 | -21.2496 | 46.3097 | -15.2246 | 7.3229 | -16.4771 | 1.6925 | -46.5443 | -41.2631 | -50.1302 | -47.6381 | -47.3881 | -38.9349 | -43.3536 | -44.049 | -47.8575 | -47.6466 | -46.963 | -39.4747 | -47.6505 | 381 | -30.5342 | -37.7664 | -29.4043 | -34.3655 | -31.0634 | -44.8068 | -30.7529 | -35.9748 | 381 | -35.4415 | -39.25 | -39.0306 | -39.5579 | -31.1047 | -34.6289 | -36.2188 | -39.1328 | -39.6204 | -38.6634 | -30.9172 | -35.3359 | -32.6556 | -41.5227 | -39.0391 | -39.1328 | -31.6445 | -38.9258 | -33.4329 | -41.4055 | -39.6289 | -38.2383 | -31.457 | -39.6328
382 | -8.7179 | 0 | -7.8872 | 0 | -8.6071 | 0 | -7.958 | 0 | -44.1321 | -167.9439 | -33.0197 | 154.29 | -42.4334 | -45.4018 | -43.0033 | -91.1106 | -44.8231 | 143.5058 | -36.6452 | -67.8201 | -45.636 | -87.2381 | -32.7849 | -107.9633 | -40.779 | 62.2413 | -52.837 | 157.3357 | -49.9092 | -106.0006 | -36.6916 | 29.7907 | -11.2756 | -25.8578 | -19.7992 | 29.952 | -22.3794 | -34.9496 | -17.2509 | 7.0417 | -10.9881 | 30.0249 | -18.9239 | 52.6499 | -16.4635 | -1.0365 | -17.8295 | -6.9118 | -46.3513 | -44.0009 | -48.9008 | -46.4021 | -48.3748 | -37.9813 | -43.0943 | -46.4118 | -47.296 | -49.2779 | -47.0083 | -38.4977 | -52.6694 | 382 | -32.2575 | -39.1494 | -31.1605 | -35.135 | -31.955 | -43.6927 | -31.2723 | -35.1145 | 382 | -37.6939 | -38.5781 | -37.6842 | -40.4876 | -30.0941 | -34.4872 | -38.5246 | -38.6889 | -38.4441 | -39.7677 | -30.0233 | -35.1363 | -35.283 | -40.1829 | -40.56 | -39.1211 | -30.6105 | -44.0623 | -36.1137 | -40.2937 | -41.3199 | -38.4012 | -30.5397 | -44.7114
383 | -8.8976 | 0 | -7.9452 | 0 | -8.5213 | 0 | -7.893 | 0 | -42.9557 | -175.9394 | -34.8723 | 158.3005 | -43.9238 | -64.5561 | -42.7101 | -69.7914 | -47.1825 | 141.9267 | -39.1426 | -74.3365 | -44.7462 | -96.4705 | -33.4258 | -106.8346 | -42.388 | 49.6978 | -46.4681 | 110.554 | -49.6528 | -104.2787 | -38.2148 | 14.3743 | -9.8681 | -34.1158 | -17.1621 | 22.7859 | -24.6291 | -23.4196 | -19.5573 | 5.417 | -9.5749 | 23.5955 | -16.8815 | 47.7157 | -17.8071 | 5.1141 | -20.2519 | -3.0769 | -45.4015 | -45.8799 | -48.1507 | -44.1906 | -49.7726 | -38.7315 | -42.0702 | -50.5564 | -46.3976 | -51.4061 | -47.8319 | -39.0564 | -65.6694 | 383 | -33.8006 | -39.0889 | -33.001 | -37.4119 | -32.6312 | -41.7451 | -32.022 | -36.5881 | 383 | -41.6588 | -37.5 | -35.293 | -41.8274 | -30.7863 | -33.5489 | -42.6112 | -37.8763 | -36.2976 | -41.2513 | -30.8385 | -34.1772 | -36.9823 | -39.2531 | -42.5085 | -39.8867 | -31.1112 | -57.1481 | -37.9347 | -39.6294 | -43.5131 | -39.3106 | -31.1634 | -57.7764
384 | -8.9425 | 0 | -7.9629 | 0 | -8.6248 | 0 | -7.8935 | 0 | -42.5633 | 174.9273 | -34.4624 | 166.1308 | -46.4237 | -75.9004 | -39.0175 | -68.7632 | -47.358 | 150.8213 | -40.3339 | -59.0402 | -44.4756 | -106.106 | -33.0786 | -104.2724 | -43.7912 | 51.6534 | -43.5351 | 77.5325 | -48.7792 | -101.7805 | -40.4489 | 19.1315 | -9.5797 | -47.6155 | -15.8946 | 10.214 | -22.5299 | -17.2907 | -20.0779 | 13.9803 | -9.1046 | 12.0494 | -16.002 | 35.5373 | -16.903 | 10.6168 | -21.568 | 17.1377 | -44.2903 | -43.9249 | -47.6528 | -42.5247 | -49.9466 | -40.6437 | -41.0528 | -49.8162 | -45.6417 | -49.3418 | -47.627 | -40.949 | -52.9447 | 384 | -33.6041 | -37.0075 | -32.3966 | -38.7368 | -32.4439 | -40.3042 | -32.0295 | -38.3804 | 384 | -40.8737 | -36.6992 | -33.5822 | -41.9837 | -32.6808 | -32.428 | -41.8533 | -37.0169 | -34.6312 | -41.3218 | -32.7502 | -33.1593 | -34.9824 | -38.7103 | -40.3993 | -39.6641 | -32.9861 | -44.3199 | -35.962 | -39.028 | -41.4483 | -39.0022 | -33.0555 | -45.0512
385 | -8.8197 | 0 | -7.9486 | 0 | -8.8314 | 0 | -7.9134 | 0 | -42.4014 | 168.0793 | -32.9591 | 164.0272 | -48.9953 | -76.9075 | -36.6827 | -85.3216 | -46.3596 | 151.4732 | -37.8041 | -49.5369 | -44.5487 | -111.4826 | -32.091 | -108.2565 | -42.723 | 54.8366 | -41.893 | 48.9488 | -46.908 | -106.9759 | -39.9958 | 31.3452 | -10.6536 | -61.6634 | -16.0283 | -1.9169 | -20.7619 | -31.9778 | -18.9701 | 16.407 | -9.7785 | 0.9934 | -16.5795 | 25.574 | -15.6614 | 7.1445 | -19.6044 | 22.8507 | -43.5924 | -41.7799 | -46.9088 | -41.5807 | -49.483 | -41.5572 | -40.6165 | -45.8236 | -45.1673 | -45.9173 | -45.929 | -41.9564 | -49.0378 | 385 | -32.3953 | -35.2974 | -30.5238 | -36.9567 | -31.5096 | -39.2033 | -31.0644 | -37.5971 | 385 | -37.0039 | -36.3476 | -32.761 | -41.5344 | -33.6086 | -31.7851 | -37.875 | -36.3359 | -33.6673 | -40.6516 | -33.6438 | -32.7031 | -32.9602 | -38.0891 | -37.0976 | -37.9804 | -34.0078 | -40.2064 | -33.8313 | -38.0774 | -38.0039 | -37.0976 | -34.043 | -41.1244
386 | -8.6303 | 0 | -7.9371 | 0 | -9.0516 | 0 | -7.947 | 0 | -42.295 | 162.4039 | -32.0006 | 151.2743 | -49.7569 | -68.3716 | -36.117 | -106.2667 | -45.2435 | 150.5853 | -35.037 | -58.405 | -44.3929 | -112.6548 | -31.7093 | -118.4436 | -41.2145 | 47.6992 | -41.7708 | 19.0652 | -46.2423 | -117.5595 | -37.9833 | 35.6547 | -12.9619 | -67.5074 | -17.4462 | -4.9308 | -21.8352 | -53.419 | -18.4237 | 7.6893 | -11.1435 | -4.556 | -18.0288 | 23.7362 | -14.9451 | -3.7909 | -18.6794 | 18.7278 | -43.7567 | -40.8048 | -46.0241 | -41.2762 | -49.7528 | -39.7462 | -40.9331 | -43.7039 | -44.8568 | -43.6519 | -44.6363 | -40.3055 | -47.965 | 386 | -31.5466 | -34.7708 | -29.2484 | -34.5097 | -31.0424 | -38.9744 | -30.4564 | -35.8761 | 386 | -35.0736 | -36.2265 | -32.6459 | -41.8157 | -31.8091 | -31.8815 | -35.7668 | -35.8052 | -33.3292 | -40.7012 | -31.7992 | -32.9861 | -32.1745 | -37.3938 | -35.0216 | -36.6992 | -32.3684 | -38.9134 | -32.8677 | -36.9725 | -35.7049 | -35.5847 | -32.3585 | -40.018
387 | -8.5067 | 0 | -7.9962 | 0 | -9.1218 | 0 | -7.9801 | 0 | -42.412 | 158.7385 | -32.4177 | 133.6952 | -48.2041 | -68.9744 | -37.2655 | -124.5008 | -43.1748 | 140.4336 | -33.4459 | -76.6694 | -43.5497 | -113.6773 | -32.1767 | -127.7796 | -40.1014 | 34.3799 | -44.9952 | -8.5149 | -45.2273 | -125.4866 | -35.4585 | 28.5401 | -14.9087 | -58.8453 | -18.047 | 4.9804 | -25.6654 | -78.2132 | -19.5101 | -3.1148 | -12.1757 | -0.7751 | -18.5421 | 35.2449 | -15.3936 | -16.5865 | -19.0219 | 14.6496 | -44.7573 | -41.1915 | -45.3966 | -41.8198 | -49.9916 | -37.4297 | -41.6408 | -43.3523 | -44.8504 | -43.2384 | -44.6954 | -37.9656 | -48.2577 | 387 | -31.9003 | -35.3281 | -29.1611 | -32.8773 | -31.263 | -39.754 | -30.3527 | -33.8484 | 387 | -34.8456 | -36.3437 | -33.3131 | -41.9954 | -29.4335 | -32.519 | -35.3561 | -35.7286 | -33.8397 | -40.8698 | -29.4496 | -33.6607 | -32.6848 | -36.8899 | -34.7317 | -36.6992 | -29.9694 | -39.1359 | -33.1953 | -36.2748 | -35.2583 | -35.5736 | -29.9855 | -40.2776
388 | -8.5075 | 0 | -8.0894 | 0 | -8.964 | 0 | -7.989 | 0 | -41.8057 | 158.787 | -34.4616 | 119.8586 | -47.0676 | -86.0971 | -39.8104 | -133.7363 | -42.7417 | 120.4581 | -33.3851 | -98.2204 | -42.2027 | -117.6619 | -32.9725 | -134.6038 | -39.7333 | 15.4241 | -52.9865 | 13.7534 | -44.7181 | -140.1046 | -34.3876 | 8.2214 | -13.6316 | -49.722 | -16.0139 | 11.0956 | -33.6173 | -95.4474 | -22.2829 | -4.108 | -11.58 | 3.6076 | -16.4314 | 43.202 | -16.7023 | -23.3056 | -19.9883 | 19.693 | -45.2957 | -43.1977 | -45.042 | -42.5535 | -51.034 | -36.1156 | -41.5894 | -44.6163 | -44.4996 | -44.9995 | -45.0073 | -36.4561 | -49.3693 | 388 | -33.5302 | -36.5046 | -30.357 | -32.745 | -31.7333 | -40.0441 | -30.5873 | -32.974 | 388 | -36.1088 | -35.9921 | -34.046 | -42.9446 | -28.0262 | -32.6254 | -36.5269 | -35.5356 | -34.5645 | -42.07 | -28.1266 | -33.6004 | -34.6902 | -36.5345 | -36.492 | -36.9179 | -28.3667 | -40.4053 | -35.1083 | -36.078 | -37.0105 | -36.0433 | -28.4671 | -41.3803
389 | -8.5981 | 0 | -8.1821 | 0 | -8.7739 | 0 | -7.979 | 0 | -40.734 | 152.6202 | -37.1906 | 119.5216 | -48.1697 | -109.0868 | -42.3249 | -118.647 | -43.8632 | 106.7964 | -35.3189 | -114.4269 | -41.0533 | -127.7811 | -34.0242 | -137.7343 | -40.9716 | -2.9524 | -45.9394 | 57.4114 | -45.118 | -153.5632 | -36.1307 | -9.1929 | -12.0019 | -57.2358 | -13.9586 | 2.9796 | -40.1399 | 24.5453 | -23.3712 | 16.5559 | -10.5503 | -0.0896 | -14.2632 | 35.3189 | -17.3974 | -22.0949 | -19.1279 | 27.8901 | -44.4767 | -45.9431 | -44.8631 | -42.1222 | -54.1336 | -36.3957 | -40.5992 | -47.3694 | -43.7231 | -47.9027 | -45.7335 | -36.7785 | -50.0603 | 389 | -35.3663 | -37.3499 | -32.6492 | -34.5573 | -32.5625 | -38.706 | -31.7711 | -34.5042 | 389 | -38.7713 | -35.125 | -33.5241 | -45.9515 | -28.2136 | -31.8253 | -39.1873 | -34.9492 | -34.1432 | -45.3597 | -28.4167 | -32.6202 | -37.345 | -36.265 | -39.3046 | -37.5514 | -28.5964 | -41.2864 | -37.761 | -36.0892 | -39.9237 | -36.9596 | -28.7995 | -42.0813
390 | -8.6399 | 0 | -8.2308 | 0 | -8.7573 | 0 | -7.9938 | 0 | -40.3197 | 144.4066 | -38.1369 | 129.3486 | -51.7406 | -123.2641 | -39.5695 | -99.6725 | -44.986 | 100.438 | -38.1669 | -114.4642 | -40.7233 | -140.3281 | -34.6463 | -135.5561 | -43.575 | -11.6842 | -41.0263 | 44.2936 | -46.3097 | -161.1266 | -38.8928 | -5.0159 | -12.1823 | -73.2737 | -13.316 | -9.7792 | -32.5704 | 27.4044 | -21.0189 | 29.6685 | -10.1476 | -9.1379 | -13.2208 | 22.9103 | -17.2502 | -22.7358 | -17.5876 | 30.5013 | -43.1565 | -46.1929 | -44.7819 | -40.9087 | -55.5902 | -37.5943 | -39.5939 | -48.7286 | -43.1098 | -48.0957 | -46.4803 | -38.6778 | -50.8926 | 390 | -35.9658 | -36.2884 | -33.8038 | -37.1911 | -33.2641 | -37.2815 | -32.5881 | -37.0701 | 390 | -40.0887 | -34.4699 | -32.2688 | -47.3594 | -29.3635 | -30.8366 | -40.4978 | -34.3525 | -32.9149 | -46.8329 | -29.6005 | -31.6001 | -37.553 | -36.142 | -39.4558 | -38.2495 | -30.447 | -42.1353 | -37.9621 | -36.0246 | -40.1019 | -37.723 | -30.684 | -42.8988
391 | -8.6029 | 0 | -8.2099 | 0 | -8.9579 | 0 | -8.0115 | 0 | -40.1821 | 137.6792 | -37.2732 | 131.7729 | -56.5219 | -107.6277 | -35.9869 | -108.8153 | -45.5311 | 96.2939 | -38.615 | -97.1711 | -41.1831 | -151.7675 | -34.1632 | -135.4825 | -45.1972 | -2.935 | -38.2559 | 25.1657 | -46.566 | -161.0504 | -38.3332 | 10.7975 | -13.546 | -86.6405 | -13.5561 | -23.3419 | -33.5027 | -5.7755 | -18.4967 | 16.052 | -10.4585 | -17.7617 | -13.4166 | 10.9562 | -16.798 | -28.3015 | -16.2484 | 24.6825 | -42.2523 | -44.3206 | -44.4578 | -39.4906 | -53.4945 | -38.8402 | -39.12 | -46.3642 | -42.6889 | -44.8857 | -45.999 | -40.8954 | -52.3159 | 391 | -35.4442 | -34.2502 | -32.3892 | -37.7528 | -33.0998 | -36.0621 | -31.6773 | -37.0103 | 391 | -37.7613 | -34.086 | -30.8877 | -45.2846 | -30.6303 | -30.1621 | -38.1543 | -33.731 | -31.4791 | -44.5366 | -30.8287 | -31.1085 | -35.7177 | -35.8549 | -36.2828 | -37.7891 | -32.6855 | -43.358 | -36.1107 | -35.4999 | -36.8742 | -37.0411 | -32.8839 | -44.3044
392 | -8.5028 | 0 | -8.1407 | 0 | -9.2656 | 0 | -8.0081 | 0 | -40.0874 | 130.9561 | -36.5382 | 123.729 | -53.0704 | -78.1155 | -34.3781 | -130.0675 | -46.0898 | 93.0809 | -35.5673 | -92.9721 | -42.4828 | -157.4488 | -33.7589 | -141.9561 | -43.8065 | 3.2638 | -36.8392 | 0.4491 | -45.8768 | -167.2311 | -35.7901 | 13.0243 | -17.0219 | -92.8798 | -15.1794 | -30.7236 | -39.4609 | 124.5381 | -18.5661 | -2.1557 | -11.2321 | -22.245 | -14.4005 | 4.1018 | -16.8422 | -38.4642 | -15.7174 | 15.5768 | -42.1714 | -42.8862 | -43.8381 | -38.3745 | -52.4487 | -38.3822 | -39.3009 | -43.9414 | -42.4246 | -42.0157 | -44.2735 | -39.9531 | -55.0415 | 392 | -34.8832 | -33.12 | -30.6332 | -35.128 | -32.849 | -35.3857 | -30.4987 | -34.8005 | 392 | -35.4386 | -33.9218 | -29.8717 | -44.308 | -30.2415 | -30.0353 | -35.8007 | -33.159 | -30.3664 | -43.1831 | -30.3741 | -31.2928 | -34.3834 | -35.3353 | -33.5129 | -36.1328 | -31.8124 | -45.7759 | -34.7455 | -34.5725 | -34.0076 | -35.0079 | -31.945 | -47.0334
393 | -8.4587 | 0 | -8.1305 | 0 | -9.4587 | 0 | -8.0212 | 0 | -40.3622 | 126.7377 | -36.9621 | 108.2971 | -48.6929 | -90.9083 | -34.5449 | -152.1704 | -45.8886 | 93.3899 | -32.9114 | -105.2833 | -43.5124 | -150.6325 | -34.0721 | -149.3806 | -42.0054 | -3.9573 | -37.5972 | -27.9534 | -45.8531 | -173.9605 | -33.4424 | 2.3707 | -18.6722 | -68.5945 | -16.5548 | -24.7995 | -27.2576 | 101.4865 | -20.5936 | -21.0376 | -11.7004 | -20.721 | -15.6028 | 7.9367 | -17.9111 | -50.2841 | -16.1568 | 9.9767 | -42.8683 | -42.5714 | -43.2433 | -37.9386 | -53.3448 | -36.5987 | -39.8532 | -43.0407 | -42.4157 | -40.5602 | -42.7438 | -37.2087 | -59.0586 | 393 | -35.1317 | -33.2889 | -29.7308 | -32.5901 | -33.018 | -36.1187 | -29.9221 | -32.6628 | 393 | -34.582 | -33.957 | -29.4799 | -45.2143 | -28.4682 | -30.3945 | -34.9102 | -32.957 | -29.9174 | -43.8861 | -28.5775 | -31.832 | -34.1127 | -34.7846 | -32.1015 | -34.6133 | -29.0782 | -49.5999 | -34.4409 | -33.7846 | -32.539 | -33.2851 | -29.1875 | -51.0374
394 | -8.4756 | 0 | -8.2099 | 0 | -9.3615 | 0 | -8.037 | 0 | -40.0545 | 125.7973 | -39.1808 | 92.895 | -46.6998 | -118.6595 | -36.4371 | -170.7314 | -44.6921 | 87.6671 | -31.7702 | -126.4655 | -41.7952 | -143.1841 | -34.6127 | -155.5302 | -40.9423 | -18.617 | -42.4594 | -47.1082 | -44.9396 | -179.8732 | -32.4142 | -15.9229 | -16.3528 | -60.3882 | -15.9615 | -15.0664 | -22.7652 | 80.9548 | -26.956 | -27.2693 | -11.3264 | -20.3353 | -14.9627 | 13.9819 | -19.3891 | -54.8516 | -16.4791 | 8.8467 | -43.5687 | -43.5211 | -42.8813 | -38.0218 | -56.6351 | -35.1618 | -40.12 | -43.635 | -42.6787 | -40.6044 | -42.3661 | -35.3225 | -55.9497 | 394 | -36.1818 | -34.4389 | -29.9433 | -31.4232 | -33.0772 | -38.0975 | -30.1053 | -31.636 | 394 | -35.1594 | -34.2031 | -29.5462 | -48.4252 | -26.9519 | -30.7585 | -35.4251 | -33.3172 | -29.9848 | -47.2736 | -27.1248 | -32.083 | -35.0455 | -34.4057 | -32.1288 | -34.1562 | -27.1126 | -46.5882 | -35.3112 | -33.5198 | -32.5674 | -33.0046 | -27.2855 | -47.9127
395 | -8.5295 | 0 | -8.306 | 0 | -9.1271 | 0 | -8.0838 | 0 | -39.2758 | 119.284 | -43.0011 | 87.5625 | -46.7886 | -150.1281 | -39.9775 | -173.6508 | -44.2124 | 70.3977 | -32.1802 | -149.3236 | -39.8345 | -150.7594 | -35.1996 | -161.2402 | -40.9398 | -37.3421 | -45.2163 | 5.9129 | -44.1778 | 161.4545 | -33.0221 | -34.6422 | -14.4362 | -74.1444 | -14.1691 | -19.1575 | -21.5154 | 65.3948 | -30.5858 | 50.3414 | -10.6879 | -25.3951 | -13.213 | 12.3314 | -20.883 | -50.1605 | -16.2888 | 9.4754 | -43.0204 | -45.4665 | -42.8649 | -38.3524 | -63.4422 | -34.4704 | -39.4896 | -45.1896 | -42.924 | -42.0638 | -43.6615 | -34.4748 | -48.6957 | 395 | -37.2308 | -35.9078 | -31.2151 | -31.7772 | -33.1296 | -37.6401 | -30.8053 | -32.0943 | 395 | -36.6601 | -34.3945 | -29.8229 | -55.1362 | -26.1644 | -30.3625 | -36.8836 | -33.7969 | -30.2686 | -54.3151 | -26.3866 | -31.4058 | -36.937 | -34.3354 | -33.5343 | -35.3555 | -26.1688 | -39.5686 | -37.1605 | -33.7378 | -33.98 | -34.5344 | -26.391 | -40.6119
396 | -8.58 | 0 | -8.3808 | 0 | -9.0096 | 0 | -8.0959 | 0 | -39.0705 | 111.7989 | -47.009 | 100.5757 | -49.1427 | 178.0682 | -40.513 | -149.3268 | -46.0812 | 58.2388 | -34.4191 | -167.3407 | -38.9318 | -162.2693 | -36.3214 | -167.0191 | -42.6095 | -55.3875 | -38.606 | 6.7729 | -45.9563 | 141.0809 | -35.4153 | -45.6022 | -14.0141 | -89.5262 | -13.0931 | -31.111 | -22.3064 | 53.5086 | -23.1827 | 53.2634 | -10.6451 | -33.4464 | -12.42 | 3.7487 | -20.6975 | -49.9646 | -15.9292 | 5.9122 | -41.8139 | -47.4349 | -42.8217 | -37.6732 | -70.9857 | -34.6966 | -38.6933 | -46.4744 | -42.4667 | -42.9042 | -45.6893 | -34.8924 | -45.9804 | 396 | -38.0699 | -36.2456 | -33.2767 | -33.9977 | -33.8092 | -35.3595 | -31.8144 | -34.3463 | 396 | -37.8944 | -33.8867 | -29.0932 | -62.6049 | -26.3158 | -29.6837 | -38.0936 | -33.4571 | -29.5773 | -61.9761 | -26.6007 | -30.5974 | -38.8549 | -34.2417 | -34.3242 | -37.3085 | -26.5116 | -36.9708 | -39.0541 | -33.8121 | -34.8083 | -36.6797 | -26.7965 | -37.8845
397 | -8.5413 | 0 | -8.3655 | 0 | -9.1507 | 0 | -8.0569 | 0 | -39.0304 | 105.4598 | -48.3041 | 129.5611 | -54.7715 | 149.8935 | -36.7555 | -148.0003 | -47.343 | 59.4565 | -38.1834 | -168.4076 | -38.7377 | -174.6269 | -37.4103 | -166.1983 | -45.7814 | -61.5403 | -35.675 | -14.1373 | -49.0237 | 136.6344 | -37.3235 | -36.766 | -15.7249 | -106.3446 | -13.7044 | -46.0982 | -23.3187 | 62.6298 | -20.6278 | 35.8598 | -11.3344 | -39.8591 | -12.3605 | -7.3876 | -20.5919 | -61.1569 | -15.9228 | -0.7425 | -41.1034 | -47.4549 | -42.4549 | -36.4237 | -60.0252 | -35.5994 | -38.3147 | -45.5765 | -41.6897 | -41.4085 | -47.0257 | -36.5687 | -46.3207 | 397 | -38.4429 | -34.5034 | -34.2274 | -37.6018 | -34.6637 | -33.7991 | -31.9555 | -36.4948 | 397 | -37.0352 | -33.1484 | -27.8824 | -51.6597 | -27.2339 | -29.164 | -37.211 | -32.539 | -28.3668 | -50.8745 | -27.5425 | -30.2578 | -38.9136 | -33.9136 | -32.8672 | -38.6602 | -28.2032 | -37.17 | -39.0894 | -33.3042 | -33.3516 | -37.875 | -28.5118 | -38.2638
398 | -8.4802 | 0 | -8.3003 | 0 | -9.3765 | 0 | -8.0312 | 0 | -39.002 | 97.8008 | -46.1454 | 141.4165 | -75.0396 | -134.3428 | -34.8162 | -167.7435 | -47.7015 | 59.1734 | -38.376 | -143.4445 | -39.3156 | 173.9723 | -37.7641 | -165.5587 | -47.5189 | -44.3813 | -34.6707 | -38.0608 | -51.0199 | 145.9911 | -35.7782 | -26.9186 | -18.4941 | -109.1521 | -15.2421 | -56.6915 | -20.6456 | 72.0597 | -21.0833 | 22.2486 | -12.5206 | -42.123 | -13.4039 | -16.4421 | -22.0295 | -78.6529 | -17.3088 | -6.1188 | -41.1202 | -46.0441 | -41.8431 | -35.4874 | -57.4757 | -36.3683 | -38.4957 | -43.9351 | -41.0154 | -39.3785 | -46.1128 | -37.8648 | -47.8746 | 398 | -38.2345 | -33.2541 | -33.0143 | -37.8954 | -35.1983 | -33.3151 | -31.1192 | -35.3766 | 398 | -35.4549 | -32.5352 | -27.0072 | -49.1754 | -28.068 | -29.1192 | -35.6348 | -31.6389 | -27.4562 | -48.0992 | -28.3371 | -30.4645 | -37.5639 | -33.3629 | -30.8983 | -37.8125 | -29.5645 | -38.4981 | -37.7438 | -32.4666 | -31.3473 | -36.7363 | -29.8336 | -39.8434
399 | -8.4707 | 0 | -8.2411 | 0 | -9.4442 | 0 | -8.0317 | 0 | -39.7311 | 90.5501 | -46.1746 | 135.1364 | -54.3227 | -100.6862 | -34.874 | 171.1465 | -47.3798 | 65.169 | -34.7542 | -145.0811 | -40.8464 | 168.7829 | -38.1009 | -167.8803 | -45.0677 | -31.1022 | -35.4195 | -61.3729 | -50.9248 | 165.3204 | -33.5507 | -35.5994 | -18.5584 | -88.795 | -16.9412 | -53.9268 | -18.0093 | 58.3462 | -22.4887 | 17.7844 | -12.4235 | -38.1458 | -14.6588 | -17.602 | -25.8236 | -98.5284 | -18.6857 | -1.2906 | -41.768 | -45.0298 | -41.2672 | -35.3578 | -57.1938 | -36.4126 | -39.0809 | -43.1669 | -40.7012 | -38.2254 | -44.1747 | -37.1591 | -49.6258 | 399 | -38.7221 | -33.4659 | -31.6475 | -34.4779 | -35.7142 | -34.231 | -30.5381 | -33.1811 | 399 | -34.6962 | -32.2305 | -26.8871 | -48.9527 | -28.1715 | -29.6367 | -34.9258 | -31.257 | -27.3261 | -47.7496 | -28.3809 | -31.0492 | -36.5591 | -32.7965 | -29.7547 | -35.9336 | -28.918 | -40.1816 | -36.7887 | -31.823 | -30.1937 | -34.7305 | -29.1274 | -41.5941
400 | -8.5559 | 0 | -8.2454 | 0 | -9.2802 | 0 | -8.0945 | 0 | -40.5159 | 91.3815 | -49.7212 | 144.7834 | -49.2503 | -129.9131 | -36.266 | 152.334 | -45.0116 | 61.3363 | -32.9888 | -164.2356 | -41.3844 | 176.2019 | -38.6316 | -170.5947 | -42.0652 | -38.5712 | -38.5211 | -80.4113 | -46.6417 | 170.3733 | -32.8764 | -53.1882 | -15.696 | -90.0168 | -17.0368 | -42.7694 | -17.061 | 43.3107 | -22.3826 | 34.2844 | -11.3694 | -38.6521 | -14.84 | -11.0943 | -32.301 | -85.3923 | -18.4915 | 13.3766 | -42.6395 | -45.065 | -40.954 | -35.9989 | -57.8231 | -36.2486 | -39.511 | -43.4247 | -40.8333 | -38.1829 | -42.7923 | -35.9365 | -50.9305 | 400 | -39.5332 | -34.4781 | -31.2528 | -32.6288 | -35.6559 | -36.2904 | -31.0058 | -32.2223 | 400 | -34.8688 | -32.2774 | -27.443 | -49.5777 | -28.0032 | -30.2308 | -35.1793 | -31.5531 | -27.9044 | -48.5429 | -28.1541 | -31.4165 | -36.5091 | -32.3981 | -29.627 | -34.5469 | -27.6911 | -41.6503 | -36.8196 | -31.6738 | -30.0884 | -33.5121 | -27.842 | -42.836
401 | -8.7176 | 0 | -8.3309 | 0 | -9.0418 | 0 | -8.1785 | 0 | -39.9662 | 91.9607 | -48.7946 | -174.5679 | -47.5234 | -159.5995 | -39.4908 | 138.4236 | -43.2549 | 41.522 | -33.3407 | 173.4091 | -39.8996 | 177.582 | -39.5401 | -175.0959 | -40.2372 | -55.9227 | -44.0965 | -65.754 | -43.528 | 146.3132 | -34.0214 | -69.0672 | -13.8009 | -106.3343 | -15.3802 | -43.7443 | -17.5432 | 32.5862 | -19.5446 | 40.1316 | -10.3847 | -45.3107 | -13.5215 | -9.3406 | -29.969 | -45.3148 | -16.2745 | 19.4401 | -42.5376 | -45.936 | -41.0805 | -37.0844 | -57.5063 | -36.143 | -39.1746 | -44.3895 | -41.3231 | -39.1863 | -42.5457 | -35.4051 | -51.8951 | 401 | -38.8052 | -35.8422 | -32.2988 | -32.771 | -35.1118 | -37.3129 | -32.626 | -32.7147 | 401 | -35.6719 | -32.6055 | -28.3668 | -49.1754 | -27.8121 | -30.1328 | -36.0586 | -32.2813 | -28.9059 | -48.4645 | -27.9645 | -30.9961 | -37.2184 | -32.3629 | -30.4687 | -34.2148 | -27.0742 | -42.8533 | -37.6051 | -32.0387 | -31.0078 | -33.5039 | -27.2266 | -43.7166
402 | -8.8451 | 0 | -8.4313 | 0 | -8.9255 | 0 | -8.2558 | 0 | -39.4417 | 88.7434 | -44.6102 | -161.4126 | -47.8597 | 177.455 | -44.155 | 154.2416 | -44.0231 | 13.8557 | -35.3218 | 157.3784 | -38.9786 | 169.5882 | -41.1551 | -175.7414 | -39.849 | -77.1757 | -40.2601 | -29.9522 | -43.7773 | 114.1969 | -36.1919 | -75.597 | -13.3762 | -125.0046 | -14.1563 | -53.3969 | -18.3856 | 25.2538 | -16.8946 | 22.7691 | -9.945 | -55.8466 | -12.5577 | -15.5019 | -28.0448 | -63.8095 | -14.2586 | 13.5485 | -41.4506 | -47.1596 | -41.4542 | -37.974 | -55.5404 | -35.8822 | -38.4391 | -45.3786 | -41.7944 | -40.861 | -43.7282 | -35.6872 | -47.9194 | 402 | -37.8336 | -37.173 | -34.3575 | -34.5641 | -35.1329 | -35.8069 | -33.8598 | -34.1367 | 402 | -36.5335 | -32.9493 | -29.1289 | -47.1091 | -27.4509 | -29.5136 | -36.9473 | -32.8689 | -29.7182 | -46.6149 | -27.6264 | -30.1833 | -38.3145 | -32.6091 | -32.0159 | -35.2969 | -27.2559 | -38.9939 | -38.7283 | -32.5287 | -32.6052 | -34.8027 | -27.4314 | -39.6636
403 | -8.8732 | 0 | -8.4546 | 0 | -9.0154 | 0 | -8.2513 | 0 | -39.238 | 83.9502 | -41.047 | -160.0101 | -48.492 | 164.6576 | -41.0464 | -174.1174 | -47.5967 | -3.3378 | -38.2991 | 153.5947 | -38.6642 | 161.1508 | -42.7636 | -166.8709 | -40.7676 | -94.8724 | -36.0075 | -41.5194 | -47.5532 | 92.2319 | -37.4187 | -68.4032 | -14.1174 | -150.878 | -14.4608 | -68.666 | -18.8236 | 27.6642 | -16.1603 | 1.5571 | -10.3899 | -68.058 | -12.479 | -25.7441 | -28.5016 | -95.1624 | -13.3643 | 3.2355 | -40.6653 | -47.9214 | -41.5799 | -37.1731 | -54.1731 | -36.1987 | -38.0054 | -44.7888 | -41.5646 | -41.2476 | -45.6343 | -36.9216 | -44.2358 | 403 | -36.7385 | -36.6724 | -35.1555 | -37.4597 | -35.6426 | -33.9326 | -33.1438 | -35.489 | 403 | -35.9156 | -32.6914 | -28.2999 | -45.7185 | -27.7441 | -28.99 | -36.3342 | -32.5492 | -28.9218 | -45.1577 | -27.9474 | -29.7541 | -39.0482 | -32.7067 | -32.3744 | -37.1797 | -28.467 | -35.2204 | -39.4668 | -32.5645 | -32.9963 | -36.6189 | -28.6703 | -35.9845
404 | -8.758 | 0 | -8.4256 | 0 | -9.2936 | 0 | -8.2027 | 0 | -39.0017 | 78.621 | -38.0317 | -169.4764 | -48.3333 | 153.6901 | -36.8776 | 173.2445 | -51.3263 | 0.207 | -39.9902 | 167.8532 | -38.7729 | 152.6639 | -42.4809 | -155.7791 | -42.1839 | -105.7848 | -34.1473 | -63.1896 | -52.2276 | 104.7967 | -36.6071 | -63.1037 | -16.0172 | -171.5792 | -15.9168 | -83.6588 | -18.0204 | 36.3311 | -17.5223 | -23.2017 | -11.4035 | -77.847 | -12.8255 | -34.0972 | -30.5813 | -139.1438 | -13.1829 | -7.2399 | -40.4722 | -46.6215 | -41.2851 | -35.7222 | -54.9097 | -37.2504 | -37.9764 | -43.0631 | -40.9182 | -39.3865 | -46.8162 | -38.7233 | -43.9475 | 404 | -35.2599 | -34.7052 | -33.3461 | -39.1267 | -36.0273 | -32.8111 | -31.8063 | -35.4533 | 404 | -34.3051 | -32.1602 | -26.9642 | -46.4841 | -28.8248 | -28.6828 | -34.6375 | -31.6246 | -27.5195 | -45.6161 | -29.0477 | -29.7737 | -37.8635 | -32.5271 | -30.6285 | -38.3906 | -30.2977 | -34.6539 | -38.1959 | -31.9915 | -31.1838 | -37.5226 | -30.5206 | -35.7448
405 | -8.6243 | 0 | -8.3547 | 0 | -9.4329 | 0 | -8.1555 | 0 | -39.2711 | 72.3271 | -36.7409 | 175.8693 | -48.2933 | 143.8205 | -35.6453 | 150.7083 | -53.7994 | 21.128 | -37.7791 | 179.199 | -39.7818 | 146.3812 | -41.8853 | -152.7626 | -43.4052 | -110.5877 | -34.3414 | -87.5872 | -51.3427 | 131.2888 | -35.2087 | -66.2605 | -19.0013 | 179.0683 | -18.3286 | -86.8092 | -15.9134 | 25.987 | -20.2179 | -44.4798 | -12.9924 | -83.1857 | -14.1652 | -39.0734 | -30.6248 | 144.1888 | -13.7303 | -15.0477 | -40.7178 | -44.4444 | -40.9288 | -34.9092 | -58.2491 | -38.0342 | -38.3274 | -41.8626 | -40.2766 | -37.7727 | -46.0852 | -39.0266 | -44.5086 | 405 | -34.6233 | -34.0339 | -31.8634 | -37.3109 | -36.6637 | -33.183 | -31.3419 | -34.5052 | 405 | -33.2383 | -31.6523 | -26.2849 | -49.8944 | -29.6795 | -28.8945 | -33.5079 | -30.8437 | -26.7537 | -48.8162 | -29.8787 | -30.1719 | -35.8201 | -32.3045 | -29.1484 | -37.7305 | -30.6719 | -35.0757 | -36.0897 | -31.4959 | -29.6172 | -36.6523 | -30.8711 | -36.3531
406 | -8.5139 | 0 | -8.3057 | 0 | -9.3388 | 0 | -8.1607 | 0 | -39.7873 | 72.7253 | -37.0226 | 165.5934 | -47.7795 | 136.3598 | -36.1427 | 127.6396 | -50.3293 | 45.9525 | -35.1856 | 168.4789 | -40.5381 | 152.019 | -41.5841 | -153.0961 | -43.7468 | -109.6842 | -36.612 | -107.5323 | -47.4779 | 136.3737 | -34.1106 | -76.9596 | -21.6027 | -167.1969 | -19.411 | -74.8585 | -15.2318 | 10.4183 | -26.7813 | -46.0073 | -13.9257 | -80.6749 | -14.7454 | -34.1215 | -28.926 | 77.1409 | -13.9753 | -17.8218 | -41.29 | -43.1746 | -40.6075 | -34.9306 | -71.8407 | -37.9988 | -38.8292 | -41.5107 | -39.9554 | -37.2784 | -44.544 | -37.874 | -45.0863 | 406 | -34.946 | -34.469 | -31.281 | -34.8288 | -36.99 | -34.8893 | -31.7024 | -33.4856 | 406 | -32.9968 | -31.4415 | -26.4167 | -63.535 | -29.6931 | -29.4904 | -33.205 | -30.6166 | -26.7699 | -62.5019 | -29.8381 | -30.6685 | -34.6607 | -32.0936 | -28.7645 | -36.2383 | -29.5683 | -35.7475 | -34.8689 | -31.2687 | -29.1177 | -35.2052 | -29.7133 | -36.9256
407 | -8.5314 | 0 | -8.3706 | 0 | -9.109 | 0 | -8.1944 | 0 | -39.0662 | 74.7946 | -37.5417 | 165.2117 | -46.6363 | 123.6135 | -38.3079 | 105.1349 | -46.363 | 30.764 | -34.5619 | 148.3755 | -39.0792 | 156.4728 | -42.1419 | -154.856 | -42.469 | -112.7154 | -41.4196 | -111.8673 | -44.1672 | 118.2358 | -34.1552 | -91.6161 | -19.0588 | -161.9762 | -17.9147 | -73.8184 | -16.0285 | -3.1666 | -29.837 | 34.8942 | -13.7989 | -80.861 | -14.2129 | -29.789 | -27.7526 | 29.7927 | -14.2192 | -21.0802 | -41.4876 | -42.9448 | -40.5196 | -35.5462 | -58.7806 | -37.4878 | -38.9175 | -41.7145 | -40.1017 | -37.8042 | -43.3745 | -37.0114 | -45.5245 | 407 | -34.924 | -35.3057 | -31.7162 | -34.0385 | -36.174 | -36.3071 | -32.8624 | -33.196 | 407 | -33.1831 | -31.5703 | -27.0148 | -50.41 | -29.1172 | -29.8085 | -33.3439 | -30.9927 | -27.3518 | -49.6716 | -29.2934 | -30.7231 | -34.4134 | -31.9882 | -29.2728 | -35.0039 | -28.6408 | -36.4155 | -34.5742 | -31.4106 | -29.6098 | -34.2655 | -28.817 | -37.3301
408 | -8.6041 | 0 | -8.4835 | 0 | -8.9389 | 0 | -8.2059 | 0 | -38.0255 | 69.2834 | -37.1297 | 170.1461 | -46.4073 | 105.8279 | -44.3764 | 86.6577 | -45.9013 | 6.3734 | -35.6505 | 132.1697 | -37.6802 | 148.3398 | -43.6984 | -146.5215 | -41.3109 | -128.1413 | -42.4113 | -70.1398 | -43.6154 | 90.8168 | -35.2414 | -102.8465 | -16.4919 | -175.948 | -16.7166 | -89.965 | -17.5847 | -12.2897 | -22.8057 | 29.0516 | -13.2434 | -85.9584 | -12.9597 | -31.4043 | -30.6526 | -5.2893 | -14.0263 | -25.0029 | -40.7413 | -43.4701 | -40.7447 | -36.085 | -52.0772 | -36.8724 | -38.5148 | -42.1108 | -40.5885 | -38.9289 | -43.382 | -37.0561 | -46.6512 | 408 | -34.2703 | -36.5804 | -32.9895 | -34.9376 | -35.4179 | -35.6624 | -33.9881 | -33.8031 | 408 | -33.5067 | -31.9844 | -27.4809 | -43.5937 | -28.3889 | -29.5759 | -33.6273 | -31.6496 | -27.8791 | -43.1383 | -28.6665 | -30.3089 | -34.866 | -32.1406 | -30.3248 | -34.8985 | -28.5726 | -37.7123 | -34.9866 | -31.8058 | -30.723 | -34.4431 | -28.8502 | -38.4453
409 | -8.6833 | 0 | -8.6013 | 0 | -8.9724 | 0 | -8.1989 | 0 | -37.3302 | 62.9486 | -35.3401 | 174.4611 | -46.7475 | 93.2718 | -49.2498 | 163.1048 | -47.664 | -6.9868 | -36.7705 | 123.0263 | -37.2619 | 138.5901 | -42.9321 | -124.9151 | -41.4094 | -146.4729 | -37.1446 | -67.9726 | -45.504 | 70.5734 | -36.4207 | -109.1381 | -15.7591 | 167.1698 | -16.7313 | -111.0178 | -18.6509 | -13.4356 | -20.6899 | 5.2147 | -13.3143 | -98.8335 | -12.0978 | -38.8371 | -47.4261 | -81.8405 | -14.0125 | -29.952 | -40.0231 | -44.5622 | -40.6598 | -36.0856 | -50.2887 | -36.3668 | -38.1403 | -42.32 | -40.9372 | -39.738 | -44.9099 | -38.0778 | -46.7432 | 409 | -33.0236 | -36.6973 | -32.8849 | -36.0446 | -35.0718 | -33.8828 | -33.2615 | -34.8354 | 409 | -33.6367 | -32.2539 | -27.4023 | -41.6874 | -27.7655 | -29.1679 | -33.7187 | -31.9648 | -27.8867 | -41.3163 | -28.1679 | -29.9414 | -35.8789 | -31.9765 | -31.0547 | -36.3086 | -29.4765 | -37.7708 | -35.9609 | -31.6874 | -31.5391 | -35.9375 | -29.8789 | -38.5443
410 | -8.6917 | 0 | -8.584 | 0 | -9.1039 | 0 | -8.137 | 0 | -36.9687 | 54.0134 | -33.026 | 167.7632 | -46.761 | 83.6684 | -40.821 | 162.3476 | -48.4903 | -6.4027 | -38.4229 | 112.1284 | -37.2994 | 130.0633 | -39.6785 | -118.6969 | -42.6943 | -162.9991 | -34.8861 | -88.5914 | -48.072 | 67.4758 | -37.6715 | -111.014 | -15.8817 | 147.1344 | -18.1386 | -135.934 | -19.3875 | -9.98 | -21.4375 | -18.1984 | -14.4785 | -112.0684 | -11.6512 | -46.9193 | -30.3326 | 126.5661 | -14.733 | -38.1608 | -39.6543 | -45.3031 | -40.3166 | -35.373 | -50.3301 | -36.7406 | -37.959 | -42.0492 | -40.6292 | -39.0058 | -47.5879 | -39.6156 | -43.5192 | 410 | -31.4252 | -35.2593 | -31.3981 | -37.4709 | -34.5881 | -32.7864 | -32.195 | -36.1924 | 410 | -33.3575 | -31.9375 | -26.6813 | -41.7461 | -28.1566 | -28.8551 | -33.4652 | -31.5253 | -27.236 | -41.2262 | -28.6036 | -29.822 | -36.6114 | -31.6249 | -30.3141 | -39.0039 | -31.0316 | -34.4153 | -36.7191 | -31.2127 | -30.8688 | -38.484 | -31.4786 | -35.3822
411 | -8.6071 | 0 | -8.5186 | 0 | -9.2001 | 0 | -8.0882 | 0 | -37.2389 | 44.4262 | -31.7542 | 155.1313 | -46.5044 | 73.9202 | -38.3815 | 139.846 | -48.0034 | -11.7515 | -40.9477 | 118.0733 | -37.9301 | 122.999 | -37.423 | -126.9427 | -44.6274 | -173.69 | -35.1743 | -109.591 | -48.1748 | 73.4839 | -38.2093 | -107.2796 | -16.6857 | 128.8745 | -21.9982 | -164.5706 | -17.7558 | -14.867 | -24.1655 | -31.6386 | -17.208 | -121.7038 | -11.6085 | -54.4711 | -24.2167 | 93.5715 | -15.381 | -39.1999 | -39.6983 | -44.1727 | -40.0524 | -34.8663 | -51.1866 | -37.8563 | -38.0576 | -41.7352 | -40.0837 | -37.5967 | -48.8272 | -40.6532 | -42.584 | 411 | -30.5606 | -34.5612 | -30.4902 | -39.2593 | -34.2421 | -33.1869 | -31.9666 | -36.9743 | 411 | -33.1281 | -31.4766 | -26.2592 | -42.668 | -29.3377 | -28.8575 | -33.2166 | -30.8836 | -26.7781 | -41.9865 | -29.7681 | -29.9694 | -35.5656 | -31.4453 | -28.9896 | -40.3086 | -32.1346 | -33.3839 | -35.6541 | -30.8523 | -29.5085 | -39.6271 | -32.565 | -34.4958
412 | -8.5375 | 0 | -8.4066 | 0 | -9.1672 | 0 | -8.0788 | 0 | -38.0567 | 40.0137 | -31.7657 | 142.1768 | -46.2657 | 62.0137 | -37.9701 | 118.75 | -48.4253 | -18.3266 | -39.6298 | 127.9516 | -38.7184 | 122.7733 | -36.8805 | -139.2164 | -46.9238 | -176.3776 | -37.0323 | -123.5974 | -47.4451 | 71.6427 | -37.6293 | -108.666 | -17.7823 | 116.4009 | -29.9888 | 153.7665 | -18.2654 | -31.0753 | -29.6156 | -12.0807 | -21.0314 | -126.2678 | -12.0298 | -63.9736 | -22.2267 | 71.01 | -15.9549 | -39.0701 | -40.2308 | -42.8118 | -39.8423 | -34.8832 | -52.8949 | -38.7181 | -38.2855 | -41.6087 | -39.768 | -36.8987 | -48.3128 | -40.218 | -42.6449 | 412 | -30.7263 | -34.8098 | -30.2946 | -38.3299 | -34.4403 | -34.5546 | -32.3976 | -36.7587 | 412 | -33.0712 | -31.2305 | -26.3457 | -44.4883 | -30.3115 | -29.1183 | -33.2021 | -30.6008 | -26.8044 | -43.7277 | -30.6393 | -30.2067 | -34.2743 | -31.3048 | -28.3612 | -39.9062 | -31.8114 | -33.4777 | -34.4052 | -30.6751 | -28.8199 | -39.1456 | -32.1392 | -34.5661
413 | -8.4963 | 0 | -8.3596 | 0 | -9.0588 | 0 | -8.1486 | 0 | -38.0232 | 42.7575 | -32.5983 | 135.5387 | -46.234 | 48.4264 | -38.7726 | 96.9857 | -47.8004 | -20.113 | -38.0327 | 116.8008 | -38.1646 | 126.7594 | -38.01 | -145.3348 | -47.8483 | -164.0683 | -39.6433 | -125.5093 | -46.0508 | 67.9629 | -37.3917 | -116.452 | -18.649 | 106.0452 | -34.0302 | -5.4359 | -19.972 | -44.9392 | -23.8419 | 15.4485 | -23.2678 | -90.4882 | -12.3274 | -68.3251 | -21.5212 | 44.5671 | -15.1597 | -35.6112 | -41.1487 | -42.2425 | -39.6487 | -35.3167 | -56.7542 | -39.1605 | -38.5354 | -41.6877 | -39.6916 | -36.9963 | -47.1643 | -39.5119 | -42.9582 | 413 | -31.3596 | -35.13 | -30.7587 | -37.04 | -34.8528 | -35.4366 | -33.4775 | -36.5061 | 413 | -33.1914 | -31.1953 | -26.8204 | -48.3946 | -30.8009 | -29.4766 | -33.3281 | -30.6328 | -27.1681 | -47.6954 | -31.0119 | -30.3868 | -33.7462 | -31.1524 | -28.5 | -38.8047 | -31.1523 | -33.8994 | -33.8829 | -30.5899 | -28.8477 | -38.1055 | -31.3633 | -34.8096
414 | -8.5101 | 0 | -8.3721 | 0 | -8.9153 | 0 | -8.2217 | 0 | -36.6905 | 40.5332 | -33.1783 | 137.394 | -46.9344 | 34.0687 | -42.092 | 74.3154 | -46.4994 | -34.5378 | -38.3554 | 99.72 | -36.723 | 122.3512 | -39.0087 | -133.7486 | -45.3667 | -160.5589 | -40.9925 | -108.5886 | -44.3145 | 52.1514 | -38.125 | -124.7483 | -18.8553 | 100.0093 | -25.6763 | -55.3304 | -23.5497 | -48.6403 | -20.2556 | 1.0445 | -19.7441 | -77.0639 | -12.514 | -71.8119 | -22.1226 | 29.5257 | -14.0668 | -38.3824 | -41.716 | -42.4545 | -39.5805 | -36.2238 | -57.7785 | -39.3998 | -38.4775 | -42.052 | -39.8812 | -37.665 | -46.0869 | -39.22 | -43.5569 | 414 | -31.4536 | -35.2516 | -31.6188 | -37.2427 | -34.349 | -34.8245 | -34.4466 | -36.5741 | 414 | -33.5419 | -31.3711 | -27.7137 | -49.4064 | -31.0277 | -29.5622 | -33.6799 | -30.9659 | -28.0021 | -48.8632 | -31.1781 | -30.2558 | -33.9444 | -31.0704 | -29.1549 | -37.7148 | -30.8479 | -34.6416 | -34.0824 | -30.6652 | -29.4433 | -37.1716 | -30.9983 | -35.3352
415 | -8.5241 | 0 | -8.3894 | 0 | -8.8341 | 0 | -8.2794 | 0 | -35.7949 | 29.4621 | -32.1797 | 143.3964 | -48.3008 | 23.6081 | -51.724 | 84.8965 | -47.3884 | -56.5865 | -39.9234 | 89.8136 | -36.0117 | 111.6329 | -36.6125 | -120.2503 | -43.8557 | -175.9945 | -38.4923 | -96.7573 | -44.3635 | 27.8307 | -39.4378 | -126.6058 | -19.1091 | 89.8326 | -24.1338 | -91.1177 | -26.988 | -33.9252 | -18.2893 | -23.4596 | -17.6395 | -86.8176 | -12.7513 | -76.3178 | -23.2891 | 25.129 | -13.6347 | -48.6118 | -41.3075 | -43.139 | -39.5945 | -36.9481 | -52.081 | -39.4007 | -38.2019 | -42.4708 | -40.1998 | -38.5261 | -45.948 | -39.3654 | -45.1045 | 415 | -30.5379 | -35.4015 | -31.4637 | -38.7027 | -32.9259 | -33.6792 | -33.2471 | -37.1763 | 415 | -33.9467 | -31.6757 | -28.424 | -43.6916 | -31.0113 | -29.3678 | -34.0814 | -31.3657 | -28.6687 | -43.2469 | -31.1213 | -29.9225 | -34.6149 | -31.0704 | -30.002 | -37.5586 | -30.976 | -36.2704 | -34.7496 | -30.7604 | -30.2467 | -37.1139 | -31.086 | -36.8251
416 | -8.5134 | 0 | -8.3909 | 0 | -8.8807 | 0 | -8.2952 | 0 | -35.7413 | 16.9905 | -30.0807 | 140.3735 | -49.6293 | 19.5615 | -44.8315 | 150.3202 | -50.3672 | -66.7441 | -40.8563 | 85.6439 | -36.1246 | 101.1389 | -33.6841 | -125.3561 | -43.9464 | 168.2322 | -35.8352 | -106.894 | -46.3878 | 7.9191 | -39.8565 | -124.2489 | -20.0021 | 77.3508 | -25.847 | -121.2804 | -25.2752 | -19.8919 | -17.2474 | -48.0921 | -17.2554 | -99.787 | -12.948 | -82.2416 | -24.4401 | 31.2346 | -13.5987 | -61.3558 | -40.8521 | -43.9043 | -39.3378 | -36.7271 | -49.895 | -39.3887 | -38.0042 | -42.1854 | -40.3337 | -38.9183 | -46.9964 | -40.1737 | -46.3971 | 416 | -28.9994 | -35.1051 | -29.5996 | -39.9061 | -31.4719 | -32.774 | -31.0105 | -37.7823 | 416 | -33.672 | -31.8203 | -28.2137 | -41.5041 | -30.9978 | -29.1235 | -33.7945 | -31.453 | -28.4319 | -41.0143 | -31.0935 | -29.709 | -35.3909 | -30.8244 | -30.4049 | -38.6055 | -31.7828 | -37.5164 | -35.5134 | -30.4571 | -30.6231 | -38.1157 | -31.8785 | -38.1019
417 | -8.4695 | 0 | -8.3406 | 0 | -9.0008 | 0 | -8.2938 | 0 | -36.5255 | 6.0969 | -28.6102 | 127.4678 | -51.1064 | 19.4625 | -40.0149 | 128.755 | -52.1233 | -56.9918 | -41.9768 | 78.127 | -36.9425 | 92.0343 | -31.9884 | -137.2265 | -44.5279 | 158.4916 | -35.1824 | -125.5396 | -49.0127 | 2.305 | -40.1082 | -121.8402 | -21.4004 | 62.7253 | -32.9755 | -163.5096 | -23.5492 | -25.0832 | -17.5024 | -75.7363 | -18.3264 | -111.6544 | -13.1271 | -85.7708 | -22.9945 | 38.1849 | -14.1784 | -73.9257 | -40.6143 | -43.419 | -39.1768 | -35.794 | -49.8213 | -40.3253 | -38.0828 | -41.7039 | -39.9227 | -38.161 | -48.6297 | -41.325 | -43.8335 | 417 | -27.9386 | -34.8366 | -28.1241 | -41.1172 | -30.6044 | -32.857 | -29.8573 | -38.376 | 417 | -33.2344 | -31.4532 | -27.3245 | -41.4807 | -31.9847 | -29.082 | -33.3633 | -30.9219 | -27.5002 | -40.8205 | -32.0315 | -29.789 | -34.9495 | -30.7073 | -29.6915 | -40.2891 | -32.9844 | -34.8327 | -35.0784 | -30.176 | -29.8672 | -39.6289 | -33.0312 | -35.5397
418 | -8.4431 | 0 | -8.3209 | 0 | -9.0514 | 0 | -8.2699 | 0 | -37.9993 | 0.1882 | -28.4895 | 112.5156 | -51.438 | 28.6352 | -38.9163 | 103.4563 | -51.1028 | -52.3597 | -43.3749 | 75.7987 | -38.3704 | 89.5208 | -31.5119 | -152.3071 | -44.7504 | 148.4297 | -36.4403 | -140.3184 | -50.4704 | 1.8876 | -39.2096 | -119.2725 | -24.4552 | 64.6907 | -36.3794 | 31.8082 | -25.1507 | -46.7611 | -17.966 | -98.3662 | -19.9431 | -121.5742 | -13.1572 | -89.7076 | -21.241 | 34.4394 | -15.7704 | -86.2632 | -40.7587 | -42.1181 | -39.0879 | -35.2196 | -50.6337 | -41.7431 | -38.4381 | -41.5788 | -39.5095 | -37.2818 | -49.2076 | -41.8952 | -42.7435 | 418 | -28.0089 | -35.3075 | -27.9853 | -42.1529 | -30.5304 | -34.1853 | -29.776 | -37.8934 | 418 | -33.1357 | -31.0664 | -26.7765 | -42.3128 | -33.4222 | -29.3867 | -33.2579 | -30.4581 | -26.9497 | -41.5823 | -33.4732 | -30.1682 | -33.675 | -30.6448 | -28.8387 | -40.8867 | -33.5743 | -33.6921 | -33.7972 | -30.0365 | -29.0119 | -40.1562 | -33.6253 | -34.4736
419 | -8.4448 | 0 | -8.3403 | 0 | -8.9772 | 0 | -8.2433 | 0 | -39.026 | 4.4647 | -29.4351 | 103.2998 | -50.3003 | 32.739 | -39.3746 | 79.9058 | -49.6181 | -54.5474 | -43.9249 | 72.9333 | -38.5942 | 97.2101 | -32.3704 | -162.6483 | -45.3238 | 138.3951 | -38.4905 | -145.2421 | -51.5586 | 2.2644 | -37.9289 | -126.7253 | -26.1299 | 73.9531 | -26.9343 | -27.5862 | -29.7064 | -58.994 | -18.6641 | -113.8067 | -21.5353 | -113.555 | -12.8856 | -95.0214 | -20.0758 | 22.8535 | -18.657 | -93.7882 | -41.3875 | -41.5283 | -39.0467 | -35.2742 | -52.243 | -42.5595 | -38.8208 | -41.5514 | -39.2886 | -37.0552 | -48.8052 | -41.8444 | -42.5871 | 419 | -28.9504 | -35.9938 | -28.8776 | -42.1641 | -31.2671 | -35.4247 | -30.5451 | -37.0456 | 419 | -33.1066 | -30.8438 | -26.8294 | -43.9027 | -34.2192 | -29.8436 | -33.2111 | -30.3114 | -27.0309 | -43.2658 | -34.3162 | -30.5775 | -33.0835 | -30.6019 | -28.6104 | -40.4649 | -33.5041 | -33.6099 | -33.188 | -30.0695 | -28.8119 | -39.828 | -33.6011 | -34.3438
420 | -8.454 | 0 | -8.4393 | 0 | -8.8985 | 0 | -8.2341 | 0 | -37.931 | 8.8274 | -30.4926 | 103.0845 | -49.2574 | 33.6361 | -41.8225 | 51.8226 | -47.5138 | -65.8882 | -44.6927 | 64.8907 | -36.9541 | 100.0032 | -33.6891 | -159.6142 | -46.0134 | 131.0398 | -40.1137 | -137.4654 | -51.4296 | 6.3033 | -37.8173 | -140.4994 | -25.1805 | 85.0266 | -22.0553 | -61.3127 | -35.4611 | -14.8454 | -18.4811 | -128.6045 | -21.1633 | -112.3929 | -12.605 | -102.0709 | -20.4092 | 14.36 | -22.7367 | -85.8609 | -42.0295 | -41.8012 | -39.0324 | -35.7756 | -55.0217 | -42.8715 | -38.9354 | -41.6485 | -39.3095 | -37.3886 | -47.9042 | -41.9532 | -42.8599 | 420 | -29.7238 | -36.1175 | -30.033 | -41.97 | -31.842 | -35.1391 | -31.6092 | -37.0435 | 420 | -33.1945 | -30.8555 | -27.3216 | -46.5824 | -34.4322 | -30.0369 | -33.2092 | -30.411 | -27.5415 | -46.1232 | -34.6374 | -30.7013 | -33.3472 | -30.5784 | -28.9346 | -39.4649 | -33.5139 | -33.9614 | -33.3619 | -30.1339 | -29.1545 | -39.0057 | -33.7191 | -34.6258
421 | -8.4703 | 0 | -8.5289 | 0 | -8.7867 | 0 | -8.2711 | 0 | -36.562 | 1.3198 | -30.083 | 108.2209 | -47.9316 | 32.1788 | -49.7946 | 22.9168 | -46.4428 | -91.7281 | -46.5519 | 55.7048 | -35.5308 | 90.6712 | -32.7474 | -149.8498 | -46.638 | 124.399 | -39.2521 | -124.775 | -50.7432 | -2.1554 | -39.3408 | -153.823 | -23.4696 | 84.6213 | -19.9126 | -104.0462 | -30.2728 | 6.9876 | -17.4087 | -143.4321 | -20.9202 | -120.9528 | -12.4427 | -111.2828 | -20.4643 | 7.1056 | -23.0721 | -46.9057 | -41.9081 | -42.5175 | -39.08 | -36.6425 | -55.5722 | -42.8691 | -38.7867 | -41.9273 | -39.5367 | -38.0328 | -47.3726 | -42.2086 | -43.8105 | 421 | -29.144 | -35.9539 | -29.941 | -42.1534 | -30.7949 | -33.9033 | -31.1555 | -38.3415 | 421 | -33.457 | -31.0664 | -28.1722 | -47.0433 | -34.3402 | -30 | -33.3984 | -30.75 | -28.3714 | -46.7855 | -34.598 | -30.5156 | -34.0472 | -30.6097 | -29.5625 | -38.8437 | -33.6797 | -35.0238 | -33.9886 | -30.2933 | -29.7617 | -38.5859 | -33.9375 | -35.5394
422 | -8.4799 | 0 | -8.5824 | 0 | -8.7661 | 0 | -8.385 | 0 | -36.0993 | -10.23 | -28.3548 | 106.71 | -46.4464 | 30.095 | -52.6153 | 160.793 | -47.7981 | -118.1706 | -48.8974 | 49.663 | -35.0329 | 78.4777 | -30.336 | -151.5602 | -47.6014 | 121.1672 | -37.1059 | -125.3861 | -51.6455 | -11.5701 | -41.6791 | -153.9379 | -22.6603 | 73.379 | -19.0161 | -136.4061 | -27.4423 | -9.8125 | -16.2842 | -159.5716 | -21.6237 | -136.5338 | -12.5883 | -123.2832 | -21.6889 | 3.9375 | -19.1683 | -40.693 | -41.3249 | -43.0868 | -39.117 | -37.114 | -52.8249 | -42.4618 | -38.6293 | -41.9536 | -39.8041 | -38.555 | -47.7191 | -42.7075 | -46.5281 | 422 | -27.6227 | -35.7253 | -28.3005 | -42.8267 | -29.0075 | -32.8785 | -29.2511 | -40.3549 | 422 | -33.4737 | -31.3242 | -28.6341 | -44.2425 | -33.8794 | -29.8632 | -33.3712 | -31.038 | -28.729 | -44.0588 | -34.0768 | -30.2443 | -34.6069 | -30.6371 | -30.0751 | -39.1367 | -34.1251 | -37.762 | -34.5044 | -30.3509 | -30.17 | -38.953 | -34.3225 | -38.1431
423 | -8.4918 | 0 | -8.5543 | 0 | -8.8394 | 0 | -8.4909 | 0 | -36.5566 | -21.8236 | -26.941 | 97.0881 | -44.4614 | 22.9476 | -43.4775 | 132.1682 | -51.0844 | -134.7462 | -52.7424 | 33.7113 | -35.3831 | 66.7609 | -28.8683 | -163.7374 | -47.5675 | 125.7251 | -35.8089 | -135.6648 | -52.5445 | -9.6998 | -42.68 | -148.0473 | -23.0909 | 59.147 | -19.0731 | -168.3165 | -29.6487 | -32.6166 | -15.5936 | -176.9009 | -23.0523 | -154.1897 | -12.9446 | -137.2151 | -21.8183 | 6.5448 | -16.478 | -53.3644 | -40.7657 | -42.7812 | -38.879 | -36.8008 | -51.2188 | -42.2031 | -38.5192 | -41.3902 | -39.8629 | -38.4449 | -48.7379 | -44.4097 | -50.5154 | 423 | -26.4219 | -35.6278 | -26.8345 | -43.1063 | -27.946 | -32.5369 | -27.9206 | -41.1336 | 423 | -32.8984 | -31.3711 | -28.309 | -42.6645 | -33.6488 | -29.6798 | -32.8359 | -31.0235 | -28.3099 | -42.3794 | -33.7122 | -30.0283 | -34.2894 | -30.3872 | -29.9531 | -40.1836 | -35.8554 | -41.676 | -34.2269 | -30.0396 | -29.954 | -39.8985 | -35.9188 | -42.0245
424 | -8.4922 | 0 | -8.4863 | 0 | -8.9026 | 0 | -8.5807 | 0 | -37.701 | -28.4713 | -26.6777 | 83.5369 | -43.0066 | 8.8887 | -41.5984 | 103.5312 | -53.8746 | -130.3986 | -75.5014 | -31.4538 | -36.5309 | 57.6872 | -28.5388 | -176.4494 | -45.8235 | 125.9066 | -35.5554 | -147.329 | -51.8758 | -9.8318 | -43.5192 | -138.7684 | -25.1636 | 45.9949 | -19.7529 | 160.2556 | -35.7482 | -49.1476 | -15.0273 | 166.6162 | -27.727 | -164.0305 | -14.4997 | -147.9683 | -20.3377 | 6.7304 | -15.4462 | -67.1541 | -40.4633 | -41.6803 | -38.5863 | -36.2016 | -50.9516 | -43.1491 | -38.6035 | -41.219 | -39.4414 | -37.6972 | -49.9629 | -46.7424 | -46.5901 | 424 | -26.2547 | -36.1423 | -26.54 | -42.6625 | -27.8293 | -32.9495 | -27.6379 | -41.1281 | 424 | -32.7268 | -30.9492 | -27.7094 | -42.4653 | -34.6628 | -29.7009 | -32.7327 | -30.5388 | -27.6209 | -42.049 | -34.5684 | -30.0228 | -33.1881 | -30.0941 | -29.205 | -41.4766 | -38.2561 | -37.6875 | -33.194 | -29.6837 | -29.1165 | -41.0603 | -38.1617 | -38.0094
425 | -8.5063 | 0 | -8.3657 | 0 | -8.8852 | 0 | -8.5766 | 0 | -38.6334 | -27.6158 | -27.5845 | 72.2387 | -42.4333 | -5.7882 | -42.25 | 81.5521 | -53.5587 | -126.1512 | -53.1955 | 178.5503 | -38.0231 | 57.2806 | -29.2674 | 172.2244 | -43.7142 | 113.7727 | -36.0372 | -156.2842 | -51.1333 | -19.0693 | -41.8841 | -127.7639 | -29.2256 | 38.6215 | -20.6137 | 139.4339 | -38.9789 | 43.4999 | -15.2539 | 153.4423 | -33.5203 | -153.0775 | -16.3551 | -155.1029 | -19.8292 | 0.2014 | -15.7792 | -85.1892 | -40.3934 | -41.2606 | -38.4481 | -35.7919 | -51.3036 | -44.7645 | -38.9907 | -41.5532 | -39.0883 | -37.1508 | -50.6782 | -46.9008 | -44.5961 | 425 | -27.1262 | -36.969 | -27.4271 | -41.7847 | -28.5889 | -33.8258 | -28.246 | -39.3921 | 425 | -33.0469 | -30.582 | -27.2856 | -42.9379 | -36.3988 | -30.1055 | -33.1875 | -30.2031 | -27.2153 | -42.4184 | -36.1879 | -30.4141 | -32.7543 | -29.9418 | -28.6445 | -42.3125 | -38.5351 | -35.7109 | -32.8949 | -29.5629 | -28.5742 | -41.793 | -38.3242 | -36.0195
426 | -8.5195 | 0 | -8.33 | 0 | -8.8313 | 0 | -8.5481 | 0 | -38.0683 | -23.6999 | -28.9186 | 70.9393 | -42.6053 | -18.1562 | -44.9975 | 62.5276 | -52.8214 | -130.4782 | -47.5821 | 157.5992 | -37.9711 | 64.745 | -30.5793 | 171.8115 | -42.58 | 92.6741 | -36.8618 | -161.1472 | -51.3561 | -31.2086 | -39.7578 | -133.6491 | -33.4506 | 64.4618 | -22.8939 | 118.7885 | -28.5958 | 38.5327 | -15.6607 | 144.6192 | -33.7065 | -121.2356 | -18.2375 | -151.4773 | -19.7046 | -9.9729 | -17.671 | -99.084 | -40.5922 | -41.5856 | -38.3911 | -35.7914 | -52.1859 | -46.4763 | -39.5487 | -41.8234 | -38.9414 | -37.0565 | -50.8769 | -46.5656 | -44.1085 | 426 | -28.2575 | -37.1471 | -28.7555 | -41.1037 | -29.6262 | -34.2847 | -29.2561 | -37.7402 | 426 | -33.3039 | -30.4219 | -27.2719 | -43.8559 | -38.1463 | -30.7174 | -33.4934 | -30.1101 | -27.2433 | -43.3546 | -37.9282 | -31.0006 | -33.0661 | -29.8716 | -28.537 | -42.5469 | -38.2356 | -35.2772 | -33.2556 | -29.5598 | -28.5084 | -42.0456 | -38.0175 | -35.5604
427 | -8.549 | 0 | -8.3214 | 0 | -8.7581 | 0 | -8.552 | 0 | -36.6531 | -29.516 | -28.8452 | 78.6088 | -43.2668 | -28.4202 | -53.9603 | 68.5351 | -51.563 | -137.88 | -45.379 | 138.0716 | -36.4454 | 63.6478 | -30.2958 | -179.0805 | -42.8754 | 69.4547 | -37.6048 | -159.5627 | -52.236 | -42.7078 | -39.1929 | -147.1146 | -29.4079 | 112.2374 | -23.1953 | 126.4153 | -27.6583 | 17.5409 | -15.1974 | 142.5715 | -34.1215 | -76.4199 | -18.4676 | -140.9073 | -19.5293 | -16.7867 | -21.1681 | -92.1002 | -40.654 | -42.1805 | -38.4205 | -36.2282 | -53.2594 | -47.8602 | -39.9386 | -41.9261 | -39.0411 | -37.4738 | -50.3605 | -46.68 | -44.4102 | 427 | -28.0469 | -36.4376 | -28.7367 | -40.8045 | -29.1634 | -33.9119 | -29.1074 | -37.4964 | 427 | -33.3771 | -30.4921 | -27.6792 | -44.938 | -39.5388 | -31.1805 | -33.6047 | -30.283 | -27.6762 | -44.5013 | -39.3082 | -31.3866 | -33.6315 | -29.8715 | -28.9248 | -42.0391 | -38.3586 | -35.6521 | -33.8591 | -29.6624 | -28.9218 | -41.6024 | -38.128 | -35.8582
428 | -8.5701 | 0 | -8.3443 | 0 | -8.7315 | 0 | -8.6279 | 0 | -35.991 | -42.2184 | -27.1882 | 78.2682 | -44.2959 | -30.3178 | -46.9426 | 144.2498 | -50.1766 | -155.9622 | -45.1451 | 122.3711 | -35.4697 | 53.756 | -28.2586 | -179.4658 | -45.1909 | 48.0829 | -36.8656 | -155.4714 | -54.0701 | -53.0717 | -39.9209 | -157.0677 | -24.79 | 115.3789 | -20.9098 | 125.5197 | -29.329 | -11.1232 | -14.0971 | 138.3414 | -31.1491 | -56.7836 | -17.128 | -140.8511 | -19.5821 | -20.7378 | -20.2449 | -65.3286 | -40.3894 | -42.3003 | -38.553 | -36.9447 | -53.34 | -48.4116 | -39.9537 | -41.87 | -39.3587 | -38.2151 | -49.7502 | -47.5027 | -46.0143 | 428 | -26.5767 | -35.5048 | -27.0742 | -41.1141 | -27.4296 | -33.0669 | -27.4451 | -38.664 | 428 | -33.2999 | -30.7886 | -28.3746 | -44.9957 | -40.0673 | -31.2222 | -33.5257 | -30.6272 | -28.3168 | -44.6085 | -39.7837 | -31.3258 | -33.7302 | -29.9829 | -29.645 | -41.4059 | -39.1584 | -37.2828 | -33.956 | -29.8215 | -29.5872 | -41.0187 | -38.8748 | -37.3864
429 | -8.6072 | 0 | -8.367 | 0 | -8.7576 | 0 | -8.8024 | 0 | -36.3904 | -56.579 | -25.7457 | 68.8799 | -43.9435 | -26.0425 | -40.8085 | 125.5591 | -50.1402 | -179.0592 | -46.3287 | 115.5334 | -35.4626 | 41.4977 | -26.7321 | 169.7323 | -49.7233 | 38.2334 | -35.5613 | -160.3134 | -57.5005 | -48.9485 | -41.0875 | -162.8577 | -22.9656 | 102.1276 | -18.8308 | 111.3819 | -36.2014 | -54.657 | -12.8645 | 130.7303 | -27.8215 | -53.2211 | -15.7769 | -150.7977 | -19.7223 | -25.0266 | -16.4917 | -66.0928 | -40.1585 | -41.8207 | -38.5492 | -37.3382 | -52.566 | -47.5901 | -39.8337 | -41.4793 | -39.6833 | -38.7243 | -49.6326 | -49.1881 | -49.2902 | 429 | -25.3265 | -34.9175 | -25.5757 | -41.3488 | -26.167 | -32.4877 | -26.0591 | -40.4439 | 429 | -32.8721 | -31.0761 | -28.731 | -44.199 | -39.2231 | -31.0761 | -33.1123 | -30.9257 | -28.5358 | -43.8084 | -38.7877 | -31.0313 | -33.2135 | -29.942 | -30.1171 | -41.2656 | -40.8211 | -40.5326 | -33.4537 | -29.7916 | -29.9219 | -40.875 | -40.3857 | -40.4878
430 | -8.6328 | 0 | -8.3643 | 0 | -8.8365 | 0 | -8.9483 | 0 | -37.7998 | -66.6768 | -25.2617 | 55.1786 | -42.2038 | -28.81 | -38.6339 | 98.9284 | -51.3387 | 161.2927 | -47.3316 | 124.7023 | -36.3399 | 31.1462 | -26.3022 | 156.3627 | -53.9991 | 78.9574 | -34.9655 | -169.8459 | -57.4443 | -21.6815 | -42.9098 | -164.3631 | -22.8854 | 92.5239 | -17.7446 | 94.7101 | -39.4813 | 175.5306 | -11.8499 | 119.9733 | -25.3376 | -58.532 | -15.4664 | -163.0794 | -19.2486 | -28.8837 | -14.1281 | -81.7638 | -40.2048 | -40.8839 | -38.3638 | -37.1774 | -51.8337 | -46.5285 | -39.6065 | -41.0904 | -39.5742 | -38.587 | -50.0167 | -52.0279 | -51.8161 | 430 | -24.9437 | -35.0825 | -25.0407 | -40.6532 | -25.885 | -32.5741 | -25.6656 | -42.4448 | 430 | -32.4576 | -30.9414 | -28.5446 | -43.4694 | -38.1642 | -30.77 | -32.7261 | -30.7377 | -28.2291 | -42.9972 | -37.5802 | -30.6582 | -32.2511 | -29.731 | -29.9542 | -41.6524 | -43.6636 | -42.9796 | -32.5196 | -29.5273 | -29.6387 | -41.1802 | -43.0796 | -42.8678
431 | -8.6186 | 0 | -8.3479 | 0 | -8.8475 | 0 | -8.9794 | 0 | -39.1382 | -65.7474 | -26.0515 | 43.9624 | -40.9501 | -38.6875 | -38.8129 | 74.8551 | -52.2691 | 150.6406 | -44.8559 | 132.6092 | -37.7658 | 29.473 | -26.9568 | 146.3044 | -47.1324 | 95.3743 | -35.3251 | -179.8522 | -53.8818 | -22.0265 | -43.5155 | -148.7186 | -24.1051 | 89.7026 | -18.2543 | 78.233 | -30.6778 | 129.8069 | -11.4702 | 108.477 | -24.1538 | -68.7716 | -16.4587 | -173.1919 | -19.3363 | -42.1167 | -13.5577 | -103.314 | -40.3987 | -40.1754 | -38.1439 | -36.8139 | -51.7312 | -46.4971 | -39.6075 | -41.264 | -39.1398 | -38.1602 | -50.7831 | -52.9041 | -49.7707 | 431 | -25.7112 | -35.8617 | -25.7734 | -39.2456 | -26.5722 | -33.3275 | -26.2835 | -41.6779 | 431 | -32.6454 | -30.5212 | -28.1953 | -43.3833 | -38.1492 | -30.76 | -32.9161 | -30.2923 | -27.8345 | -42.8837 | -37.5177 | -30.6281 | -31.5568 | -29.5253 | -29.5416 | -42.4352 | -44.5562 | -40.9232 | -31.8275 | -29.2964 | -29.1808 | -41.9356 | -43.9247 | -40.7913
432 | -8.6475 | 0 | -8.3317 | 0 | -8.8159 | 0 | -8.9241 | 0 | -39.049 | -61.3358 | -27.2698 | 39.9471 | -40.2161 | -52.8181 | -40.5146 | 53.1708 | -52.6519 | 140.9965 | -42.4269 | 127.7181 | -38.2788 | 34.5093 | -27.9801 | 143.0032 | -43.2365 | 77.1128 | -36.1001 | 173.9953 | -51.9291 | -34.1706 | -41.6843 | -140.2121 | -25.0603 | 104.0527 | -19.8301 | 70.2755 | -27.7739 | 109.1649 | -11.4233 | 98.3005 | -23.5937 | -73.3153 | -17.4445 | -176.8783 | -19.8276 | -54.4952 | -13.9895 | -124.1969 | -40.5235 | -40.0232 | -37.919 | -36.6584 | -51.9607 | -47.0509 | -39.8086 | -41.7393 | -38.8286 | -37.894 | -51.5805 | -52.3903 | -48.5462 | 432 | -26.7888 | -36.6008 | -26.9441 | -38.0199 | -27.4757 | -33.9738 | -27.1999 | -39.1461 | 432 | -33.0918 | -30.1811 | -28.0109 | -43.629 | -38.7192 | -30.9927 | -33.4076 | -30.0127 | -27.7343 | -43.1448 | -38.1268 | -30.8845 | -31.3757 | -29.2715 | -29.2465 | -43.2488 | -44.0586 | -39.7303 | -31.6915 | -29.1031 | -28.9699 | -42.7646 | -43.4662 | -39.6221
433 | -8.6847 | 0 | -8.3683 | 0 | -8.7589 | 0 | -8.8175 | 0 | -37.6482 | -62.1202 | -27.8997 | 44.3954 | -40.128 | -67.7359 | -44.6676 | 39.2625 | -52.8425 | 130.7761 | -40.939 | 114.1913 | -37.2392 | 39.0804 | -28.408 | 147.9124 | -41.4023 | 50.5303 | -36.9902 | 172.9705 | -51.172 | -50.3253 | -39.6767 | -146.046 | -23.7953 | 111.956 | -21.7791 | 77.8102 | -26.7451 | 86.5995 | -11.6403 | 88.361 | -23.4329 | -72.8911 | -17.6525 | -176.4923 | -21.3416 | -65.065 | -15.7275 | -145.4039 | -40.5486 | -40.2204 | -37.7322 | -36.8532 | -52.4118 | -47.9665 | -40.1417 | -42.5284 | -38.6847 | -37.8839 | -52.255 | -51.3604 | -48.6209 | 433 | -27.2334 | -36.7531 | -27.603 | -37.3791 | -27.6853 | -34.0182 | -27.5684 | -37.2638 | 433 | -33.8437 | -30 | -28.1685 | -44.0435 | -39.5982 | -31.3828 | -34.1601 | -29.9258 | -28.0357 | -43.6529 | -39.149 | -31.3242 | -31.5357 | -29.0475 | -29.1992 | -43.8867 | -42.9921 | -39.862 | -31.8521 | -28.9733 | -29.0664 | -43.4961 | -42.5429 | -39.8034
434 | -8.7548 | 0 | -8.4468 | 0 | -8.7422 | 0 | -8.6879 | 0 | -36.5041 | -75.9398 | -26.5372 | 46.8131 | -41.3836 | -79.9688 | -49.3024 | 80.6706 | -52.5218 | 122.3207 | -40.8526 | 101.0228 | -35.7427 | 31.2095 | -26.8055 | 149.7044 | -41.8129 | 23.0266 | -36.7577 | 177.2589 | -51.5804 | -66.8168 | -39.3784 | -159.8117 | -21.4058 | 116.5818 | -19.4396 | 92.6702 | -27.5554 | 85.9412 | -12.216 | 82.641 | -22.2154 | -75.9548 | -16.4535 | -176.5394 | -23.1338 | -64.8862 | -19.5909 | -154.6846 | -40.4279 | -40.239 | -37.6617 | -37.2365 | -52.7248 | -49.0671 | -40.3023 | -43.4063 | -38.7782 | -38.2906 | -52.3452 | -50.1915 | -50.4401 | 434 | -25.9929 | -36.1799 | -26.3572 | -37.9456 | -26.1636 | -33.1476 | -26.1744 | -37.2536 | 434 | -34.6515 | -30.0234 | -28.4817 | -44.278 | -40.6203 | -31.5601 | -34.9595 | -30.036 | -28.5486 | -43.9826 | -40.3792 | -31.6144 | -31.4842 | -28.9069 | -29.5358 | -43.8984 | -41.7447 | -41.6979 | -31.7922 | -28.9195 | -29.6027 | -43.603 | -41.5036 | -41.7522
435 | -8.7995 | 0 | -8.548 | 0 | -8.7252 | 0 | -8.6427 | 0 | -36.6366 | -92.5008 | -25.0908 | 38.5607 | -43.1866 | -79.9937 | -42.9133 | 99.773 | -51.8524 | 110.6103 | -41.8351 | 93.069 | -35.1556 | 18.0094 | -25.2178 | 140.7049 | -44.252 | -1.8958 | -35.6238 | 175.2156 | -53.1806 | -78.2169 | -40.6405 | -170.1127 | -19.7221 | 106.0798 | -16.1097 | 89.2648 | -26.5376 | 85.8577 | -12.5793 | 79.7462 | -20.8928 | -85.2025 | -14.7857 | 172.1208 | -23.7826 | -60.5986 | -22.4226 | -130.5344 | -40.5331 | -39.8977 | -37.6869 | -37.5604 | -52.7166 | -49.8743 | -40.259 | -43.5416 | -38.9909 | -38.6144 | -52.0324 | -49.5064 | -54.4776 | 435 | -24.7343 | -35.613 | -24.9302 | -39.2054 | -24.7492 | -32.3372 | -24.7265 | -38.9055 | 435 | -34.7421 | -30.1914 | -28.7609 | -44.1686 | -41.3263 | -31.5338 | -34.9936 | -30.2657 | -28.9177 | -43.9914 | -41.2316 | -31.6163 | -31.0982 | -28.8874 | -29.8149 | -43.4844 | -40.9584 | -45.7524 | -31.3497 | -28.9617 | -29.9717 | -43.3072 | -40.8637 | -45.8349
436 | -8.8239 | 0 | -8.632 | 0 | -8.7482 | 0 | -8.6739 | 0 | -38.1868 | -106.6445 | -24.6215 | 24.9369 | -43.2444 | -71.5653 | -39.5891 | 81.582 | -51.7325 | 95.0339 | -42.6353 | 96.3819 | -35.6186 | 4.8828 | -24.798 | 127.2368 | -49.8036 | -14.1848 | -34.9024 | 166.5964 | -54.8324 | -75.9099 | -42.9852 | -166.9549 | -19.5295 | 99.7588 | -14.0611 | 74.221 | -25.3726 | 90.9648 | -12.5092 | 77.1077 | -20.6182 | -93.0971 | -14.1778 | 154.9229 | -22.5316 | -61.7353 | -18.5634 | -115.3343 | -41.0155 | -39.5575 | -37.8441 | -37.6092 | -52.7303 | -49.6161 | -40.214 | -42.5529 | -39.0973 | -38.5578 | -51.7414 | -49.9045 | -60.4497 | 436 | -24.3777 | -35.7114 | -24.4193 | -39.6419 | -24.4399 | -32.2116 | -24.3338 | -41.9355 | 436 | -33.729 | -30.2734 | -28.7853 | -44.0983 | -40.9841 | -31.4658 | -33.9209 | -30.3491 | -28.9353 | -43.9821 | -40.9422 | -31.5401 | -30.7336 | -29.0202 | -29.7339 | -43.1094 | -41.2725 | -51.7015 | -30.9255 | -29.0959 | -29.8839 | -42.9932 | -41.2306 | -51.7758
437 | -8.8304 | 0 | -8.6546 | 0 | -8.7601 | 0 | -8.725 | 0 | -40.4656 | -108.7345 | -25.301 | 12.6728 | -41.508 | -70.2648 | -38.6037 | 60.8311 | -52.466 | 82.0121 | -41.6831 | 102.1908 | -36.8955 | -4.2248 | -25.4774 | 115.6492 | -53.2251 | 43.2624 | -34.7848 | 157.6162 | -53.9824 | -69.9744 | -42.829 | -146.648 | -20.0638 | 97.6238 | -13.2285 | 57.2102 | -23.5944 | 83.2793 | -12.1244 | 73.2654 | -21.0941 | -97.4867 | -14.3413 | 136.4194 | -21.4839 | -71.7694 | -15.7062 | -127.9858 | -41.4522 | -39.5342 | -38.046 | -37.4913 | -53.0499 | -48.4874 | -40.3304 | -41.8929 | -38.8383 | -38.2601 | -51.6 | -51.057 | -61.1685 | 437 | -25.071 | -36.3186 | -25.0082 | -38.4102 | -25.1681 | -32.6706 | -24.9248 | -42.1547 | 437 | -33.0625 | -30.0079 | -28.6609 | -44.3953 | -39.8328 | -31.5703 | -33.2383 | -30.0782 | -28.7663 | -44.2898 | -39.7624 | -31.6054 | -30.7038 | -29.2156 | -29.4297 | -42.9454 | -42.4024 | -52.4084 | -30.8796 | -29.2859 | -29.5351 | -42.8399 | -42.332 | -52.4435
438 | -8.8545 | 0 | -8.6241 | 0 | -8.7653 | 0 | -8.7291 | 0 | -41.0515 | -100.9074 | -26.7983 | 7.6284 | -39.8765 | -77.847 | -39.196 | 40.6116 | -52.9543 | 78.1222 | -39.6883 | 99.3315 | -38.0346 | -5.434 | -26.7934 | 111.3467 | -45.7858 | 49.6405 | -35.0776 | 150.0261 | -52.4588 | -77.444 | -39.7246 | -143.3028 | -20.1924 | 106.8542 | -13.5985 | 40.9292 | -22.8141 | 75.245 | -12.0072 | 66.5246 | -21.9413 | -92.7578 | -15.3826 | 116.7612 | -22.3253 | -79.6346 | -14.9206 | -148.668 | -41.5037 | -39.9769 | -38.0817 | -37.3552 | -53.8162 | -47.3285 | -40.6631 | -42.4411 | -38.4287 | -37.8897 | -51.6163 | -51.8747 | -58.6579 | 438 | -26.4369 | -36.9059 | -26.3491 | -36.6677 | -26.4281 | -33.2465 | -26.0039 | -38.582 | 438 | -33.5866 | -29.5742 | -28.5007 | -45.1921 | -38.7044 | -31.8978 | -33.817 | -29.6634 | -28.6261 | -45.0509 | -38.5994 | -31.934 | -31.1224 | -29.2272 | -29.0352 | -42.9922 | -43.2506 | -49.8926 | -31.3528 | -29.3164 | -29.1606 | -42.851 | -43.1456 | -49.9288
439 | -8.9271 | 0 | -8.5462 | 0 | -8.7505 | 0 | -8.6853 | 0 | -39.6778 | -101.395 | -27.6104 | 13.0142 | -38.8935 | -89.95 | -41.542 | 24.4892 | -52.322 | 72.3032 | -38.1075 | 88.1961 | -38.0486 | -3.7714 | -27.3882 | 117.1131 | -42.418 | 27.0106 | -35.6496 | 144.9163 | -51.9751 | -91.4449 | -37.7393 | -153.7894 | -18.4881 | 109.1384 | -14.8149 | 30.5431 | -23.0061 | 68.9398 | -12.1996 | 58.3479 | -20.6011 | -93.2644 | -17.5027 | 105.4444 | -23.9962 | -99.3499 | -15.01 | -168.5096 | -41.379 | -40.4778 | -37.8848 | -37.2735 | -54.7969 | -46.4192 | -41.4212 | -43.9067 | -37.9622 | -37.7415 | -51.7611 | -51.3052 | -57.7953 | 439 | -27.0545 | -37.3595 | -27.081 | -35.3836 | -26.9065 | -33.6114 | -26.4489 | -36.3461 | 439 | -34.9796 | -29.0351 | -28.3464 | -46.2507 | -37.873 | -32.6707 | -35.3605 | -29.2117 | -28.5882 | -46.0464 | -37.7339 | -32.7359 | -31.5507 | -28.9577 | -28.8144 | -43.2149 | -42.759 | -49.0448 | -31.9316 | -29.1343 | -29.0562 | -43.0106 | -42.6199 | -49.11
440 | -8.9744 | 0 | -8.4833 | 0 | -8.7285 | 0 | -8.6048 | 0 | -38.7206 | -113.2391 | -26.4566 | 17.5978 | -38.5716 | -104.1784 | -45.857 | 27.6844 | -52.0437 | 59.2553 | -37.5822 | 71.419 | -37.4267 | -7.9191 | -26.0104 | 119.8936 | -41.5434 | 0.2495 | -35.9587 | 142.611 | -52.1194 | -103.943 | -37.243 | -168.108 | -16.6183 | 105.4541 | -16.2542 | 30.9325 | -23.2924 | 63.0494 | -12.944 | 51.1133 | -18.2511 | -98.69 | -20.0746 | 111.3216 | -25.1085 | -104.83 | -16.5082 | 176.3491 | -41.6676 | -40.6433 | -37.5884 | -37.3786 | -55.4879 | -46.0456 | -42.0419 | -44.6387 | -37.4197 | -37.7841 | -51.8857 | -50.0723 | -59.0662 | 440 | -25.9612 | -37.7868 | -26.0877 | -34.9528 | -25.5959 | -33.5597 | -25.3045 | -35.7692 | 440 | -35.6643 | -28.4453 | -28.4042 | -47.0046 | -37.5623 | -33.3134 | -36.1554 | -28.6912 | -28.7738 | -46.7594 | -37.4408 | -33.4371 | -31.6689 | -28.614 | -28.8097 | -43.4024 | -41.589 | -50.3377 | -32.16 | -28.8599 | -29.1793 | -43.1572 | -41.4675 | -50.4614
441 | -8.9958 | 0 | -8.4685 | 0 | -8.7263 | 0 | -8.57 | 0 | -39.0699 | -127.4144 | -24.8732 | 12.0319 | -39.1383 | -117.758 | -45.1256 | 61.9515 | -53.5649 | 48.862 | -38.4776 | 56.3767 | -36.84 | -17.4735 | -24.4776 | 112.4807 | -43.0362 | -25.5606 | -35.6818 | 140.4684 | -52.6901 | -116.4283 | -37.904 | -178.9032 | -15.3362 | 97.0161 | -16.0371 | 39.4751 | -23.6421 | 68.2987 | -14.3182 | 49.896 | -16.9575 | -109.1746 | -19.5258 | 120.1472 | -25.8253 | -97.8971 | -18.4644 | 174.047 | -42.6411 | -40.3715 | -37.4575 | -37.6215 | -55.2036 | -46.2661 | -42.1677 | -43.4255 | -37.0075 | -38.0505 | -51.7653 | -48.7067 | -62.9935 | 441 | -24.5571 | -37.9859 | -24.6487 | -35.7133 | -24.1757 | -33.1634 | -23.9807 | -36.6331 | 441 | -34.4297 | -28.0117 | -28.6257 | -46.7351 | -37.7976 | -33.4414 | -34.957 | -28.2812 | -29.0515 | -46.4773 | -37.6961 | -33.5977 | -31.3757 | -28.4617 | -29.0547 | -43.2968 | -40.2382 | -54.2672 | -31.903 | -28.7312 | -29.4805 | -43.039 | -40.1367 | -54.4235
442 | -8.9564 | 0 | -8.5254 | 0 | -8.7319 | 0 | -8.5648 | 0 | -40.3679 | -138.3311 | -24.1395 | -0.9164 | -40.875 | -126.3693 | -40.8722 | 59.6737 | -55.0704 | 59.2039 | -40.551 | 49.7668 | -37.0319 | -32.2083 | -23.9051 | 99.7789 | -47.8304 | -40.1812 | -35.3478 | 134.0227 | -54.2039 | -125.4735 | -39.3015 | 177.5865 | -14.9106 | 87.6152 | -14.5715 | 39.4013 | -23.2351 | 79.9117 | -15.0946 | 57.0752 | -16.6616 | -122.8485 | -17.826 | 117.0042 | -24.5696 | -102.8314 | -18.3161 | -178.9093 | -43.8972 | -39.8733 | -37.5236 | -37.8308 | -54.5183 | -46.8577 | -42.2246 | -42.0093 | -36.7806 | -38.2988 | -51.2207 | -47.8061 | -71.7099 | 442 | -23.9482 | -37.5253 | -23.9522 | -37.6208 | -23.6819 | -33.0649 | -23.4888 | -38.6098 | 442 | -33.0529 | -27.8242 | -28.8744 | -45.9929 | -38.3323 | -33.4927 | -33.4839 | -28.0487 | -29.266 | -45.7864 | -38.2929 | -33.6598 | -30.9169 | -28.5672 | -29.3424 | -42.6953 | -39.2807 | -62.978 | -31.3479 | -28.7917 | -29.734 | -42.4888 | -39.2413 | -63.1451
443 | -8.9426 | 0 | -8.6004 | 0 | -8.7415 | 0 | -8.6273 | 0 | -41.6683 | -141.8996 | -24.5823 | -14.3551 | -42.374 | -118.7238 | -39.053 | 40.2675 | -52.8287 | 68.2628 | -41.8564 | 58.8859 | -38.4882 | -46.8543 | -24.3777 | 87.3641 | -51.4661 | 15.5677 | -35.4035 | 127.0856 | -55.4115 | -121.6674 | -39.8193 | -174.7151 | -15.324 | 80.9306 | -13.3372 | 31.5156 | -21.1205 | 78.269 | -14.1556 | 63.8002 | -17.2152 | -135.8092 | -16.8623 | 101.5025 | -23.9521 | -124.896 | -16.2841 | 177.1084 | -44.7964 | -39.5626 | -37.5566 | -37.941 | -54.2535 | -47.0821 | -42.6277 | -41.429 | -36.6965 | -38.3387 | -50.909 | -47.5345 | -70.9342 | 443 | -24.4279 | -37.0403 | -24.352 | -38.9171 | -24.2042 | -33.6383 | -23.9342 | -39.4211 | 443 | -32.4864 | -27.7539 | -28.9984 | -45.6531 | -38.4817 | -33.8862 | -32.8286 | -27.955 | -29.3137 | -45.512 | -38.4548 | -34.0004 | -30.62 | -28.614 | -29.3961 | -42.3086 | -38.9341 | -62.1927 | -30.9622 | -28.8151 | -29.7114 | -42.1675 | -38.9072 | -62.3069
444 | -8.9291 | 0 | -8.6183 | 0 | -8.7543 | 0 | -8.7053 | 0 | -42.38 | -143.5036 | -26.0073 | -20.9124 | -40.5513 | -110.0662 | -39.3829 | 18.6525 | -50.476 | 61.6381 | -40.5015 | 65.9919 | -41.2126 | -55.2386 | -25.6728 | 80.9617 | -43.2322 | 22.0121 | -35.8033 | 119.73 | -54.3369 | -116.1478 | -38.3128 | -170.568 | -16.0537 | 80.9409 | -13.1263 | 21.8907 | -19.7906 | 72.9939 | -12.7129 | 61.1922 | -18.1888 | -141.1451 | -17.2487 | 84.5366 | -24.936 | -145.6008 | -14.8322 | 162.9195 | -44.9433 | -39.5871 | -37.1681 | -38.0527 | -54.2832 | -46.3879 | -43.1301 | -42.1958 | -36.5033 | -38.2512 | -51.1613 | -47.7934 | -63.9234 | 444 | -25.7617 | -37.3983 | -25.6671 | -37.3017 | -25.4797 | -34.6578 | -25.0602 | -37.0187 | 444 | -33.2667 | -27.5742 | -29.1236 | -45.6649 | -37.7696 | -34.3758 | -33.5775 | -27.749 | -29.3474 | -45.5289 | -37.6826 | -34.4248 | -30.658 | -28.239 | -29.3221 | -42.543 | -39.1751 | -55.1691 | -30.9688 | -28.4138 | -29.5459 | -42.407 | -39.0881 | -55.2181
445 | -8.9503 | 0 | -8.5987 | 0 | -8.7511 | 0 | -8.7159 | 0 | -42.4018 | -146.0519 | -27.1112 | -17.0841 | -38.2582 | -119.4208 | -41.8305 | 1.9361 | -48.8791 | 49.1469 | -38.6806 | 59.685 | -44.0379 | -47.307 | -26.5632 | 84.352 | -39.4118 | -3.4147 | -36.3436 | 115.662 | -51.984 | -122.2007 | -36.5856 | -176.5015 | -16.0495 | 88.3685 | -13.8275 | 15.9582 | -19.5802 | 68.5935 | -11.9847 | 52.4366 | -18.8184 | -134.2447 | -19.1777 | 73.8446 | -28.0808 | -164.3086 | -14.5658 | 144.5896 | -44.7245 | -39.7401 | -36.5917 | -38.2792 | -54.3807 | -45.4315 | -43.3683 | -44.1222 | -36.2315 | -38.2042 | -51.837 | -47.8136 | -60.8536 | 445 | -26.6722 | -38.6623 | -26.6838 | -35.261 | -26.2702 | -35.5614 | -25.7545 | -34.6809 | 445 | -35.1719 | -27.2812 | -29.3289 | -45.782 | -36.8328 | -34.6172 | -35.5235 | -27.4804 | -29.5633 | -45.6296 | -36.7156 | -34.6524 | -30.7898 | -27.6414 | -29.2539 | -43.2383 | -39.2149 | -52.1025 | -31.1414 | -27.8406 | -29.4883 | -43.0859 | -39.0977 | -52.1377
446 | -8.9913 | 0 | -8.5806 | 0 | -8.7434 | 0 | -8.7029 | 0 | -42.1154 | -153.2009 | -26.1682 | -11.2042 | -37.2277 | -136.3524 | -45.9974 | 8.3101 | -48.059 | 35.1634 | -37.7496 | 47.0873 | -43.8022 | -31.7445 | -25.6398 | 88.6114 | -38.257 | -31.5614 | -36.6897 | 113.4616 | -49.9247 | -139.0011 | -35.7525 | 171.3278 | -14.4088 | 89.4327 | -14.1193 | 17.2581 | -19.0744 | 61.7396 | -11.9768 | 41.9302 | -16.9826 | -135.6224 | -22.058 | 83.7344 | -33.7194 | -157.546 | -15.4321 | 127.5854 | -44.8001 | -39.4004 | -36.2304 | -38.5345 | -54.1399 | -44.7442 | -43.3618 | -45.2903 | -35.9093 | -38.3774 | -52.6899 | -46.9504 | -60.0685 | 446 | -25.7394 | -39.9051 | -25.8344 | -34.2845 | -25.3459 | -35.7488 | -24.9359 | -33.7112 | 446 | -36.299 | -26.918 | -29.5432 | -45.5593 | -36.1636 | -34.6184 | -36.7097 | -27.1659 | -29.8316 | -45.3965 | -36.0413 | -34.6589 | -30.4091 | -27.2391 | -29.3861 | -44.1093 | -38.3698 | -51.3251 | -30.8198 | -27.487 | -29.6745 | -43.9465 | -38.2475 | -51.3656
447 | -9.0378 | 0 | -8.6325 | 0 | -8.7828 | 0 | -8.6588 | 0 | -42.5591 | -165.2047 | -24.5583 | -17.2502 | -37.5092 | -155.0274 | -45.0266 | 39.0346 | -48.0127 | 22.246 | -37.9957 | 31.9048 | -42.1867 | -33.5968 | -24.2118 | 82.3318 | -39.0056 | -58.3955 | -36.5422 | 110.5297 | -48.9236 | -162.851 | -35.9976 | 158.2048 | -13.215 | 87.3401 | -13.6587 | 18.7307 | -19.3323 | 62.8062 | -13.4105 | 35.1545 | -15.5809 | -147.9778 | -20.2382 | 103.014 | -30.4227 | -125.9183 | -17.451 | 119.1182 | -45.3325 | -38.5023 | -36.1948 | -38.7505 | -53.3794 | -44.725 | -43.3317 | -43.6344 | -35.6979 | -38.6169 | -53.3044 | -45.7672 | -61.8499 | 447 | -24.2786 | -39.884 | -24.3287 | -34.5358 | -24.0036 | -35.3024 | -23.7012 | -34.0908 | 447 | -34.5966 | -26.6601 | -29.7127 | -44.7469 | -36.0925 | -34.5489 | -35.0019 | -26.9151 | -30.0917 | -44.5966 | -36.0662 | -34.6729 | -29.4645 | -27.157 | -29.5791 | -44.6719 | -37.1347 | -53.0671 | -29.8698 | -27.412 | -29.9581 | -44.5216 | -37.1084 | -53.1911
448 | -9.0557 | 0 | -8.7422 | 0 | -8.8102 | 0 | -8.6353 | 0 | -43.7468 | -175.7744 | -23.7419 | -30.8074 | -39.3304 | -170.4034 | -41.3015 | 36.8414 | -47.9342 | 11.4628 | -39.5525 | 19.2895 | -41.847 | -44.0119 | -23.5179 | 70.6686 | -41.8114 | -77.973 | -36.3736 | 105.8321 | -49.4727 | 170.4755 | -37.238 | 149.6666 | -12.6222 | 80.1836 | -12.5726 | 12.9161 | -19.6417 | 68.0495 | -15.0281 | 37.7402 | -15.3067 | -162.384 | -16.9477 | 99.738 | -25.2379 | -139.4943 | -18.911 | 124.8124 | -45.8212 | -37.6938 | -36.3222 | -38.7899 | -52.6571 | -45.0688 | -43.5821 | -41.6383 | -35.712 | -38.8321 | -53.7188 | -44.8961 | -66.0099 | 448 | -23.5816 | -38.7812 | -23.5558 | -36.133 | -23.3916 | -35.1267 | -23.1266 | -35.75 | 448 | -32.5826 | -26.6563 | -29.7342 | -43.9149 | -36.3266 | -34.7719 | -32.8961 | -26.9018 | -30.1546 | -43.8469 | -36.4335 | -34.9468 | -28.6381 | -27.2665 | -29.7764 | -44.9766 | -36.1539 | -57.1997 | -28.9516 | -27.512 | -30.1968 | -44.9086 | -36.2608 | -57.3746
449 | -9.0337 | 0 | -8.8813 | 0 | -8.8345 | 0 | -8.6587 | 0 | -45.1902 | 178.0505 | -24.0444 | -43.071 | -42.1131 | -170.1644 | -39.5393 | 20.1856 | -48.2139 | -0.8955 | -41.9041 | 18.9232 | -42.7326 | -53.9013 | -23.786 | 58.3816 | -46.8315 | -70.9044 | -36.5204 | 99.0354 | -51.7681 | 149.2446 | -38.6798 | 151.752 | -12.8021 | 73.8316 | -11.6374 | 2.67 | -18.2731 | 64.2466 | -15.2778 | 47.4646 | -16.128 | -174.4612 | -15.1666 | 85.4311 | -22.7957 | -162.8649 | -17.7548 | 132.9692 | -45.9251 | -37.472 | -36.4056 | -38.8939 | -52.4642 | -45.3509 | -44.0493 | -40.7954 | -35.9126 | -38.9595 | -54.6899 | -44.7563 | -79.5223 | 449 | -23.9444 | -38.0536 | -23.855 | -38.5058 | -23.7098 | -35.4855 | -23.429 | -37.8802 | 449 | -31.7617 | -26.8789 | -29.8602 | -43.5829 | -36.4696 | -35.2148 | -31.9141 | -27.0781 | -30.2352 | -43.6297 | -36.6922 | -35.3906 | -28.4383 | -27.3719 | -29.9258 | -45.8086 | -35.875 | -70.6878 | -28.5907 | -27.5711 | -30.3008 | -45.8554 | -36.0976 | -70.8636
450 | -8.9979 | 0 | -8.9265 | 0 | -8.8143 | 0 | -8.689 | 0 | -46.6254 | 175.8885 | -25.2977 | -52.3474 | -42.1125 | -155.601 | -39.5572 | 2.2021 | -49.4918 | -11.1167 | -42.4329 | 31.3611 | -44.1253 | -59.5914 | -24.9816 | 49.4688 | -43.9765 | -35.0439 | -36.7672 | 94.0078 | -55.0999 | 144.8936 | -38.4184 | 159.077 | -13.0217 | 70.984 | -11.3607 | -8.9214 | -17.3058 | 54.8853 | -13.3431 | 48.6245 | -18.5537 | -176.7225 | -14.1265 | 65.9485 | -23.3807 | 166.5598 | -15.6842 | 124.3654 | -45.5966 | -37.8789 | -36.1797 | -39.0341 | -52.7567 | -44.8047 | -44.3327 | -41.1151 | -35.9589 | -38.8874 | -55.3718 | -44.7127 | -67.256 | 450 | -25.177 | -38.4247 | -25.0576 | -38.8661 | -24.8753 | -35.9811 | -24.5221 | -37.2804 | 450 | -32.1172 | -26.961 | -30.0362 | -43.8302 | -35.8782 | -35.5184 | -32.1886 | -27.1446 | -30.3451 | -43.9424 | -36.1157 | -35.6437 | -28.881 | -27.1818 | -29.8895 | -46.4453 | -35.7862 | -58.4417 | -28.9524 | -27.3654 | -30.1984 | -46.5575 | -36.0237 | -58.567
451 | -9.0662 | 0 | -8.9216 | 0 | -8.8257 | 0 | -8.7411 | 0 | -47.1014 | 177.9449 | -26.6395 | -51.7169 | -39.82 | -155.4886 | -41.1373 | -11.2861 | -51.2372 | -11.513 | -40.6664 | 35.1497 | -45.3485 | -59.358 | -26.4196 | 50.2387 | -39.2223 | -46.7009 | -37.0279 | 89.2572 | -55.352 | 160.9767 | -36.8976 | 159.1739 | -12.9907 | 74.3602 | -12.2621 | -23.327 | -17.6336 | 46.3652 | -12.6185 | 40.4868 | -18.3163 | -161.0815 | -14.7378 | 46.8702 | -24.8782 | 142.2661 | -14.9457 | 110.6444 | -45.2293 | -38.6529 | -35.9871 | -39.3113 | -53.4715 | -44.0865 | -44.5974 | -42.2788 | -35.9255 | -38.8357 | -55.1365 | -44.5952 | -60.8095 | 451 | -26.3985 | -39.8307 | -26.3252 | -37.0437 | -26.1451 | -36.3761 | -25.7137 | -34.857 | 451 | -33.2126 | -26.8593 | -30.2451 | -44.5499 | -35.1649 | -35.7717 | -33.3572 | -27.0998 | -30.5702 | -44.6458 | -35.3454 | -35.8563 | -29.5867 | -26.9209 | -29.7695 | -46.2149 | -35.6736 | -51.9838 | -29.7313 | -27.1614 | -30.0946 | -46.3108 | -35.8541 | -52.0684
452 | -9.1757 | 0 | -8.8166 | 0 | -8.838 | 0 | -8.7425 | 0 | -46.7218 | 172.8766 | -26.2575 | -45.3816 | -38.2012 | -168.8551 | -43.362 | -12.1554 | -51.8313 | -1.8463 | -39.2979 | 25.3883 | -46.0646 | -59.8595 | -26.0551 | 57.364 | -37.1188 | -71.5965 | -37.0465 | 85.0693 | -52.0728 | 158.1146 | -35.7775 | 149.5932 | -12.026 | 75.0361 | -13.7338 | -31.0609 | -18.2962 | 41.3108 | -12.5715 | 29.8814 | -15.5918 | -159.4706 | -16.4018 | 30.6939 | -28.61 | 139.379 | -15.0998 | 95.5116 | -44.9915 | -38.6379 | -35.8545 | -39.5228 | -53.8939 | -43.5793 | -44.8206 | -42.5607 | -35.8124 | -38.8713 | -54.4299 | -44.1974 | -58.4468 | 452 | -25.9519 | -41.3111 | -25.9672 | -35.6 | -25.6878 | -36.4139 | -25.3136 | -33.3279 | 452 | -33.385 | -26.6367 | -30.3471 | -45.0773 | -34.7627 | -35.9826 | -33.7441 | -26.9744 | -30.7803 | -45.0559 | -34.8368 | -36.0781 | -29.4622 | -26.6788 | -29.6956 | -45.6133 | -35.3808 | -49.6088 | -29.8213 | -27.0165 | -30.1288 | -45.5919 | -35.4549 | -49.7043
453 | -9.2806 | 0 | -8.6712 | 0 | -8.8587 | 0 | -8.6947 | 0 | -46.8756 | 160.327 | -24.8289 | -48.8239 | -37.8701 | 175.0084 | -43.5425 | -0.1653 | -50.7284 | 5.4319 | -39.3555 | 11.1487 | -46.7663 | -61.4177 | -24.5511 | 55.6173 | -36.9607 | -97.6304 | -37.0363 | 78.466 | -49.6738 | 137.2563 | -35.732 | 138.0818 | -10.614 | 68.9973 | -15.4544 | -31.2561 | -18.5411 | 44.2931 | -13.7187 | 22.8623 | -13.6528 | -172.6377 | -18.8843 | 23.8093 | -28.9485 | 162.437 | -16.5185 | 85.9917 | -45.0687 | -37.6156 | -35.9594 | -39.6859 | -53.9008 | -43.5414 | -44.8978 | -41.0658 | -35.8118 | -39.0658 | -53.7884 | -44.0306 | -58.8189 | 453 | -24.5927 | -41.3536 | -24.6223 | -35.4098 | -24.284 | -36.3884 | -24.0103 | -33.1939 | 453 | -31.7852 | -26.5312 | -30.4053 | -45.2296 | -34.8702 | -36.0391 | -32.3946 | -26.9531 | -30.9912 | -45.0421 | -34.8467 | -36.2031 | -28.335 | -26.6788 | -29.7852 | -45.1172 | -35.3594 | -49.9602 | -28.9444 | -27.1007 | -30.3711 | -44.9297 | -35.3359 | -50.1242
454 | -9.3398 | 0 | -8.6053 | 0 | -8.9134 | 0 | -8.6659 | 0 | -48.2979 | 147.7941 | -23.9917 | -60.2336 | -38.8657 | 158.8583 | -41.9119 | -0.4942 | -48.9244 | 6.5146 | -41.1243 | 0.8448 | -47.7348 | -64.4859 | -23.5619 | 44.2473 | -38.6235 | -122.2603 | -37.3275 | 70.8546 | -48.9797 | 109.0634 | -36.8124 | 128.97 | -9.907 | 59.9888 | -16.2191 | -26.2165 | -17.6939 | 47.3056 | -15.2693 | 26.0241 | -13.2103 | 170.5882 | -21.1407 | 27.3367 | -24.2531 | 168.6636 | -17.9057 | 87.6415 | -45.2372 | -36.5414 | -36.2061 | -39.9013 | -53.9872 | -43.8344 | -45.0311 | -39.4838 | -35.918 | -39.4452 | -53.0311 | -44.0853 | -62.6704 | 454 | -23.837 | -40.3622 | -23.8402 | -36.5788 | -23.4125 | -36.6852 | -23.1903 | -34.4578 | 454 | -30.144 | -26.5782 | -30.5615 | -45.3819 | -35.2291 | -36.1177 | -30.8785 | -27.0046 | -31.2354 | -45.0738 | -35.1685 | -36.3652 | -27.2016 | -26.8663 | -30.1054 | -44.4258 | -35.48 | -53.757 | -27.9361 | -27.2927 | -30.7793 | -44.1177 | -35.4194 | -54.0045
455 | -9.3069 | 0 | -8.5979 | 0 | -8.9581 | 0 | -8.7009 | 0 | -50.368 | 142.35 | -24.2136 | -73.4945 | -40.9288 | 149.9923 | -41.055 | -10.7277 | -47.0789 | -0.6203 | -43.5659 | 6.1096 | -49.2886 | -64.5307 | -23.5654 | 31.5124 | -42.7922 | -135.6516 | -38.0304 | 63.1505 | -49.926 | 77.8986 | -38.3387 | 130.311 | -10.0914 | 53.0213 | -15.9255 | -24.9195 | -16.6578 | 42.9182 | -15.2818 | 38.7944 | -14.2641 | 155.9351 | -19.6897 | 37.8633 | -21.8484 | 145.518 | -17.2935 | 93.6707 | -45.3703 | -36.1134 | -36.3723 | -40.2219 | -54.2649 | -43.9376 | -45.258 | -38.8019 | -36.0842 | -39.8283 | -52.3166 | -44.1535 | -67.1251 | 455 | -24.1117 | -39.6975 | -24.0755 | -38.4063 | -23.5023 | -37.4633 | -23.2753 | -36.7914 | 455 | -29.495 | -26.7773 | -30.915 | -45.667 | -35.3397 | -36.2999 | -30.204 | -27.1261 | -31.521 | -45.3068 | -35.2367 | -36.5571 | -26.8065 | -27.0654 | -30.5214 | -43.7187 | -35.5556 | -58.167 | -27.5155 | -27.4142 | -31.1274 | -43.3585 | -35.4526 | -58.4242
456 | -9.2921 | 0 | -8.6049 | 0 | -8.996 | 0 | -8.7783 | 0 | -51.3131 | 144.8423 | -25.5085 | -84.1829 | -43.0004 | 152.1266 | -41.3396 | -23.1505 | -46.125 | -13.5898 | -43.3934 | 23.7959 | -50.7946 | -59.462 | -24.6107 | 21.6171 | -46.5122 | -103.2442 | -39.1307 | 58.6835 | -52.7552 | 44.6856 | -38.1234 | 141.0202 | -10.6224 | 49.97 | -15.826 | -31.5565 | -16.1908 | 32.8212 | -13.4348 | 41.8811 | -16.4128 | 154.5963 | -18.6932 | 31.7128 | -20.8319 | 123.6218 | -15.8221 | 89.1136 | -45.3774 | -36.6005 | -36.3106 | -40.5219 | -54.2953 | -43.6122 | -45.5151 | -39.203 | -36.1866 | -40.058 | -52.4643 | -43.7929 | -56.1706 | 456 | -25.4206 | -39.7776 | -25.3282 | -39.1974 | -24.5724 | -38.6713 | -24.277 | -37.407 | 456 | -29.9109 | -26.8945 | -31.2298 | -45.6904 | -35.0073 | -36.5191 | -30.5981 | -27.1906 | -31.7436 | -45.2993 | -34.8339 | -36.7368 | -27.3084 | -27.0185 | -30.7659 | -43.8594 | -35.188 | -47.1746 | -27.9956 | -27.3146 | -31.2797 | -43.4683 | -35.0146 | -47.3923
457 | -9.3521 | 0 | -8.6139 | 0 | -9.0357 | 0 | -8.86 | 0 | -50.2239 | 139.4701 | -27.2194 | -83.4932 | -42.8116 | 162.9279 | -42.3746 | -30.3264 | -46.2 | -22.5002 | -40.8304 | 28.0086 | -51.6855 | -51.3291 | -26.2023 | 20.156 | -40.9959 | -88.7972 | -40.0593 | 59.2348 | -60.284 | -6.1948 | -36.1179 | 142.0626 | -10.7251 | 51.7352 | -16.5899 | -38.3106 | -16.6938 | 23.7399 | -12.0463 | 34.5704 | -16.6983 | 165.5393 | -17.9599 | 23.6777 | -20.7205 | 100.5484 | -14.5419 | 77.0164 | -45.4214 | -37.6519 | -36.1128 | -40.6714 | -54.1402 | -42.8277 | -45.735 | -40.2076 | -36.0709 | -40.0318 | -53.3326 | -43.0787 | -51.4681 | 457 | -27.0801 | -40.3921 | -26.9091 | -37.9881 | -26.0487 | -39.7321 | -25.6214 | -34.8824 | 457 | -30.8555 | -26.7188 | -31.3193 | -45.5263 | -34.2138 | -36.6993 | -31.5937 | -27.0352 | -31.8114 | -45.1045 | -33.9677 | -36.875 | -28.2998 | -26.7607 | -30.6797 | -44.7187 | -34.4648 | -42.4324 | -29.038 | -27.0771 | -31.1718 | -44.2969 | -34.2187 | -42.6081
458 | -9.5376 | 0 | -8.5782 | 0 | -9.0555 | 0 | -8.8963 | 0 | -49.0032 | 118.0991 | -27.2887 | -76.3439 | -41.1892 | 160.6201 | -43.4727 | -31.649 | -46.4061 | -25.6438 | -38.7347 | 18.094 | -52.4457 | -43.7655 | -26.4266 | 27.2323 | -37.5799 | -107.8629 | -39.8582 | 61.7047 | -59.1794 | -160.3047 | -34.5183 | 131.4638 | -9.581 | 51.4118 | -18.259 | -40.3566 | -18.6146 | 19.7974 | -11.7657 | 23.4071 | -13.7361 | 170.745 | -18.9063 | 10.3226 | -23.1578 | 96.7677 | -15.1074 | 62.1335 | -45.5967 | -38.0584 | -36.0756 | -40.5302 | -53.9717 | -42.0818 | -45.8633 | -40.4266 | -35.9048 | -39.6914 | -54.4024 | -42.2743 | -49.3393 | 458 | -27.0873 | -40.9471 | -26.8916 | -36.3312 | -26.0957 | -39.5774 | -25.6328 | -32.7645 | 458 | -30.889 | -26.3672 | -30.9926 | -45.3935 | -33.5036 | -36.8078 | -31.8484 | -26.8493 | -31.6339 | -44.9162 | -33.1855 | -36.967 | -28.5208 | -26.538 | -30.1538 | -45.8242 | -33.6961 | -40.2838 | -29.4802 | -27.0201 | -30.7951 | -45.3469 | -33.378 | -40.443
459 | -9.7684 | 0 | -8.5274 | 0 | -9.0626 | 0 | -8.8748 | 0 | -48.6302 | 85.2522 | -25.7949 | -76.7866 | -40.602 | 148.7547 | -43.8761 | -30.2568 | -45.601 | -24.755 | -38.0277 | 2.0841 | -52.8571 | -30.6808 | -25.1105 | 26.8714 | -36.4602 | -133.9206 | -39.2085 | 55.8785 | -51.0931 | 147.7333 | -34.1616 | 116.4723 | -8.5279 | 45.1016 | -20.2594 | -36.5545 | -19.0615 | 30.4083 | -12.2902 | 14.4224 | -11.4458 | 159.7056 | -20.2816 | 1.6905 | -23.4863 | 99.9471 | -16.9732 | 49.5183 | -45.8076 | -37.1592 | -36.2712 | -40.1982 | -53.9912 | -41.6787 | -45.8477 | -39.1524 | -35.9246 | -39.3906 | -55.1055 | -41.9063 | -49.1079 | 459 | -25.6318 | -40.8509 | -25.4794 | -35.6531 | -24.7965 | -38.7633 | -24.4534 | -32.0952 | 459 | -29.384 | -26.1562 | -30.4298 | -45.4638 | -33.1513 | -36.7851 | -30.625 | -26.862 | -31.3234 | -44.9286 | -32.8039 | -36.9729 | -27.3908 | -26.5028 | -29.6222 | -46.5781 | -33.3789 | -40.0453 | -28.6318 | -27.2086 | -30.5158 | -46.0429 | -33.0315 | -40.2331
460 | -9.9118 | 0 | -8.497 | 0 | -9.0615 | 0 | -8.817 | 0 | -48.987 | 45.943 | -24.7605 | -86.3654 | -41.2731 | 137.7592 | -43.4193 | -31.8827 | -44.0737 | -30.5578 | -38.9045 | -13.2232 | -51.7213 | -16.6559 | -23.9925 | 18.4216 | -37.0854 | -159.2772 | -39.2346 | 44.9571 | -47.9318 | 111.1088 | -35.1604 | 102.6619 | -8.2876 | 34.4906 | -20.925 | -22.423 | -18.4916 | 35.785 | -13.4312 | 10.3574 | -10.5498 | 144.4617 | -21.8132 | -9.1808 | -22.51 | 108.4685 | -20.3811 | 48.2404 | -45.9686 | -35.9237 | -36.5905 | -40.1131 | -54.4608 | -41.7948 | -45.8095 | -37.8467 | -36.0759 | -39.3759 | -55.2314 | -42.0459 | -51.013 | 460 | -24.6486 | -40.12 | -24.5398 | -36.1542 | -23.7775 | -38.4741 | -23.5537 | -32.8693 | 460 | -27.9349 | -26.1641 | -30.2013 | -45.9638 | -33.2978 | -36.748 | -29.3497 | -27.0144 | -31.2961 | -45.3993 | -32.9778 | -36.9925 | -26.0119 | -26.6787 | -29.4641 | -46.7344 | -33.5489 | -41.9515 | -27.4267 | -27.529 | -30.5589 | -46.1699 | -33.2289 | -42.196
461 | -9.8964 | 0 | -8.4979 | 0 | -9.0956 | 0 | -8.7792 | 0 | -49.7619 | 3.6348 | -24.7523 | -98.8434 | -42.9229 | 133.0612 | -43.3463 | -39.6599 | -43.0393 | -41.4747 | -41.24 | -20.5218 | -49.5907 | -11.6496 | -23.7353 | 6.1377 | -39.7115 | 178.3187 | -40.0962 | 35.072 | -46.9965 | 78.5716 | -37.2542 | 97.5002 | -8.5487 | 26.7735 | -19.7064 | -7.9947 | -16.6251 | 33.5808 | -13.7912 | 13.3169 | -10.7166 | 128.629 | -22.784 | -11.1696 | -20.6895 | 97.2495 | -21.2694 | 73.2264 | -45.9773 | -35.1726 | -36.7859 | -40.5086 | -54.9851 | -42.2156 | -45.8182 | -37.3182 | -36.2597 | -39.705 | -54.744 | -42.4472 | -56.8673 | 461 | -24.6731 | -39.7262 | -24.5976 | -37.5487 | -23.616 | -38.902 | -23.4513 | -35.0166 | 461 | -27.4218 | -26.3633 | -30.6122 | -46.4872 | -33.7177 | -36.7226 | -28.8203 | -27.1641 | -31.7294 | -45.8895 | -33.4364 | -37.039 | -25.2762 | -26.8895 | -29.8086 | -46.2461 | -33.9493 | -47.7717 | -26.6747 | -27.6903 | -30.9258 | -45.6484 | -33.668 | -48.0881
462 | -9.7423 | 0 | -8.5077 | 0 | -9.1542 | 0 | -8.8052 | 0 | -51.2075 | -37.1145 | -25.8283 | -110.717 | -44.0573 | 145.5146 | -44.4514 | -46.4267 | -42.5907 | -54.5314 | -43.2548 | -9.0939 | -47.826 | -15.8636 | -24.5152 | -5.4279 | -44.9752 | 175.7883 | -41.6728 | 29.3967 | -47.7319 | 48.9192 | -38.7155 | 107.922 | -9.7319 | 22.0025 | -18.2201 | -3.9636 | -16.4933 | 23.3303 | -13.2779 | 13.076 | -12.0684 | 121.5095 | -24.0558 | -25.6381 | -20.57 | 83.0284 | -18.9461 | 84.2396 | -45.8347 | -35.1336 | -36.6709 | -41.1902 | -54.4089 | -42.4891 | -45.8397 | -37.8105 | -36.1915 | -40.1835 | -54.3319 | -42.4941 | -50.9648 | 462 | -25.7511 | -40.0645 | -25.6923 | -38.4886 | -24.4563 | -39.9401 | -24.2734 | -37.3736 | 462 | -28.0682 | -26.4492 | -31.4479 | -45.9012 | -33.9814 | -36.6855 | -29.3028 | -27.0373 | -32.385 | -45.2547 | -33.6839 | -37.0345 | -25.3913 | -26.9286 | -30.4412 | -45.8242 | -33.9864 | -41.8106 | -26.6259 | -27.5167 | -31.3783 | -45.1777 | -33.6889 | -42.1596
463 | -9.6814 | 0 | -8.5098 | 0 | -9.2163 | 0 | -8.8662 | 0 | -55.053 | -71.287 | -27.7154 | -114.5048 | -41.6433 | 154.6733 | -45.8155 | -45.8131 | -42.8515 | -67.232 | -41.8319 | 4.0878 | -47.3156 | -25.3357 | -26.135 | -10.621 | -44.9726 | -143.7721 | -43.2123 | 31.3625 | -50.5736 | 20.8471 | -37.2442 | 117.8627 | -10.9664 | 24.4996 | -17.3405 | -8.6389 | -17.2687 | 16.1565 | -13.2976 | 1.9298 | -12.8448 | 123.5352 | -27.1707 | -39.5484 | -21.4392 | 69.7051 | -16.6709 | 78.3815 | -45.8368 | -35.6332 | -36.4302 | -41.7665 | -53.0712 | -42.2894 | -45.9004 | -39.1655 | -35.8728 | -40.5293 | -54.709 | -41.978 | -45.5698 | 463 | -27.5354 | -40.9047 | -27.486 | -37.3062 | -26.0461 | -41.2468 | -25.7327 | -36.3978 | 463 | -29.4841 | -26.1914 | -32.0851 | -44.5614 | -33.7796 | -36.6841 | -30.6557 | -26.6565 | -32.9003 | -43.8549 | -33.4232 | -37.0342 | -25.9518 | -26.7488 | -30.8479 | -46.1992 | -33.4682 | -36.3535 | -27.1234 | -27.2139 | -31.6631 | -45.4927 | -33.1118 | -36.7036
464 | -9.819 | 0 | -8.5437 | 0 | -9.2835 | 0 | -8.9139 | 0 | -65.4081 | -34.9951 | -28.5333 | -105.9786 | -38.9696 | 145.257 | -46.1855 | -41.8414 | -43.7567 | -75.446 | -39.5434 | 0.8469 | -48.1685 | -28.6239 | -27.002 | -5.0803 | -40.12 | -147.5022 | -43.0355 | 37.5506 | -58.6105 | 10.7213 | -35.1088 | 113.1643 | -9.9809 | 31.903 | -16.7894 | -14.6908 | -18.46 | 17.2758 | -13.6207 | -5.3143 | -11.7807 | 127.2646 | -32.5729 | -67.6559 | -22.8623 | 66.6528 | -15.7035 | 68.1016 | -46.1285 | -35.9465 | -36.3881 | -41.7418 | -52.0113 | -41.6769 | -46.0632 | -40.221 | -35.5729 | -40.5007 | -55.9187 | -41.2249 | -43.1798 | 464 | -28.1565 | -41.7743 | -28.1335 | -35.5289 | -26.7636 | -41.7827 | -26.2848 | -33.9035 | 464 | -30.402 | -25.7539 | -31.9228 | -43.4676 | -33.1332 | -36.7797 | -31.6773 | -26.2894 | -32.8279 | -42.7278 | -32.763 | -37.1493 | -26.1275 | -26.5691 | -30.6817 | -47.375 | -32.6812 | -33.8963 | -27.4028 | -27.1046 | -31.5868 | -46.6352 | -32.311 | -34.2659
465 | -10.0852 | 0 | -8.5695 | 0 | -9.3195 | 0 | -8.9211 | 0 | -52.856 | 4.7212 | -27.2109 | -102.1944 | -37.7353 | 129.1077 | -46.0141 | -40.0046 | -44.5354 | -75.4926 | -38.3204 | -12.9666 | -48.7029 | -19.1531 | -25.988 | -1.917 | -37.9039 | -169.6612 | -42.2079 | 32.4011 | -56.5462 | 98.5557 | -34.0237 | 100.4118 | -8.7296 | 27.3438 | -16.5557 | -20.7504 | -18.4788 | 22.5547 | -15.5716 | -16.693 | -10.1118 | 119.9108 | -40.7687 | 98.6735 | -23.9709 | 76.6077 | -15.6974 | 58.588 | -46.3652 | -35.5371 | -36.6817 | -41.1582 | -51.7051 | -41.0879 | -46.1242 | -39.4328 | -35.4875 | -40.257 | -57.8742 | -40.8 | -42.6883 | 465 | -26.8313 | -41.8435 | -26.8341 | -34.5487 | -25.6955 | -41.2009 | -25.2652 | -32.5166 | 465 | -29.3476 | -25.4023 | -31.073 | -43.1356 | -32.5184 | -36.8047 | -30.8633 | -26.168 | -32.2371 | -42.3856 | -32.1668 | -37.2031 | -25.4519 | -26.5965 | -30.1718 | -49.3047 | -32.2305 | -33.3688 | -26.9676 | -27.3622 | -31.3359 | -48.5547 | -31.8789 | -33.7672
466 | -10.3096 | 0 | -8.6008 | 0 | -9.3237 | 0 | -8.8857 | 0 | -46.9565 | -20.2838 | -25.9382 | -110.729 | -37.5112 | 113.0018 | -45.7465 | -41.0622 | -43.7883 | -73.3634 | -38.5253 | -29.1819 | -46.7996 | -10.5213 | -24.7508 | -8.2629 | -37.607 | 165.6561 | -42.4044 | 22.0687 | -48.9036 | 82.9296 | -34.237 | 85.6457 | -7.9843 | 18.1969 | -16.8714 | -24.1817 | -16.8724 | 23.121 | -18.5927 | -13.414 | -9.2248 | 107.2044 | -31.0766 | 79.2961 | -21.7552 | 82.4035 | -16.2225 | 52.8434 | -46.373 | -34.8109 | -37.1053 | -40.7051 | -52.3144 | -40.8226 | -46.0383 | -37.9683 | -35.6768 | -40.1828 | -60.1164 | -41.0152 | -43.3994 | 466 | -25.6139 | -40.5266 | -25.6624 | -34.4418 | -24.5058 | -40.3976 | -24.2211 | -32.4923 | 466 | -27.6587 | -25.3672 | -30.3955 | -43.7136 | -32.2218 | -36.7146 | -29.3675 | -26.3531 | -31.8194 | -42.9907 | -31.9369 | -37.1526 | -24.5013 | -26.7957 | -29.8732 | -51.5156 | -32.4144 | -34.0757 | -26.2101 | -27.7816 | -31.2971 | -50.7927 | -32.1295 | -34.5137
467 | -10.304 | 0 | -8.5857 | 0 | -9.3453 | 0 | -8.867 | 0 | -44.2395 | -47.8376 | -25.7846 | -123.391 | -38.1595 | 97.884 | -46.0705 | -44.4146 | -42.487 | -82.0142 | -40.6755 | -40.5701 | -44.5157 | -16.5248 | -24.4183 | -20.2616 | -39.341 | 141.2382 | -43.6142 | 13.6694 | -46.0001 | 56.0532 | -35.6511 | 76.7235 | -8.4254 | 8.2553 | -17.5752 | -28.6861 | -16.6881 | 12.3262 | -19.9013 | 5.0292 | -9.6108 | 94.7573 | -28.5062 | 59.4392 | -20.3599 | 73.1644 | -16.8614 | 49.5227 | -46.063 | -34.3743 | -37.3747 | -40.9633 | -53.2466 | -41.1357 | -45.8824 | -37.1639 | -35.9626 | -40.3735 | -61.0531 | -41.7913 | -44.4804 | 467 | -25.482 | -39.2521 | -25.6068 | -35.3051 | -24.2398 | -39.8305 | -24.0547 | -33.8331 | 467 | -26.8599 | -25.6586 | -30.6593 | -44.6609 | -32.55 | -36.5371 | -28.5782 | -26.6173 | -32.0963 | -43.9013 | -32.2687 | -37.0154 | -24.0703 | -27.0707 | -30.0695 | -52.4674 | -33.2056 | -35.1351 | -25.7886 | -28.0294 | -31.5065 | -51.7078 | -32.9243 | -35.6134
468 | -10.1615 | 0 | -8.5877 | 0 | -9.3688 | 0 | -8.8482 | 0 | -43.2942 | -73.7994 | -26.5943 | -135.5926 | -39.195 | 87.6851 | -46.7686 | -44.3463 | -42.0004 | -94.1161 | -43.3487 | -35.4508 | -43.3323 | -28.5159 | -24.9841 | -31.7598 | -42.8193 | 126.264 | -45.1469 | 11.6366 | -45.1679 | 29.1795 | -37.138 | 77.638 | -9.5747 | 1.6632 | -18.2182 | -27.5445 | -17.043 | 2.7502 | -18.6485 | 16.5623 | -10.3424 | 85.9104 | -28.5743 | 47.0745 | -19.5685 | 60.861 | -17.2095 | 48.6925 | -45.7181 | -34.2989 | -37.3496 | -41.6756 | -53.4335 | -41.5146 | -45.8668 | -37.0604 | -36.1795 | -40.6991 | -60.2787 | -42.4486 | -44.2443 | 468 | -26.2749 | -38.8283 | -26.4629 | -36.3883 | -24.8511 | -39.6891 | -24.6881 | -35.5916 | 468 | -26.8989 | -26.018 | -31.5141 | -44.8458 | -32.9269 | -36.498 | -28.4727 | -26.8107 | -32.8274 | -44.0647 | -32.6664 | -37.0186 | -24.1374 | -27.1881 | -30.5376 | -51.691 | -33.8609 | -34.8755 | -25.7112 | -27.9808 | -31.8509 | -50.9099 | -33.6004 | -35.3961
469 | -9.9813 | 0 | -8.5829 | 0 | -9.4032 | 0 | -8.8524 | 0 | -43.8259 | -95.658 | -28.366 | -142.1167 | -40.2892 | 84.2986 | -47.034 | -40.2413 | -42.1366 | -104.5982 | -44.0192 | -15.3332 | -43.4839 | -44.506 | -26.4739 | -41.0494 | -48.536 | 137.8912 | -46.3938 | 15.5746 | -45.7889 | 4.0118 | -37.2707 | 84.9123 | -10.994 | 3.3442 | -18.4705 | -22.7797 | -18.531 | -6.0273 | -17.4492 | 15.164 | -11.3077 | 83.1213 | -31.81 | 36.352 | -19.8582 | 47.6915 | -17.6559 | 47.0139 | -45.4957 | -34.5856 | -37.0348 | -42.4293 | -52.4489 | -41.5035 | -46.0321 | -37.7313 | -36.1688 | -40.9774 | -58.3368 | -42.3095 | -42.0057 | 469 | -27.9811 | -39.123 | -28.1923 | -37.1145 | -26.3619 | -40.262 | -26.086 | -36.4235 | 469 | -27.75 | -26.1875 | -32.448 | -43.866 | -32.9206 | -36.6289 | -29.1484 | -26.7656 | -33.5769 | -43.0457 | -32.6511 | -37.1797 | -24.6043 | -27.0535 | -30.9961 | -49.7539 | -33.7266 | -32.6025 | -26.0027 | -27.6316 | -32.125 | -48.9336 | -33.4571 | -33.1533
470 | -9.9884 | 0 | -8.5963 | 0 | -9.468 | 0 | -8.8731 | 0 | -46.1135 | -105.3172 | -29.8332 | -135.9527 | -39.8035 | 82.8296 | -46.9625 | -40.249 | -42.454 | -114.8675 | -41.3399 | -8.3427 | -45.842 | -52.5614 | -27.8779 | -36.7442 | -45.2552 | 167.7637 | -45.8185 | 17.8202 | -48.117 | -12.7553 | -35.6867 | 83.3559 | -10.7516 | 11.6679 | -18.1685 | -25.6639 | -20.6429 | -5.2234 | -17.9716 | 9.2403 | -11.0214 | 85.7709 | -32.1698 | 68.0927 | -20.9004 | 39.3899 | -17.9673 | 49.7935 | -45.427 | -34.9277 | -36.7137 | -41.927 | -50.5716 | -40.5058 | -46.483 | -39.0032 | -35.9533 | -40.815 | -57.1861 | -41.1126 | -39.8555 | 470 | -29.3246 | -39.9384 | -29.4587 | -36.2909 | -27.7315 | -41.6962 | -27.1529 | -35.0138 | 470 | -29.0148 | -25.9649 | -31.9386 | -41.9753 | -31.9095 | -37.015 | -30.4069 | -26.4853 | -33.0539 | -41.1036 | -31.6327 | -37.6099 | -24.9393 | -26.7253 | -30.8266 | -48.5898 | -32.5163 | -30.3875 | -26.3314 | -27.2457 | -31.9419 | -47.7181 | -32.2395 | -30.9824
471 | -10.2166 | 0 | -8.6212 | 0 | -9.507 | 0 | -8.8988 | 0 | -47.3772 | -90.1877 | -28.8936 | -128.0687 | -38.8307 | 73.8964 | -47.382 | -35.5155 | -43.5637 | -124.5198 | -39.0416 | -17.4723 | -48.4673 | -34.3354 | -27.2315 | -30.9465 | -41.9741 | 154.1146 | -45.3067 | 9.4955 | -51.7154 | -14.122 | -34.8417 | 73.4418 | -9.0557 | 13.2078 | -18.3542 | -24.3512 | -20.7186 | 7.7165 | -19.124 | 13.7533 | -9.7636 | 81.8156 | -29.7895 | 86.3899 | -22.1366 | 39.5752 | -17.8206 | 54.4096 | -45.3816 | -34.9432 | -36.7427 | -40.7019 | -49.3738 | -39.4745 | -46.8829 | -39.6788 | -35.8768 | -40.3907 | -57.3633 | -40.257 | -39.1795 | 471 | -28.4184 | -40.9375 | -28.4372 | -35.2345 | -27.0567 | -42.9726 | -26.4799 | -33.9992 | 471 | -29.4622 | -25.6602 | -30.4853 | -40.7526 | -30.8533 | -37.3759 | -31.0576 | -26.3698 | -31.8031 | -39.8668 | -30.5757 | -37.9841 | -24.7266 | -26.5261 | -30.1741 | -48.7421 | -31.6358 | -29.6725 | -26.322 | -27.2357 | -31.4919 | -47.8563 | -31.3582 | -30.2807
472 | -10.444 | 0 | -8.6408 | 0 | -9.5088 | 0 | -8.9236 | 0 | -44.2143 | -79.2875 | -27.4494 | -133.5623 | -38.5183 | 58.0818 | -46.5258 | -28.2863 | -45.3272 | -123.8148 | -38.416 | -35.5478 | -45.5647 | -12.1766 | -25.9428 | -36.0003 | -41.3181 | 130.9867 | -46.3228 | -3.4873 | -52.6227 | 12.2854 | -35.0352 | 61.7645 | -8.2302 | 3.8157 | -19.0919 | -26.5393 | -20.9148 | 5.1911 | -19.2714 | 26.7012 | -9.1153 | 71.4561 | -28.5821 | 88.5018 | -23.1227 | 42.0272 | -16.8599 | 56.7016 | -45.1434 | -34.7341 | -37.0169 | -39.7841 | -49.1317 | -38.8669 | -46.9611 | -39.4697 | -35.9752 | -40.0471 | -58.301 | -40.0947 | -39.6265 | 472 | -27.0385 | -40.4829 | -27.0655 | -35.0307 | -25.7728 | -42.4754 | -25.4028 | -34.0565 | 472 | -29.0257 | -25.5312 | -29.3401 | -40.4909 | -30.2261 | -37.4523 | -30.8289 | -26.4664 | -30.8605 | -39.6229 | -29.9433 | -38.0375 | -24.2901 | -26.5729 | -29.6031 | -49.6602 | -31.4539 | -30.1177 | -26.0933 | -27.5081 | -31.1235 | -48.7922 | -31.1711 | -30.7029
473 | -10.4749 | 0 | -8.6546 | 0 | -9.4788 | 0 | -8.9475 | 0 | -40.9797 | -89.9518 | -26.9021 | -146.428 | -39.3182 | 40.4835 | -45.1715 | -29.1707 | -44.7502 | -113.5905 | -40.0426 | -52.0076 | -42.0389 | -17.7388 | -25.3764 | -46.9709 | -43.0578 | 106.1422 | -48.4548 | -12.0297 | -48.4112 | 19.5456 | -36.0135 | 51.047 | -8.254 | -6.3622 | -19.723 | -20.5664 | -21.6921 | 1.2417 | -17.1033 | 32.2752 | -9.4363 | 59.5912 | -27.2783 | 93.6123 | -23.3831 | 45.5757 | -15.7598 | 53.9693 | -44.7001 | -34.7392 | -37.2939 | -39.5126 | -49.8759 | -38.7158 | -46.7171 | -39.1663 | -36.1467 | -39.9671 | -59.1233 | -40.2639 | -40.5729 | 473 | -26.5023 | -38.4255 | -26.6351 | -36.029 | -25.2118 | -40.3989 | -24.997 | -35.0268 | 473 | -28.6914 | -25.6718 | -29.0377 | -41.2213 | -30.0612 | -37.2383 | -30.5117 | -26.6679 | -30.5651 | -40.3971 | -29.7683 | -37.7696 | -24.2643 | -26.819 | -29.4922 | -50.4687 | -31.6093 | -31.0941 | -26.0846 | -27.8151 | -31.0196 | -49.6445 | -31.3164 | -31.6254
474 | -10.3279 | 0 | -8.6805 | 0 | -9.4459 | 0 | -9.0024 | 0 | -39.2404 | -107.6609 | -27.6144 | -160.3381 | -41.1969 | 29.8477 | -44.5308 | -32.3032 | -42.7524 | -117.453 | -43.9992 | -52.3057 | -40.1669 | -32.1641 | -25.8599 | -59.8326 | -48.7512 | 89.6039 | -50.8814 | -13.047 | -45.5672 | 2.0618 | -37.8053 | 46.0934 | -9.0833 | -13.3851 | -18.8059 | -9.9478 | -23.0359 | 8.8199 | -15.3355 | 25.4355 | -10.4854 | 52.4062 | -24.9645 | 102.7902 | -23.1728 | 52.7777 | -15.0466 | 48.4074 | -44.2417 | -35.2259 | -37.3813 | -39.9644 | -50.8902 | -38.9329 | -46.4266 | -39.2155 | -36.2225 | -40.2274 | -58.7508 | -40.6764 | -40.7157 | 474 | -27.151 | -36.8319 | -27.4302 | -37.7266 | -25.6803 | -38.7895 | -25.5781 | -36.8437 | 474 | -28.8876 | -25.8946 | -29.6365 | -42.2097 | -30.2524 | -36.9807 | -30.535 | -26.7766 | -30.962 | -41.4443 | -29.9305 | -37.4242 | -24.898 | -27.0534 | -29.8995 | -50.0703 | -31.9959 | -31.2698 | -26.5454 | -27.9354 | -31.225 | -49.3049 | -31.674 | -31.7133
475 | -10.1472 | 0 | -8.7541 | 0 | -9.4835 | 0 | -9.0316 | 0 | -39.2126 | -128.0119 | -29.6909 | -169.4809 | -43.1683 | 28.8664 | -44.0787 | -33.4792 | -41.9793 | -130.3588 | -45.0985 | -17.4329 | -40.0151 | -49.898 | -27.417 | -70.5508 | -53.6816 | 161.3946 | -53.7093 | -8.4337 | -45.1412 | -21.1936 | -39.4624 | 54.4053 | -9.9714 | -11.8039 | -16.9699 | -8.6831 | -22.7922 | 26.4856 | -15.0177 | 13.8176 | -12.0147 | 53.9508 | -22.3575 | 105.5045 | -22.1673 | 57.8221 | -15.0559 | 41.0802 | -44.1512 | -36.1189 | -37.388 | -40.9793 | -50.9871 | -39.1228 | -46.5002 | -39.4327 | -36.112 | -40.8087 | -57.7189 | -41.1046 | -39.2961 | 475 | -29.0593 | -36.5292 | -29.4166 | -38.4611 | -27.1748 | -38.7121 | -27.1444 | -38.2953 | 475 | -29.2855 | -25.9648 | -30.8321 | -42.233 | -30.3687 | -37.0167 | -30.6786 | -26.6285 | -31.9477 | -41.5036 | -30.0912 | -37.4686 | -25.9717 | -27.2408 | -30.6615 | -48.9648 | -32.3505 | -29.8126 | -27.3648 | -27.9045 | -31.7771 | -48.2354 | -32.073 | -30.2645
476 | -10.1772 | 0 | -8.8355 | 0 | -9.6053 | 0 | -9.0636 | 0 | -40.8557 | -140.2964 | -31.8153 | -162.1799 | -43.7465 | 37.5553 | -43.448 | -34.7835 | -42.2458 | -140.3743 | -40.71 | -5.1137 | -41.7399 | -62.7823 | -29.5656 | -69.5791 | -44.8765 | 165.1981 | -54.9297 | 5.8054 | -47.0175 | -39.1397 | -38.3967 | 63.7511 | -9.7348 | -9.2667 | -15.7201 | -15.8662 | -20.6899 | 34.0419 | -16.2162 | 3.2532 | -11.7285 | 61.9248 | -20.2456 | 98.2936 | -20.7033 | 54.2361 | -15.3881 | 37.0145 | -44.5764 | -36.7836 | -37.3438 | -41.6818 | -50.3225 | -38.7836 | -46.8863 | -39.4725 | -35.8843 | -41.2886 | -56.4254 | -40.8826 | -37.5271 | 476 | -31.0641 | -37.2828 | -31.032 | -37.2875 | -29.1911 | -40.4539 | -29.0203 | -37.054 | 476 | -29.2953 | -25.7071 | -31.5046 | -41.487 | -29.9481 | -37.281 | -30.637 | -26.279 | -32.6182 | -40.7172 | -29.72 | -37.8227 | -26.6064 | -27.1666 | -31.1114 | -47.5899 | -32.0471 | -27.9218 | -27.9481 | -27.7385 | -32.225 | -46.8201 | -31.819 | -28.4635
477 | -10.4059 | 0 | -8.8669 | 0 | -9.7497 | 0 | -9.0661 | 0 | -42.4762 | -135.8613 | -31.2301 | -151.2672 | -41.6178 | 40.0103 | -42.8091 | -36.2487 | -42.5895 | -148.2944 | -37.5197 | -15.654 | -44.2019 | -55.0694 | -29.9993 | -59.5129 | -41.5344 | 141.9368 | -55.2901 | 2.0252 | -50.4206 | -42.21 | -37.0065 | 58.16 | -8.6696 | -12.055 | -15.468 | -22.5946 | -19.1377 | 26.9136 | -18.1942 | 4.1758 | -10.2332 | 60.2768 | -18.7108 | 88.3314 | -19.8736 | 47.3608 | -15.6155 | 35.4284 | -44.9592 | -36.6585 | -37.2913 | -40.8342 | -49.0491 | -37.928 | -47.1286 | -39.2028 | -35.6794 | -41.1676 | -55.3981 | -40.2184 | -36.6831 | 477 | -30.5612 | -37.8515 | -30.0756 | -35.2142 | -29.553 | -43.0071 | -29.1997 | -35.5511 | 477 | -28.7969 | -25.2735 | -30.4283 | -40.1822 | -29.0611 | -37.3789 | -30.3359 | -25.9297 | -31.7681 | -39.2994 | -28.8619 | -38.0625 | -26.2526 | -26.8854 | -30.7617 | -46.5312 | -31.3515 | -26.9334 | -27.7916 | -27.5416 | -32.1015 | -45.6484 | -31.1523 | -27.617
478 | -10.6316 | 0 | -8.8664 | 0 | -9.8186 | 0 | -9.0741 | 0 | -41.3697 | -123.8728 | -29.6358 | -153.9109 | -39.8905 | 25.2923 | -41.9582 | -38.1925 | -43.5566 | -153.8073 | -36.0789 | -32.2341 | -42.8605 | -35.4637 | -28.5974 | -58.4344 | -40.7796 | 116.2561 | -62.0368 | -7.587 | -51.9672 | -16.5647 | -36.9408 | 49.9615 | -8.1146 | -19.7008 | -16.1597 | -29.6106 | -18.7632 | 19.2869 | -19.3648 | 16.705 | -9.1423 | 51.4677 | -18.5409 | 80.0066 | -19.7898 | 38.7531 | -15.3468 | 34.797 | -44.9119 | -36.2235 | -37.3646 | -39.5994 | -47.9666 | -37.079 | -46.9172 | -38.803 | -35.6707 | -40.6047 | -55.0578 | -40.0882 | -36.6816 | 478 | -28.986 | -37.4293 | -28.5454 | -34.0527 | -28.1915 | -42.3108 | -28.0022 | -35.3433 | 478 | -28.1714 | -25.0391 | -28.9678 | -39.1002 | -28.2126 | -37.0986 | -29.9366 | -25.8521 | -30.5253 | -38.148 | -28.0049 | -37.8431 | -25.5919 | -26.733 | -29.9731 | -46.1914 | -31.2218 | -26.863 | -27.3571 | -27.546 | -31.5306 | -45.2392 | -31.0141 | -27.6075
479 | -10.6433 | 0 | -8.8747 | 0 | -9.8095 | 0 | -9.0739 | 0 | -38.7467 | -125.8377 | -28.8412 | -164.2256 | -39.6268 | 8.2324 | -41.1611 | -43.4375 | -43.9458 | -147.4102 | -36.2954 | -49.6374 | -39.595 | -36.1599 | -27.6897 | -67.862 | -42.1586 | 91.6118 | -61.1464 | 101.5077 | -47.6864 | 1.62 | -37.2718 | 43.5139 | -8.3296 | -29.0568 | -16.9154 | -26.9723 | -19.3111 | 15.5939 | -17.6087 | 27.9369 | -9.2871 | 39.5267 | -19.3904 | 77.7872 | -20.6875 | 29.6682 | -15.0626 | 29.792 | -44.4397 | -36.0347 | -37.4701 | -38.8654 | -47.9748 | -36.6128 | -46.359 | -38.747 | -35.7058 | -40.07 | -55.6637 | -40.2548 | -37.2817 | 479 | -28.1016 | -36.0153 | -27.9128 | -34.1572 | -27.2749 | -38.9422 | -27.2343 | -35.7628 | 479 | -28.1037 | -25.0625 | -28.2221 | -39.1001 | -27.7381 | -36.5495 | -29.8723 | -25.8963 | -29.7915 | -38.1653 | -27.5389 | -37.2851 | -25.3914 | -26.8268 | -29.4267 | -46.789 | -31.3801 | -27.4722 | -27.16 | -27.6606 | -30.9961 | -45.8542 | -31.1809 | -28.2078
480 | -10.4635 | 0 | -8.9175 | 0 | -9.7381 | 0 | -9.0796 | 0 | -36.7903 | -139.1094 | -29.3353 | -178.53 | -40.2186 | -5.5296 | -40.8303 | -48.3462 | -41.9745 | -145.6044 | -38.2155 | -59.1573 | -37.5713 | -49.4901 | -27.9473 | -80.9014 | -45.963 | 78.0984 | -53.9748 | 87.8884 | -43.5607 | -11.1417 | -38.2078 | 36.8316 | -9.2585 | -34.7977 | -16.3336 | -19.9564 | -19.9537 | 17.7278 | -16.1101 | 24.1356 | -10.3626 | 31.2082 | -19.091 | 84.98 | -22.0744 | 28.818 | -15.1769 | 23.6547 | -43.8692 | -36.4241 | -37.4543 | -38.7559 | -49.1934 | -36.6468 | -45.8628 | -39.3084 | -35.737 | -39.9018 | -56.3315 | -40.4295 | -37.7882 | 480 | -28.3272 | -34.4921 | -28.5424 | -35.0951 | -27.4364 | -36.5172 | -27.5465 | -36.5666 | 480 | -28.8449 | -25.2735 | -28.2924 | -40.2759 | -27.7293 | -36.1247 | -30.3909 | -25.9989 | -29.6763 | -39.4553 | -27.5672 | -36.7832 | -25.9606 | -26.9908 | -29.4383 | -47.414 | -31.512 | -28.0501 | -27.5066 | -27.7162 | -30.8222 | -46.5934 | -31.3499 | -28.7086
481 | -10.3018 | 0 | -9.0323 | 0 | -9.7159 | 0 | -9.1026 | 0 | -36.2173 | -157.8711 | -31.4039 | 170.0241 | -41.0183 | -15.8296 | -40.8735 | -52.4216 | -40.1459 | -157.2547 | -40.0198 | -50.2746 | -36.9922 | -65.981 | -29.3951 | -91.8155 | -49.885 | 104.108 | -53.1735 | 75.6787 | -41.6024 | -33.9881 | -40.1065 | 39.7687 | -10.0388 | -36.396 | -14.7603 | -23.2181 | -19.724 | 17.0429 | -15.7626 | 14.9545 | -11.6031 | 33.115 | -17.2756 | 88.8146 | -22.3132 | 38.0158 | -15.8628 | 18.0265 | -43.6559 | -37.4488 | -37.4684 | -39.3981 | -50.7692 | -36.9528 | -45.8253 | -40.3097 | -35.6886 | -40.3097 | -55.5597 | -40.6964 | -37.4183 | 481 | -29.8221 | -33.7944 | -30.433 | -35.6013 | -28.6659 | -35.6249 | -29.0245 | -37.5205 | 481 | -30.0079 | -25.3868 | -29.0963 | -41.7369 | -27.9205 | -36.1094 | -31.2774 | -25.9727 | -30.2955 | -41.0533 | -27.8502 | -36.7227 | -27.147 | -27.1666 | -30.0079 | -46.5274 | -31.6641 | -27.7024 | -28.4165 | -27.7525 | -31.2071 | -45.8438 | -31.5938 | -28.3157
482 | -10.3941 | 0 | -9.1316 | 0 | -9.8074 | 0 | -9.1051 | 0 | -37.2376 | -172.5594 | -34.167 | 176.0896 | -41.1391 | -19.7373 | -40.547 | -49.8243 | -39.596 | -173.6114 | -38.2935 | -37.2167 | -37.9024 | -80.3424 | -31.8509 | -94.9873 | -45.3891 | 120.3782 | -53.5937 | 80.7936 | -41.6928 | -57.5482 | -39.5796 | 54.3154 | -9.7668 | -32.7758 | -13.7747 | -31.9278 | -18.3193 | 18.8111 | -16.5539 | 8.6442 | -11.2242 | 39.6379 | -15.1924 | 83.9815 | -20.7434 | 40.0874 | -16.8574 | 16.9798 | -44.0599 | -38.5872 | -37.5996 | -40.5794 | -50.8099 | -37.0442 | -46.241 | -40.78 | -35.7808 | -40.9988 | -53.8621 | -40.9558 | -36.9354 | 482 | -31.8781 | -34.1249 | -32.0804 | -34.752 | -30.7366 | -36.3044 | -31.149 | -36.8446 | 482 | -30.3859 | -25.3867 | -30.1853 | -41.6783 | -27.9126 | -36.4336 | -31.6484 | -25.9734 | -31.4743 | -41.0025 | -27.9391 | -37.1359 | -28.1931 | -27.2055 | -30.6047 | -44.7305 | -31.8242 | -27.128 | -29.4556 | -27.7922 | -31.8937 | -44.0547 | -31.8507 | -27.8303
483 | -10.7134 | 0 | -9.1893 | 0 | -9.9481 | 0 | -9.1037 | 0 | -39.2358 | -175.2062 | -34.1411 | -167.7936 | -40.4725 | -29.5537 | -39.3027 | -49.7661 | -40.1696 | 173.0828 | -35.797 | -40.5472 | -39.8844 | -83.2738 | -33.4658 | -82.1929 | -42.6034 | 104.5274 | -53.5137 | 95.3956 | -43.3364 | -74.5148 | -37.54 | 53.6198 | -8.7685 | -37.0931 | -13.8537 | -45.1019 | -18.3236 | 8.4356 | -17.884 | 9.9189 | -9.4865 | 39.3025 | -13.5613 | 75.4773 | -19.6438 | 33.1248 | -17.3437 | 19.7886 | -45.0354 | -38.8685 | -37.708 | -41.1682 | -50.0081 | -36.6342 | -46.4783 | -40.2958 | -35.9829 | -41.3025 | -52.2713 | -40.495 | -36.4549 | 483 | -32.2599 | -34.7778 | -31.1577 | -33.4769 | -32.1622 | -38.138 | -32.0006 | -35.5675 | 483 | -29.5824 | -25.2695 | -30.4548 | -40.8188 | -27.4449 | -36.5302 | -31.1065 | -26.0348 | -32.0645 | -40.06 | -27.5305 | -37.3746 | -28.1551 | -26.9946 | -30.5891 | -43.082 | -31.3057 | -26.5068 | -29.6792 | -27.7599 | -32.1988 | -42.3232 | -31.3913 | -27.3512
484 | -10.9989 | 0 | -9.1665 | 0 | -10.103 | 0 | -9.1148 | 0 | -39.6625 | -164.364 | -32.3602 | -165.9755 | -39.9209 | -43.1701 | -37.7546 | -56.6972 | -40.7134 | 165.994 | -34.1765 | -52.4295 | -40.3902 | -70.1341 | -32.1672 | -72.0209 | -42.0357 | 83.8163 | -50.031 | 119.4309 | -45.6226 | -77.4379 | -36.4996 | 45.9598 | -8.2456 | -47.0897 | -15.2591 | -55.5469 | -19.1104 | 2.6605 | -18.2184 | 18.6223 | -8.4192 | 30.3093 | -13.2278 | 64.714 | -19.4982 | 25.3739 | -17.141 | 21.987 | -46.0713 | -38.3671 | -37.6381 | -40.2978 | -49.4463 | -36.0702 | -45.9712 | -39.6772 | -35.995 | -40.6821 | -50.7446 | -39.6967 | -36.0901 | 484 | -31.0201 | -34.4293 | -29.4666 | -32.4493 | -31.1855 | -38.903 | -30.7523 | -35.0325 | 484 | -28.6783 | -24.9961 | -29.2989 | -40.2798 | -26.9037 | -35.8682 | -30.5107 | -25.892 | -31.183 | -39.3433 | -26.9554 | -36.8564 | -27.3682 | -26.6392 | -29.6832 | -41.5781 | -30.5302 | -25.9871 | -29.2006 | -27.5351 | -31.5673 | -40.6416 | -30.5819 | -26.9753
485 | -11.022 | 0 | -9.1157 | 0 | -10.1392 | 0 | -9.1392 | 0 | -37.722 | -158.3941 | -31.232 | -174.8954 | -39.9787 | -61.9865 | -36.8767 | -67.4877 | -41.1335 | 157.118 | -33.546 | -67.516 | -38.2254 | -65.5171 | -30.7161 | -77.4099 | -43.2254 | 63.2944 | -44.6887 | 114.0398 | -46.5999 | -69.8707 | -36.0251 | 36.3276 | -8.5907 | -59.2515 | -17.9272 | -57.6804 | -20.5674 | 1.1589 | -17.6316 | 23.8151 | -8.1618 | 17.028 | -13.283 | 56.5704 | -20.0626 | 14.1242 | -16.9537 | 17.5759 | -46.2666 | -37.9306 | -37.4697 | -38.9189 | -47.9814 | -35.4619 | -44.9439 | -39.2876 | -35.9009 | -39.9009 | -49.6001 | -39.3345 | -36.009 | 485 | -29.9035 | -33.4557 | -28.5379 | -32.0796 | -29.8045 | -36.8545 | -29.4627 | -34.9593 | 485 | -28.2656 | -24.8789 | -27.8969 | -38.8657 | -26.3462 | -34.8047 | -30.1719 | -25.7617 | -29.7797 | -37.8422 | -26.3227 | -35.8047 | -26.9086 | -26.4477 | -28.8789 | -40.4844 | -30.2188 | -25.8698 | -28.8149 | -27.3305 | -30.7617 | -39.4609 | -30.1953 | -26.8698
486 | -10.7812 | 0 | -9.0834 | 0 | -10.0912 | 0 | -9.1396 | 0 | -35.4827 | -165.8914 | -31.382 | 170.9638 | -40.939 | -79.4202 | -36.6793 | -77.8483 | -41.9752 | 154.5436 | -34.5547 | -82.9042 | -36.1541 | -73.5335 | -30.431 | -88.8156 | -46.7025 | 54.2048 | -41.8868 | 94.5953 | -45.2012 | -59.5154 | -36.1178 | 23.5157 | -9.6537 | -71.8179 | -19.4797 | -43.459 | -21.3213 | 8.2672 | -17.0816 | 23.6567 | -8.6782 | 5.6129 | -13.4433 | 52.2281 | -21.394 | 5.6583 | -17.7673 | 11.5957 | -45.4607 | -37.9764 | -37.2445 | -38.0389 | -47.2693 | -35.2381 | -44.0521 | -39.5131 | -35.746 | -39.517 | -49.8607 | -39.0873 | -35.914 | 486 | -29.6219 | -32.5085 | -28.8852 | -33.0593 | -29.3207 | -34.7187 | -29.1551 | -35.2867 | 486 | -28.7319 | -24.9648 | -27.2577 | -38.1859 | -26.1547 | -33.9609 | -30.4297 | -25.6548 | -28.8993 | -37.1781 | -26.0985 | -34.9125 | -27.1952 | -26.4633 | -28.7358 | -40.7773 | -30.0039 | -25.8228 | -28.893 | -27.1533 | -30.3774 | -39.7695 | -29.9477 | -26.7744
487 | -10.3951 | 0 | -9.1223 | 0 | -10.0124 | 0 | -9.1579 | 0 | -34.1019 | 179.7934 | -33.2488 | 157.6665 | -43.0472 | -92.521 | -37.0997 | -86.9918 | -41.1182 | 155.4745 | -36.8498 | -85.9091 | -35.2158 | -87.6992 | -31.2842 | -98.7313 | -48.9044 | 80.3735 | -41.386 | 76.5305 | -42.2995 | -65.2769 | -38.0666 | 12.8142 | -11.641 | -77.9952 | -17.8305 | -29.3757 | -20.9044 | 12.4269 | -16.7986 | 23.3522 | -9.8335 | -1.1599 | -13.1737 | 50.6464 | -22.7804 | 10.9676 | -19.6369 | 12.5181 | -44.5348 | -38.5929 | -37.1279 | -37.902 | -48.1207 | -35.628 | -43.6575 | -40.3601 | -35.524 | -39.6262 | -51.4778 | -38.9733 | -35.5303 | 487 | -30.4013 | -31.7968 | -30.5808 | -34.77 | -29.756 | -33.6405 | -30.1199 | -36.4237 | 487 | -29.965 | -25.1289 | -27.5069 | -38.9984 | -26.5057 | -33.6451 | -31.2378 | -25.5116 | -28.7441 | -38.1083 | -26.4701 | -34.4996 | -28.1978 | -26.7328 | -29.2311 | -42.3555 | -29.851 | -25.5179 | -29.4706 | -27.1155 | -30.4683 | -41.4654 | -29.8154 | -26.3724
488 | -10.1419 | 0 | -9.1482 | 0 | -10.004 | 0 | -9.2081 | 0 | -34.003 | 163.381 | -36.8171 | 158.2101 | -45.1449 | -88.5295 | -37.8009 | -90.3703 | -39.5915 | 144.6629 | -36.9799 | -68.7279 | -35.5572 | -102.147 | -33.189 | -105.005 | -44.4399 | 91.4656 | -41.9669 | 69.4189 | -40.6798 | -83.122 | -40.5661 | 24.2642 | -13.1172 | -73.5317 | -15.7678 | -33.5541 | -20.819 | 7.5188 | -16.6731 | 24.72 | -10.906 | -0.5364 | -12.6595 | 47.8425 | -22.5042 | 18.289 | -20.6742 | 28.1677 | -44.0998 | -39.6078 | -37.1676 | -38.5177 | -49.4396 | -36.0766 | -43.8943 | -41.1172 | -35.3997 | -40.1443 | -53.2889 | -38.9649 | -35.2639 | 488 | -31.9618 | -31.7159 | -32.4072 | -34.6737 | -31.002 | -33.6933 | -31.9983 | -36.793 | 488 | -30.9753 | -25.2578 | -28.3758 | -40.2914 | -26.9284 | -33.8903 | -31.969 | -25.3957 | -29.3096 | -39.4356 | -26.8685 | -34.6862 | -29.4659 | -27.0257 | -30.0024 | -44.1407 | -29.8167 | -25.2599 | -30.4596 | -27.1636 | -30.9362 | -43.2849 | -29.7568 | -26.0558
489 | -10.1054 | 0 | -9.164 | 0 | -10.0937 | 0 | -9.2578 | 0 | -35.2469 | 150.6293 | -38.0924 | -176.5339 | -43.6073 | -83.5011 | -37.7817 | -88.8542 | -39.248 | 126.8104 | -33.7462 | -65.5182 | -37.0538 | -110.5913 | -35.372 | -98.3835 | -41.3241 | 73.7183 | -41.5541 | 70.4683 | -40.7285 | -103.0234 | -39.0707 | 37.9241 | -12.748 | -67.7886 | -15.2671 | -42.8289 | -21.8926 | 5.3839 | -16.3105 | 26.7516 | -10.8239 | 1.2329 | -12.3365 | 41.0892 | -22.0872 | 11.2267 | -18.9475 | 39.976 | -44.2601 | -40.2835 | -37.3538 | -39.2718 | -49.432 | -35.721 | -44.4062 | -40.914 | -35.6445 | -40.5625 | -53.1289 | -38.75 | -35.4473 | 489 | -33.0322 | -32.3335 | -31.285 | -32.3318 | -32.5099 | -34.5402 | -33.1511 | -35.4954 | 489 | -30.8086 | -25.5391 | -29.1664 | -40.268 | -26.557 | -34.3125 | -31.75 | -25.5508 | -30.014 | -39.3383 | -26.4632 | -35.1484 | -30.1781 | -27.2484 | -30.4571 | -43.9649 | -29.586 | -25.3536 | -31.1195 | -27.2601 | -31.3047 | -43.0352 | -29.4922 | -26.1895
490 | -10.1955 | 0 | -9.1542 | 0 | -10.2728 | 0 | -9.2986 | 0 | -36.8402 | 150.2578 | -35.5857 | -166.0629 | -41.9242 | -95.4132 | -36.7597 | -90.6125 | -40.4619 | 110.9301 | -31.3046 | -79.4113 | -38.3753 | -104.5467 | -35.1191 | -84.0095 | -40.494 | 48.3273 | -40.38 | 67.8314 | -41.9943 | -116.9055 | -37.0754 | 37.1683 | -11.6683 | -73.574 | -15.876 | -52.2293 | -23.5838 | 9.2242 | -15.4057 | 27.5536 | -10.1491 | -0.693 | -12.3099 | 37.0341 | -22.4221 | 5.7634 | -17.0536 | 36.9765 | -44.8947 | -40.2282 | -37.3853 | -39.0275 | -48.6799 | -34.736 | -44.5253 | -40.3861 | -35.9573 | -40.0682 | -51.6034 | -38.058 | -35.6145 | 490 | -32.6158 | -32.9431 | -29.109 | -30.4835 | -32.6577 | -35.2263 | -32.252 | -34.5777 | 490 | -30.1906 | -25.7618 | -28.832 | -39.5257 | -25.5818 | -34.2525 | -31.2319 | -25.6845 | -29.7289 | -38.4071 | -25.4374 | -35.2267 | -30.0327 | -27.1898 | -29.8727 | -42.4492 | -28.9038 | -25.3417 | -31.074 | -27.1125 | -30.7696 | -41.3306 | -28.7594 | -26.3159
491 | -10.193 | 0 | -9.1578 | 0 | -10.413 | 0 | -9.3343 | 0 | -36.757 | 157.0076 | -33.8822 | -172.1852 | -41.0621 | -111.7154 | -35.7312 | -98.6089 | -41.664 | 105.3427 | -30.4554 | -99.6097 | -37.2835 | -96.0886 | -33.5735 | -83.4491 | -41.7393 | 25.4002 | -39.1255 | 63.1043 | -43.7004 | -122.8279 | -35.4898 | 27.2058 | -11.6622 | -85.4597 | -17.7991 | -47.7481 | -22.4142 | 31.6048 | -14.4486 | 24.5432 | -9.8215 | -9.4186 | -12.4723 | 34.9536 | -23.3566 | 2.6935 | -16.442 | 26.5673 | -45.3593 | -39.9231 | -37.1484 | -38.0429 | -47.6249 | -33.8176 | -43.9156 | -40.1865 | -35.9313 | -39.0719 | -49.5719 | -37.0224 | -35.7546 | 491 | -31.5592 | -32.6248 | -28.0224 | -29.8008 | -31.592 | -34.5361 | -30.7366 | -34.0654 | 491 | -29.9935 | -25.7383 | -27.8499 | -38.4671 | -24.6598 | -33.5026 | -31.0287 | -25.5183 | -28.7086 | -37.2119 | -24.4833 | -34.5813 | -29.7301 | -26.9554 | -28.8789 | -40.4141 | -27.8646 | -25.3416 | -30.7653 | -26.7354 | -29.7376 | -39.1589 | -27.6881 | -26.4203
492 | -10.0683 | 0 | -9.2205 | 0 | -10.4459 | 0 | -9.3469 | 0 | -35.1572 | 157.4939 | -33.7746 | 175.6132 | -41.0286 | -130.8006 | -35.3424 | -107.4021 | -42.5114 | 97.8178 | -30.9183 | -118.9421 | -35.3077 | -99.6259 | -32.93 | -92.3755 | -45.1391 | 11.8556 | -37.8919 | 55.1279 | -45.1687 | -120.7149 | -35.0642 | 9.0161 | -12.6758 | -98.4222 | -17.59 | -34.768 | -20.3285 | 34.7392 | -14.0345 | 20.9219 | -10.194 | -18.8038 | -12.3134 | 33.9482 | -24.4449 | 1.8826 | -17.4841 | 15.2108 | -44.961 | -39.8974 | -36.8595 | -37.2501 | -46.0899 | -33.2997 | -43.0174 | -40.6217 | -35.7597 | -38.3963 | -48.1775 | -35.9967 | -35.9397 | 492 | -30.9517 | -31.8487 | -28.1788 | -30.2484 | -30.7855 | -33.1203 | -30.0727 | -34.2872 | 492 | -30.5534 | -25.6914 | -27.1818 | -36.8694 | -24.0792 | -32.5715 | -31.4012 | -25.3138 | -27.9032 | -35.644 | -23.9528 | -33.6705 | -29.8291 | -26.7912 | -28.328 | -38.957 | -26.7762 | -25.4938 | -30.6769 | -26.4136 | -29.0494 | -37.7316 | -26.6498 | -26.5928
493 | -9.8608 | 0 | -9.3178 | 0 | -10.3647 | 0 | -9.353 | 0 | -33.6847 | 148.293 | -35.4518 | 166.9807 | -42.5708 | -147.0265 | -35.4809 | -115.9737 | -43.7336 | 98.8064 | -32.791 | -134.4907 | -34.1291 | -110.9547 | -33.6105 | -102.7755 | -48.4077 | 31.5214 | -37.3402 | 43.789 | -44.43 | -109.8981 | -37.2435 | -9.3121 | -15.1423 | -106.7534 | -15.6085 | -29.8574 | -18.7728 | 31.2875 | -13.6062 | 19.6085 | -11.3598 | -24.6449 | -11.6234 | 35.1025 | -25.1118 | 19.5259 | -20.5774 | 14.2716 | -44.2731 | -40.4372 | -36.6989 | -36.9684 | -45.8005 | -33.3356 | -42.478 | -41.7866 | -35.5991 | -38.1733 | -48.6733 | -35.6459 | -35.6357 | 493 | -31.1442 | -31.2292 | -29.61 | -32.0513 | -30.7762 | -32.1681 | -30.9227 | -36.2136 | 493 | -31.9258 | -25.7383 | -27.1076 | -36.4827 | -24.0178 | -32.1133 | -32.4688 | -25.2344 | -27.6154 | -35.4358 | -23.9826 | -33.125 | -30.5764 | -26.8381 | -28.3125 | -39.3555 | -26.3281 | -25.271 | -31.1194 | -26.3342 | -28.8203 | -38.3086 | -26.2929 | -26.2827
494 | -9.7302 | 0 | -9.402 | 0 | -10.2803 | 0 | -9.4188 | 0 | -33.2205 | 134.569 | -38.3799 | 173.7782 | -44.7791 | -146.8721 | -35.9419 | -122.8987 | -42.7903 | 101.0115 | -35.886 | -135.4633 | -34.0897 | -125.0414 | -35.8974 | -110.7014 | -44.4845 | 47.7007 | -37.6388 | 35.7526 | -42.1137 | -113.798 | -43.0132 | -3.0229 | -17.197 | -103.2137 | -13.9316 | -38.4054 | -18.5841 | 23.7971 | -12.9902 | 16.6102 | -12.4986 | -24.7269 | -10.7961 | 31.3273 | -24.0822 | 20.4436 | -22.912 | 44.6216 | -43.8378 | -41.4699 | -36.8027 | -37.5722 | -46.705 | -33.6613 | -42.445 | -43.042 | -35.656 | -38.4606 | -50.652 | -35.9131 | -34.9495 | 494 | -31.8385 | -31.0594 | -31.82 | -34.6377 | -31.6573 | -32.0505 | -33.1931 | -38.3256 | 494 | -33.3118 | -25.9258 | -27.842 | -37.303 | -24.2593 | -32.1647 | -33.64 | -25.3757 | -28.1534 | -36.4247 | -24.2425 | -33.0262 | -31.7397 | -27.0725 | -28.7304 | -41.25 | -26.5111 | -24.6692 | -32.0679 | -26.5224 | -29.0418 | -40.3717 | -26.4943 | -25.5307
495 | -9.6802 | 0 | -9.4188 | 0 | -10.2875 | 0 | -9.536 | 0 | -33.8769 | 121.6674 | -38.4653 | -161.415 | -43.6582 | -138.8529 | -36.1385 | -124.3366 | -41.2875 | 90.395 | -36.0807 | -116.167 | -35.1456 | -133.8689 | -39.5782 | -98.8157 | -41.1723 | 31.1437 | -37.6868 | 34.284 | -40.848 | -129.2635 | -40.6141 | 43.9575 | -17.6887 | -95.7682 | -13.7293 | -50.5673 | -18.888 | 23.2391 | -12.268 | 11.0729 | -12.8423 | -20.2955 | -10.2659 | 23.7166 | -24.079 | 7.3619 | -19.0436 | 67.1247 | -43.796 | -42.5591 | -37.0144 | -38.8585 | -47.71 | -33.7037 | -42.743 | -42.9554 | -36.1256 | -38.8993 | -52.786 | -36.2718 | -34.5113 | 495 | -32.2548 | -31.3834 | -31.9911 | -34.3892 | -33.0773 | -32.5305 | -34.3491 | -36.1009 | 495 | -33.2752 | -26.4454 | -29.1783 | -38.2912 | -24.2849 | -32.4555 | -33.5366 | -25.8381 | -29.3225 | -37.4225 | -24.1677 | -33.207 | -32.8789 | -27.3342 | -29.2191 | -43.3672 | -26.853 | -24.2238 | -33.1403 | -26.7269 | -29.3633 | -42.4985 | -26.7358 | -24.9753
496 | -9.683 | 0 | -9.3925 | 0 | -10.4395 | 0 | -9.6298 | 0 | -35.081 | 117.2675 | -35.5094 | -151.5069 | -41.4392 | -147.3332 | -35.5798 | -126.381 | -41.0417 | 70.6842 | -33.1534 | -117.2207 | -36.4652 | -133.6487 | -38.5451 | -66.1191 | -39.9787 | 6.2242 | -37.1015 | 30.7763 | -40.8847 | -145.6877 | -35.8049 | 37.47 | -16.5592 | -100.0565 | -14.6536 | -61.2752 | -18.7197 | 24.8019 | -11.8307 | 2.5726 | -12.2377 | -20.2785 | -10.1841 | 16.7877 | -26.1818 | 2.8911 | -15.6817 | 63.4432 | -44.1915 | -42.9729 | -37.0054 | -39.6094 | -47.8243 | -33.3518 | -42.8339 | -42.0137 | -36.8119 | -38.6855 | -52.6776 | -35.9669 | -34.4991 | 496 | -31.7822 | -31.7668 | -29.8225 | -31.9773 | -33.3165 | -32.9916 | -32.237 | -33.5184 | 496 | -32.3307 | -27.1289 | -29.9264 | -38.4318 | -23.9593 | -32.3944 | -32.6212 | -26.3724 | -29.9796 | -37.3848 | -23.722 | -33.2041 | -33.2899 | -27.3224 | -29.0025 | -43.2851 | -26.5744 | -24.0596 | -33.5804 | -26.5659 | -29.0557 | -42.2381 | -26.3371 | -24.8693
497 | -9.6825 | 0 | -9.3896 | 0 | -10.6357 | 0 | -9.6708 | 0 | -35.4589 | 120.437 | -33.3045 | -155.982 | -39.9175 | -164.1701 | -34.5123 | -133.9269 | -42.755 | 52.5975 | -31.7579 | -131.7498 | -36.1225 | -125.259 | -35.102 | -62.884 | -40.7341 | -18.0316 | -36.2726 | 27.1055 | -42.3983 | -156.9013 | -33.7899 | 19.282 | -16.9565 | -114.1111 | -16.6979 | -59.0394 | -17.2501 | 27.1282 | -11.8896 | -7.6129 | -11.8038 | -25.3695 | -10.3497 | 13.0568 | -29.2148 | 13.135 | -13.9436 | 54.09 | -44.8838 | -42.5909 | -36.712 | -38.7706 | -47.6104 | -33.0557 | -42.3739 | -41.3271 | -37.0692 | -37.6825 | -51.9325 | -34.9403 | -34.6248 | 497 | -30.687 | -31.603 | -28.2734 | -30.8509 | -31.9549 | -32.6948 | -30.1654 | -32.5192 | 497 | -31.6446 | -27.3867 | -29.0881 | -38.2208 | -23.6661 | -31.7382 | -31.9375 | -26.4335 | -29.0998 | -36.9747 | -23.3849 | -32.7031 | -32.9084 | -27.0295 | -28 | -42.5429 | -25.5507 | -23.9891 | -33.2013 | -26.0763 | -28.0117 | -41.2968 | -25.2695 | -24.954
498 | -9.6313 | 0 | -9.5266 | 0 | -10.75 | 0 | -9.6307 | 0 | -34.602 | 119.3483 | -32.4432 | -165.5559 | -39.3332 | 174.9567 | -34.2847 | -147.7943 | -45.4232 | 51.57 | -31.6901 | -148.268 | -34.2988 | -126.3748 | -33.4658 | -71.4754 | -43.251 | -35.2609 | -35.555 | 20.1049 | -43.6726 | -153.8964 | -33.7566 | 0.8127 | -18.8964 | -130.4356 | -16.8325 | -41.5373 | -16.2358 | 20.0079 | -12.7324 | -16.8654 | -11.9725 | -31.7887 | -10.2729 | 13.2621 | -28.4562 | 55.6717 | -13.3884 | 43.8417 | -45.4583 | -42.0802 | -36.3209 | -37.3685 | -47.8294 | -32.8966 | -41.5578 | -41.3203 | -36.6665 | -36.8781 | -50.9172 | -34.0273 | -34.6882 | 498 | -29.8593 | -31.2603 | -27.9043 | -30.8465 | -30.609 | -31.5936 | -29.3947 | -32.9133 | 498 | -31.689 | -27.0352 | -27.7372 | -38.3028 | -23.37 | -30.8078 | -31.7937 | -25.9165 | -27.7378 | -37.0794 | -23.2659 | -31.9271 | -32.4489 | -26.6896 | -27.2468 | -41.3906 | -24.5007 | -23.9382 | -32.5536 | -25.5709 | -27.2474 | -40.1672 | -24.3966 | -25.0575
499 | -9.568 | 0 | -9.7235 | 0 | -10.7043 | 0 | -9.5859 | 0 | -33.6122 | 112.8511 | -32.8111 | -170.3492 | -40.3124 | 151.5414 | -35.3923 | -160.8514 | -45.7827 | 57.4042 | -32.7455 | -165.2254 | -32.9656 | -136.6478 | -33.3905 | -81.4156 | -46.4652 | -33.5539 | -35.3146 | 12.4013 | -42.7227 | -150.0522 | -35.6802 | -14.9479 | -23.3995 | -140.1351 | -14.1019 | -36.287 | -15.9935 | 11.7583 | -14.2472 | -19.2095 | -12.3509 | -38.7062 | -9.496 | 9.1014 | -25.5564 | 53.068 | -13.6175 | 37.5846 | -45.2255 | -42.1399 | -36.0896 | -36.5966 | -47.6005 | -32.8235 | -40.8368 | -41.9582 | -36.0837 | -37.0008 | -48.911 | -33.4895 | -34.6307 | 499 | -29.7806 | -31.2458 | -28.7166 | -31.8648 | -30.062 | -30.6919 | -29.9029 | -34.6045 | 499 | -32.3902 | -26.5157 | -27.0286 | -37.877 | -23.1 | -30.1325 | -32.2347 | -25.3794 | -27.0107 | -36.8962 | -23.2376 | -31.2509 | -32.5719 | -26.5216 | -27.4328 | -39.1875 | -23.766 | -23.9264 | -32.4164 | -25.3853 | -27.4149 | -38.2067 | -23.9036 | -25.0448
500 | -9.5155 | 0 | -9.8764 | 0 | -10.567 | 0 | -9.5647 | 0 | -33.2623 | 101.8805 | -33.5673 | -166.2948 | -43.2645 | 137.0865 | -36.8397 | -164.9641 | -45.4998 | 58.9146 | -35.8244 | -175.3688 | -32.6726 | -149.4907 | -34.663 | -85.4761 | -45.7949 | -14.4091 | -35.2691 | 7.8594 | -41.2877 | -155.0624 | -38.9505 | -7.4742 | -30.0271 | -116.8601 | -12.0417 | -44.7136 | -16.695 | 4.6629 | -15.1694 | -12.7009 | -13.1072 | -41.4658 | -8.814 | 2.6096 | -22.9177 | 48.7162 | -13.8273 | 37.8423 | -44.6635 | -43.0299 | -36.1425 | -36.7612 | -47.7885 | -33.1159 | -40.5404 | -42.9537 | -35.7967 | -37.6732 | -48.4311 | -33.4732 | -34.4502 | 500 | -30.1828 | -31.5056 | -30.4172 | -34.725 | -30.4167 | -30.4001 | -31.156 | -36.4205 | 500 | -33.4382 | -26.2812 | -27.2457 | -37.9121 | -23.2395 | -29.9734 | -33.0773 | -25.2297 | -27.1965 | -37.2215 | -23.5512 | -30.9757 | -33.5144 | -26.627 | -28.1577 | -38.5547 | -23.5968 | -23.8832 | -33.1535 | -25.5755 | -28.1085 | -37.8641 | -23.9085 | -24.8855
501 | -9.4965 | 0 | -9.8988 | 0 | -10.4965 | 0 | -9.6488 | 0 | -33.784 | 91.3212 | -32.6059 | -156.2137 | -46.3591 | 149.9907 | -37.7615 | -163.5306 | -44.1523 | 56.5469 | -38.6126 | -153.69 | -33.2727 | -160.7477 | -35.8879 | -73.8695 | -42.2025 | -20.4935 | -34.9558 | 4.9997 | -40.0539 | -166.6658 | -37.2439 | 16.7976 | -25.8177 | -82.56 | -10.916 | -59.0601 | -17.9017 | 2.9211 | -14.3163 | -7.3982 | -13.5779 | -42.7992 | -8.4888 | -6.6608 | -22.7783 | 33.8839 | -13.1675 | 39.8591 | -44.2172 | -44.8969 | -36.35 | -37.8656 | -49.143 | -33.2914 | -40.7074 | -43.3051 | -36.059 | -38.6488 | -49.2426 | -33.6137 | -34.4616 | 501 | -30.0422 | -32.0462 | -30.6861 | -37.007 | -31.0311 | -30.5114 | -31.1586 | -34.589 | 501 | -33.8086 | -26.5625 | -28.3691 | -39.2442 | -23.3926 | -30.2109 | -33.4063 | -25.5625 | -28.2168 | -38.6465 | -23.6426 | -31.0586 | -35.4004 | -26.8535 | -29.1523 | -39.3438 | -23.7149 | -23.9651 | -34.9981 | -25.8535 | -29 | -38.7461 | -23.9649 | -24.8128
502 | -9.4906 | 0 | -9.7785 | 0 | -10.6291 | 0 | -9.8008 | 0 | -34.9419 | 85.5827 | -30.278 | -154.5998 | -43.6525 | 166.5041 | -37.8968 | -161.6826 | -42.5275 | 44.503 | -34.8075 | -140.0337 | -34.3272 | -164.7799 | -33.9017 | -58.4473 | -40.1496 | -43.9022 | -34.2006 | 2.114 | -39.4129 | 179.2837 | -33.6651 | 11.387 | -23.1616 | -93.9261 | -10.9459 | -73.6185 | -17.7827 | 12.3408 | -12.9681 | -11.8847 | -13.9099 | -43.6207 | -8.7804 | -16.5547 | -24.0383 | 30.9764 | -11.9937 | 37.7394 | -43.8234 | -47.3107 | -36.5316 | -39.2258 | -50.5383 | -32.9318 | -41.0207 | -42.7893 | -36.8891 | -39.3254 | -49.7785 | -33.4533 | -34.8988 | 502 | -28.8552 | -32.6868 | -28.444 | -33.6697 | -30.5896 | -30.6357 | -29.1457 | -31.9307 | 502 | -33.2987 | -27.3985 | -29.7352 | -40.7598 | -23.1533 | -30.3916 | -33.0108 | -26.26 | -29.425 | -39.9092 | -23.131 | -31.2199 | -37.8201 | -27.041 | -29.8348 | -40 | -23.6748 | -24.2697 | -37.5322 | -25.9025 | -29.5246 | -39.1494 | -23.6525 | -25.098
503 | -9.4631 | 0 | -9.5898 | 0 | -10.8772 | 0 | -9.9097 | 0 | -35.7192 | 87.7959 | -28.3249 | -162.7851 | -40.4672 | 155.4445 | -37.3278 | -161.6099 | -42.0716 | 23.2448 | -32.1408 | -157.3361 | -34.7323 | -162.9202 | -31.1582 | -61.5541 | -40.1053 | -72.0576 | -33.2138 | -3.6475 | -39.5737 | 161.9756 | -31.8954 | -5.8394 | -23.1286 | -113.34 | -11.9149 | -84.7204 | -16.2392 | 13.4932 | -12.2674 | -22.7638 | -14.0033 | -46.602 | -9.6592 | -24.1934 | -24.6362 | 38.6471 | -11.103 | 30.7231 | -43.6855 | -47.6877 | -36.422 | -39.4199 | -50.8691 | -32.4806 | -41.2695 | -42.2131 | -37.6623 | -38.8711 | -49.582 | -32.7912 | -35.4397 | 503 | -27.3792 | -32.8815 | -26.4464 | -31.1765 | -29.2087 | -30.3444 | -27.2368 | -30.6841 | 503 | -32.75 | -28.1992 | -29.9568 | -41.2793 | -22.8908 | -30.3923 | -32.6233 | -26.7851 | -29.5102 | -39.9919 | -22.5709 | -31.3598 | -38.2246 | -26.9589 | -29.408 | -39.9922 | -23.2014 | -24.5625 | -38.0979 | -25.5448 | -28.9614 | -38.7048 | -22.8815 | -25.53
504 | -9.4524 | 0 | -9.4901 | 0 | -11.0534 | 0 | -9.9188 | 0 | -35.0683 | 90.774 | -27.3146 | -173.5163 | -38.9686 | 135.4429 | -36.5058 | -167.4377 | -43.5649 | 2.0727 | -31.9174 | -178.5449 | -33.7795 | -161.3379 | -29.6649 | -71.7437 | -41.8869 | -98.5222 | -32.4071 | -14.0326 | -40.8218 | 147.8587 | -31.8693 | -24.4844 | -26.3293 | -133.4483 | -13.5773 | -88.0145 | -14.9491 | 3.8233 | -12.4011 | -35.187 | -14.2063 | -50.689 | -10.8759 | -25.4219 | -23.2216 | 49.6396 | -10.7873 | 21.6694 | -43.7732 | -45.6178 | -36.1145 | -38.1521 | -50.5584 | -32.3287 | -41.2284 | -42.0143 | -37.6634 | -37.5721 | -49.9393 | -32.0417 | -35.5806 | 504 | -26.3942 | -32.3742 | -25.6503 | -30.8944 | -28.0581 | -29.6815 | -26.3734 | -30.9813 | 504 | -32.5619 | -28.211 | -28.6997 | -41.0683 | -22.8386 | -30.175 | -32.5242 | -26.61 | -28.2333 | -39.505 | -22.4099 | -31.3096 | -36.1654 | -26.6621 | -28.1197 | -40.4492 | -22.5516 | -24.5272 | -36.1277 | -25.0611 | -27.6533 | -38.8859 | -22.1229 | -25.6618
505 | -9.451 | 0 | -9.4979 | 0 | -10.994 | 0 | -9.8182 | 0 | -33.8764 | 86.4206 | -27.3387 | 174.4985 | -38.7995 | 114.4042 | -36.8172 | -178.0503 | -46.3589 | -5.3338 | -33.32 | 162.9984 | -32.5269 | -168.3883 | -29.3586 | -82.7151 | -45.3906 | -118.99 | -32.3322 | -25.0005 | -42.4554 | 142.6563 | -33.148 | -39.2973 | -34.9403 | -138.8334 | -14.0229 | -82.7536 | -14.6805 | -4.3261 | -13.3764 | -45.8365 | -14.5605 | -54.5389 | -11.1065 | -20.8794 | -21.4275 | 44.9249 | -11.2113 | 12.9486 | -43.9802 | -43.945 | -35.7615 | -36.8669 | -50.3669 | -32.4216 | -40.908 | -42.3065 | -36.9432 | -36.6034 | -51.326 | -31.6737 | -35.4859 | 505 | -26.2215 | -31.9326 | -25.9873 | -32.0722 | -27.5773 | -29.2075 | -26.5208 | -32.4404 | 505 | -32.8555 | -27.4922 | -27.4159 | -40.869 | -22.9237 | -29.914 | -32.8086 | -25.9492 | -27.0487 | -39.3729 | -22.6034 | -31.0898 | -34.494 | -26.3105 | -27.1524 | -41.8281 | -22.1758 | -24.4919 | -34.4471 | -24.7675 | -26.7852 | -40.332 | -21.8555 | -25.6677
506 | -9.4462 | 0 | -9.5655 | 0 | -10.7867 | 0 | -9.7076 | 0 | -33.4018 | 75.8913 | -28.0512 | 171.4016 | -40.22 | 95.514 | -37.8565 | -179.2218 | -47.2564 | -5.6253 | -36.0903 | 150.7898 | -32.2545 | 179.4063 | -30.0718 | -89.2592 | -50.9924 | -100.81 | -32.7954 | -31.9873 | -42.974 | 141.4868 | -35.3213 | -42.091 | -32.7947 | -70.0509 | -12.8993 | -83.9322 | -15.253 | -14.2707 | -14.7496 | -51.5761 | -15.1026 | -57.2503 | -10.3953 | -20.2622 | -20.9093 | 36.5746 | -12.2598 | 8.8056 | -44.0537 | -43.7485 | -35.6042 | -36.7863 | -50.3523 | -32.6649 | -40.753 | -43.0357 | -36.2946 | -36.9069 | -50.9678 | -31.6855 | -35.1098 | 506 | -26.7402 | -31.9415 | -27.0418 | -34.4383 | -27.9953 | -29.3151 | -27.4409 | -34.5339 | 506 | -33.5895 | -26.8484 | -27.3401 | -40.7868 | -23.0994 | -29.9663 | -33.4702 | -25.5079 | -27.0787 | -39.5656 | -22.9573 | -31.0454 | -34.3023 | -26.158 | -27.4607 | -41.4023 | -22.12 | -24.3231 | -34.183 | -24.8175 | -27.1993 | -40.1811 | -21.9779 | -25.4022
507 | -9.4358 | 0 | -9.6115 | 0 | -10.6452 | 0 | -9.6544 | 0 | -33.5852 | 65.6151 | -28.1402 | 174.2332 | -42.4239 | 90.3579 | -37.8523 | -177.6494 | -48.0944 | -7.5983 | -40.0722 | 165.469 | -32.8067 | 168.38 | -30.7063 | -87.3135 | -49.1452 | -67.7137 | -32.9037 | -35.8947 | -42.9221 | 138.286 | -36.1043 | -32.2348 | -26.5212 | -75.4039 | -11.9894 | -91.8906 | -15.9495 | -20.4869 | -15.6094 | -53.9183 | -15.5343 | -59.8332 | -9.5886 | -25.2536 | -21.6287 | 30.2822 | -13.2571 | 11.6702 | -43.8873 | -44.8416 | -35.7043 | -37.5695 | -51.0171 | -32.8793 | -40.8219 | -43.7477 | -36.1326 | -37.6766 | -50.672 | -31.9093 | -34.7947 | 507 | -26.9255 | -32.0937 | -27.4548 | -37.6678 | -28.5821 | -29.6359 | -27.9383 | -35.1084 | 507 | -34.3119 | -26.6968 | -28.1337 | -41.4056 | -23.2678 | -30.1767 | -34.1362 | -25.4874 | -27.9151 | -40.3719 | -23.2249 | -31.1675 | -35.4058 | -26.2685 | -28.2408 | -41.0605 | -22.2978 | -24.1495 | -35.2301 | -25.0591 | -28.0222 | -40.0268 | -22.2549 | -25.1403
508 | -9.4459 | 0 | -9.5942 | 0 | -10.6422 | 0 | -9.6784 | 0 | -34.3384 | 57.9963 | -26.9978 | 177.5941 | -43.4787 | 99.1694 | -37.2882 | 179.1156 | -48.372 | -3.2667 | -39.1603 | -158.1013 | -33.9702 | 162.0824 | -30.0937 | -78.6171 | -43.5435 | -71.6274 | -32.6144 | -40.0247 | -42.4786 | 134.3694 | -34.2061 | -24.0658 | -24.7988 | -95.0156 | -11.9198 | -103.6755 | -16.5435 | -20.1577 | -15.6435 | -56.2603 | -16.0415 | -62.825 | -9.2629 | -33.1804 | -23.1949 | 33.4948 | -13.26 | 19.2624 | -43.5373 | -47.4408 | -36.0023 | -39.01 | -52.1076 | -32.7181 | -41.0629 | -44.0524 | -36.5162 | -38.5238 | -51.3637 | -32.1734 | -34.864 | 508 | -26.1809 | -32.4449 | -26.3746 | -37.4288 | -28.4657 | -29.978 | -27.1987 | -33.1841 | 508 | -34.6065 | -27.0703 | -29.5641 | -42.5134 | -23.1239 | -30.4207 | -34.4582 | -25.874 | -29.3316 | -41.4654 | -23.0397 | -31.3845 | -37.9949 | -26.5564 | -29.0779 | -41.7695 | -22.5792 | -24.2218 | -37.8466 | -25.3601 | -28.8454 | -40.7215 | -22.495 | -25.1856
509 | -9.4176 | 0 | -9.5348 | 0 | -10.8551 | 0 | -9.7965 | 0 | -35.1983 | 56.8136 | -25.1927 | 172.3719 | -40.8891 | 99.1846 | -37.1312 | 175.725 | -46.3879 | -10.0106 | -34.1833 | -169.4763 | -34.8349 | 164.4967 | -27.9471 | -79.5884 | -41.3686 | -99.2876 | -32.1321 | -45.4173 | -41.9146 | 124.4156 | -32.0708 | -38.2695 | -26.1011 | -125.2643 | -13.1828 | -115.7543 | -16.1109 | -18.2716 | -15.6089 | -67.6132 | -16.8481 | -66.2016 | -9.8278 | -40.6483 | -22.1852 | 52.4657 | -12.0285 | 23.0108 | -43.3256 | -49.2396 | -36.3021 | -39.9974 | -51.5912 | -32.0951 | -41.3317 | -43.6832 | -37.1676 | -38.7457 | -51.9723 | -32.0895 | -35.3463 | 509 | -24.6742 | -32.851 | -24.4366 | -33.1326 | -26.9772 | -29.9788 | -25.4712 | -31.2029 | 509 | -34.2656 | -27.75 | -30.5798 | -42.0564 | -22.5603 | -30.4766 | -34.1484 | -26.3125 | -30.2009 | -40.7361 | -22.2986 | -31.5352 | -39.822 | -26.8845 | -29.3281 | -42.4375 | -22.5547 | -24.4912 | -39.7048 | -25.447 | -28.9492 | -41.1172 | -22.293 | -25.5498
510 | -9.4307 | 0 | -9.4832 | 0 | -11.0421 | 0 | -9.8748 | 0 | -35.1781 | 58.1729 | -24.0513 | 161.6844 | -39.1157 | 84.8363 | -36.6965 | 171.8846 | -45.8541 | -31.1301 | -32.9982 | 166.3164 | -34.2728 | 168.0209 | -26.4803 | -89.5665 | -41.4054 | -126.423 | -31.7921 | -54.8337 | -42.0248 | 111.5094 | -31.8752 | -60.0191 | -28.7406 | -150.7398 | -15.2774 | -120.0048 | -15.3147 | -24.4667 | -16.4223 | -85.6447 | -17.5038 | -68.3911 | -10.5417 | -43.4193 | -19.7273 | 52.0227 | -10.7626 | 19.7562 | -43.2857 | -46.3719 | -36.4246 | -39.1919 | -50.3755 | -31.6805 | -41.3973 | -43.1319 | -37.3448 | -38.034 | -52.2957 | -31.7022 | -35.791 | 510 | -23.6047 | -32.6483 | -23.3258 | -31.8712 | -25.6942 | -29.592 | -24.4853 | -31.0544 | 510 | -33.7012 | -27.9141 | -29.7612 | -40.8923 | -22.1973 | -30.3552 | -33.6487 | -26.3027 | -29.3171 | -39.3334 | -21.8057 | -31.5225 | -36.9412 | -26.9939 | -28.6033 | -42.8125 | -22.219 | -24.7489 | -36.8887 | -25.3825 | -28.1592 | -41.2536 | -21.8274 | -25.9162
511 | -9.4298 | 0 | -9.4953 | 0 | -11.0403 | 0 | -9.8954 | 0 | -34.4181 | 55.8167 | -23.817 | 149.0567 | -38.3033 | 65.2652 | -36.6126 | 162.4273 | -48.2517 | -52.5973 | -34.0615 | 146.9971 | -32.9615 | 163.4662 | -26.0512 | -101.2059 | -42.5659 | -147.0836 | -31.8856 | -63.9918 | -43.1093 | 99.59 | -33.4386 | -78.2074 | -34.9215 | -177.6177 | -16.2359 | -110.8451 | -15.159 | -36.9271 | -18.7993 | -108.7005 | -18.7235 | -69.9973 | -11.1193 | -41.1084 | -18.0301 | 43.6573 | -9.9558 | 13.4076 | -43.3212 | -43.8857 | -36.326 | -37.5946 | -50.0087 | -31.6943 | -41.1281 | -42.8099 | -36.8166 | -36.9758 | -53.3195 | -31.5208 | -36.1055 | 511 | -23.3145 | -32.2573 | -23.2211 | -32.555 | -25.1663 | -29.1998 | -24.4572 | -32.5391 | 511 | -33.3801 | -27.3868 | -28.1648 | -40.5134 | -22.199 | -30.0878 | -33.3146 | -25.7763 | -27.6992 | -38.9684 | -21.7989 | -31.2327 | -34.4559 | -26.8962 | -27.546 | -43.8242 | -22.0255 | -25.0652 | -34.3904 | -25.2857 | -27.0804 | -42.2792 | -21.6254 | -26.2101
512 | -9.4419 | 0 | -9.6289 | 0 | -10.8359 | 0 | -9.8646 | 0 | -33.9412 | 48.9675 | -24.4512 | 139.7844 | -38.71 | 42.1703 | -37.765 | 154.415 | -51.4412 | -44.1482 | -36.4089 | 136.7926 | -32.3043 | 152.0193 | -26.5966 | -111.6 | -44.4053 | -162.2059 | -32.5879 | -72.7993 | -44.5146 | 93.8371 | -36.6499 | -89.5962 | -49.1608 | -153.8165 | -14.7176 | -106.2609 | -16.2354 | -47.3474 | -24.622 | -137.9669 | -19.7433 | -68.2912 | -10.2402 | -39.8586 | -17.5611 | 30.1412 | -9.6592 | 6.0738 | -43.2556 | -43.0484 | -36.1505 | -36.5642 | -50.6149 | -31.9469 | -40.7227 | -42.9257 | -36.0981 | -36.5 | -54.8086 | -31.7304 | -36.229 | 512 | -23.8443 | -32.3806 | -23.9966 | -34.3135 | -25.5068 | -29.3007 | -25.2917 | -35.4075 | 512 | -33.4838 | -26.6562 | -27.1223 | -40.986 | -22.318 | -29.8868 | -33.2968 | -25.2622 | -26.6996 | -39.779 | -22.0823 | -30.8581 | -33.6065 | -26.7086 | -27.0581 | -45.1797 | -22.1015 | -25.3931 | -33.4195 | -25.3146 | -26.6354 | -43.9727 | -21.8658 | -26.3644
513 | -9.4541 | 0 | -9.7276 | 0 | -10.6065 | 0 | -9.8447 | 0 | -33.995 | 40.9206 | -25.3411 | 139.2934 | -40.8617 | 21.2662 | -38.7989 | 158.3502 | -49.862 | -41.0331 | -39.8105 | 141.9408 | -32.7631 | 140.2206 | -27.6378 | -112.1907 | -46.3827 | -163.0662 | -33.4291 | -75.925 | -45.3673 | 93.1222 | -41.2663 | -75.9461 | -38.625 | -97.0355 | -13.2327 | -115.6965 | -17.6646 | -54.0688 | -39.1299 | 123.847 | -20.6299 | -66.2724 | -9.4487 | -44.8856 | -18.427 | 21.8665 | -9.6441 | 0.0695 | -43.0573 | -43.4909 | -36.0456 | -36.5651 | -51.6979 | -32.2956 | -40.4619 | -43.5088 | -35.7354 | -37.0283 | -53.8096 | -32.2666 | -35.8745 | 513 | -24.6801 | -32.6701 | -25.0035 | -37.0601 | -26.4301 | -29.9466 | -26.4753 | -38.9699 | 513 | -34.0547 | -26.2813 | -27.111 | -41.9703 | -22.568 | -29.8554 | -33.7812 | -25.1289 | -26.7204 | -41.0914 | -22.4509 | -30.6172 | -34.0368 | -26.5915 | -27.5742 | -44.082 | -22.539 | -25.268 | -33.7633 | -25.4391 | -27.1836 | -43.2031 | -22.4219 | -26.0298
514 | -9.4753 | 0 | -9.752 | 0 | -10.5327 | 0 | -9.8353 | 0 | -34.254 | 35.878 | -24.9235 | 144.1383 | -44.8732 | 11.4091 | -38.0683 | 160.0317 | -50.2975 | -49.6173 | -38.5302 | 172.8883 | -33.9923 | 133.8816 | -27.4283 | -104.1878 | -45.5583 | -157.1015 | -33.5988 | -75.5434 | -45.4314 | 96.3166 | -38.9788 | -41.4849 | -34.336 | -133.6858 | -12.8741 | -131.1062 | -18.8225 | -53.0768 | -25.8881 | 11.3307 | -21.3051 | -63.9359 | -9.066 | -52.8612 | -19.6488 | 22.5355 | -9.7754 | -4.3682 | -42.7028 | -45.0264 | -36.0667 | -37.4254 | -53.1559 | -32.5733 | -40.4863 | -44.4467 | -35.9088 | -38.0293 | -52.6582 | -32.767 | -35.7888 | 514 | -24.4051 | -32.6693 | -24.541 | -37.3952 | -26.5082 | -30.6344 | -26.2506 | -37.3767 | 514 | -34.9714 | -26.4335 | -27.9501 | -43.4039 | -22.8213 | -29.9536 | -34.6947 | -25.3761 | -27.5901 | -42.6232 | -22.738 | -30.651 | -35.5511 | -26.5914 | -28.554 | -42.9062 | -23.015 | -25.2561 | -35.2744 | -25.534 | -28.194 | -42.1255 | -22.9317 | -25.9535
515 | -9.4914 | 0 | -9.7347 | 0 | -10.6425 | 0 | -9.8276 | 0 | -34.5062 | 30.9096 | -23.3043 | 142.7524 | -48.4098 | 35.3147 | -37.5125 | 156.9639 | -49.8461 | -43.6068 | -34.0518 | 166.9552 | -35.1103 | 135.5358 | -25.56 | -103.9514 | -43.4599 | -167.7267 | -33.1684 | -78.4136 | -44.2596 | 93.3739 | -35.1675 | -48.5322 | -31.8962 | -167.7309 | -13.7162 | -148.1749 | -19.0505 | -49.3245 | -22.0337 | -23.4745 | -22.6802 | -63.1217 | -9.3808 | -61.7263 | -19.3854 | 31.7805 | -9.7891 | -8.3926 | -42.3691 | -45.937 | -36.2 | -38.7128 | -54.1738 | -32.4605 | -40.7074 | -44.8847 | -36.5617 | -38.9769 | -52.0629 | -32.6542 | -36.2618 | 515 | -22.9744 | -32.6601 | -22.8038 | -33.7865 | -25.0403 | -30.8201 | -24.4781 | -34.1246 | 515 | -35.3933 | -27.0703 | -29.2214 | -44.4391 | -22.7258 | -30.0649 | -35.15 | -25.9192 | -28.8852 | -43.5313 | -22.6329 | -30.8798 | -36.4456 | -26.7086 | -29.4855 | -42.3282 | -22.9195 | -25.6193 | -36.2023 | -25.5575 | -29.1493 | -41.4204 | -22.8266 | -26.4342
516 | -9.5061 | 0 | -9.6605 | 0 | -10.7935 | 0 | -9.8042 | 0 | -34.4672 | 28.6414 | -22.011 | 133.108 | -45.2441 | 54.4363 | -37.4219 | 151.7007 | -47.2213 | -54.5394 | -32.1528 | 145.315 | -34.7955 | 141.4814 | -24.008 | -112.4561 | -42.3536 | 174.1194 | -32.6593 | -83.7113 | -43.2122 | 82.0799 | -34.104 | -67.6024 | -29.5475 | 151.225 | -15.8794 | -159.8588 | -18.3421 | -55.1131 | -21.2735 | -52.4561 | -24.363 | -56.0928 | -10.1851 | -66.6044 | -17.5794 | 31.9644 | -9.7612 | -12.8938 | -42.3221 | -43.9552 | -36.3435 | -39.4432 | -53.4901 | -32.2208 | -40.9183 | -44.399 | -37.1038 | -39.2816 | -51.7581 | -32.0631 | -36.7526 | 516 | -21.7516 | -32.5374 | -21.4973 | -31.8177 | -23.6018 | -30.356 | -23.094 | -33.0577 | 516 | -34.8929 | -27.5977 | -29.9371 | -43.8296 | -22.5603 | -30.1248 | -34.7385 | -26.3103 | -29.639 | -42.6966 | -22.4166 | -31.1141 | -34.4491 | -26.8374 | -29.7755 | -42.0976 | -22.4026 | -25.9591 | -34.2947 | -25.55 | -29.4774 | -40.9646 | -22.2589 | -26.9484
517 | -9.5492 | 0 | -9.6546 | 0 | -10.8226 | 0 | -9.7367 | 0 | -34.1839 | 22.9537 | -21.5707 | 120.4296 | -42.4192 | 42.7369 | -37.5957 | 146.5266 | -46.445 | -78.2775 | -32.3734 | 120.7604 | -33.3749 | 139.7168 | -23.4323 | -124.7906 | -42.2429 | 153.4672 | -32.8186 | -92.4006 | -43.128 | 64.8729 | -34.8594 | -83.1283 | -28.8946 | 122.4567 | -18.3626 | -156.9863 | -18.2645 | -68.5451 | -22.7987 | -81.2263 | -25.6719 | -39.58 | -10.8983 | -66.6212 | -16.5958 | 23.9974 | -9.8435 | -17.7813 | -42.5038 | -41.9061 | -36.3163 | -38.7889 | -52.4139 | -32.0741 | -40.9828 | -43.6625 | -37.0062 | -38.9007 | -52.2445 | -31.6898 | -37.0042 | 517 | -21.3053 | -32.379 | -21.1249 | -31.8116 | -22.9616 | -29.8676 | -22.6872 | -33.6155 | 517 | -34.1133 | -27.457 | -29.2397 | -42.7593 | -22.4195 | -30.1602 | -34.0079 | -26.1836 | -29.0522 | -41.5913 | -22.3374 | -31.2461 | -32.3569 | -26.7671 | -29.3515 | -42.5899 | -22.0352 | -26.1816 | -32.2515 | -25.4937 | -29.164 | -41.4219 | -21.9531 | -27.2675
518 | -9.5708 | 0 | -9.7373 | 0 | -10.7064 | 0 | -9.6464 | 0 | -34.1796 | 15.7109 | -21.991 | 111.3233 | -41.7704 | 25.8519 | -38.1268 | 145.8063 | -47.9156 | -99.6427 | -34.3211 | 100.528 | -32.3379 | 129.6858 | -23.8337 | -134.8077 | -43.0955 | 133.1117 | -33.7819 | -99.399 | -44.2504 | 50.3681 | -36.8975 | -93.4056 | -27.7094 | 97.276 | -17.6427 | -143.891 | -19.736 | -82.3442 | -27.6452 | -103.9176 | -24.5614 | -18.6891 | -10.532 | -64.6176 | -16.4652 | 10.3895 | -10.2013 | -22.6358 | -42.727 | -41.0516 | -36.1387 | -37.6489 | -51.8638 | -32.1493 | -40.7959 | -43.6791 | -36.4146 | -38.3818 | -53.3271 | -31.8158 | -36.8097 | 518 | -21.6934 | -32.5801 | -21.6454 | -33.4446 | -23.2155 | -29.83 | -23.2245 | -35.3626 | 518 | -34.1083 | -26.8438 | -28.0781 | -42.1265 | -22.412 | -30.0895 | -33.9418 | -25.7082 | -28.0025 | -41.1574 | -22.5029 | -31.1495 | -31.4808 | -26.5679 | -28.811 | -43.5898 | -22.0785 | -26.1033 | -31.3143 | -25.4323 | -28.7354 | -42.6207 | -22.1694 | -27.1633
519 | -9.6205 | 0 | -9.9037 | 0 | -10.5543 | 0 | -9.6244 | 0 | -34.6889 | 9.3294 | -22.9727 | 104.9568 | -42.2474 | 10.726 | -37.639 | 150.6102 | -50.4231 | -108.5682 | -37.7487 | 92.2653 | -32.3541 | 117.763 | -24.8509 | -138.9879 | -45.1436 | 117.1706 | -34.5176 | -96.5774 | -46.2543 | 41.5257 | -39.7136 | -86.5813 | -28.4405 | 73.0623 | -15.1064 | -149.5177 | -21.4459 | -93.066 | -37.308 | -92.8837 | -22.6789 | -8.7637 | -9.6868 | -68.4179 | -17.7955 | 4.5662 | -10.6004 | -25.2222 | -42.8427 | -41.1691 | -35.9774 | -37.0692 | -51.8387 | -32.337 | -40.6147 | -44.7262 | -35.8431 | -38.4193 | -54.4545 | -32.3903 | -36.4818 | 519 | -22.6418 | -32.8315 | -22.6892 | -36.2598 | -24.1062 | -30.1835 | -24.2795 | -37.929 | 519 | -35.1057 | -26.2226 | -27.4487 | -41.935 | -22.4333 | -30.0604 | -34.8225 | -25.2888 | -27.4448 | -41.2844 | -22.7126 | -30.9903 | -31.5486 | -26.3569 | -28.7988 | -44.5508 | -22.4866 | -25.9275 | -31.2654 | -25.4231 | -28.7949 | -43.9002 | -22.7659 | -26.8574
520 | -9.6652 | 0 | -10.0679 | 0 | -10.4895 | 0 | -9.6352 | 0 | -35.1125 | 6.5904 | -23.232 | 108.9976 | -43.734 | -2.0966 | -36.2173 | 146.6407 | -51.433 | -108.4764 | -40.8265 | 105.9548 | -33.2719 | 109.217 | -25.1181 | -134.0979 | -47.5805 | 114.5545 | -33.8824 | -93.9343 | -47.99 | 42.9128 | -39.059 | -64.4161 | -31.1017 | 45.1581 | -13.6548 | -167.783 | -23.5863 | -95.0127 | -29.8575 | -36.221 | -20.2211 | -6.9694 | -9.0623 | -76.3602 | -18.6112 | 6.5128 | -10.8366 | -25.8228 | -42.6084 | -41.5143 | -35.9518 | -37.5889 | -52.2139 | -32.612 | -40.5093 | -46.2473 | -35.6887 | -39.0523 | -55.4195 | -33.2082 | -36.4754 | 520 | -22.9229 | -32.5629 | -22.9476 | -38.7882 | -24.4786 | -30.4784 | -24.4241 | -38.0262 | 520 | -36.5821 | -26.0235 | -27.9237 | -42.146 | -22.5441 | -30.0198 | -36.1794 | -25.1992 | -27.9537 | -41.7244 | -22.9768 | -30.8741 | -31.8491 | -26.2866 | -29.3871 | -45.3516 | -23.1403 | -25.9859 | -31.4464 | -25.4623 | -29.4171 | -44.93 | -23.573 | -26.8402
521 | -9.691 | 0 | -10.152 | 0 | -10.5035 | 0 | -9.7028 | 0 | -35.0907 | 4.3303 | -22.0557 | 110.2755 | -47.0889 | -2.8904 | -35.8343 | 137.6442 | -52.3981 | -107.5773 | -39.122 | 124.412 | -34.1688 | 107.3073 | -23.6396 | -131.2977 | -47.9715 | 123.497 | -33.0095 | -97.3613 | -48.1399 | 50.6709 | -35.9614 | -65.1017 | -38.3421 | 39.874 | -13.2566 | 168.8265 | -24.9663 | -94.7192 | -24.2291 | -60.9504 | -18.6476 | -8.3709 | -9.0501 | -87.0746 | -18.3004 | 13.652 | -10.5003 | -26.9596 | -42.2002 | -41.0245 | -36.1885 | -38.837 | -52.5713 | -32.8526 | -40.4879 | -46.0973 | -36.0075 | -39.6559 | -55.1871 | -33.4918 | -36.9463 | 521 | -21.832 | -32.3927 | -21.7963 | -38.3059 | -23.2565 | -30.4655 | -22.9422 | -35.4557 | 521 | -36.4063 | -26.3165 | -29.146 | -42.4193 | -22.7006 | -29.9844 | -35.9453 | -25.504 | -29.1342 | -42.0678 | -23.1498 | -30.7851 | -31.3335 | -26.4975 | -29.9649 | -45.0351 | -23.3398 | -26.4428 | -30.8725 | -25.685 | -29.9531 | -44.6836 | -23.789 | -27.2435
522 | -9.7003 | 0 | -10.1291 | 0 | -10.6301 | 0 | -9.7732 | 0 | -34.8842 | -0.3659 | -20.7964 | 102.2228 | -47.5623 | 19.4348 | -35.9119 | 133.6502 | -51.2585 | -100.4938 | -36.4827 | 112.9172 | -34.2744 | 108.9459 | -22.099 | -138.8842 | -45.9534 | 123.113 | -32.4131 | -102.7106 | -46.7658 | 49.8192 | -34.5156 | -78.3518 | -38.4193 | 163.4373 | -14.2581 | 145.5481 | -23.7015 | -104.6161 | -21.6615 | -93.934 | -17.4249 | -12.4071 | -9.6397 | -97.5834 | -16.9885 | 13.375 | -10.0898 | -32.1015 | -42.0719 | -39.4322 | -36.565 | -40.2125 | -52.2399 | -32.897 | -40.6409 | -44.2394 | -36.5363 | -40.0666 | -54.4221 | -33.1144 | -37.6274 | 522 | -20.6214 | -32.3018 | -20.5524 | -36.0244 | -21.8267 | -30.139 | -21.4907 | -33.9795 | 522 | -34.5391 | -26.836 | -30.5122 | -42.1108 | -22.7679 | -30.0108 | -34.1103 | -25.9062 | -30.4393 | -41.6098 | -23.1238 | -30.8677 | -29.7319 | -26.8647 | -30.3663 | -44.293 | -22.9853 | -26.9973 | -29.3031 | -25.9349 | -30.2934 | -43.792 | -23.3412 | -27.8542
523 | -9.7116 | 0 | -10.0101 | 0 | -10.6753 | 0 | -9.785 | 0 | -34.6287 | -5.7154 | -20.2692 | 90.7826 | -45.3007 | 22.488 | -35.763 | 128.6328 | -48.7772 | -109.7966 | -36.4662 | 90.4936 | -33.5308 | 107.6828 | -21.4339 | -150.206 | -44.2381 | 107.7682 | -32.0364 | -109.3121 | -45.6351 | 40.071 | -34.5362 | -92.4257 | -29.141 | 149.7556 | -16.5109 | 124.2039 | -22.9955 | -126.6314 | -19.7373 | -130.8505 | -16.5163 | -17.1376 | -10.5901 | -105.6961 | -16.0687 | 5.8609 | -9.7858 | -38.8521 | -42.3161 | -37.9149 | -36.7989 | -40.8357 | -51.6169 | -32.9891 | -40.9241 | -42.5542 | -36.7116 | -40.1351 | -53.9163 | -32.5112 | -38.0358 | 523 | -20.0998 | -32.0552 | -20.0481 | -35.7125 | -21.1525 | -29.5998 | -20.8801 | -33.7999 | 523 | -32.8426 | -27 | -31.1241 | -41.6068 | -22.979 | -30.2488 | -32.5441 | -26.0363 | -31.0507 | -40.9416 | -23.2041 | -31.1391 | -28.2033 | -27.0873 | -30.4235 | -43.9062 | -22.5011 | -27.3605 | -27.9048 | -26.1236 | -30.3501 | -43.241 | -22.7262 | -28.2508
524 | -9.7529 | 0 | -9.8728 | 0 | -10.6158 | 0 | -9.7441 | 0 | -34.5228 | -12.9292 | -20.5932 | 79.1597 | -43.8029 | 21.932 | -35.6734 | 124.8028 | -47.6059 | -128.8958 | -39.4639 | 70.0143 | -32.7249 | 100.1738 | -21.6605 | -161.5204 | -43.8357 | 86.6294 | -32.0192 | -116.6326 | -45.4814 | 25.1269 | -35.4674 | -102.1089 | -24.7352 | 123.808 | -20.5674 | 113.7836 | -23.5699 | -155.4786 | -18.7925 | -162.4766 | -15.614 | -21.5578 | -11.7226 | -108.6973 | -15.8851 | -4.7919 | -10.2777 | -48.5389 | -42.8116 | -37.1483 | -36.7699 | -40.3428 | -51.1983 | -33.164 | -41.2556 | -42.0728 | -36.4912 | -39.986 | -53.8728 | -32.2993 | -38.0113 | 524 | -20.4011 | -31.9306 | -20.4061 | -37.6409 | -21.3089 | -29.2429 | -21.1155 | -34.5147 | 524 | -32.3199 | -26.7383 | -30.5899 | -41.3255 | -23.2912 | -30.6398 | -32.2 | -25.8754 | -30.5987 | -40.5825 | -23.4199 | -31.5115 | -27.3954 | -27.017 | -30.2331 | -44 | -22.4265 | -27.3955 | -27.2755 | -26.1541 | -30.2419 | -43.257 | -22.5552 | -28.2672
525 | -9.7859 | 0 | -9.7859 | 0 | -10.4929 | 0 | -9.657 | 0 | -34.8889 | -22.349 | -21.5926 | 72.7447 | -42.069 | 15.2405 | -35.5494 | 120.5882 | -47.6844 | -148.356 | -46.1856 | 71.8267 | -32.5844 | 88.2905 | -22.5711 | -168.6267 | -44.9866 | 65.8593 | -32.0908 | -121.5286 | -46.2881 | 11.5077 | -37.0961 | -106.8115 | -23.5384 | 98.4954 | -23.5484 | 136.5445 | -25.0785 | 178.8113 | -18.5074 | 171.2884 | -15.0435 | -27.0605 | -12.138 | -110.3056 | -16.8587 | -11.0396 | -11.3028 | -54.814 | -43.2716 | -37.0958 | -36.5216 | -39.6036 | -50.9825 | -33.4747 | -41.5242 | -43.032 | -36.0789 | -39.8328 | -53.9539 | -32.3406 | -37.5251 | 525 | -21.3569 | -32.0753 | -21.4069 | -39.8627 | -22.1358 | -29.2339 | -21.9756 | -36.0139 | 525 | -33.2461 | -26.293 | -29.8177 | -41.1966 | -23.6888 | -31.0313 | -33.2461 | -25.586 | -29.9466 | -40.4896 | -23.8177 | -31.8672 | -27.3099 | -26.7357 | -30.0469 | -44.168 | -22.5547 | -27.0322 | -27.3099 | -26.0287 | -30.1758 | -43.461 | -22.6836 | -27.8681
526 | -9.822 | 0 | -9.7906 | 0 | -10.3796 | 0 | -9.5735 | 0 | -35.5637 | -27.2056 | -22.3513 | 74.7256 | -40.8991 | 4.4269 | -35.1356 | 117.5675 | -48.6443 | -164.9862 | -46.3161 | 134.3103 | -33.4074 | 78.0689 | -23.2478 | -166.0566 | -47.6094 | 51.483 | -32.1272 | -126.8309 | -47.8395 | 2.2924 | -37.8906 | -97.9381 | -24.7531 | 71.1547 | -19.9722 | 147.236 | -27.3356 | 164.3584 | -19.0396 | 153.3375 | -14.6421 | -32.3723 | -12.1107 | -113.5096 | -17.6716 | -9.7663 | -12.8836 | -57.2094 | -43.6044 | -37.4669 | -36.2842 | -39.3622 | -51.1161 | -33.9122 | -41.564 | -44.8562 | -35.8454 | -39.9078 | -54.4273 | -32.7546 | -37.3844 | 526 | -22.0913 | -32.2337 | -22.1118 | -39.2694 | -22.8337 | -29.6437 | -22.5891 | -37.0704 | 526 | -35.0342 | -26.0234 | -29.5402 | -41.3255 | -24.1216 | -31.1844 | -35.0656 | -25.4658 | -29.7887 | -40.7365 | -24.3387 | -31.9905 | -27.6449 | -26.4622 | -30.0858 | -44.6367 | -22.964 | -27.0048 | -27.6763 | -25.9046 | -30.3343 | -44.0477 | -23.1811 | -27.8109
527 | -9.8611 | 0 | -9.8569 | 0 | -10.3958 | 0 | -9.5525 | 0 | -35.8728 | -29.4291 | -21.4638 | 76.6377 | -40.441 | -6.6435 | -34.8491 | 110.5626 | -50.4148 | -173.0461 | -39.9114 | 136.3547 | -34.7801 | 73.9625 | -22.3624 | -164.2558 | -51.3607 | 62.3011 | -32.271 | -130.8614 | -49.2707 | 4.2221 | -36.6378 | -94.5161 | -29.0709 | 57.4295 | -17.6777 | 129.615 | -27.6239 | 166.2462 | -19.5398 | 148.7368 | -14.3301 | -37.1697 | -12.1497 | -120.8738 | -17.0648 | -7.7601 | -13.6252 | -51.5541 | -43.3915 | -37.6705 | -36.2354 | -39.7728 | -51.5612 | -34.398 | -41.287 | -44.3202 | -35.9774 | -40.5277 | -55.0153 | -33.2178 | -37.7635 | 527 | -21.2565 | -32.2537 | -21.2101 | -36.9574 | -22.1152 | -30.2814 | -21.7953 | -36.2705 | 527 | -34.4591 | -26.1163 | -29.9117 | -41.7043 | -24.5411 | -30.8912 | -34.4633 | -25.5816 | -30.2203 | -41.1654 | -24.8455 | -31.7345 | -27.8094 | -26.3743 | -30.6666 | -45.1584 | -23.3609 | -27.3677 | -27.8136 | -25.8396 | -30.9752 | -44.6195 | -23.6653 | -28.211
528 | -9.8797 | 0 | -9.8963 | 0 | -10.477 | 0 | -9.573 | 0 | -35.7929 | -32.9201 | -20.2282 | 71.0617 | -40.488 | -16.1847 | -34.9277 | 103.9856 | -51.7444 | -169.7138 | -37.0426 | 118.0494 | -35.6323 | 75.9268 | -21.1064 | -168.4144 | -50.3428 | 85.7788 | -32.1691 | -134.6357 | -49.1701 | 7.7611 | -35.2516 | -100.0291 | -36.286 | 94.8098 | -16.7784 | 109.3796 | -25.5423 | 165.2296 | -18.6547 | 149.6824 | -14.135 | -41.9118 | -12.5375 | -129.291 | -16.0992 | -11.4896 | -13.2403 | -48.4026 | -43.1138 | -37.3873 | -36.4418 | -40.5323 | -51.8895 | -34.5819 | -41.0974 | -42.1548 | -36.3469 | -41.2619 | -55.089 | -33.3951 | -38.3652 | 528 | -20.0696 | -32.2791 | -19.9969 | -35.3218 | -20.9509 | -30.4946 | -20.6267 | -34.9516 | 528 | -32.2751 | -26.4672 | -30.6526 | -41.9932 | -24.6856 | -30.6204 | -32.2585 | -25.8699 | -30.9593 | -41.4125 | -25.0089 | -31.5244 | -27.5076 | -26.5621 | -31.3822 | -45.1927 | -23.4988 | -27.8882 | -27.491 | -25.9648 | -31.6889 | -44.612 | -23.8221 | -28.7922
529 | -9.8806 | 0 | -9.8572 | 0 | -10.5994 | 0 | -9.6111 | 0 | -35.5692 | -37.9895 | -19.4304 | 61.2175 | -40.5484 | -23.9993 | -35.1351 | 99.6843 | -50.873 | -160.8997 | -36.2989 | 94.3512 | -35.4383 | 79.2067 | -20.2419 | -178.4426 | -46.1543 | 87.7085 | -31.8938 | -138.837 | -47.9889 | 5.9061 | -34.857 | -111.544 | -28.2223 | 140.5659 | -17.0668 | 88.1394 | -22.3719 | 154.4682 | -16.8333 | 145.8729 | -13.8645 | -46.1615 | -13.2641 | -137.5814 | -15.4266 | -20.5499 | -12.3005 | -50.4789 | -43.1202 | -36.6631 | -36.792 | -41.3077 | -51.8428 | -34.4756 | -41.1267 | -40.0916 | -36.7869 | -41.7244 | -55.0252 | -33.2713 | -38.9827 | 529 | -19.2934 | -32.276 | -19.2291 | -34.8044 | -20.1018 | -30.2304 | -19.8165 | -34.354 | 529 | -30.211 | -26.9063 | -31.4271 | -41.9856 | -24.6184 | -30.5273 | -30.2344 | -26.1875 | -31.6966 | -41.2434 | -24.8645 | -31.5156 | -26.7825 | -26.9114 | -31.8438 | -45.168 | -23.4141 | -28.3833 | -26.8059 | -26.1926 | -32.1133 | -44.4258 | -23.6602 | -29.3716
530 | -9.9166 | 0 | -9.7778 | 0 | -10.6034 | 0 | -9.6585 | 0 | -35.583 | -46.2614 | -19.6149 | 49.294 | -40.6207 | -28.3197 | -35.1174 | 96.2537 | -48.367 | -167.3893 | -38.3822 | 75.6669 | -34.5173 | 75.2302 | -20.3118 | 169.9839 | -44.0659 | 66.2357 | -31.8233 | -144.8624 | -47.1947 | -5.7911 | -35.6482 | -122.4917 | -24.0422 | 122.9371 | -19.4976 | 71.787 | -19.9175 | 134.9529 | -14.9816 | 134.8017 | -13.7871 | -50.317 | -14.153 | -142.8154 | -15.9053 | -32.9677 | -11.9824 | -59.6275 | -43.4978 | -35.9718 | -37.0155 | -41.4392 | -51.6345 | -34.3742 | -41.4224 | -39.2948 | -36.858 | -41.9028 | -55.5669 | -33.1698 | -39.1039 | 530 | -19.4729 | -32.2267 | -19.4385 | -36.0839 | -20.1324 | -29.8732 | -19.8984 | -34.806 | 530 | -29.3782 | -26.9414 | -31.5226 | -41.8567 | -24.5964 | -30.819 | -29.517 | -26.2546 | -31.7807 | -41.0311 | -24.7157 | -31.7639 | -26.0552 | -27.0989 | -31.9862 | -45.7891 | -23.392 | -28.5005 | -26.194 | -26.4121 | -32.2443 | -44.9635 | -23.5113 | -29.4454
531 | -9.9481 | 0 | -9.6934 | 0 | -10.5247 | 0 | -9.6588 | 0 | -35.9896 | -54.6199 | -20.548 | 40.8271 | -40.3771 | -31.3933 | -34.9883 | 92.1245 | -46.8568 | 177.5715 | -41.9385 | 71.7115 | -34.0904 | 66.0966 | -21.1874 | 161.2807 | -44.0734 | 45.5966 | -31.948 | -150.6064 | -47.0529 | -20.4078 | -37.2874 | -125.8459 | -23.2203 | 102.6566 | -23.0007 | 76.152 | -19.1674 | 115.9276 | -13.9324 | 122.3853 | -13.6984 | -52.7171 | -14.9943 | -146.0876 | -17.2228 | -41.7846 | -12.6182 | -69.8455 | -44.0814 | -35.9165 | -36.965 | -41.2142 | -51.5384 | -34.4947 | -41.6661 | -39.8763 | -36.62 | -42.0215 | -56.0606 | -33.302 | -38.7087 | 531 | -20.382 | -32.2952 | -20.3642 | -37.5375 | -20.9491 | -29.7957 | -20.7401 | -36.0976 | 531 | -29.9282 | -26.6719 | -31.2661 | -41.845 | -24.8013 | -31.1414 | -30.1829 | -26.0953 | -31.5554 | -41.0137 | -24.8359 | -32.0073 | -25.9684 | -27.0169 | -32.0734 | -46.3672 | -23.6086 | -28.184 | -26.2231 | -26.4403 | -32.3627 | -45.5359 | -23.6432 | -29.0499
532 | -10.0055 | 0 | -9.6939 | 0 | -10.4014 | 0 | -9.627 | 0 | -36.7517 | -61.963 | -21.5541 | 40.0503 | -39.8178 | -36.7154 | -34.7799 | 86.5953 | -46.1697 | 160.9212 | -44.7089 | 94.5174 | -34.545 | 55.5404 | -22.1875 | 161.7657 | -44.8719 | 31.992 | -32.0894 | -155.1018 | -47.9747 | -37.3277 | -38.3432 | -118.0135 | -26.4245 | 87.5948 | -22.3088 | 98.977 | -19.6157 | 100.4032 | -13.7576 | 111.0727 | -13.3397 | -55.4787 | -14.9837 | -148.037 | -19.0184 | -43.1019 | -14.2375 | -73.614 | -44.4373 | -36.1956 | -36.7606 | -41.0389 | -51.3865 | -34.8167 | -41.7955 | -41.3624 | -36.3531 | -42.1392 | -56.1314 | -33.6475 | -38.2298 | 532 | -21.3624 | -32.4558 | -21.3322 | -37.898 | -21.9201 | -30.0648 | -21.6701 | -37.1006 | 532 | -31.3569 | -26.3476 | -31.0334 | -41.6926 | -25.1228 | -31.3941 | -31.6685 | -25.9517 | -31.4119 | -40.9851 | -25.1897 | -32.1685 | -26.1901 | -26.7551 | -32.1337 | -46.4375 | -23.9536 | -27.8284 | -26.5017 | -26.3592 | -32.5122 | -45.73 | -24.0205 | -28.6028
533 | -10.0729 | 0 | -9.7408 | 0 | -10.3307 | 0 | -9.5885 | 0 | -37.5105 | -64.9958 | -21.3014 | 43.4496 | -38.9888 | -43.3112 | -34.8221 | 80.261 | -46.3827 | 144.8224 | -41.645 | 115.2208 | -35.7586 | 48.5536 | -21.8693 | 166.8671 | -46.1289 | 22.1482 | -32.3713 | -159.954 | -50.477 | -49.7717 | -37.375 | -110.5444 | -31.2497 | 133.4301 | -18.6316 | 98.4158 | -20.2864 | 95.2153 | -13.9831 | 102.8555 | -12.7751 | -58.6538 | -15.1738 | -154.8024 | -19.6735 | -37.0645 | -16.1327 | -69.2773 | -44.5077 | -36.2069 | -36.5936 | -41.1561 | -51.2108 | -35.3123 | -41.6666 | -41.5729 | -36.2213 | -42.3151 | -55.8815 | -34.2018 | -38.4051 | 533 | -21.127 | -32.7585 | -21.0742 | -36.6217 | -21.6798 | -30.6866 | -21.3879 | -36.6481 | 533 | -31.5 | -26.1484 | -31.0832 | -41.47 | -25.5715 | -31.3359 | -31.8321 | -25.8906 | -31.5676 | -40.8801 | -25.7238 | -32.0781 | -26.134 | -26.5207 | -32.2422 | -46.1407 | -24.461 | -28.0744 | -26.4661 | -26.2629 | -32.7266 | -45.5508 | -24.6133 | -28.8166
534 | -10.165 | 0 | -9.7668 | 0 | -10.3412 | 0 | -9.5959 | 0 | -37.7644 | -67.3279 | -20.0191 | 40.5461 | -38.7314 | -54.3089 | -35.2327 | 75.4034 | -47.533 | 133.9561 | -38.8135 | 108.6947 | -37.0226 | 47.842 | -20.5028 | 163.5034 | -47.6758 | 24.7783 | -32.6172 | -162.8869 | -53.8677 | -43.5692 | -35.6634 | -113.4044 | -23.2835 | 164.1572 | -16.8846 | 82.8949 | -20.4657 | 96.794 | -14.1141 | 101.2661 | -12.1796 | -65.0067 | -15.4356 | -164.2374 | -18.9748 | -35.6073 | -16.2317 | -58.4395 | -44.1703 | -35.7213 | -36.6623 | -41.5336 | -51.1664 | -36.026 | -41.341 | -39.7162 | -36.3134 | -42.8566 | -55.7668 | -34.681 | -39.0757 | 534 | -19.8896 | -33.1452 | -19.835 | -35.4823 | -20.3989 | -31.2496 | -20.1209 | -35.3371 | 534 | -29.5512 | -26.1484 | -31.3686 | -41.3996 | -26.2592 | -30.9998 | -29.9494 | -25.9722 | -31.9377 | -40.8252 | -26.4301 | -31.7451 | -25.5563 | -26.4973 | -32.6916 | -46 | -24.9142 | -28.7345 | -25.9545 | -26.3211 | -33.2607 | -45.4256 | -25.0851 | -29.4798
535 | -10.2342 | 0 | -9.7353 | 0 | -10.4313 | 0 | -9.6399 | 0 | -37.5962 | -71.2159 | -19.173 | 30.5392 | -38.8089 | -61.3799 | -35.5417 | 74.1807 | -48.034 | 134.5492 | -37.6742 | 95.3927 | -37.1822 | 51.3574 | -19.5155 | 154.4916 | -45.8143 | 31.6875 | -32.3453 | -164.1365 | -53.2075 | -23.2885 | -34.6408 | -125.4365 | -18.3213 | 150.4073 | -16.6336 | 65.9195 | -19.1773 | 96.4666 | -13.4055 | 101.3176 | -11.8715 | -73.441 | -16.1813 | -174.1031 | -18.4527 | -41.2862 | -14.6341 | -56.8605 | -43.9591 | -35.0731 | -36.9893 | -42.0216 | -51.2755 | -36.4716 | -41.204 | -38.0641 | -36.6912 | -43.5908 | -55.7822 | -34.9704 | -40.0134 | 535 | -19.0647 | -33.2901 | -19.0144 | -34.9741 | -19.4318 | -31.0855 | -19.1698 | -34.2656 | 535 | -27.8299 | -26.457 | -31.7874 | -41.5402 | -26.7363 | -30.7727 | -28.3288 | -26.2599 | -32.3817 | -40.8442 | -26.8317 | -31.5641 | -24.8389 | -26.7551 | -33.3566 | -46.0469 | -25.2351 | -29.5821 | -25.3378 | -26.558 | -33.9509 | -45.3509 | -25.3305 | -30.3735
536 | -10.2773 | 0 | -9.6817 | 0 | -10.4621 | 0 | -9.7244 | 0 | -37.5288 | -78.3651 | -19.2617 | 17.0079 | -38.5619 | -68.95 | -35.3534 | 72.6782 | -46.9584 | 132.8548 | -38.0503 | 82.536 | -36.4697 | 49.4197 | -19.4122 | 142.9615 | -43.5788 | 18.0611 | -31.9349 | -169.0766 | -50.6997 | -23.566 | -35.1383 | -138.1513 | -16.1076 | 132.6687 | -17.6007 | 53.6757 | -17.8829 | 89.0161 | -12.3111 | 96.014 | -12.1285 | -82.3721 | -17.2744 | 178.8063 | -18.6141 | -50.8669 | -13.469 | -65.7693 | -44.3196 | -34.6782 | -37.466 | -42.2727 | -51.4563 | -36.5024 | -41.4434 | -37.2864 | -37.0156 | -44.1582 | -56.2246 | -34.9426 | -40.927 | 536 | -19.1475 | -33.113 | -19.1005 | -35.0023 | -19.3112 | -30.5827 | -19.0671 | -34.4528 | 536 | -27.0091 | -26.7383 | -31.9954 | -41.7746 | -26.8207 | -30.9813 | -27.6047 | -26.5535 | -32.5483 | -40.9942 | -26.778 | -31.719 | -24.4009 | -27.1887 | -33.8809 | -46.5429 | -25.2609 | -30.4649 | -24.9965 | -27.0039 | -34.4338 | -45.7625 | -25.2182 | -31.2026
537 | -10.261 | 0 | -9.636 | 0 | -10.4251 | 0 | -9.7688 | 0 | -37.749 | -87.6767 | -20.186 | 9.4409 | -38.6241 | -76.7582 | -34.9004 | 67.9534 | -45.6832 | 127.1373 | -39.6119 | 78.8848 | -36.0614 | 41.3802 | -20.1295 | 132.6157 | -42.9943 | -1.8281 | -31.7636 | -176.9266 | -48.8725 | -34.6813 | -36.8084 | -145.4877 | -15.576 | 117.6659 | -19.118 | 52.612 | -17.4793 | 79.1761 | -11.5569 | 87.5305 | -12.8275 | -88.5437 | -18.5617 | 173.2838 | -19.5918 | -58.3994 | -13.3535 | -78.4502 | -44.9888 | -34.852 | -37.6645 | -42.3208 | -51.7036 | -36.4067 | -41.8079 | -37.4602 | -37.0227 | -44.6321 | -56.9407 | -35.1438 | -41.5461 | 537 | -20.0498 | -32.8525 | -19.9941 | -35.6282 | -19.9982 | -30.3298 | -19.7547 | -35.6595 | 537 | -27.1992 | -26.7617 | -32.0598 | -42.0676 | -26.7707 | -31.3828 | -27.8242 | -26.5976 | -32.552 | -41.2785 | -26.6379 | -32.0391 | -24.591 | -27.4035 | -34.3711 | -47.3047 | -25.5078 | -31.121 | -25.216 | -27.2394 | -34.8633 | -46.5156 | -25.375 | -31.7773
538 | -10.2656 | 0 | -9.61 | 0 | -10.3443 | 0 | -9.7628 | 0 | -38.2499 | -96.6173 | -21.4262 | 6.5654 | -38.5258 | -84.396 | -34.5408 | 61.0668 | -44.6164 | 114.2967 | -40.2933 | 86.0756 | -36.4898 | 31.6155 | -21.2241 | 130.4924 | -43.4449 | -20.1479 | -31.8562 | 175.9914 | -48.0884 | -50.7832 | -38.1911 | -140.2333 | -16.2782 | 110.5993 | -19.278 | 60.6679 | -18.2889 | 70.7155 | -11.6235 | 78.3264 | -13.6637 | -88.732 | -19.3118 | 173.0795 | -20.8321 | -60.8601 | -14.2634 | -89.851 | -45.6463 | -35.5135 | -37.5402 | -42.4588 | -51.9705 | -36.4431 | -41.985 | -38.2584 | -36.8749 | -45.028 | -57.3287 | -35.5084 | -41.7583 | 538 | -21.2547 | -32.7111 | -21.1658 | -35.7117 | -21.0716 | -30.4957 | -20.7844 | -36.7277 | 538 | -27.9928 | -26.6093 | -32.1932 | -42.3605 | -26.8331 | -31.6407 | -28.6484 | -26.5306 | -32.696 | -41.6262 | -26.6803 | -32.2222 | -25.2479 | -27.2746 | -34.7624 | -47.7187 | -25.8984 | -31.414 | -25.9035 | -27.1959 | -35.2652 | -46.9844 | -25.7456 | -31.9955
539 | -10.3436 | 0 | -9.6448 | 0 | -10.2779 | 0 | -9.7104 | 0 | -39.0227 | -104.25 | -21.6636 | 11.1869 | -38.4975 | -94.1994 | -34.7373 | 52.0789 | -44.2632 | 99.8979 | -39.1354 | 93.1122 | -37.7071 | 24.5854 | -21.39 | 133.8434 | -44.9802 | -38.4174 | -32.2264 | 168.7067 | -48.3973 | -67.0917 | -37.8402 | -131.2753 | -16.301 | 116.1604 | -17.7889 | 62.8648 | -19.141 | 73.3419 | -12.0802 | 71.7868 | -13.5202 | -85.5722 | -19.3414 | 168.7951 | -21.3019 | -60.5452 | -15.9573 | -96.5966 | -45.8452 | -35.7518 | -37.251 | -42.8256 | -52.0756 | -36.7518 | -42.0315 | -38.3365 | -36.6951 | -45.3088 | -56.844 | -36.0748 | -41.8442 | 539 | -21.497 | -33.022 | -21.3812 | -35.2167 | -21.2712 | -31.0628 | -20.9559 | -36.7642 | 539 | -27.9929 | -26.3515 | -32.482 | -42.4308 | -27.107 | -31.7536 | -28.6917 | -26.4172 | -33.1152 | -41.7977 | -27.0414 | -32.3211 | -25.4082 | -26.9074 | -34.9652 | -47.1992 | -26.43 | -31.5663 | -26.107 | -26.9731 | -35.5984 | -46.5661 | -26.3644 | -32.1338
540 | -10.5199 | 0 | -9.6523 | 0 | -10.2715 | 0 | -9.679 | 0 | -39.8303 | -111.5824 | -20.5785 | 11.0486 | -39.2683 | -104.8088 | -35.5925 | 45.2939 | -44.6232 | 86.7318 | -37.2794 | 90.3816 | -39.0393 | 22.0817 | -20.2515 | 133.2289 | -48.401 | -47.4611 | -32.773 | 164.0371 | -49.2942 | -79.5998 | -36.3179 | -131.7555 | -14.5192 | 119.5156 | -16.5234 | 56.328 | -18.7228 | 80.469 | -12.8968 | 71.2296 | -12.4081 | -86.4674 | -19.0839 | 162.927 | -21.3048 | -63.4113 | -17.3068 | -92.2585 | -45.6418 | -35.1125 | -37.0172 | -43.3019 | -51.9543 | -37.3078 | -42.0625 | -37.0332 | -36.6723 | -45.4726 | -55.9375 | -36.5879 | -42.3337 | 540 | -20.4696 | -33.8261 | -20.3546 | -34.6861 | -20.1879 | -31.7744 | -19.9145 | -35.8557 | 540 | -26.5133 | -26.1524 | -32.782 | -42.302 | -27.6555 | -31.791 | -27.3809 | -26.4008 | -33.6229 | -41.6828 | -27.6288 | -32.3835 | -24.5926 | -26.4973 | -34.9527 | -46.2852 | -26.9356 | -32.0622 | -25.4602 | -26.7457 | -35.7936 | -45.666 | -26.9089 | -32.6547
541 | -10.6951 | 0 | -9.6365 | 0 | -10.3318 | 0 | -9.7107 | 0 | -40.5716 | -118.5903 | -19.6185 | 2.6917 | -40.3388 | -109.8948 | -36.392 | 45.788 | -45.4357 | 78.6504 | -35.8186 | 78.7824 | -39.7583 | 25.1055 | -19.2179 | 124.9713 | -50.0028 | -30.5431 | -33.0745 | 161.9307 | -50.2963 | -86.9537 | -35.2431 | -140.4779 | -12.5932 | 111.8452 | -16.1595 | 46.2395 | -17.3149 | 79.357 | -12.9895 | 74.2079 | -11.4851 | -93.6674 | -19.162 | 150.7379 | -21.6135 | -71.9131 | -16.7966 | -88.6252 | -45.4268 | -34.1846 | -37.0752 | -43.7549 | -51.5752 | -38.0518 | -42.0936 | -35.8357 | -36.8943 | -45.7615 | -55.6717 | -37.0115 | -43.2066 | 541 | -19.5474 | -34.612 | -19.4273 | -34.168 | -19.1761 | -32.1629 | -18.9398 | -34.971 | 541 | -25.1406 | -26.1992 | -33.0598 | -41.9387 | -28.4153 | -31.7618 | -26.1992 | -26.5625 | -34.0442 | -41.2434 | -28.3411 | -32.3829 | -23.4895 | -26.3801 | -35.0664 | -46.0352 | -27.375 | -32.8748 | -24.5481 | -26.7434 | -36.0508 | -45.3399 | -27.3008 | -33.4959
542 | -10.8242 | 0 | -9.6307 | 0 | -10.3666 | 0 | -9.7738 | 0 | -41.2206 | -124.8763 | -19.4654 | -8.8647 | -41.3797 | -110.8431 | -36.2413 | 47.7403 | -45.7676 | 77.0362 | -35.767 | 64.5146 | -39.3354 | 26.809 | -18.9592 | 114.3611 | -47.8036 | -30.0281 | -32.9682 | 159.4869 | -50.7324 | -90.3191 | -35.4126 | -151.2648 | -11.5544 | 100.9952 | -16.4464 | 40.2551 | -16.3613 | 73.7881 | -11.9113 | 74.7427 | -11.0952 | -103.4286 | -19.9202 | 139.0145 | -22.6743 | -81.299 | -15.6705 | -93.7763 | -45.5147 | -33.606 | -37.3801 | -44.046 | -51.253 | -38.4771 | -42.2752 | -35.4369 | -37.2578 | -46.3182 | -56.4549 | -37.1634 | -44.4639 | 542 | -19.4088 | -34.6902 | -19.2766 | -34.3852 | -18.9139 | -32.0076 | -18.6965 | -35.0501 | 542 | -24.6127 | -26.4336 | -33.2218 | -41.6223 | -28.8464 | -31.9086 | -25.8062 | -26.8912 | -34.2722 | -40.8864 | -28.7033 | -32.5014 | -22.7818 | -26.5559 | -35.494 | -46.8242 | -27.5327 | -34.0973 | -23.9753 | -27.0135 | -36.5444 | -46.0883 | -27.3896 | -34.6901
543 | -10.8481 | 0 | -9.6069 | 0 | -10.3528 | 0 | -9.8649 | 0 | -41.8482 | -133.2671 | -20.1809 | -19.1015 | -41.4106 | -103.6567 | -35.4612 | 45.71 | -45.1882 | 74.7614 | -36.8213 | 54.9176 | -38.8147 | 21.5289 | -19.5571 | 103.7557 | -46.9213 | -44.5548 | -32.7351 | 155.0247 | -50.2978 | -95.4697 | -36.4845 | -156.7334 | -11.6684 | 89.9388 | -16.8814 | 39.1872 | -16.3761 | 66.6079 | -10.9704 | 69.952 | -11.3702 | -111.8195 | -21.4336 | 132.6361 | -24.2321 | -86.7801 | -15.4672 | -105.4605 | -45.9831 | -33.6391 | -37.6305 | -44.3737 | -51.1472 | -38.5571 | -42.5796 | -35.9504 | -37.4223 | -46.9897 | -57.771 | -37.3293 | -46.1414 | 543 | -20.119 | -34.2023 | -19.9635 | -35.08 | -19.498 | -31.7171 | -19.2698 | -35.9461 | 543 | -25.1023 | -26.5742 | -33.5256 | -41.5403 | -28.9502 | -32.2268 | -26.3435 | -27.0695 | -34.5088 | -40.7944 | -28.6922 | -32.7147 | -22.791 | -26.7824 | -36.1416 | -48.1641 | -27.7224 | -35.7886 | -24.0322 | -27.2777 | -37.1248 | -47.4182 | -27.4644 | -36.2765
544 | -10.8153 | 0 | -9.6249 | 0 | -10.316 | 0 | -9.9233 | 0 | -42.8032 | -144.573 | -21.4436 | -24.3026 | -39.8962 | -103.8982 | -34.8671 | 37.9858 | -44.3331 | 68.6507 | -38.195 | 51.8361 | -38.8584 | 12.9464 | -20.685 | 97.5608 | -47.9631 | -64.4518 | -32.6417 | 147.2562 | -49.5567 | -106.5049 | -37.4091 | -155.2011 | -12.5701 | 86.2455 | -16.4883 | 41.899 | -16.8251 | 64.1096 | -10.6618 | 62.9011 | -11.9707 | -115.8754 | -22.3542 | 134.2968 | -25.6784 | -83.1093 | -16.1459 | -120.9092 | -46.0831 | -34.075 | -37.5861 | -44.755 | -51.3292 | -38.6375 | -42.9725 | -37.0309 | -37.3661 | -47.8319 | -58.0116 | -37.5973 | -47.5617 | 544 | -21.3508 | -33.8157 | -21.1636 | -35.3637 | -20.6114 | -31.6404 | -20.3307 | -36.8059 | 544 | -26.2156 | -26.5508 | -33.9397 | -41.7043 | -29.0126 | -32.6565 | -27.406 | -27.0501 | -34.8317 | -41.0132 | -28.7142 | -33.0492 | -23.2597 | -26.7708 | -37.0166 | -48.3867 | -27.9724 | -37.2457 | -24.4501 | -27.2701 | -37.9086 | -47.6956 | -27.674 | -37.6384
545 | -10.9294 | 0 | -9.6662 | 0 | -10.3088 | 0 | -9.928 | 0 | -44.4175 | -156.9575 | -21.9363 | -22.4736 | -38.5618 | -112.6697 | -35.1276 | 27.8806 | -43.6483 | 57.8181 | -38.602 | 57.0503 | -39.4624 | 2.7574 | -21.0931 | 99.7588 | -53.0419 | -74.5471 | -32.9374 | 139.4498 | -49.0611 | -120.3331 | -37.0876 | -149.7421 | -12.5365 | 91.817 | -15.5625 | 39.1685 | -16.4414 | 67.008 | -10.8293 | 56.8317 | -11.7881 | -116.1278 | -21.3385 | 134.4637 | -25.1854 | -82.7994 | -17.949 | -131.9345 | -45.6278 | -34.019 | -37.3641 | -45.0554 | -51.9095 | -38.8973 | -43.5691 | -37.1505 | -37.381 | -48.5238 | -56.534 | -38.008 | -48.3731 | 545 | -21.8189 | -34.1296 | -21.6445 | -34.9431 | -21.0276 | -31.9787 | -20.7166 | -36.7179 | 545 | -26.2211 | -26.4516 | -34.126 | -42.2433 | -29.2311 | -33.2603 | -27.4843 | -27.0722 | -35.1274 | -41.6007 | -28.9693 | -33.6411 | -23.0896 | -26.4347 | -37.5944 | -46.8678 | -28.3418 | -38.0643 | -24.3528 | -27.0553 | -38.5958 | -46.2252 | -28.08 | -38.4451
546 | -11.2109 | 0 | -9.7063 | 0 | -10.3517 | 0 | -9.9213 | 0 | -46.4595 | -167.2953 | -21.4478 | -21.5362 | -37.9965 | -126.1062 | -36.0285 | 21.4757 | -43.3676 | 47.0707 | -37.8201 | 60.1472 | -40.686 | -8.1003 | -20.5908 | 99.5561 | -56.2803 | -35.8863 | -33.5444 | 132.8122 | -48.9986 | -137.8403 | -36.0638 | -150.0465 | -11.1512 | 94.7347 | -14.7063 | 34.221 | -15.4641 | 66.2829 | -11.2211 | 54.1678 | -10.854 | -119.0053 | -20.0563 | 127.8179 | -24.1525 | -92.6512 | -20.004 | -133.3831 | -45.056 | -33.333 | -37.2392 | -45.1918 | -52.7048 | -39.4646 | -44.0997 | -36.0419 | -37.544 | -49.015 | -55.0389 | -38.5278 | -48.9811 | 546 | -21.3393 | -34.9731 | -21.2034 | -34.3196 | -20.5474 | -32.6751 | -20.2605 | -35.8091 | 546 | -24.831 | -26.3331 | -33.9809 | -42.9985 | -29.7583 | -33.748 | -26.3356 | -27.1923 | -35.2705 | -42.3531 | -29.5433 | -34.1784 | -22.1221 | -26.0283 | -37.8041 | -45.3326 | -28.8215 | -38.6294 | -23.6267 | -26.8875 | -39.0937 | -44.6872 | -28.6065 | -39.0598
547 | -11.5831 | 0 | -9.7319 | 0 | -10.4012 | 0 | -9.9561 | 0 | -48.8002 | -178.0543 | -20.6337 | -25.2476 | -38.2477 | -140.1829 | -37.1596 | 19.7996 | -43.5382 | 36.5407 | -36.6083 | 55.2502 | -42.6645 | -16.9026 | -19.7866 | 94.809 | -50.5505 | -2.4607 | -34.3453 | 127.5582 | -49.5094 | -154.8587 | -35.0921 | -155.685 | -9.4184 | 90.3319 | -14.2373 | 26.6665 | -14.3743 | 61.3812 | -11.5904 | 55.0199 | -9.7387 | -126.6394 | -18.9186 | 113.7473 | -23.4072 | -110.35 | -21.3012 | -121.8532 | -44.6745 | -32.3478 | -37.2679 | -45.2409 | -53.4714 | -40.1681 | -44.4468 | -34.5536 | -37.7823 | -49.4897 | -53.8764 | -38.9637 | -49.5882 | 547 | -20.5526 | -36.0243 | -20.4321 | -33.8475 | -19.7606 | -33.6349 | -19.5152 | -34.8202 | 547 | -22.9705 | -26.1992 | -33.6578 | -43.7395 | -30.4362 | -34.0456 | -24.8217 | -27.3811 | -35.2848 | -43.0702 | -30.212 | -34.4907 | -20.7647 | -25.6848 | -37.9066 | -44.1445 | -29.2318 | -39.187 | -22.6159 | -26.8667 | -39.5336 | -43.4752 | -29.0076 | -39.6321
548 | -11.8567 | 0 | -9.7104 | 0 | -10.4142 | 0 | -10.0366 | 0 | -51.7219 | 170.7557 | -20.3393 | -35.3521 | -39.4552 | -148.5871 | -37.1728 | 24.9874 | -44.1631 | 29.3274 | -36.0887 | 46.6016 | -45.0086 | -18.8775 | -19.5025 | 85.0144 | -47.4987 | -23.0613 | -34.9827 | 126.1338 | -50.5329 | -170.0816 | -34.8092 | -162.0477 | -8.4031 | 79.2771 | -14.1269 | 18.8965 | -13.9164 | 52.1633 | -10.8399 | 54.5666 | -9.1691 | -137.3293 | -18.9959 | 95.4568 | -23.9826 | -134.5217 | -19.1407 | -121.7547 | -44.7351 | -31.7514 | -37.5337 | -45.489 | -53.8015 | -40.9116 | -44.4722 | -33.6955 | -38.0559 | -50.1167 | -53.3823 | -39.3283 | -50.273 | 548 | -20.2833 | -36.2559 | -20.1384 | -34.0031 | -19.4834 | -34.4624 | -19.2585 | -34.4725 | 548 | -21.8388 | -26.1992 | -33.6323 | -44.0911 | -31.2012 | -34.058 | -23.9851 | -27.6417 | -35.4524 | -43.3873 | -30.875 | -34.4356 | -19.8947 | -25.677 | -38.26 | -43.6719 | -29.6179 | -39.8588 | -22.041 | -27.1195 | -40.0801 | -42.9681 | -29.2917 | -40.2364
549 | -11.8717 | 0 | -9.6842 | 0 | -10.3795 | 0 | -10.1803 | 0 | -55.9947 | 154.9616 | -20.7164 | -45.3943 | -40.4827 | -151.6286 | -36.2614 | 23.2654 | -44.4703 | 25.0215 | -36.4248 | 36.1243 | -47.4506 | -18.6492 | -19.889 | 76.2419 | -47.0756 | -38.9365 | -35.1676 | 124.0357 | -51.5404 | 178.2927 | -34.9635 | -168.1453 | -8.2588 | 67.8006 | -14.2848 | 12.8977 | -14.3157 | 44.0037 | -10.0083 | 50.3402 | -9.2843 | -150.3019 | -20.014 | 77.1672 | -25.4654 | -160.33 | -17.5923 | -138.0558 | -44.8846 | -31.6932 | -37.8182 | -46.0135 | -53.8924 | -41.3221 | -44.4107 | -33.5553 | -38.2818 | -50.817 | -53.6412 | -39.6139 | -51.7421 | 549 | -20.6695 | -35.6105 | -20.4849 | -34.5224 | -19.8731 | -34.8247 | -19.6329 | -34.6153 | 549 | -21.6836 | -26.4101 | -34.1418 | -44.2082 | -31.6379 | -34.0312 | -23.8711 | -27.9023 | -35.8332 | -43.5129 | -31.1418 | -34.2304 | -19.8215 | -25.9465 | -38.9453 | -43.957 | -29.9297 | -41.3626 | -22.009 | -27.4387 | -40.6367 | -43.2617 | -29.4336 | -41.5618
550 | -11.6359 | 0 | -9.67 | 0 | -10.3099 | 0 | -10.3372 | 0 | -62.4851 | 137.8765 | -21.709 | -51.8568 | -41.0343 | -149.0679 | -35.5894 | 15.8392 | -44.4421 | 21.255 | -37.6786 | 30.9706 | -50.6919 | -14.2654 | -20.814 | 70.2939 | -47.6091 | -47.4163 | -35.066 | 119.15 | -52.0988 | 168.6622 | -35.0899 | -171.8389 | -8.9451 | 58.6368 | -14.666 | 7.2958 | -15.1256 | 39.8929 | -9.5795 | 43.0692 | -10.0635 | -161.7009 | -22.5734 | 65.3192 | -28.1059 | 177.8422 | -16.4898 | -160.867 | -44.9759 | -32.151 | -37.9808 | -46.7884 | -54.4095 | -41.6041 | -44.3496 | -34.181 | -38.3038 | -51.5567 | -54.0957 | -40.0599 | -54.8249 | 550 | -21.6582 | -35.0499 | -21.4305 | -35.445 | -20.8005 | -34.8658 | -20.5002 | -34.7722 | 550 | -22.5451 | -26.6679 | -35.1525 | -44.7395 | -31.9341 | -34.0397 | -24.511 | -27.9939 | -36.4512 | -44.0996 | -31.2669 | -34.0124 | -20.5151 | -26.3449 | -39.9208 | -44.4257 | -30.3899 | -44.515 | -22.481 | -27.6709 | -41.2195 | -43.7858 | -29.7227 | -44.4877
551 | -11.3766 | 0 | -9.6815 | 0 | -10.2857 | 0 | -10.409 | 0 | -73.8596 | 78.1234 | -22.6155 | -51.6871 | -40.3819 | -145.3142 | -35.7608 | 5.423 | -43.9568 | 17.1378 | -38.4651 | 35.6423 | -53.5519 | 9.9587 | -21.6069 | 70.134 | -48.1204 | -43.0488 | -35.3033 | 111.4777 | -52.1648 | 156.594 | -34.8505 | -173.2925 | -10.0325 | 57.1593 | -14.9521 | 4.1433 | -15.5176 | 40.8961 | -9.5774 | 34.5827 | -11.1821 | -166.4166 | -25.4968 | 76.6204 | -31.1443 | 167.2994 | -17.1573 | 173.7309 | -44.8937 | -32.8456 | -37.956 | -47.6828 | -56.0539 | -42.0057 | -44.4901 | -35.356 | -38.1384 | -52.2128 | -53.7089 | -40.4107 | -60.2694 | 551 | -22.5434 | -35.1476 | -22.3035 | -35.6196 | -21.5945 | -35.1515 | -21.2323 | -34.5743 | 551 | -23.9794 | -26.7618 | -36.3062 | -46.3724 | -32.3242 | -34.2044 | -25.6745 | -27.8527 | -37.2738 | -45.7682 | -31.5967 | -34.0811 | -21.469 | -26.5794 | -40.8362 | -44.0274 | -30.7292 | -49.9837 | -23.1641 | -27.6703 | -41.8038 | -43.4232 | -30.0017 | -49.8604
552 | -11.3365 | 0 | -9.6775 | 0 | -10.3195 | 0 | -10.3531 | 0 | -70.1176 | -25.4896 | -22.2737 | -48.4604 | -38.8999 | -151.0911 | -36.8245 | -3.4345 | -43.7121 | 7.7581 | -37.7868 | 38.8914 | -52.8191 | 36.7745 | -21.2529 | 73.2822 | -45.8971 | -36.9844 | -36.1291 | 103.6815 | -52.9742 | 139.6651 | -34.2574 | -176.4017 | -10.1822 | 62.4563 | -15.2218 | 0.9639 | -15.0375 | 40.4404 | -9.9263 | 27.1361 | -11.5296 | -165.1992 | -24.7408 | 94.854 | -31.0233 | -178.9154 | -18.6435 | 148.5189 | -44.8897 | -33.0903 | -37.9041 | -48.4913 | -59.4952 | -42.52 | -44.7674 | -36.0968 | -37.981 | -52.5994 | -52.5994 | -40.9171 | -65.6157 | 552 | -22.1802 | -36.0138 | -22.0077 | -34.713 | -21.235 | -35.95 | -20.9082 | -33.9152 | 552 | -24.7603 | -26.6445 | -37.1548 | -49.8177 | -32.8425 | -34.4479 | -26.4193 | -27.6615 | -38.1382 | -49.1757 | -32.1669 | -34.4143 | -21.7538 | -26.5676 | -41.2629 | -42.9219 | -31.2396 | -55.2962 | -23.4128 | -27.5846 | -42.2463 | -42.2799 | -30.564 | -55.2626
553 | -11.5438 | 0 | -9.6727 | 0 | -10.368 | 0 | -10.2899 | 0 | -72.9477 | -7.9341 | -21.3925 | -53.3218 | -38.1879 | -161.4666 | -38.1451 | -4.2314 | -44.2547 | 0.4988 | -36.7948 | 35.7695 | -51.4378 | 48.8915 | -20.3372 | 68.243 | -43.38 | -50.0679 | -37.4851 | 98.199 | -54.9794 | 129.1887 | -33.866 | 175.507 | -9.0599 | 63.7216 | -15.4668 | -2.3513 | -14.4498 | 35.74 | -10.5886 | 22.1996 | -10.7364 | -167.9904 | -21.289 | 92.9149 | -27.268 | 178.21 | -21.5556 | 127.9271 | -45.1661 | -32.5958 | -38.006 | -49.2716 | -61.9005 | -43.3458 | -44.9617 | -35.3797 | -37.9539 | -52.6414 | -51.6649 | -41.2938 | -63.2071 | 553 | -21.3026 | -37.1925 | -21.1808 | -33.9957 | -20.3123 | -37.24 | -20.0692 | -33.3755 | 553 | -23.8359 | -26.4101 | -37.7278 | -52.2278 | -33.6731 | -34.5937 | -25.707 | -27.5859 | -38.9817 | -51.5325 | -33.0559 | -34.6718 | -21.052 | -26.4622 | -41.0976 | -41.9922 | -31.6211 | -52.8391 | -22.9231 | -27.638 | -42.3515 | -41.2969 | -31.0039 | -52.9172
554 | -11.7928 | 0 | -9.6836 | 0 | -10.3953 | 0 | -10.2051 | 0 | -61.325 | 43.2851 | -21.0266 | -63.2061 | -38.017 | -171.2253 | -38.4882 | 0.9582 | -44.6934 | -0.8244 | -36.0182 | 30.22 | -50.381 | 59.6296 | -19.9043 | 59.6642 | -42.7396 | -68.8812 | -39.0733 | 99.493 | -56.053 | 134.6826 | -34.084 | 166.0343 | -7.9982 | 58.97 | -15.8119 | -5.3892 | -14.5099 | 28.3148 | -11.0402 | 21.4194 | -10.0012 | -177.9654 | -19.3627 | 78.4375 | -24.1745 | 158.8409 | -26.2598 | 120.9505 | -45.638 | -32.1192 | -38.2316 | -50.4348 | -60.1965 | -44.3614 | -45.1601 | -34.2898 | -38.0975 | -52.9453 | -51.0273 | -41.7078 | -63.7539 | 554 | -20.9402 | -37.5372 | -20.8163 | -33.5463 | -19.8779 | -38.6829 | -19.6911 | -33.5049 | 554 | -22.497 | -26.3047 | -38.642 | -50.5129 | -34.6778 | -34.7648 | -24.6062 | -27.7022 | -40.2297 | -49.8012 | -34.1563 | -34.955 | -20.3264 | -26.4388 | -41.1525 | -41.3437 | -32.0242 | -53.3586 | -22.4356 | -27.8363 | -42.7402 | -40.632 | -31.5027 | -53.5488
555 | -11.8599 | 0 | -9.6724 | 0 | -10.389 | 0 | -10.1817 | 0 | -53.9779 | 27.872 | -21.4238 | -74.0752 | -38.1354 | -179.906 | -37.7893 | 2.0183 | -44.4034 | -2.7913 | -35.8391 | 21.879 | -48.5225 | 69.8282 | -20.1634 | 50.2895 | -43.244 | -81.5468 | -39.6728 | 107.3318 | -54.4115 | 134.0101 | -34.6296 | 159.8838 | -7.5942 | 50.7931 | -16.4991 | -8.7894 | -15.3709 | 20.4449 | -11.4012 | 18.6641 | -10.2447 | 171.1214 | -18.9391 | 60.918 | -22.5936 | 137.3036 | -28.0761 | 139.6038 | -45.9901 | -32.0895 | -38.4979 | -52.2596 | -58.8182 | -45.7067 | -45.1958 | -33.6234 | -38.3521 | -53.8638 | -50.7115 | -42.0101 | -67.4273 | 555 | -21.3298 | -36.8477 | -21.1737 | -33.4623 | -20.1358 | -39.0136 | -19.9641 | -34.0298 | 555 | -21.7635 | -26.4922 | -40.3997 | -49.1458 | -36.0343 | -34.8068 | -23.951 | -27.9631 | -42.0779 | -48.4292 | -35.525 | -35.0141 | -20.2296 | -26.638 | -42.0039 | -41.0391 | -32.3377 | -57.0383 | -22.4171 | -28.1089 | -43.6821 | -40.3225 | -31.8284 | -57.2456
556 | -11.7402 | 0 | -9.6852 | 0 | -10.3644 | 0 | -10.2242 | 0 | -50.1046 | 7.4448 | -22.5645 | -80.7401 | -38.54 | 172.1261 | -37.1544 | -3.9298 | -44.1144 | -5.5396 | -36.2006 | 14.69 | -46.0214 | 72.2666 | -20.9757 | 43.3601 | -43.7854 | -89.1277 | -38.931 | 109.0063 | -53.409 | 120.464 | -35.2898 | 155.6222 | -7.8534 | 44.1093 | -17.4162 | -7.9341 | -16.8328 | 16.759 | -11.3205 | 16.1281 | -11.1323 | 159.5103 | -19.3489 | 50.2854 | -21.5205 | 116.306 | -22.8914 | 157.5199 | -45.9443 | -32.6743 | -38.7337 | -54.2842 | -58.1279 | -46.7524 | -45.1266 | -33.6222 | -38.5254 | -55.3571 | -50.7595 | -42.5363 | -68.0941 | 556 | -22.4487 | -36.1781 | -22.2381 | -33.7822 | -20.9395 | -38.0281 | -20.7512 | -34.6572 | 556 | -21.882 | -26.7852 | -42.544 | -48.4427 | -37.0672 | -34.7622 | -23.937 | -28.161 | -44.06 | -47.7635 | -36.5282 | -34.9024 | -20.9341 | -26.9935 | -43.6169 | -41.0743 | -32.8511 | -57.7297 | -22.9891 | -28.3693 | -45.1329 | -40.3951 | -32.3121 | -57.8699
557 | -11.583 | 0 | -9.6963 | 0 | -10.3447 | 0 | -10.2744 | 0 | -48.3006 | -12.2342 | -23.8646 | -80.9992 | -38.603 | 167.3361 | -37.2076 | -13.1226 | -43.737 | -7.858 | -36.5149 | 13.184 | -44.1825 | 63.7078 | -21.8711 | 40.9568 | -44.2206 | -92.7301 | -38.3105 | 102.6513 | -54.2397 | 108.4117 | -35.864 | 153.534 | -8.1831 | 42.4704 | -18.0196 | -1.5017 | -17.8788 | 22.7226 | -11.4175 | 10.8347 | -12.6309 | 156.9303 | -20.0178 | 43.8994 | -21.4594 | 100.214 | -19.908 | 138.7576 | -45.6976 | -33.8773 | -38.8929 | -54.9984 | -57.5374 | -47.4593 | -45.0557 | -34.1807 | -38.5908 | -56.9815 | -51.2197 | -43.083 | -61.0666 | 557 | -23.706 | -36.0678 | -23.4482 | -33.9432 | -21.8206 | -37.2241 | -21.6075 | -35.2174 | 557 | -22.5977 | -27.0078 | -43.4154 | -47.8411 | -37.763 | -34.711 | -24.4844 | -28.2461 | -44.724 | -47.1927 | -37.1849 | -34.7813 | -22.2943 | -27.3099 | -45.3985 | -41.5234 | -33.3867 | -50.7219 | -24.181 | -28.5482 | -46.7071 | -40.875 | -32.8086 | -50.7922
558 | -11.6504 | 0 | -9.7747 | 0 | -10.338 | 0 | -10.2853 | 0 | -48.296 | -27.5042 | -23.9117 | -76.7604 | -38.4294 | 161.3699 | -38.2124 | -20.3755 | -42.9456 | -11.7475 | -36.3136 | 11.7817 | -43.8054 | 55.9399 | -21.9653 | 41.9463 | -43.6977 | -92.7078 | -38.5536 | 92.9433 | -54.9385 | 111.5595 | -35.9203 | 154.5991 | -8.031 | 43.2297 | -17.3249 | 6.5899 | -18.1152 | 28.3084 | -11.9921 | 4.5935 | -12.9009 | 165.3504 | -19.8689 | 41.2983 | -21.8989 | 92.1183 | -18.8373 | 119.0747 | -45.4674 | -34.894 | -39.1127 | -54.0846 | -57.4596 | -47.9838 | -45.2278 | -34.7481 | -38.6817 | -57.5833 | -52.138 | -43.7794 | -57.9231 | 558 | -23.7456 | -36.6458 | -23.5189 | -33.6855 | -21.9081 | -37.3432 | -21.7034 | -35.2038 | 558 | -23.0977 | -27.0313 | -42.4342 | -47.6849 | -38.2091 | -34.8898 | -24.9734 | -28.3437 | -43.7993 | -47.1216 | -37.6985 | -34.9425 | -23.2436 | -27.4623 | -45.9329 | -42.3633 | -34.0047 | -47.5851 | -25.1193 | -28.7747 | -47.298 | -41.8 | -33.4941 | -47.6378
559 | -11.9647 | 0 | -9.8406 | 0 | -10.3533 | 0 | -10.257 | 0 | -49.1605 | -28.4219 | -23.0083 | -78.7989 | -38.1531 | 154.3263 | -39.6789 | -20.3112 | -42.0336 | -18.5124 | -35.6923 | 8.0698 | -44.495 | 52.5247 | -21.3375 | 39.6431 | -42.3792 | -100.2454 | -39.856 | 83.5054 | -53.1905 | 116.684 | -35.6967 | 150.3501 | -7.2627 | 41.3147 | -15.7416 | 7.0539 | -17.7793 | 30.3149 | -12.9996 | -0.7184 | -11.0723 | 166.3433 | -19.0632 | 32.5223 | -21.6354 | 91.9806 | -18.91 | 96.4452 | -45.7677 | -34.7336 | -39.3215 | -53.3068 | -57.4435 | -48.3742 | -45.2351 | -34.6932 | -38.8944 | -56.9226 | -53.2742 | -44.6424 | -56.7861 | 559 | -22.8672 | -37.3894 | -22.6925 | -33.1404 | -21.2827 | -38.4257 | -21.1226 | -34.7889 | 559 | -22.7285 | -26.9297 | -41.3421 | -47.6029 | -38.5336 | -34.8818 | -24.8526 | -28.5411 | -43.0498 | -47.0902 | -38.1172 | -34.9781 | -22.7689 | -27.3568 | -44.9579 | -43.4336 | -34.8018 | -46.4328 | -24.893 | -28.9682 | -46.6656 | -42.9209 | -34.3854 | -46.5291
560 | -12.281 | 0 | -9.9409 | 0 | -10.4039 | 0 | -10.1859 | 0 | -48.0256 | -17.8053 | -22.5552 | -87.6899 | -37.9906 | 145.545 | -40.3725 | -12.0444 | -41.526 | -27.1055 | -35.3405 | 1.6003 | -44.7238 | 61.2011 | -20.9849 | 32.0639 | -41.9191 | -113.8572 | -42.4928 | 79.1733 | -50.7778 | 110.259 | -35.7272 | 145.9261 | -6.6081 | 35.3679 | -14.2942 | 0.4742 | -17.7292 | 29.3086 | -14.1631 | -0.3964 | -9.7454 | 156.6272 | -18.6875 | 15.6055 | -20.5627 | 89.6802 | -20.272 | 78.5707 | -46.5047 | -33.8857 | -39.4738 | -53.536 | -56.7118 | -49.2919 | -45.062 | -34.2047 | -39.1756 | -56.0698 | -54.4096 | -45.6578 | -57.9889 | 560 | -22.4207 | -37.498 | -22.2647 | -32.8267 | -20.9318 | -40.0706 | -20.812 | -34.6837 | 560 | -21.9237 | -26.8946 | -41.255 | -46.7709 | -39.351 | -34.6581 | -24.2638 | -28.7717 | -43.3501 | -46.3079 | -39.106 | -34.8761 | -21.6047 | -27.1928 | -43.7888 | -44.4687 | -35.7169 | -47.585 | -23.9448 | -29.0699 | -45.8839 | -44.0057 | -35.4719 | -47.803
561 | -12.3683 | 0 | -9.9933 | 0 | -10.4543 | 0 | -10.134 | 0 | -45.1486 | -18.8478 | -22.8825 | -98.7403 | -38.411 | 135.2885 | -39.5199 | -5.7353 | -41.2668 | -36.5932 | -35.3126 | -5.5603 | -43.1259 | 69.9145 | -21.2193 | 23.8736 | -42.3475 | -124.9383 | -45.2649 | 94.2863 | -48.6826 | 98.4701 | -35.9845 | 142.0935 | -6.4415 | 27.36 | -13.784 | -11.9423 | -18.3068 | 27.2804 | -15.4168 | 0.6213 | -9.2144 | 142.9036 | -19.2676 | -6.8706 | -19.4525 | 82.7328 | -21.9074 | 69.0146 | -47.0611 | -33.397 | -39.5728 | -55.3306 | -56.022 | -50.8111 | -44.7394 | -33.7512 | -39.3801 | -56.2043 | -54.8176 | -46.7433 | -61.9534 | 561 | -22.7376 | -36.6364 | -22.5529 | -32.8976 | -21.1582 | -40.363 | -21.0602 | -34.8962 | 561 | -21.3829 | -27.0118 | -42.9623 | -46.0287 | -40.8178 | -34.2851 | -23.7579 | -28.9258 | -45.1966 | -45.5677 | -40.6771 | -34.6054 | -21.0287 | -27.2045 | -43.836 | -44.8243 | -36.75 | -51.4991 | -23.4037 | -29.1185 | -46.0703 | -44.3633 | -36.6093 | -51.8194
562 | -12.1764 | 0 | -10.0161 | 0 | -10.5035 | 0 | -10.1153 | 0 | -42.8044 | -27.8827 | -23.9412 | -105.6759 | -39.0421 | 130.3615 | -38.017 | -5.4351 | -41.1555 | -45.4076 | -35.3668 | -11.5651 | -40.7618 | 69.0855 | -21.9283 | 16.4513 | -42.8988 | -132.435 | -44.0285 | 113.2103 | -47.1837 | 80.9534 | -36.3442 | 138.7975 | -6.7004 | 20.9235 | -13.9589 | -22.5064 | -18.8327 | 32.1435 | -15.6902 | 6.9719 | -9.7956 | 129.6271 | -21.0663 | -33.1713 | -18.6598 | 74.1373 | -23.3202 | 75.4162 | -47.1424 | -33.5283 | -39.6972 | -59.1737 | -55.7166 | -53.2978 | -44.5043 | -33.5856 | -39.5631 | -58.1098 | -54.4653 | -47.5231 | -70.7877 | 562 | -23.7547 | -35.4221 | -23.4835 | -33.0809 | -21.8377 | -38.4592 | -21.7482 | -35.1931 | 562 | -21.4092 | -27.3867 | -46.9973 | -45.7005 | -43.2817 | -34.0008 | -23.5695 | -29.0596 | -49.0584 | -45.2131 | -43.1825 | -34.389 | -21.3519 | -27.5208 | -45.9334 | -44.4492 | -37.507 | -60.2842 | -23.5122 | -29.1937 | -47.9945 | -43.9618 | -37.4078 | -60.6724
563 | -11.883 | 0 | -10.0043 | 0 | -10.5512 | 0 | -10.1244 | 0 | -41.4991 | -44.2336 | -25.2736 | -108.6991 | -39.2425 | 125.8764 | -36.8155 | -13.5807 | -41.5604 | -54.7018 | -35.654 | -19.2844 | -38.8812 | 59.6128 | -22.8577 | 14.1684 | -43.1211 | -135.3531 | -42.3352 | 111.9092 | -46.7536 | 61.4497 | -36.5319 | 136.6454 | -7.3444 | 16.6679 | -15.2606 | -36.7568 | -19.1495 | 38.1174 | -15.8112 | 6.9553 | -11.2167 | 122.1935 | -24.8515 | -66.6105 | -18.1953 | 67.5481 | -22.1141 | 80.1076 | -46.697 | -34.3416 | -39.8882 | -64.6892 | -55.197 | -54.4627 | -44.3754 | -33.7661 | -39.6095 | -62.7074 | -54.18 | -47.77 | -71.4565 | 563 | -25.0044 | -34.5741 | -24.6226 | -33.364 | -22.7108 | -36.8004 | -22.6285 | -35.3448 | 563 | -21.8831 | -27.7265 | -52.8062 | -45.1927 | -44.4584 | -33.8242 | -23.7618 | -29.0583 | -54.5648 | -44.6458 | -44.3383 | -34.251 | -22.4586 | -28.0052 | -50.8244 | -44.1757 | -37.7657 | -60.9053 | -24.3373 | -29.337 | -52.583 | -43.6288 | -37.6456 | -61.3321
564 | -11.7382 | 0 | -9.9787 | 0 | -10.5927 | 0 | -10.1437 | 0 | -41.4689 | -56.9004 | -25.6214 | -104.0062 | -39.2789 | 122.089 | -36.467 | -25.5972 | -42.4691 | -59.5622 | -36.101 | -22.7275 | -38.1002 | 47.2785 | -23.2978 | 14.0937 | -42.6361 | -138.7238 | -42.3059 | 105.8957 | -47.5525 | 43.8716 | -36.4849 | 134.8819 | -7.6897 | 16.258 | -17.2465 | -41.952 | -18.2032 | 44.3433 | -15.9737 | 4.3361 | -12.4176 | 125.9736 | -31.2478 | -120.4529 | -17.7948 | 59.8349 | -20.7775 | 75.4593 | -46.1988 | -35.6643 | -40.1301 | -61.6168 | -54.6441 | -53.6917 | -44.4552 | -34.1591 | -39.5936 | -77.7443 | -54.4044 | -47.3505 | -63.2557 | 564 | -25.3312 | -34.5159 | -24.9327 | -33.7663 | -23.1077 | -36.3592 | -23.0424 | -35.2765 | 564 | -22.4209 | -27.8554 | -49.8786 | -44.6654 | -43.713 | -33.8625 | -24.1804 | -29.0009 | -51.4731 | -44.0514 | -43.548 | -34.3115 | -23.9261 | -28.3919 | -66.0061 | -44.4257 | -37.3718 | -52.663 | -25.6856 | -29.5374 | -67.6006 | -43.8117 | -37.2068 | -53.112
565 | -11.9232 | 0 | -9.9584 | 0 | -10.5951 | 0 | -10.1459 | 0 | -42.5756 | -64.6327 | -24.905 | -105.9237 | -38.9375 | 118.4034 | -37.4184 | -36.7486 | -42.6502 | -58.2742 | -36.3494 | -25.427 | -38.5921 | 36.8607 | -22.892 | 13.5525 | -41.8347 | -148.0677 | -43.5895 | 103.5565 | -49.019 | 35.8698 | -36.5594 | 131.1566 | -7.3343 | 15.5364 | -19.5777 | -43.1458 | -16.8557 | 43.4557 | -16.6005 | 1.2928 | -11.2501 | 131.5981 | -30.3188 | 146.9955 | -17.2546 | 55.1787 | -20.4379 | 65.3736 | -46.073 | -36.4207 | -40.3386 | -58.3621 | -54.9754 | -52.9636 | -44.7162 | -34.3021 | -39.7084 | -64.7279 | -55.4388 | -47.3919 | -56.7113 | 565 | -24.6658 | -35.3643 | -24.3828 | -33.832 | -22.723 | -37.109 | -22.6739 | -35.2446 | 565 | -22.3789 | -27.7852 | -46.4389 | -45.017 | -43.0052 | -34.1211 | -24.3437 | -29.1133 | -48.2162 | -44.3803 | -42.8177 | -34.5703 | -24.4975 | -28.4154 | -52.8047 | -45.4804 | -37.4335 | -46.1162 | -26.4623 | -29.7435 | -54.582 | -44.8437 | -37.246 | -46.5654
566 | -12.1785 | 0 | -9.9244 | 0 | -10.6198 | 0 | -10.143 | 0 | -43.1463 | -58.459 | -24.5235 | -114.4771 | -38.6462 | 107.4576 | -39.5738 | -42.464 | -41.9444 | -59.3492 | -36.4762 | -30.1804 | -39.5331 | 37.032 | -22.4898 | 7.0464 | -41.7009 | -161.5278 | -45.3132 | 116.8909 | -49.856 | 36.2331 | -36.731 | 129.4021 | -6.7864 | 10.93 | -20.8656 | -33.1432 | -16.104 | 36.2091 | -17.8921 | -1.3914 | -9.6324 | 125.5537 | -27.4418 | 104.1018 | -16.6007 | 46.8741 | -21.1694 | 56.1588 | -46.3438 | -35.9494 | -40.4299 | -58.586 | -55.8477 | -53.5079 | -44.9752 | -34.1394 | -39.9168 | -59.3346 | -57.4283 | -48.0847 | -53.654 | 566 | -24.3016 | -36.5232 | -24.1292 | -33.7101 | -22.3541 | -38.2071 | -22.3075 | -35.3729 | 566 | -21.9609 | -27.7383 | -46.4075 | -45.9233 | -43.5835 | -34.3554 | -24.215 | -29.297 | -48.443 | -45.2279 | -43.3649 | -34.8322 | -23.7709 | -28.2514 | -47.1561 | -47.5039 | -38.1603 | -43.0342 | -26.025 | -29.8101 | -49.1916 | -46.8085 | -37.9417 | -43.511
567 | -12.3069 | 0 | -9.9305 | 0 | -10.652 | 0 | -10.1094 | 0 | -41.2639 | -51.3966 | -25.0386 | -124.7361 | -38.9814 | 99.3636 | -41.0681 | -29.2193 | -41.0582 | -63.071 | -36.5431 | -33.2661 | -39.1418 | 43.3655 | -22.5651 | -0.6641 | -42.3709 | -172.9716 | -43.1983 | 140.5601 | -49.1572 | 38.691 | -36.8559 | 126.1912 | -6.59 | 3.4711 | -21.1402 | -26.6988 | -16.0837 | 28.1564 | -18.9864 | 2.947 | -8.8626 | 113.4652 | -26.7015 | 86.6033 | -16.4147 | 37.387 | -22.5073 | 52.3661 | -46.6937 | -35.2081 | -40.3825 | -62.7562 | -57.0882 | -56.4073 | -44.993 | -33.8903 | -40.1429 | -57.4579 | -59.6219 | -49.6246 | -53.2759 | 567 | -24.7684 | -36.3578 | -24.6418 | -33.7011 | -22.4264 | -37.4023 | -22.3703 | -35.5857 | 567 | -21.5834 | -27.836 | -50.4493 | -47.1577 | -46.4768 | -34.341 | -23.9598 | -29.4909 | -52.6468 | -46.4362 | -46.2979 | -34.8836 | -22.9012 | -28.0756 | -45.151 | -49.6914 | -39.6941 | -42.6239 | -25.2776 | -29.7305 | -47.3485 | -48.9699 | -39.5152 | -43.1665
568 | -12.1579 | 0 | -9.9343 | 0 | -10.7175 | 0 | -10.109 | 0 | -38.7189 | -56.3789 | -26.3092 | -131.0118 | -39.5294 | 93.5912 | -39.6405 | -18.086 | -40.1352 | -70.5671 | -36.4597 | -34.6636 | -37.364 | 44.6307 | -23.1442 | -9.4054 | -43.6535 | 179.4077 | -39.5175 | 139.9709 | -47.5573 | 34.0308 | -36.9507 | 124.7457 | -6.812 | -3.1899 | -21.4356 | -22.6001 | -17.0309 | 21.8925 | -19.3387 | 10.7495 | -9.065 | 100.2881 | -27.231 | 78.1915 | -16.6407 | 27.2182 | -22.0629 | 59.301 | -46.5333 | -34.8127 | -40.4094 | -64.5255 | -58.2091 | -63.2463 | -44.9382 | -33.7918 | -40.2517 | -58.3327 | -59.7663 | -50.8543 | -55.0797 | 568 | -25.8754 | -34.6868 | -25.7286 | -33.6217 | -22.9458 | -35.0475 | -22.872 | -35.8092 | 568 | -21.6339 | -28.0938 | -52.3676 | -48.2748 | -53.312 | -34.2207 | -23.8575 | -29.5342 | -54.4165 | -47.4916 | -53.1373 | -34.8292 | -22.6548 | -28.2515 | -46.1748 | -49.832 | -40.92 | -44.3622 | -24.8784 | -29.6919 | -48.2237 | -49.0488 | -40.7453 | -44.9707
569 | -11.8296 | 0 | -9.9468 | 0 | -10.7827 | 0 | -10.1343 | 0 | -36.92 | -67.8829 | -27.793 | -132.2729 | -39.8313 | 90.9484 | -37.6304 | -21.6925 | -39.5513 | -81.974 | -36.2598 | -39.5312 | -35.7223 | 35.6105 | -24.0775 | -15.8476 | -44.9669 | -179.2971 | -37.4276 | 128.6012 | -46.1606 | 20.4957 | -37.0052 | 122.9769 | -7.5382 | -8.8948 | -22.2544 | -17.5154 | -18.4392 | 23.1319 | -19.3146 | 15.5967 | -10.1952 | 90.554 | -26.8785 | 89.5934 | -17.3064 | 19.9447 | -22.6607 | 65.7139 | -45.8506 | -34.9834 | -40.5264 | -57.3623 | -57.0342 | -62.6787 | -44.8101 | -33.8882 | -40.3101 | -62.8023 | -58.4624 | -50.9507 | -57.8949 | 569 | -27.0565 | -33.1275 | -26.8373 | -33.4539 | -23.7569 | -33.2532 | -23.6747 | -35.9285 | 569 | -22.0586 | -28.4805 | -45.5327 | -47.0874 | -52.7319 | -34.0274 | -23.9414 | -29.5274 | -47.228 | -46.2515 | -52.5444 | -34.6758 | -23.1538 | -28.6968 | -50.9727 | -48.5156 | -41.0039 | -47.1122 | -25.0366 | -29.7437 | -52.668 | -47.6797 | -40.8164 | -47.7606
570 | -11.5925 | 0 | -9.9585 | 0 | -10.8287 | 0 | -10.1716 | 0 | -36.1927 | -84.4304 | -28.4028 | -126.6543 | -39.3951 | 87.6268 | -36.8863 | -34.2981 | -39.636 | -93.0583 | -36.2144 | -45.819 | -34.949 | 22.9556 | -25.0109 | -16.2337 | -44.4295 | -174.3575 | -36.7515 | 114.7022 | -45.8443 | 2.7338 | -36.9 | 122.362 | -8.2919 | -10.831 | -23.0466 | -12.3273 | -19.0626 | 31.142 | -19.7981 | 17.0664 | -11.7004 | 91.7369 | -25.0844 | 93.5687 | -18.1314 | 16.5158 | -20.7067 | 67.6292 | -45.1787 | -35.7247 | -40.5822 | -53.6006 | -54.5303 | -56.3966 | -44.8921 | -34.2389 | -40.2722 | -65.4937 | -57.6148 | -49.7623 | -56.7886 | 570 | -27.4479 | -32.5661 | -27.239 | -33.3463 | -24.5465 | -32.5393 | -24.4736 | -35.7468 | 570 | -22.6464 | -28.6797 | -42.0081 | -44.5718 | -46.4381 | -34.0634 | -24.2804 | -29.4435 | -43.429 | -43.7016 | -46.225 | -34.7205 | -24.1322 | -28.9897 | -53.9012 | -47.6563 | -39.8038 | -45.9599 | -25.7662 | -29.7535 | -55.3221 | -46.7861 | -39.5907 | -46.617
571 | -11.5748 | 0 | -9.9829 | 0 | -10.8316 | 0 | -10.2114 | 0 | -36.6046 | -97.3135 | -27.8716 | -125.3135 | -38.5109 | 79.1476 | -37.8526 | -46.5669 | -40.3784 | -101.8138 | -36.3971 | -50.7039 | -35.3565 | 10.244 | -25.2995 | -15.3618 | -43.0043 | -179.1326 | -37.1214 | 104.9837 | -47.2732 | -18.8054 | -36.7763 | 120.0058 | -8.3691 | -10.2427 | -22.2326 | 0.0107 | -18.2089 | 36.925 | -20.4093 | 26.5404 | -11.6696 | 97.9096 | -23.6959 | 83.3728 | -18.2609 | 14.1941 | -18.812 | 63.4683 | -44.8867 | -36.7042 | -40.5411 | -52.1211 | -52.9062 | -54.3526 | -45.2368 | -34.6793 | -40.1959 | -56.7837 | -57.0883 | -49.3277 | -50.9828 | 571 | -27.0073 | -33.2407 | -26.9344 | -33.3555 | -24.8242 | -32.9751 | -24.7422 | -35.5459 | 571 | -23.1045 | -28.6211 | -40.5463 | -42.9233 | -44.3697 | -34.4052 | -24.6964 | -29.3643 | -41.9097 | -42.0746 | -44.1412 | -35.0254 | -25.1294 | -28.9663 | -45.2089 | -47.1054 | -39.3448 | -40.1512 | -26.7213 | -29.7095 | -46.5723 | -46.2567 | -39.1163 | -40.7714
572 | -11.681 | 0 | -10.0008 | 0 | -10.7812 | 0 | -10.2415 | 0 | -37.7289 | -102.862 | -27.5154 | -131.7542 | -38.294 | 65.8775 | -40.1936 | -47.3737 | -41.1173 | -104.3009 | -36.5311 | -56.6501 | -36.7441 | 3.6566 | -25.1516 | -18.7208 | -42.5731 | 168.9178 | -38.1546 | 101.977 | -51.986 | -31.7905 | -36.7166 | 115.9292 | -7.9866 | -13.1376 | -21.6884 | 2.6088 | -17.3282 | 33.7288 | -21.1341 | 38.0974 | -10.1363 | 97.7993 | -22.6064 | 82.7488 | -18.286 | 11.0871 | -17.3775 | 56.7875 | -44.9749 | -37.1459 | -40.5067 | -52.8343 | -52.9945 | -55.0209 | -45.5594 | -34.9335 | -40.2318 | -52.4149 | -56.1532 | -50.1718 | -47.0496 | 572 | -26.801 | -34.6641 | -26.7987 | -33.4901 | -24.7877 | -34.3073 | -24.6601 | -35.6129 | 572 | -23.2525 | -28.5508 | -41.1533 | -42.9937 | -45.0201 | -34.7782 | -24.9327 | -29.4506 | -42.5928 | -42.2133 | -44.7794 | -35.3179 | -25.4649 | -28.8257 | -40.7339 | -46.1524 | -40.171 | -36.2684 | -27.1451 | -29.7255 | -42.1734 | -45.372 | -39.9303 | -36.8081
573 | -11.7595 | 0 | -10.029 | 0 | -10.7946 | 0 | -10.3102 | 0 | -37.7615 | -98.164 | -28.0766 | -139.7668 | -38.7961 | 51.4778 | -40.6932 | -29.1051 | -41.0003 | -105.3346 | -36.7553 | -62.1188 | -37.5235 | 10.6602 | -25.2741 | -24.1135 | -42.9235 | 158.8025 | -38.1915 | 110.0748 | -56.7937 | 14.8819 | -36.7173 | 112.8819 | -7.8547 | -19.4687 | -20.5422 | 7.9803 | -17.3064 | 28.5416 | -18.108 | 51.2544 | -9.1025 | 88.2517 | -21.6639 | 77.2515 | -18.1143 | 5.0492 | -16.5587 | 47.2075 | -45.132 | -36.9719 | -40.5969 | -56.1516 | -54.9406 | -59.7961 | -45.5759 | -35.0173 | -40.4274 | -50.4079 | -55.6188 | -53.1852 | -45.7466 | 573 | -27.3129 | -34.7872 | -27.32 | -33.7421 | -24.9529 | -34.8068 | -24.771 | -35.7504 | 573 | -23.2578 | -28.6679 | -44.3921 | -44.9116 | -49.7671 | -34.7813 | -24.9883 | -29.6328 | -45.8414 | -44.146 | -49.4859 | -35.2657 | -25.2124 | -28.8374 | -38.6484 | -45.5898 | -43.1562 | -34.952 | -26.9429 | -29.8023 | -40.0977 | -44.8242 | -42.875 | -35.4364
574 | -11.6664 | 0 | -10.0753 | 0 | -10.8894 | 0 | -10.35 | 0 | -36.056 | -97.3175 | -29.4978 | -145.2242 | -40.0797 | 39.6715 | -38.0299 | -20.3431 | -40.6046 | -110.0234 | -36.9864 | -68.1062 | -36.2041 | 16.3585 | -25.9096 | -32.0682 | -43.9239 | 150.8802 | -36.343 | 113.0568 | -50.5742 | 36.9917 | -36.7502 | 110.9193 | -8.3332 | -27.4472 | -20.1282 | 10.0244 | -18.5242 | 25.9912 | -16.0337 | 48.0027 | -8.9136 | 76.5006 | -20.7724 | 73.4697 | -18.2991 | -1.5108 | -15.9701 | 35.6751 | -45.0494 | -36.6448 | -40.6444 | -63.4205 | -58.7877 | -59.7268 | -45.4932 | -34.9949 | -40.639 | -50.0089 | -55.9112 | -57.8425 | -46.9233 | 574 | -28.3306 | -33.077 | -28.297 | -34.1416 | -25.4593 | -33.1828 | -25.217 | -35.84 | 574 | -23.3285 | -28.9726 | -51.7541 | -48.7124 | -49.6515 | -34.6038 | -24.9196 | -29.7496 | -53.0705 | -47.8983 | -49.3768 | -35.1432 | -24.9784 | -28.978 | -38.3425 | -45.8359 | -47.7672 | -36.0339 | -26.5695 | -29.755 | -39.6589 | -45.0218 | -47.4925 | -36.5733
575 | -11.4601 | 0 | -10.086 | 0 | -11.0315 | 0 | -10.338 | 0 | -34.3759 | -106.1047 | -30.8394 | -142.2336 | -42.1612 | 35.4305 | -35.9806 | -30.4915 | -40.2476 | -114.737 | -37.3027 | -75.1395 | -34.501 | 9.097 | -26.9514 | -35.65 | -45.0225 | 154.5577 | -34.5824 | 104.7247 | -46.651 | 26.4119 | -36.5432 | 107.9865 | -9.415 | -32.0043 | -19.0948 | 12.0749 | -19.2913 | 34.0558 | -14.4238 | 39.0275 | -9.6957 | 69.0535 | -20.4925 | 67.1046 | -19.1258 | -7.7409 | -15.9953 | 24.3683 | -44.5564 | -36.5178 | -40.7199 | -58.7764 | -62.282 | -53.0516 | -45.5563 | -35.061 | -40.8021 | -51.2512 | -55.8062 | -54.4674 | -51.066 | 575 | -29.0304 | -31.476 | -28.9871 | -34.668 | -26.1908 | -31.3996 | -25.8712 | -35.6108 | 575 | -23.6009 | -29.342 | -47.3163 | -52.196 | -42.9656 | -34.5248 | -24.975 | -29.7706 | -48.4384 | -51.2505 | -42.7136 | -35.2183 | -25.0577 | -29.2598 | -39.7911 | -45.7202 | -44.3814 | -40.0345 | -26.4318 | -29.6884 | -40.9132 | -44.7747 | -44.1294 | -40.728
576 | -11.287 | 0 | -10.1196 | 0 | -11.1275 | 0 | -10.3257 | 0 | -33.5009 | -119.1805 | -31.3878 | -135.3287 | -43.3889 | 39.9895 | -35.3731 | -44.7061 | -39.8299 | -120.8186 | -38.1944 | -84.3643 | -33.6544 | -2.3365 | -27.9957 | -36.9392 | -44.2425 | 161.1983 | -33.6489 | 92.2324 | -44.5949 | 9.3276 | -36.3421 | 103.1994 | -10.5277 | -31.9691 | -18.1763 | 10.8919 | -18.7845 | 42.9463 | -13.9574 | 28.7895 | -10.4806 | 66.2453 | -20.8844 | 62.1257 | -19.7055 | -13.4047 | -16.7923 | 11.359 | -44.1098 | -36.7167 | -40.7809 | -53.9876 | -60.3054 | -49.6603 | -45.8587 | -35.2493 | -40.9701 | -52.8393 | -54.7518 | -50.4989 | -56.1512 | 576 | -29.1404 | -30.7532 | -29.3248 | -35.209 | -26.8715 | -30.47 | -26.4777 | -35.1638 | 576 | -23.9623 | -29.6831 | -42.7006 | -50.1858 | -39.5407 | -34.7312 | -25.1297 | -29.8426 | -43.6619 | -49.1779 | -39.3346 | -35.533 | -25.4297 | -29.4939 | -41.5523 | -44.6322 | -40.3793 | -45.0237 | -26.5971 | -29.6534 | -42.5136 | -43.6243 | -40.1732 | -45.8255
577 | -11.2322 | 0 | -10.158 | 0 | -11.1463 | 0 | -10.3143 | 0 | -33.4945 | -133.0728 | -31.1237 | -131.755 | -42.7507 | 45.5313 | -36.18 | -57.6938 | -39.4639 | -128.4675 | -40.0006 | -90.9068 | -33.7714 | -14.0066 | -28.7011 | -35.5556 | -42.0467 | 159.9083 | -33.576 | 78.7363 | -44.0146 | -10.8606 | -36.6784 | 96.4125 | -10.8613 | -26.8793 | -16.987 | 9.6237 | -17.2823 | 46.3951 | -14.1323 | 19.7853 | -10.7086 | 67.7658 | -21.673 | 60.2229 | -20.6755 | -19.9121 | -18.2119 | -2.0214 | -43.933 | -37.2064 | -40.7728 | -51.7338 | -56.5189 | -48.0619 | -46.4119 | -35.5838 | -41.158 | -52.5721 | -53.4432 | -48.2478 | -53.7075 | 577 | -28.9539 | -30.9616 | -29.5351 | -35.7478 | -27.3739 | -30.4661 | -26.9845 | -34.99 | 577 | -24.3516 | -29.9258 | -40.5016 | -46.3609 | -37.9039 | -35.2656 | -25.4258 | -30.0117 | -41.4195 | -45.3726 | -37.7476 | -36.0976 | -25.9742 | -29.5406 | -41.3399 | -43.2852 | -38.0898 | -42.5612 | -27.0484 | -29.6265 | -42.2578 | -42.2969 | -37.9335 | -43.3932
578 | -11.2884 | 0 | -10.1978 | 0 | -11.0827 | 0 | -10.3032 | 0 | -34.4814 | -142.4223 | -30.8554 | -133.9876 | -41.3152 | 38.8814 | -38.1207 | -57.2208 | -39.669 | -137.9445 | -41.9247 | -86.9196 | -34.8762 | -20.7559 | -28.8118 | -35.7472 | -40.4872 | 147.2292 | -34.6858 | 69.6961 | -45.8285 | -24.3516 | -37.7848 | 95.9377 | -10.1255 | -27.2368 | -16.8507 | 3.0299 | -16.4993 | 41.6664 | -15.5484 | 11.6691 | -9.8374 | 65.2647 | -22.1106 | 72.2528 | -21.6991 | -24.8056 | -20.2511 | -3.9572 | -44.176 | -37.932 | -40.6767 | -51.5158 | -54.6408 | -48.2679 | -47.3228 | -36.1062 | -41.2376 | -49.19 | -52.8697 | -48.0046 | -48.2963 | 578 | -29.0259 | -32.0873 | -29.8315 | -36.0908 | -27.6209 | -31.6024 | -27.3965 | -35.4966 | 578 | -24.8178 | -29.9492 | -40.2274 | -44.443 | -38.0701 | -36.2401 | -25.9084 | -30.1549 | -41.2126 | -43.5581 | -37.9647 | -37.0196 | -26.6436 | -29.3883 | -37.9016 | -42.6719 | -37.8068 | -37.2136 | -27.7342 | -29.594 | -38.8868 | -41.787 | -37.7014 | -37.9931
579 | -11.3357 | 0 | -10.226 | 0 | -11.0004 | 0 | -10.2674 | 0 | -35.3964 | -141.0802 | -31.2613 | -137.1835 | -40.8352 | 24.1209 | -37.829 | -42.3276 | -40.1882 | -142.6817 | -42.3988 | -77.2556 | -35.6021 | -17.5673 | -28.9938 | -39.531 | -40.049 | 130.3247 | -36.0552 | 70.2077 | -47.6619 | -14.1435 | -37.7455 | 101.9477 | -9.6481 | -34.3602 | -16.4427 | 1.2706 | -16.3364 | 36.8467 | -16.9811 | 14.5396 | -9.2845 | 58.0278 | -20.5184 | 80.4521 | -23.5388 | -26.3047 | -22.2817 | -6.6996 | -44.5909 | -38.4473 | -40.6888 | -53.376 | -54.7628 | -50.1621 | -47.8315 | -36.7426 | -41.1911 | -46.9369 | -52.5815 | -49.9457 | -45.4483 | 579 | -29.5113 | -32.6023 | -30.1307 | -36.2741 | -27.8651 | -32.6725 | -27.7552 | -35.4658 | 579 | -25.4069 | -29.8554 | -42.0403 | -44.5368 | -39.9361 | -36.8311 | -26.5166 | -30.1907 | -43.1086 | -43.7624 | -39.8947 | -37.5641 | -27.1116 | -29.3531 | -35.6012 | -42.3555 | -39.7197 | -34.4479 | -28.2213 | -29.6884 | -36.6695 | -41.5811 | -39.6783 | -35.1809
580 | -11.3063 | 0 | -10.2727 | 0 | -11.034 | 0 | -10.2398 | 0 | -34.5988 | -136.1412 | -32.3725 | -137.1871 | -42.0077 | 9.9326 | -35.3767 | -40.6683 | -40.172 | -144.5312 | -41.8832 | -72.2915 | -34.703 | -13.1604 | -29.7033 | -45.8445 | -40.8129 | 115.0027 | -35.8581 | 77.8851 | -45.4739 | -5.5197 | -36.8244 | 100.3951 | -9.9267 | -42.5494 | -16.1899 | 0.0252 | -16.462 | 35.034 | -17.3615 | 23.9332 | -9.3997 | 48.3151 | -18.7553 | 80.4018 | -25.2371 | -18.5227 | -23.5187 | -7.5951 | -44.6024 | -38.52 | -40.9681 | -57.786 | -56.9618 | -54.1333 | -47.7961 | -37.2449 | -41.279 | -46.1711 | -51.7258 | -56.1316 | -44.5054 | 580 | -30.0484 | -31.3495 | -30.2972 | -36.4991 | -28.2616 | -32.0308 | -28.1304 | -34.9615 | 580 | -25.9386 | -29.9727 | -46.4797 | -46.6891 | -43.8606 | -36.7621 | -26.9722 | -30.245 | -47.5462 | -45.9278 | -43.8935 | -37.5563 | -27.2137 | -29.6618 | -34.8648 | -41.4531 | -45.8589 | -33.4714 | -28.2473 | -29.9341 | -35.9313 | -40.6918 | -45.8918 | -34.2656
581 | -11.162 | 0 | -10.2987 | 0 | -11.1346 | 0 | -10.2323 | 0 | -32.8166 | -140.138 | -33.312 | -129.752 | -44.1069 | 5.8248 | -33.5686 | -51.5443 | -39.7247 | -147.5208 | -41.1866 | -72.8143 | -33.0116 | -17.1335 | -31.0484 | -50.3435 | -42.5893 | 106.4167 | -34.3542 | 77.229 | -43.3007 | -12.1776 | -36.5814 | 95.8969 | -11.1637 | -51.2598 | -16.3254 | -2.9182 | -16.6963 | 35.8148 | -17.0204 | 28.1314 | -10.2289 | 40.6618 | -17.9419 | 73.7816 | -24.655 | -11.6303 | -24.2867 | -2.179 | -44.1949 | -38.2535 | -41.1753 | -59.8121 | -61.6207 | -53.941 | -47.8456 | -37.2635 | -41.5682 | -46.6815 | -50.787 | -70.037 | -45.9146 | 581 | -29.8797 | -29.7101 | -30.0779 | -36.5467 | -28.7274 | -30.3927 | -28.6259 | -34.9272 | 581 | -26.1015 | -30.4062 | -48.6501 | -51.322 | -43.6423 | -36.711 | -26.9648 | -30.4336 | -49.5798 | -50.4861 | -43.7087 | -37.6133 | -27.0915 | -30.0133 | -35.5195 | -40.4883 | -59.7383 | -34.78 | -27.9548 | -30.0407 | -36.4492 | -39.6524 | -59.8047 | -35.6823
582 | -11.0215 | 0 | -10.3378 | 0 | -11.2843 | 0 | -10.2543 | 0 | -31.5895 | -152.0428 | -33.1372 | -121.2673 | -44.8784 | 18.1013 | -33.0432 | -66.0174 | -38.9566 | -154.0763 | -41.0497 | -77.8009 | -31.9334 | -29.1877 | -33.0554 | -50.1386 | -43.9854 | 110.2494 | -33.1243 | 69.2191 | -41.5684 | -22.8567 | -36.5566 | 93.3013 | -12.6686 | -50.2675 | -16.2599 | -3.2075 | -16.0302 | 36.8406 | -16.51 | 28.242 | -11.2029 | 38.8055 | -17.9711 | 67.9458 | -24.1375 | -19.8664 | -25.4553 | -6.6837 | -43.8199 | -38.0203 | -41.2497 | -54.4957 | -71.1597 | -49.6141 | -48.2518 | -36.9562 | -42.0098 | -48.8729 | -49.9315 | -54.5109 | -50.4509 | 582 | -29.1663 | -28.8045 | -29.7455 | -36.2305 | -29.2978 | -29.2175 | -29.1979 | -34.8069 | 582 | -25.9347 | -30.9883 | -43.4742 | -60.8219 | -39.2763 | -36.9675 | -26.6184 | -30.7255 | -44.2414 | -59.8754 | -39.3598 | -37.9975 | -26.9988 | -30.2282 | -37.8514 | -39.5937 | -44.1731 | -39.1666 | -27.6825 | -29.9654 | -38.6186 | -38.6472 | -44.2566 | -40.1966
583 | -10.9792 | 0 | -10.4241 | 0 | -11.3319 | 0 | -10.2965 | 0 | -31.348 | -165.6498 | -32.2546 | -114.2583 | -42.6861 | 22.7642 | -33.9398 | -80.6337 | -38.1938 | -163.4824 | -41.9909 | -80.5889 | -31.9514 | -42.3171 | -34.9748 | -40.1712 | -43.3711 | 118.0238 | -32.7825 | 57.6696 | -40.4396 | -39.6219 | -36.425 | 91.4005 | -13.1255 | -43.8342 | -15.6662 | 0.6316 | -15.4275 | 34.7435 | -16.462 | 28.8894 | -11.3943 | 41.7278 | -18.183 | 73.2315 | -24.5358 | -33.4098 | -27.0844 | 7.5703 | -43.7031 | -38.1382 | -41.2543 | -51.6524 | -69.586 | -47.1109 | -49.0608 | -36.8514 | -42.5065 | -52.9163 | -49.0491 | -51.2186 | -64.2797 | 583 | -28.5947 | -28.8995 | -29.7391 | -35.7077 | -29.9907 | -29.0123 | -29.6949 | -34.3871 | 583 | -25.8722 | -31.5273 | -40.6732 | -59.1619 | -36.6868 | -37.7289 | -26.4273 | -31.1746 | -41.3559 | -58.2541 | -36.8144 | -38.7643 | -27.159 | -30.2751 | -41.9371 | -38.625 | -40.7945 | -52.9478 | -27.7141 | -29.9224 | -42.6198 | -37.7172 | -40.9221 | -53.9832
584 | -11.0005 | 0 | -10.4917 | 0 | -11.2911 | 0 | -10.3508 | 0 | -32.1162 | -176.7369 | -31.1567 | -112.8363 | -40.6123 | 9.145 | -36.1532 | -83.6831 | -38.152 | -175.7759 | -42.2042 | -71.652 | -32.9205 | -50.4266 | -34.92 | -25.4116 | -41.5152 | 115.2643 | -33.7852 | 48.3717 | -41.1626 | -58.2062 | -36.2697 | 90.2818 | -12.4816 | -45.8683 | -15.0385 | -1.9903 | -15.5663 | 29.2291 | -16.8064 | 31.7735 | -10.6205 | 39.6961 | -16.665 | 77.5943 | -27.1797 | -45.8829 | -27.3391 | 12.8379 | -43.7592 | -38.9725 | -41.176 | -51.397 | -64.3629 | -46.5544 | -50.0335 | -37.2793 | -42.7618 | -51.9536 | -48.7243 | -51.9346 | -56.1498 | 584 | -28.3347 | -29.9576 | -29.7108 | -35.2275 | -30.4426 | -29.9772 | -30.1034 | -34.1666 | 584 | -26.2788 | -31.7613 | -40.3965 | -53.8712 | -36.0627 | -38.7424 | -26.7876 | -31.4707 | -41.0462 | -53.0718 | -36.2036 | -39.6827 | -27.972 | -30.1755 | -40.9531 | -38.2326 | -41.4429 | -44.8587 | -28.4808 | -29.8849 | -41.6028 | -37.4332 | -41.5838 | -45.799
585 | -11.0253 | 0 | -10.5798 | 0 | -11.2402 | 0 | -10.4197 | 0 | -33.1985 | 179.1261 | -30.2327 | -112.817 | -39.7914 | -8.7589 | -37.2375 | -71.8887 | -38.7465 | 173.9764 | -40.8422 | -66.1091 | -33.7975 | -51.3389 | -33.9356 | -16.9125 | -40.2151 | 105.3877 | -34.9837 | 49.9872 | -43.1135 | -67.5601 | -35.8035 | 88.8079 | -12.2044 | -52.2849 | -14.0276 | -4.6542 | -15.6612 | 26.8641 | -16.2405 | 39.9218 | -10.1464 | 34.1433 | -14.8905 | 75.0067 | -32.5936 | -50.8796 | -27.8213 | 4.2488 | -43.6948 | -40.2112 | -41.2046 | -53.2383 | -61.5129 | -47.5717 | -50.7221 | -38.0046 | -42.8026 | -48.0643 | -49.0701 | -56.3297 | -49.7177 | 585 | -28.1487 | -30.9628 | -29.1396 | -34.9383 | -30.3795 | -31.0604 | -30.0688 | -33.9061 | 585 | -26.9793 | -31.7773 | -42.213 | -50.9331 | -36.9919 | -39.4819 | -27.4248 | -31.5624 | -42.8186 | -50.2727 | -37.152 | -40.3024 | -29.1859 | -30.1793 | -37.039 | -38.4903 | -45.7499 | -38.4775 | -29.6314 | -29.9644 | -37.6446 | -37.8299 | -45.91 | -39.298
586 | -11.039 | 0 | -10.6475 | 0 | -11.2411 | 0 | -10.517 | 0 | -33.8141 | -177.999 | -29.4904 | -112.9706 | -40.2692 | -27.7093 | -35.3357 | -58.1696 | -39.5602 | 169.3124 | -39.0998 | -69.0731 | -33.7576 | -47.6944 | -32.9601 | -15.3045 | -39.6564 | 92.4279 | -34.7394 | 59.5981 | -44.9276 | -61.7976 | -35.1991 | 84.8269 | -12.6805 | -62.3053 | -13.151 | -9.3575 | -15.8722 | 26.0976 | -14.8905 | 46.4056 | -10.0403 | 26.9715 | -13.5251 | 67.6524 | -38.0065 | 2.4231 | -29.9387 | -8.5343 | -43.4696 | -41.4343 | -41.4041 | -59.118 | -59.2156 | -50.4655 | -50.7569 | -38.7607 | -42.7382 | -45.2412 | -49.5928 | -73.0263 | -47.3374 | 586 | -27.8675 | -30.8678 | -28.1241 | -34.8455 | -29.8506 | -31.0298 | -29.4171 | -33.5414 | 586 | -27.7217 | -31.6992 | -48.079 | -48.5681 | -39.818 | -39.5158 | -28.1132 | -31.4971 | -48.601 | -47.9745 | -39.9485 | -40.2399 | -30.3953 | -30.3651 | -34.2022 | -38.9453 | -62.3788 | -36.0963 | -30.7868 | -30.163 | -34.7242 | -38.3517 | -62.5093 | -36.8204
587 | -10.9757 | 0 | -10.6942 | 0 | -11.3863 | 0 | -10.6321 | 0 | -32.6366 | -176.0412 | -28.8725 | -115.4161 | -41.8724 | -38.9112 | -32.7811 | -67.4314 | -39.4997 | 166.8949 | -38.1112 | -80.3745 | -32.4587 | -49.8272 | -32.9604 | -17.2088 | -40.1221 | 83.112 | -32.6234 | 58.2695 | -43.6238 | -55.2941 | -34.7971 | 78.4859 | -14.4072 | -69.5393 | -12.8282 | -18.1131 | -15.9571 | 25.5227 | -13.2719 | 43.6212 | -10.846 | 20.8781 | -13.0424 | 56.4183 | -31.3548 | 14.0852 | -33.1141 | -97.1492 | -43.1179 | -41.3803 | -41.8017 | -69.2897 | -56.7936 | -54.517 | -50.3426 | -38.7535 | -42.9601 | -44.4403 | -48.7098 | -53.7105 | -47.6935 | 587 | -27.198 | -29.2656 | -27.0377 | -34.7929 | -29.3155 | -29.364 | -28.5895 | -33.2606 | 587 | -27.7778 | -31.9844 | -58.314 | -46.0994 | -43.8228 | -38.9563 | -28.0593 | -31.5738 | -58.6576 | -45.4073 | -43.8849 | -39.7105 | -30.4046 | -30.826 | -33.4646 | -38.0156 | -43.0163 | -36.3072 | -30.6861 | -30.4154 | -33.8082 | -37.3235 | -43.0784 | -37.0614
588 | -10.9518 | 0 | -10.7446 | 0 | -11.5949 | 0 | -10.7979 | 0 | -31.1945 | 177.1401 | -28.3735 | -116.5896 | -43.1318 | -37.5499 | -31.9062 | -83.2704 | -38.9636 | 161.5659 | -37.8361 | -93.3937 | -31.3043 | -58.5307 | -33.6644 | -10.8665 | -40.3824 | 79.0181 | -31.0307 | 48.6153 | -42.3675 | -58.3388 | -34.7795 | 71.0271 | -16.3826 | -65.6439 | -13.0604 | -24.8686 | -15.9317 | 24.395 | -11.8308 | 37.5907 | -11.2557 | 19.921 | -13.6458 | 49.1542 | -31.2894 | -3.607 | -25.4559 | -172.1782 | -42.8635 | -40.4795 | -42.1685 | -55.5354 | -55.1643 | -53.6396 | -50.4203 | -38.2159 | -43.5221 | -45.5141 | -47.2641 | -48.8409 | -50.1442 | 588 | -26.4542 | -28.1496 | -26.452 | -34.6832 | -28.9886 | -27.9934 | -28.0924 | -33.1673 | 588 | -27.2641 | -32.5703 | -44.5836 | -44.4197 | -42.895 | -38.8254 | -27.4713 | -31.9272 | -44.7375 | -43.5694 | -42.8417 | -39.6224 | -29.5277 | -31.2167 | -34.5623 | -36.5195 | -38.0963 | -38.5493 | -29.7349 | -30.5736 | -34.7162 | -35.6692 | -38.043 | -39.3463
589 | -10.9355 | 0 | -10.791 | 0 | -11.7598 | 0 | -10.9355 | 0 | -30.5695 | 164.7264 | -27.6761 | -115.134 | -41.9794 | -34.8761 | -32.4973 | -96.875 | -38.4587 | 153.4547 | -38.8275 | -110.0853 | -31.0881 | -71.5864 | -33.1465 | 1.074 | -40.1231 | 75.0991 | -30.3007 | 34.4446 | -41.0215 | -65.425 | -35.736 | 63.1298 | -16.2235 | -53.6049 | -13.3145 | -26.1229 | -15.7405 | 23.1488 | -10.7698 | 29.5037 | -11.2231 | 19.8648 | -14.5601 | 50.6573 | -41.6398 | -40.2049 | -19.6236 | 149.4647 | -42.8631 | -40.0936 | -42.3983 | -51.4569 | -54.7381 | -50.2303 | -51.5957 | -37.9355 | -44.0801 | -48.7246 | -46.4394 | -47.1973 | -53.4849 | 589 | -25.7706 | -28.0068 | -26.1955 | -34.7238 | -28.6641 | -27.4702 | -27.735 | -33.5342 | 589 | -27 | -33.1446 | -40.5214 | -43.9471 | -39.4393 | -39.8359 | -27.1445 | -32.3203 | -40.5214 | -42.9783 | -39.2948 | -40.6602 | -29.1581 | -31.4628 | -37.7891 | -35.6484 | -36.4063 | -41.7251 | -29.3026 | -30.6385 | -37.7891 | -34.6796 | -36.2618 | -42.5494
590 | -10.9803 | 0 | -10.897 | 0 | -11.7997 | 0 | -11.0181 | 0 | -30.9472 | 152.7917 | -26.5976 | -117.2342 | -39.9799 | -45.3662 | -34.2236 | -104.3931 | -38.0861 | 141.7652 | -42.0683 | -119.3621 | -31.9378 | -82.2242 | -31.0154 | 7.0806 | -39.3733 | 70.7083 | -30.7497 | 20.0538 | -40.1688 | -81.0543 | -37.2796 | 65.6849 | -14.752 | -54.822 | -12.9597 | -24.4967 | -15.5243 | 22.1892 | -10.2291 | 21.7462 | -10.7123 | 16.8605 | -13.8507 | 57.8462 | -35.1412 | 140.6838 | -17.0758 | 126.2477 | -42.9457 | -40.6843 | -42.7204 | -50.1176 | -55.7152 | -48.1414 | -53.6157 | -38.2098 | -44.3123 | -52.1939 | -46.2759 | -47.5419 | -54.31 | 590 | -25.0955 | -28.7369 | -25.8017 | -34.9764 | -28.1048 | -28.0198 | -27.3992 | -33.9925 | 590 | -27.2295 | -33.332 | -39.1373 | -44.8182 | -37.2444 | -41.816 | -27.3128 | -32.5126 | -39.0995 | -43.9155 | -37.1233 | -42.5976 | -29.704 | -31.7401 | -41.2136 | -35.3789 | -36.6449 | -42.5103 | -29.7873 | -30.9207 | -41.1758 | -34.4762 | -36.5238 | -43.2919
591 | -11.0241 | 0 | -11.0462 | 0 | -11.7292 | 0 | -11.0134 | 0 | -32.0517 | 146.2637 | -25.5913 | -120.9017 | -38.6305 | -63.2081 | -35.5871 | -94.4391 | -38.2765 | 128.5632 | -45.8484 | -93.4397 | -33.1089 | -83.9978 | -28.9697 | 3.969 | -38.4119 | 61.2253 | -32.3941 | 11.8895 | -41.0087 | -95.6917 | -36.6834 | 76.0816 | -14.2917 | -65.8168 | -12.0861 | -27.2085 | -14.8383 | 22.3679 | -10.2467 | 12.7386 | -10.5073 | 11.0156 | -12.1625 | 58.1098 | -27.2212 | 110.8015 | -15.4223 | 103.8885 | -42.802 | -42.1568 | -43.1548 | -50.8879 | -58.7355 | -47.4107 | -55.4759 | -39.1159 | -44.1569 | -48.5267 | -46.9251 | -49.6706 | -53.0168 | 591 | -24.5342 | -29.7945 | -25.1399 | -35.0613 | -27.2109 | -29.4147 | -26.8643 | -33.5849 | 591 | -28.0918 | -33.1328 | -39.8638 | -47.6893 | -36.3645 | -43.7467 | -28.0697 | -32.4277 | -39.8745 | -47.0063 | -36.3973 | -44.4625 | -31.1327 | -32.1307 | -37.5026 | -35.8789 | -38.6244 | -41.2876 | -31.1106 | -31.4256 | -37.5133 | -35.1959 | -38.6572 | -42.0034
592 | -11.017 | 0 | -11.1976 | 0 | -11.6607 | 0 | -10.9202 | 0 | -32.859 | 148.8747 | -24.9847 | -126.7879 | -38.1698 | -86.9275 | -34.023 | -84.7628 | -39.3342 | 116.218 | -41.3225 | -72.7727 | -33.3194 | -81.2359 | -27.7808 | -3.4784 | -38.0499 | 47.3708 | -33.7405 | 16.6068 | -42.981 | -100.1197 | -35.0803 | 72.8598 | -15.2079 | -81.6315 | -11.3507 | -36.6928 | -14.6693 | 15.8567 | -10.6746 | 5.4913 | -10.6164 | 4.7251 | -10.7469 | 51.1491 | -23.5631 | 78.4374 | -14.8279 | 88.483 | -42.4104 | -43.8618 | -43.5345 | -54.18 | -64.6253 | -48.0024 | -55.8617 | -40.2935 | -43.8061 | -44.7015 | -48.4867 | -51.9302 | -53.0772 | 592 | -24.1526 | -29.8704 | -24.3852 | -34.6505 | -26.403 | -30.2752 | -26.1979 | -32.8613 | 592 | -29.2765 | -32.7891 | -43.163 | -53.4277 | -36.8048 | -44.201 | -29.0959 | -32.1454 | -43.2598 | -52.9646 | -37.0822 | -44.9415 | -32.8448 | -32.5175 | -33.6845 | -37.2891 | -40.7326 | -41.4165 | -32.6642 | -31.8738 | -33.7813 | -36.826 | -41.01 | -42.157
593 | -10.9981 | 0 | -11.2637 | 0 | -11.6895 | 0 | -10.8536 | 0 | -32.2166 | 152.1959 | -24.7502 | -133.1817 | -38.9662 | -109.9988 | -31.7641 | -89.9822 | -40.6303 | 111.8942 | -38.6306 | -87.7305 | -32.4215 | -80.8789 | -27.6794 | -11.8477 | -38.4145 | 34.0462 | -32.7953 | 23.6929 | -43.7951 | -92.6998 | -34.7983 | 63.4831 | -17.7794 | -90.6687 | -11.127 | -44.9259 | -14.7692 | 10.6048 | -11.0973 | 2.1426 | -11.4276 | -1.3594 | -10.2288 | 41.2092 | -23.7472 | 58.0268 | -15.9542 | 77.0294 | -42.168 | -44.3633 | -43.7851 | -62.2148 | -64.4531 | -49.9492 | -55.7129 | -40.4981 | -43.752 | -42.5918 | -50.2793 | -50.209 | -56.2466 | 593 | -23.897 | -28.6872 | -23.8166 | -34.5539 | -26.1565 | -29.4321 | -25.9126 | -32.8646 | 593 | -29.5 | -32.7539 | -51.2167 | -53.1894 | -38.6855 | -44.0234 | -29.2344 | -32.0625 | -51.3612 | -52.7636 | -39.0956 | -44.8593 | -33.3652 | -32.787 | -31.5937 | -39.0156 | -38.9453 | -44.5571 | -33.0996 | -32.0956 | -31.7382 | -38.5898 | -39.3554 | -45.393
594 | -10.9764 | 0 | -11.2708 | 0 | -11.8163 | 0 | -10.8299 | 0 | -30.8106 | 148.0851 | -24.7307 | -135.7695 | -41.2333 | -129.758 | -30.6826 | -104.5391 | -41.2123 | 111.5079 | -38.7988 | -106.5124 | -31.2287 | -86.0287 | -28.2242 | -12.7021 | -39.307 | 22.6229 | -31.092 | 18.8869 | -42.6164 | -84.8024 | -35.3037 | 58.5395 | -21.1795 | -81.6347 | -11.6908 | -53.359 | -15.3127 | 7.034 | -11.1884 | 2.036 | -11.7062 | -1.7224 | -10.2401 | 32.6031 | -25.2091 | 41.9051 | -16.3153 | 82.2408 | -42.1047 | -43.3494 | -43.8924 | -59.7649 | -58.1203 | -53.2986 | -55.2864 | -39.5663 | -44.2381 | -41.9622 | -49.802 | -47.0545 | -59.1624 | 594 | -23.6961 | -27.545 | -23.6141 | -35.4855 | -26.2415 | -27.997 | -25.8877 | -33.3076 | 594 | -28.5899 | -33.2617 | -48.7885 | -46.8495 | -42.0278 | -43.4701 | -28.2955 | -32.4218 | -48.935 | -46.304 | -42.4687 | -44.4565 | -32.373 | -32.916 | -30.9858 | -38.5312 | -35.7837 | -47.3461 | -32.0786 | -32.0761 | -31.1323 | -37.9857 | -36.2246 | -48.3325
595 | -10.9569 | 0 | -11.2451 | 0 | -11.955 | 0 | -10.9536 | 0 | -29.8639 | 137.5497 | -24.4611 | -136.0081 | -44.1352 | -133.3509 | -30.8731 | -118.168 | -40.9871 | 111.4831 | -40.7518 | -118.7396 | -30.4929 | -97.1393 | -27.8662 | -6.6132 | -40.7744 | 15.772 | -29.951 | 6.3311 | -40.5422 | -86.7655 | -35.6663 | 57.242 | -20.8393 | -62.1155 | -12.684 | -58.1241 | -15.7786 | 6.5559 | -10.7501 | 0.7289 | -12.178 | -5.45 | -11.0874 | 29.3285 | -30.5202 | 66.825 | -15.7901 | 88.4832 | -42.2666 | -42.3476 | -43.9822 | -53.6377 | -54.1806 | -58.1171 | -55.331 | -38.7558 | -45.3358 | -42.7607 | -47.4599 | -45.0878 | -52.6332 | 595 | -23.325 | -27.1458 | -23.4852 | -36.9387 | -25.8322 | -27.0064 | -25.3505 | -33.5342 | 595 | -27.7989 | -34.3789 | -42.6808 | -42.9355 | -46.872 | -43.376 | -27.5107 | -33.3808 | -42.6841 | -42.2256 | -47.1635 | -44.3774 | -31.3907 | -33.0253 | -31.8038 | -36.2148 | -33.8427 | -40.6782 | -31.1025 | -32.0272 | -31.8071 | -35.5049 | -34.1342 | -41.6796
596 | -10.9736 | 0 | -11.3081 | 0 | -12.0317 | 0 | -11.1259 | 0 | -29.8629 | 124.8033 | -23.5457 | -136.7272 | -44.2761 | -121.3279 | -32.0126 | -125.9057 | -39.7701 | 106.6015 | -43.9441 | -114.8675 | -30.7405 | -109.4092 | -26.2536 | -5.5221 | -41.847 | 18.1659 | -30.0059 | -9.9863 | -38.6212 | -100.1429 | -36.0248 | 59.0196 | -18.6706 | -66.2062 | -13.0124 | -57.5584 | -15.7208 | 7.6259 | -10.1259 | -5.6675 | -12.4149 | -11.0117 | -11.2682 | 32.0272 | -26.2626 | 93.9779 | -12.9757 | 86.4545 | -42.6499 | -42.1196 | -44.3193 | -51.103 | -52.2319 | -57.7446 | -56.4253 | -38.6763 | -46.4502 | -44.4682 | -45.726 | -44.52 | -48.4873 | 596 | -22.6047 | -27.5285 | -22.9332 | -37.3726 | -24.8439 | -27.035 | -24.4155 | -33.444 | 596 | -27.7027 | -35.4766 | -40.1294 | -40.9238 | -46.4365 | -44.3936 | -27.3682 | -34.4185 | -39.9771 | -40.2002 | -46.6187 | -45.2994 | -31.146 | -33.3457 | -33.4946 | -34.4179 | -33.2119 | -36.4556 | -30.8115 | -32.2876 | -33.3423 | -33.6943 | -33.3941 | -37.3614
597 | -11.0059 | 0 | -11.4864 | 0 | -11.9825 | 0 | -11.2755 | 0 | -30.7326 | 116.2409 | -22.4381 | -141.7549 | -41.5316 | -123.7731 | -33.2562 | -126.0158 | -38.7876 | 91.9049 | -44.2368 | -84.7061 | -31.7023 | -116.1419 | -24.6455 | -10.3359 | -40.8216 | 21.7847 | -31.6624 | -23.6346 | -38.1012 | -118.018 | -35.5768 | 64.0437 | -18.2277 | -83.522 | -12.3894 | -54.4472 | -15.416 | 4.7976 | -9.8395 | -14.0463 | -12.2609 | -14.4275 | -10.3801 | 33.2809 | -22.4593 | 90.8587 | -11.6096 | 74.9364 | -42.711 | -42.3751 | -45.0782 | -50.6446 | -52.0118 | -54.2267 | -57.3692 | -39.377 | -46.9512 | -45.1192 | -45.1036 | -45.3887 | -46.3091 | 597 | -21.792 | -28.388 | -22.0661 | -36.1946 | -23.7781 | -28.203 | -23.5753 | -32.8861 | 597 | -28.3711 | -35.9453 | -39.6387 | -40.5254 | -42.7403 | -45.3867 | -27.8906 | -34.9687 | -39.3691 | -40.0293 | -42.9512 | -46.0937 | -31.3692 | -34.0723 | -34.1133 | -33.6172 | -33.9023 | -34.3266 | -30.8887 | -33.0957 | -33.8437 | -33.1211 | -34.1132 | -35.0336
598 | -11.0538 | 0 | -11.6924 | 0 | -11.9257 | 0 | -11.2847 | 0 | -31.75 | 115.1494 | -21.7427 | -149.3159 | -39.2632 | -141.1026 | -32.9925 | -120.275 | -39.2247 | 74.2008 | -40.0941 | -77.1236 | -32.4354 | -116.8159 | -23.6807 | -19.6763 | -39.3272 | 12.803 | -34.2405 | -21.5816 | -39.0461 | -134.1278 | -34.0461 | 64.5036 | -20.3421 | -101.7886 | -11.4352 | -59.9829 | -15.3977 | 0.8578 | -10.1664 | -22.7543 | -12.582 | -19.6257 | -9.1782 | 29.1787 | -19.832 | 73.5471 | -10.3881 | 65.6069 | -42.3623 | -42.6933 | -45.9738 | -52.0147 | -52.9366 | -52.4316 | -57.5166 | -40.6484 | -46.8936 | -43.7627 | -45.7002 | -46.8124 | -46.0648 | 598 | -21.2601 | -28.8943 | -21.37 | -34.738 | -23.0344 | -29.6981 | -22.9625 | -31.9707 | 598 | -29.5946 | -35.8398 | -40.9609 | -41.2442 | -40.7392 | -45.5909 | -28.956 | -34.9679 | -40.73 | -41.0109 | -41.1469 | -46.2319 | -31.6395 | -34.92 | -32.7089 | -34.0078 | -35.12 | -34.1391 | -31.0009 | -34.0481 | -32.478 | -33.7745 | -35.5277 | -34.7801
599 | -11.064 | 0 | -11.8214 | 0 | -11.8839 | 0 | -11.1732 | 0 | -31.6395 | 117.9769 | -21.6418 | -156.6485 | -38.1304 | -163.9316 | -31.5881 | -119.672 | -41.0335 | 61.2287 | -37.7049 | -91.4081 | -32.2156 | -115.8232 | -23.5676 | -28.8471 | -38.6793 | -1.7826 | -34.0501 | -6.3758 | -40.5447 | -140.9851 | -32.9638 | 55.9384 | -24.6651 | -121.9525 | -11.1798 | -70.1139 | -16.0823 | -3.5449 | -11.1528 | -30.6367 | -13.2528 | -25.3421 | -8.6575 | 21.1303 | -19.9652 | 61.9737 | -10.5308 | 52.7221 | -41.9562 | -42.7102 | -46.7105 | -54.6437 | -54.1281 | -51.636 | -58.1026 | -41.548 | -46.7866 | -42.1143 | -47.3799 | -46.9113 | -48.1988 | 599 | -21.1399 | -28.3621 | -21.1264 | -33.955 | -22.8956 | -29.6571 | -22.7599 | -31.3719 | 599 | -30.484 | -35.7226 | -43.5797 | -42.3067 | -39.8146 | -46.2187 | -29.7266 | -34.9027 | -43.4705 | -42.2442 | -40.4628 | -46.9294 | -31.6462 | -35.6465 | -31.0503 | -35.5585 | -35.0899 | -36.3149 | -30.8888 | -34.8266 | -30.9411 | -35.496 | -35.7381 | -37.0256
600 | -11.0533 | 0 | -11.7943 | 0 | -11.9439 | 0 | -10.9783 | 0 | -30.4875 | 117.2638 | -21.9199 | -162.2631 | -38.0432 | 171.2421 | -30.3702 | -127.2309 | -43.0439 | 59.4902 | -37.7351 | -108.0246 | -31.3493 | -117.4616 | -24.1044 | -33.5444 | -38.9061 | -18.678 | -31.6302 | -6.3562 | -41.5394 | -141.3063 | -32.8295 | 48.9045 | -38.824 | -100.5702 | -11.5988 | -82.7257 | -16.9571 | -1.8872 | -12.439 | -36.642 | -14.1245 | -29.3682 | -8.5964 | 13.796 | -20.5856 | 57.4719 | -11.091 | 47.6761 | -41.8784 | -41.9616 | -47.1803 | -56.1753 | -54.6714 | -51.6608 | -58.9584 | -40.858 | -47.0806 | -40.9701 | -49.306 | -45.2525 | -51.3525 | 600 | -21.2623 | -27.3008 | -21.2414 | -34.2598 | -23.2348 | -28.2677 | -22.9287 | -31.4263 | 600 | -29.8047 | -36.0273 | -45.122 | -42.8771 | -39.8665 | -47.0145 | -29.0637 | -35.1367 | -45.197 | -42.7275 | -40.6825 | -47.9801 | -30.9083 | -36.127 | -29.9168 | -37.5117 | -33.4582 | -39.4086 | -30.1673 | -35.2364 | -29.9918 | -37.3621 | -34.2742 | -40.3742
601 | -11.0059 | 0 | -11.709 | 0 | -12.0762 | 0 | -10.8887 | 0 | -29.4306 | 107.9709 | -21.9722 | -163.444 | -39.2121 | 147.0253 | -29.8404 | -138.1558 | -43.2461 | 64.4631 | -38.9569 | -113.4561 | -30.4655 | -125.2374 | -24.2441 | -31.0141 | -40.1689 | -35.7428 | -30.1319 | -19.8781 | -41.5696 | -137.899 | -32.9333 | 44.3576 | -29.8086 | -27.4324 | -12.7086 | -92.1473 | -16.8953 | 2.1461 | -13.7881 | -32.4449 | -14.9592 | -32.5503 | -8.8808 | 8.9757 | -20.5782 | 63.241 | -11.8468 | 44.4408 | -42.3829 | -40.4923 | -47.379 | -55.5548 | -53.9806 | -52.4415 | -57.7793 | -39.377 | -48.3496 | -40.8379 | -48.9864 | -43.5176 | -50.3559 | 601 | -21.1861 | -26.5269 | -21.2409 | -35.3107 | -23.2257 | -27.1262 | -22.8046 | -31.7083 | 601 | -28.3711 | -37.3437 | -44.5489 | -42.2716 | -40.7325 | -45.7031 | -27.668 | -36.2734 | -44.6661 | -41.9044 | -41.5528 | -46.8906 | -29.4864 | -36.3731 | -29.832 | -37.2774 | -31.8086 | -38.2797 | -28.7833 | -35.3028 | -29.9492 | -36.9102 | -32.6289 | -39.4672
602 | -10.9906 | 0 | -11.6996 | 0 | -12.1899 | 0 | -10.8701 | 0 | -29.1254 | 95.9844 | -21.3477 | -164.3809 | -41.8258 | 129.3385 | -30.2624 | -151.4729 | -42.1528 | 64.3228 | -39.5195 | -111.6084 | -30.2412 | -136.8205 | -23.2204 | -30.3658 | -42.8957 | -47.7379 | -30.2175 | -37.6764 | -40.3255 | -139.6272 | -32.7816 | 40.6072 | -25.3403 | -42.5184 | -13.9372 | -91.0517 | -16.0973 | -0.8024 | -13.3675 | -30.6389 | -16.1388 | -32.9366 | -9.1172 | 8.434 | -19.5068 | 66.508 | -11.5749 | 46.3135 | -43.1274 | -39.1021 | -47.7895 | -56.1313 | -52.018 | -54.4107 | -55.4652 | -38.5414 | -50.7327 | -41.9574 | -46.5667 | -42.3969 | -46.6024 | 602 | -20.6445 | -26.526 | -20.7649 | -36.2289 | -22.3949 | -27.0117 | -22.0467 | -31.7318 | 602 | -27.5508 | -39.7421 | -45.1407 | -40.3184 | -42.7111 | -43.2753 | -26.8418 | -38.5428 | -45.2612 | -39.8281 | -43.5406 | -44.5951 | -28.1115 | -36.7989 | -30.9668 | -34.8671 | -30.6973 | -34.4125 | -27.4025 | -35.5996 | -31.0873 | -34.3768 | -31.5268 | -35.7323
603 | -10.9684 | 0 | -11.8623 | 0 | -12.2507 | 0 | -10.9431 | 0 | -29.7646 | 85.3947 | -20.3374 | -167.9005 | -45.0068 | 130.9564 | -31.4353 | -156.679 | -40.5507 | 54.2198 | -39.5269 | -105.4835 | -30.7776 | -146.359 | -21.8161 | -33.6789 | -46.2883 | -42.1029 | -32.1887 | -52.6863 | -39.0086 | -150.427 | -32.4695 | 40.0759 | -24.8901 | -62.413 | -13.6846 | -84.3376 | -15.3211 | -4.5153 | -12.7072 | -31.4795 | -17.3139 | -32.7032 | -8.7367 | 8.4534 | -17.5266 | 58.7363 | -10.5766 | 47.1756 | -43.4659 | -38.2216 | -48.6112 | -58.88 | -50.38 | -56.8974 | -53.6318 | -38.5789 | -53.0387 | -43.6982 | -44.8701 | -42.1531 | -43.8391 | 603 | -19.8549 | -27.2994 | -19.9643 | -36.3606 | -21.2831 | -28.0525 | -21.1053 | -31.4542 | 603 | -27.6105 | -42.0703 | -47.9116 | -38.5177 | -45.0351 | -41.3811 | -26.7166 | -40.788 | -47.9369 | -38.1293 | -45.9543 | -42.6887 | -27.2532 | -37.6428 | -32.7298 | -33.0078 | -30.2908 | -31.5884 | -26.3593 | -36.3605 | -32.7551 | -32.6194 | -31.21 | -32.896
604 | -10.9712 | 0 | -12.1345 | 0 | -12.2192 | 0 | -11.0221 | 0 | -30.8165 | 82.0543 | -19.6083 | -176.6504 | -44.683 | 147.2295 | -32.2144 | -154.9175 | -39.7182 | 35.3732 | -37.6631 | -99.5621 | -31.5537 | -150.7828 | -20.8387 | -42.732 | -45.7331 | -22.7588 | -35.6011 | -51.2283 | -38.9213 | -165.6604 | -31.8454 | 37.0136 | -27.5843 | -72.4884 | -12.3307 | -87.0835 | -15.3207 | -13.3129 | -12.2281 | -41.871 | -17.8919 | -29.3381 | -8.0589 | 5.8261 | -17.4973 | 49.3947 | -9.9767 | 39.4136 | -43.0585 | -37.9088 | -49.8522 | -55.8397 | -49.8905 | -55.3111 | -53.0095 | -39.391 | -53.4321 | -44.0993 | -44.4743 | -42.6137 | -42.7372 | 604 | -19.2788 | -28.1364 | -19.3123 | -35.0585 | -20.4722 | -29.5751 | -20.3749 | -30.922 | 604 | -28.4198 | -42.4609 | -44.8685 | -37.756 | -43.1766 | -40.7903 | -27.2565 | -41.2129 | -44.8176 | -37.6713 | -44.289 | -41.9874 | -26.9376 | -38.881 | -33.1281 | -32.3398 | -30.4792 | -30.518 | -25.7743 | -37.633 | -33.0772 | -32.2551 | -31.5916 | -31.7151
605 | -10.9823 | 0 | -12.3339 | 0 | -12.1581 | 0 | -11.0292 | 0 | -31.1803 | 83.0428 | -19.5005 | 174.8298 | -41.6148 | 146.0474 | -31.8323 | -151.8962 | -40.5095 | 12.611 | -35.1976 | -108.1195 | -32.0327 | -150.654 | -20.6728 | -52.1894 | -43.1789 | -25.693 | -35.7972 | -26.8265 | -39.9431 | -177.93 | -31.0826 | 32.8449 | -30.9536 | -66.505 | -10.8873 | -100.2775 | -16.1012 | -23.4495 | -13.0358 | -49.8382 | -18.3844 | -25.2501 | -7.4881 | -0.587 | -17.4727 | 41.7605 | -9.8906 | 34.217 | -42.4063 | -38.0587 | -50.9532 | -50.297 | -50.086 | -51.9571 | -53.5604 | -40.494 | -52.9237 | -42.9784 | -45.3144 | -43.0214 | -43.4418 | 605 | -19.1902 | -28.2196 | -19.1446 | -33.372 | -20.3437 | -30.0404 | -20.1739 | -30.3209 | 605 | -29.5117 | -41.9414 | -39.3147 | -37.7521 | -39.6232 | -41.4023 | -28.1601 | -40.7656 | -39.2678 | -37.9279 | -40.9279 | -42.5312 | -27.0764 | -39.9709 | -31.9961 | -32.9805 | -30.6875 | -31.2837 | -25.7248 | -38.7951 | -31.9492 | -33.1563 | -31.9922 | -32.4126
606 | -10.9736 | 0 | -12.357 | 0 | -12.1697 | 0 | -10.9927 | 0 | -30.5232 | 83.7346 | -19.9068 | 168.7111 | -39.3783 | 129.1723 | -30.7699 | -152.3262 | -43.0252 | -3.613 | -34.4138 | -124.657 | -31.8359 | -152.4109 | -21.243 | -60.1286 | -41.8463 | -42.6228 | -32.752 | -24.4257 | -41.4446 | 175.8947 | -30.6962 | 23.6356 | -29.8982 | -18.7697 | -11.2991 | -113.9049 | -17.299 | -20.5651 | -14.5938 | -53.7951 | -19.1559 | -30.4914 | -7.3091 | -8.438 | -18.7867 | 40.2097 | -10.2305 | 27.1259 | -42.0662 | -38.6132 | -51.2414 | -46.8513 | -50.6404 | -49.4765 | -55.5328 | -40.6111 | -52.9736 | -41.7203 | -47.1031 | -42.7283 | -45.3479 | 606 | -19.5005 | -27.5108 | -19.4247 | -32.7807 | -20.8451 | -29.0046 | -20.5092 | -30.0482 | 606 | -29.6375 | -42 | -35.8777 | -38.2834 | -37.1195 | -43.3631 | -28.2541 | -40.8039 | -35.8586 | -38.4707 | -38.4838 | -44.5401 | -27.6396 | -40.2678 | -30.7467 | -34.7461 | -30.3713 | -33.1782 | -26.2562 | -39.0717 | -30.7276 | -34.9334 | -31.7356 | -34.3552
607 | -11.0088 | 0 | -12.2141 | 0 | -12.276 | 0 | -10.915 | 0 | -29.5214 | 77.8502 | -20.1194 | 168.4226 | -38.638 | 106.1361 | -29.4808 | -159.1127 | -45.7693 | -2.3002 | -35.2476 | -138.5239 | -31.1172 | -154.744 | -21.7448 | -59.0811 | -42.1548 | -63.9253 | -30.8365 | -35.2248 | -42.498 | 179.2431 | -30.8092 | 17.8089 | -26.4226 | -16.2726 | -12.355 | -128.4612 | -17.0338 | -15.865 | -15.8254 | -46.2042 | -20.1556 | -16.1663 | -7.3947 | -13.5832 | -17.7994 | 46.8701 | -10.5208 | 28.2483 | -42.2748 | -38.2938 | -51.0188 | -45.0717 | -51.6498 | -48.0438 | -59.7062 | -39.1783 | -54.2002 | -40.8234 | -49.2062 | -42.1314 | -45.9815 | 607 | -19.5931 | -26.4398 | -19.5255 | -33.3533 | -21.2346 | -27.814 | -20.7851 | -30.2358 | 607 | -28.1695 | -43.1914 | -34.0629 | -39.4357 | -35.8297 | -47.4302 | -26.9642 | -41.9242 | -34.1567 | -39.3738 | -37.1288 | -48.7912 | -27.285 | -40.01 | -29.8146 | -36.9921 | -29.9173 | -33.7055 | -26.0797 | -38.7428 | -29.9084 | -36.9302 | -31.2164 | -35.0665
608 | -11.027 | 0 | -12.0278 | 0 | -12.4831 | 0 | -10.9521 | 0 | -28.8951 | 67.9132 | -19.574 | 167.3109 | -39.3674 | 85.6178 | -28.7429 | -171.2067 | -46.2371 | 6.7618 | -36.4168 | -142.2206 | -30.5438 | -163.7725 | -21.1851 | -58.2763 | -44.4323 | -88.5683 | -30.4823 | -53.7557 | -42.247 | -178.1567 | -31.0883 | 12.4162 | -24.3806 | -19.7104 | -14.3848 | -135.9081 | -15.8933 | -19.0172 | -14.838 | -37.1035 | -21.2819 | -9.6653 | -7.7833 | -18.017 | -16.7626 | 44.1812 | -10.1124 | 26.1648 | -43.1706 | -36.9501 | -51.3065 | -44.862 | -52.4362 | -47.6376 | -64.3911 | -37.5651 | -57.3434 | -40.7465 | -49.9145 | -41.8541 | -44.4035 | 608 | -19.0532 | -25.7689 | -18.9982 | -34.3455 | -20.6904 | -27.3594 | -20.3221 | -30.5849 | 608 | -26.5381 | -46.3164 | -33.835 | -40.4084 | -35.6098 | -51.908 | -25.5373 | -44.8603 | -33.9099 | -39.9531 | -36.6855 | -53.439 | -25.9231 | -40.2795 | -29.7195 | -37.8867 | -29.8263 | -31.9204 | -24.9223 | -38.8234 | -29.7944 | -37.4314 | -30.902 | -33.4514
609 | -11.0641 | 0 | -11.9313 | 0 | -12.5954 | 0 | -11.029 | 0 | -29.1079 | 55.6942 | -18.6724 | 162.3681 | -41.4351 | 69.655 | -29.2668 | 174.5265 | -44.6739 | 10.1219 | -36.9244 | -141.1601 | -30.572 | -173.5952 | -19.9911 | -60.6829 | -50.3815 | -108.5723 | -31.9109 | -70.0613 | -40.95 | 179.7248 | -31.097 | 10.4703 | -22.7914 | -21.9649 | -16.6225 | -127.3759 | -15.2898 | -28.0972 | -13.3674 | -38.3805 | -20.6931 | 1.3689 | -8.0182 | -20.925 | -15.5933 | 36.4529 | -9.393 | 22.5179 | -44.0976 | -35.7187 | -52.2851 | -46.8124 | -50.9999 | -48.1015 | -58.7438 | -36.6735 | -62.9665 | -41.7086 | -47.9743 | -41.8688 | -42.383 | 609 | -18.2753 | -26.1154 | -18.2499 | -35.1007 | -19.6232 | -27.9561 | -19.4152 | -30.6233 | 609 | -25.6094 | -51.9024 | -35.7483 | -39.0686 | -36.1702 | -46.1484 | -24.7422 | -50.3711 | -35.7834 | -38.4045 | -37.0725 | -47.7148 | -24.6546 | -41.221 | -30.6445 | -36.043 | -29.9375 | -29.7876 | -23.7874 | -39.6897 | -30.6796 | -35.3789 | -30.8398 | -31.354
610 | -11.0787 | 0 | -12.0375 | 0 | -12.5898 | 0 | -11.1728 | 0 | -30.0133 | 47.2777 | -18.0332 | 154.968 | -44.3633 | 70.3945 | -30.791 | 169.4897 | -41.9144 | -1.5926 | -36.6693 | -137.5777 | -31.0965 | 177.8652 | -18.9856 | -67.8393 | -60.0444 | -32.359 | -35.0593 | -73.31 | -39.8544 | 169.1564 | -30.7036 | 7.8699 | -21.3649 | -29.2362 | -15.8533 | -115.7352 | -15.5977 | -38.4017 | -12.5508 | -50.3696 | -17.8239 | 8.1125 | -7.7918 | -22.8371 | -15.4911 | 26.3954 | -8.938 | 16.3461 | -44.1687 | -35.1037 | -52.9794 | -51.8093 | -48.9304 | -49.2834 | -55.0922 | -36.5429 | -61.9303 | -43.5336 | -46.2094 | -42.0546 | -41.061 | 610 | -17.7568 | -27.2244 | -17.7528 | -34.9993 | -18.7261 | -29.2364 | -18.6033 | -30.2007 | 610 | -25.4642 | -50.8516 | -40.7306 | -36.8929 | -37.2459 | -42.5024 | -24.5054 | -49.3405 | -40.6365 | -36.3406 | -38.1106 | -43.9194 | -24.025 | -41.9007 | -32.4549 | -34.1719 | -30.0171 | -28.4712 | -23.0662 | -40.3896 | -32.3608 | -33.6196 | -30.8818 | -29.8882
611 | -11.0803 | 0 | -12.165 | 0 | -12.4546 | 0 | -11.1848 | 0 | -30.8135 | 45.4007 | -17.9699 | 145.9128 | -44.5535 | 89.3729 | -31.7785 | 172.0395 | -40.8172 | -27.9284 | -35.2068 | -137.3746 | -31.8925 | 174.0536 | -18.6414 | -78.4344 | -48.9841 | -15.5716 | -36.4683 | -52.2251 | -39.8366 | 154.2618 | -30.059 | 5.0778 | -20.3187 | -38.8149 | -13.593 | -120.4738 | -16.4561 | -49.9465 | -12.697 | -64.3644 | -16.2215 | 4.3245 | -7.4745 | -25.2811 | -16.1358 | 20.7337 | -9.0165 | 8.7962 | -43.6243 | -35.3358 | -52.6177 | -53.9798 | -47.8079 | -50.0936 | -53.8759 | -36.9624 | -58.135 | -44.372 | -45.8525 | -42.3218 | -41.1642 | 611 | -17.7409 | -28.0244 | -17.7148 | -33.7735 | -18.4368 | -30.105 | -18.2725 | -29.5743 | 611 | -25.8821 | -47.0547 | -42.8995 | -35.6429 | -37.9286 | -41.4213 | -24.7974 | -45.6804 | -42.795 | -35.3533 | -38.9088 | -42.6911 | -24.2555 | -41.5374 | -33.2917 | -33.6875 | -30.1568 | -28.7096 | -23.1708 | -40.1631 | -33.1872 | -33.3979 | -31.137 | -29.9794
612 | -11.0995 | 0 | -12.2045 | 0 | -12.3799 | 0 | -11.167 | 0 | -31.0089 | 44.798 | -18.3984 | 138.5154 | -41.2426 | 91.9503 | -31.0866 | 178.319 | -42.0314 | -56.8956 | -33.8499 | -149.0445 | -32.4303 | 173.47 | -19.1061 | -86.6396 | -45.3832 | -38.3037 | -33.6097 | -41.769 | -40.8517 | 142.1782 | -29.5078 | -2.3456 | -19.8587 | -54.7058 | -12.5586 | -133.0553 | -17.6413 | -54.5931 | -13.7109 | -75.6159 | -15.8328 | -4.8196 | -7.5196 | -31.3763 | -17.4499 | 19.7175 | -9.5796 | 1.058 | -43.3317 | -36.4837 | -51.2971 | -47.6247 | -47.5544 | -49.1712 | -54.0326 | -37.6768 | -56.5682 | -43.4584 | -46.681 | -42.2823 | -42.3708 | 612 | -18.1453 | -27.8675 | -18.0547 | -32.5974 | -18.8989 | -29.629 | -18.5883 | -29.0969 | 612 | -26.5773 | -45.4687 | -36.5252 | -35.3499 | -36.9667 | -41.6527 | -25.4723 | -44.1883 | -36.4577 | -35.1745 | -38.0042 | -42.8656 | -25.3842 | -40.1976 | -32.3589 | -34.4765 | -30.0778 | -29.9909 | -24.2792 | -38.9172 | -32.2914 | -34.3011 | -31.1153 | -31.2038
613 | -11.0989 | 0 | -12.0716 | 0 | -12.4271 | 0 | -10.9935 | 0 | -30.6195 | 41.717 | -18.8489 | 134.9954 | -38.8715 | 76.1653 | -29.3972 | 175.1321 | -45.4194 | -76.5552 | -34.0124 | -163.5071 | -32.0309 | 173.2925 | -19.8181 | -89.2155 | -44.5824 | -65.5918 | -31.1342 | -50.1052 | -42.2536 | 135.8599 | -29.3595 | -10.6858 | -19.7288 | -71.2838 | -12.6517 | -146.9195 | -17.7182 | -53.0996 | -15.7521 | -79.5228 | -16.5425 | -12.2994 | -7.9105 | -36.1684 | -16.7437 | 26.8854 | -10.7508 | 0.7685 | -43.5114 | -37.7887 | -50.0036 | -44.1559 | -47.9176 | -46.9137 | -55.5247 | -37.7825 | -56.2825 | -42.1653 | -48.2669 | -41.7864 | -43.6406 | 613 | -18.5289 | -26.8938 | -18.3622 | -32.5543 | -19.5511 | -28.3679 | -19.0809 | -29.0197 | 613 | -26.6836 | -45.1836 | -33.057 | -35.846 | -34.8421 | -43.0976 | -25.7109 | -43.8554 | -33.1624 | -35.4905 | -35.9202 | -44.5312 | -26.6898 | -38.9047 | -31.0664 | -36.1953 | -29.7148 | -31.2135 | -25.7171 | -37.5765 | -31.1718 | -35.8398 | -30.7929 | -32.6471
614 | -11.1306 | 0 | -11.8804 | 0 | -12.6244 | 0 | -10.9107 | 0 | -30.0246 | 36.08 | -18.558 | 137.4458 | -38.1525 | 56.3943 | -28.1607 | 162.733 | -49.0467 | -73.3532 | -35.5642 | -171.8968 | -31.3278 | 167.4599 | -19.6535 | -87.9085 | -46.0506 | -95.9626 | -30.153 | -68.1659 | -43.2035 | 136.6161 | -29.7741 | -19.2517 | -21.3047 | -74.6421 | -14.4941 | -158.9721 | -17.2758 | -54.4084 | -17.5173 | -72.9367 | -17.5978 | -10.8302 | -8.3882 | -42.5415 | -15.4829 | 23.3479 | -11.09 | 1.1048 | -44.5272 | -37.2517 | -49.422 | -42.7968 | -49.078 | -45.072 | -59.6734 | -36.9642 | -56.822 | -41.5405 | -50.064 | -41.3822 | -43.5411 | 614 | -18.2144 | -25.9617 | -18.0291 | -33.5342 | -19.3584 | -27.5701 | -18.9112 | -29.4844 | 614 | -25.8336 | -45.6914 | -31.6662 | -37.1976 | -33.1916 | -47.049 | -25.0838 | -44.1976 | -31.8861 | -36.4536 | -34.1613 | -48.7627 | -26.1211 | -38.2914 | -30.4099 | -38.1836 | -29.5018 | -30.9167 | -25.3713 | -36.7976 | -30.6298 | -37.4396 | -30.4715 | -32.6304
615 | -11.149 | 0 | -11.8693 | 0 | -12.7901 | 0 | -10.8759 | 0 | -30.0066 | 25.1977 | -17.7614 | 133.4412 | -38.8262 | 37.1821 | -28.2497 | 145.9079 | -49.4299 | -61.8642 | -36.8549 | -169.9996 | -31.2053 | 158.4335 | -18.6498 | -89.5201 | -51.2013 | -131.1321 | -30.9444 | -86.9381 | -43.0594 | 139.9212 | -30.4776 | -24.0632 | -21.2378 | -78.5776 | -15.7779 | -155.6824 | -16.5056 | -68.8424 | -16.2211 | -68.59 | -17.3233 | -0.4064 | -8.7141 | -40.2496 | -14.5011 | 14.6984 | -10.5644 | 1.3533 | -46.4928 | -35.5034 | -49.417 | -43.61 | -50.4537 | -44.0503 | -67.6818 | -35.9659 | -57.899 | -42.1389 | -51.299 | -41.3253 | -42.0741 | 615 | -17.4779 | -26.0098 | -17.3408 | -34.575 | -18.4128 | -27.9273 | -18.1398 | -30.2096 | 615 | -24.8169 | -46.75 | -32.461 | -38.5844 | -32.181 | -54.8917 | -24.0966 | -45.1089 | -32.7341 | -37.6636 | -33.1744 | -56.8059 | -24.3544 | -38.268 | -30.9899 | -39.4297 | -29.456 | -29.284 | -23.6341 | -36.6269 | -31.263 | -38.5089 | -30.4494 | -31.1982
616 | -11.1801 | 0 | -12.0346 | 0 | -12.7748 | 0 | -10.9112 | 0 | -30.7129 | 16.9835 | -17.132 | 125.8068 | -40.5838 | 24.9827 | -29.767 | 133.9072 | -47.5514 | -57.7402 | -36.8435 | -163.7927 | -31.5561 | 151.1463 | -17.731 | -96.487 | -67.3099 | 90.1855 | -33.8227 | -97.2594 | -41.6311 | 137.6192 | -30.814 | -23.9654 | -20.2883 | -84.7408 | -14.9189 | -149.7925 | -16.823 | -86.6552 | -15.0523 | -76.5147 | -16.2641 | 0.1028 | -8.4357 | -40.2176 | -14.3799 | 4.9498 | -10.0947 | -0.7153 | -47.201 | -34.1483 | -49.4012 | -46.033 | -49.8221 | -43.8006 | -58.3471 | -35.3998 | -59.2817 | -43.6127 | -50.3236 | -41.3451 | -40.3401 | 616 | -16.9269 | -27.164 | -16.8577 | -35.0606 | -17.5546 | -29.2729 | -17.4219 | -30.4674 | 616 | -24.2197 | -48.1016 | -34.8529 | -37.7875 | -31.766 | -45.5723 | -23.3652 | -46.5069 | -35.1218 | -37.0473 | -32.8894 | -47.4359 | -22.9682 | -38.2211 | -32.4326 | -38.289 | -29.3105 | -27.5653 | -22.1137 | -36.6264 | -32.7015 | -37.5488 | -30.4339 | -29.4289
617 | -11.2508 | 0 | -12.3094 | 0 | -12.618 | 0 | -10.9696 | 0 | -31.4758 | 13.088 | -16.9956 | 116.6602 | -42.8044 | 24.0318 | -31.6438 | 133.7875 | -45.0162 | -71.2795 | -35.756 | -159.583 | -32.0769 | 145.6587 | -17.3355 | -105.9564 | -51.012 | 0.0639 | -36.5033 | -82.185 | -40.6121 | 123.3406 | -30.5161 | -24.6426 | -19.0741 | -96.6335 | -13.1007 | -155.5658 | -17.6517 | -104.1746 | -14.6727 | -89.4395 | -15.057 | -2.7798 | -7.7762 | -44.0098 | -15.2419 | -4.9433 | -9.9089 | -7.3528 | -46.2141 | -33.5423 | -49.0266 | -45.4602 | -48.3313 | -44.1946 | -54.0321 | -35.3953 | -60.5086 | -44.825 | -48.8328 | -41.3446 | -39.4098 | 617 | -16.8325 | -28.4518 | -16.7937 | -34.5638 | -17.1903 | -30.3131 | -17.0817 | -30.0757 | 617 | -24.1445 | -49.2578 | -34.2094 | -36.0219 | -31.8852 | -41.4141 | -23.0859 | -47.8906 | -34.4906 | -35.7133 | -33.225 | -43.0625 | -22.2915 | -37.7758 | -33.5742 | -36.5234 | -29.0352 | -26.7918 | -21.2329 | -36.4086 | -33.8554 | -36.2148 | -30.375 | -28.4402
618 | -11.2652 | 0 | -12.3872 | 0 | -12.3942 | 0 | -10.927 | 0 | -31.9984 | 10.9713 | -17.4171 | 110.6717 | -42.9352 | 35.7447 | -32.1156 | 141.5815 | -44.0078 | -94.1648 | -33.9386 | -163.6298 | -32.6474 | 142.5555 | -17.6998 | -115.6705 | -46.9906 | -34.1447 | -34.6948 | -65.2334 | -40.9325 | 106.7004 | -29.7991 | -27.5617 | -19.0987 | -112.9481 | -12.1391 | -169.9031 | -19.8649 | -119.2593 | -16.027 | -103.1503 | -14.5221 | -12.4948 | -7.3426 | -50.3998 | -16.6208 | -9.2298 | -10.175 | -13.0472 | -45.1396 | -33.7912 | -48.3223 | -42.3857 | -47.5146 | -44.8341 | -52.5708 | -36.0427 | -60.2418 | -44.3716 | -48.3364 | -41.3356 | -39.6744 | 618 | -17.2567 | -28.9099 | -17.1798 | -33.0593 | -17.558 | -30.1615 | -17.359 | -29.4005 | 618 | -24.7775 | -48.9766 | -31.1205 | -35.1274 | -32.4469 | -40.1766 | -23.6555 | -47.8476 | -31.4587 | -35.1204 | -33.9071 | -41.6438 | -22.526 | -37.0571 | -33.1064 | -35.9492 | -28.9484 | -27.2802 | -21.404 | -35.9281 | -33.4446 | -35.9422 | -30.4086 | -28.7474
619 | -11.2807 | 0 | -12.2851 | 0 | -12.272 | 0 | -10.8376 | 0 | -31.9976 | 10.7361 | -18.017 | 106.5473 | -40.8623 | 34.8711 | -30.6687 | 146.155 | -45.0256 | -120.4718 | -32.8625 | -176.6571 | -32.6806 | 142.6763 | -18.4938 | -119.6761 | -46.1517 | -67.4332 | -32.1422 | -67.8231 | -42.3463 | 93.0407 | -29.2926 | -35.8138 | -18.8767 | -128.7488 | -12.1114 | 173.676 | -21.1352 | -123.4281 | -17.4946 | -105.478 | -14.8064 | -13.0126 | -7.4541 | -55.2334 | -17.0811 | -0.2273 | -11.4082 | -12.9662 | -44.6 | -34.7978 | -47.5135 | -39.9203 | -47.4242 | -45.1455 | -52.3827 | -37.061 | -59.1752 | -43.2695 | -48.832 | -41.2368 | -40.6538 | 619 | -17.8251 | -28.1815 | -17.6544 | -32.0015 | -18.3241 | -29.1781 | -17.977 | -28.9983 | 619 | -25.7803 | -47.8945 | -28.6396 | -35.1391 | -32.8604 | -40.1107 | -24.7759 | -46.9032 | -29.0827 | -35.1522 | -34.3079 | -41.5451 | -23.5171 | -36.2328 | -31.9888 | -36.5469 | -28.9517 | -28.3818 | -22.5127 | -35.2415 | -32.4319 | -36.56 | -30.3992 | -29.8162
620 | -11.2816 | 0 | -12.0735 | 0 | -12.3182 | 0 | -10.802 | 0 | -31.3342 | 6.4972 | -17.9608 | 107.6384 | -39.5253 | 21.5714 | -28.9423 | 137.8579 | -47.5876 | -134.9551 | -33.171 | 169.1891 | -32.0886 | 139.3724 | -18.6623 | -118.5368 | -48.0177 | -103.7816 | -30.6919 | -80.4549 | -44.3103 | 84.723 | -29.5654 | -45.7827 | -19.94 | -140.1251 | -13.2333 | 156.9203 | -21.2533 | -127.4823 | -18.8129 | -101.6675 | -15.5577 | -13.5612 | -7.7703 | -61.197 | -15.9601 | 5.9636 | -11.4947 | -10.2985 | -45.0408 | -35.5746 | -47.1395 | -38.3845 | -48.154 | -44.4301 | -53.3743 | -37.119 | -58.1527 | -42.3196 | -49.8 | -41.3651 | -41.618 | 620 | -17.7367 | -26.9279 | -17.508 | -32.1409 | -18.4645 | -28.216 | -18.0784 | -29.3625 | 620 | -25.8374 | -46.8711 | -27.1029 | -36.0805 | -32.3566 | -41.0561 | -25.0455 | -45.8345 | -27.5825 | -35.8358 | -33.6281 | -42.5723 | -24.293 | -35.8579 | -31.038 | -37.7265 | -29.2916 | -29.2998 | -23.5011 | -34.8213 | -31.5176 | -37.4818 | -30.5631 | -30.816
621 | -11.3557 | 0 | -11.8478 | 0 | -12.4377 | 0 | -10.8361 | 0 | -30.9092 | -2.846 | -17.1303 | 105.4884 | -39.6752 | 5.9432 | -28.312 | 122.1094 | -49.3247 | -132.8501 | -34.4852 | 161.8974 | -31.7722 | 131.3454 | -17.7787 | -118.5564 | -53.5949 | -152.3417 | -30.5406 | -96.007 | -46.0978 | 86.5548 | -30.5549 | -51.4411 | -20.0881 | -142.7827 | -15.6919 | 147.8064 | -20.1512 | -137.8426 | -17.3912 | -98.8813 | -15.4682 | -4.8205 | -8.1696 | -65.1541 | -15.1134 | -2.0256 | -11.0059 | -7.4721 | -46.6589 | -35.0144 | -47.3659 | -37.8269 | -49.6706 | -43.362 | -56.2307 | -36.0393 | -57.4025 | -41.8244 | -50.7268 | -42.0275 | -41.4798 | 621 | -16.9289 | -26.3868 | -16.7379 | -33.2287 | -17.6078 | -28.0342 | -17.3423 | -30.4144 | 621 | -24.6836 | -46.0468 | -26.4712 | -37.8228 | -31.5142 | -43.793 | -24.1915 | -44.9648 | -26.9908 | -37.2329 | -32.5259 | -45.3946 | -23.6587 | -36.0102 | -30.4687 | -38.879 | -30.1797 | -29.0421 | -23.1666 | -34.9282 | -30.9883 | -38.2891 | -31.1914 | -30.6437
622 | -11.4652 | 0 | -11.782 | 0 | -12.4857 | 0 | -10.9597 | 0 | -31.5001 | -13.8916 | -16.3761 | 99.2257 | -41.0898 | -6.505 | -29.1924 | 104.8362 | -48.7166 | -132.0369 | -35.874 | 163.0313 | -32.1532 | 122.1103 | -16.8029 | -125.8779 | -58.2687 | 89.4293 | -31.887 | -109.8325 | -46.4082 | 92.4173 | -31.357 | -51.0348 | -19.2563 | -149.2872 | -17.7207 | 153.7517 | -19.8046 | -159.7244 | -16.2419 | -113.4248 | -14.5144 | -4.1845 | -8.4102 | -66.6894 | -14.9194 | -11.6529 | -10.1679 | -10.9554 | -49.6986 | -33.8125 | -47.7138 | -38.3587 | -51.308 | -42.5742 | -60.243 | -35.0873 | -56.7504 | -41.782 | -51.368 | -42.9076 | -40.0943 | 622 | -16.2304 | -27.154 | -16.1087 | -34.5614 | -16.6777 | -28.9295 | -16.5251 | -31.2148 | 622 | -23.6221 | -45.2852 | -26.8935 | -39.526 | -30.7922 | -47.7573 | -23.3053 | -44.2647 | -27.399 | -38.8223 | -31.6145 | -49.2833 | -22.3473 | -36.2486 | -30.3168 | -39.586 | -31.1256 | -27.6086 | -22.0305 | -35.2281 | -30.8223 | -38.8823 | -31.9479 | -29.1346
623 | -11.5864 | 0 | -11.8401 | 0 | -12.3232 | 0 | -10.9945 | 0 | -32.5758 | -20.6048 | -16.1602 | 88.2557 | -43.1345 | -6.8119 | -31.4803 | 98.4959 | -47.8034 | -138.8832 | -35.37 | 169.9682 | -32.8245 | 117.5385 | -16.4853 | -136.4076 | -51.3037 | 21.5244 | -34.079 | -107.6201 | -45.3057 | 89.8313 | -31.0875 | -48.754 | -17.2808 | -156.8411 | -16.4525 | 165.9995 | -20.6639 | -175.7407 | -15.629 | -125.1303 | -13.1618 | -4.3033 | -8.3263 | -69.0189 | -15.344 | -17.1263 | -9.9283 | -16.9114 | -50.4518 | -33.0788 | -47.7015 | -39.9679 | -51.1179 | -42.336 | -56.16 | -34.9831 | -56.0279 | -41.9272 | -51.3233 | -43.2241 | -39.1331 | 623 | -16.0537 | -28.9267 | -15.9841 | -34.4907 | -16.3842 | -30.2583 | -16.2649 | -30.8865 | 623 | -23.3967 | -44.4415 | -28.3815 | -39.2778 | -30.4959 | -43.8368 | -23.143 | -43.7047 | -28.9734 | -38.7947 | -31.3415 | -45.1655 | -21.4924 | -36.1151 | -30.3408 | -39.4832 | -31.384 | -26.8099 | -21.2387 | -35.3783 | -30.9327 | -39.0001 | -32.2296 | -28.1386
624 | -11.6817 | 0 | -11.9054 | 0 | -12.1192 | 0 | -11.0085 | 0 | -33.4004 | -22.5367 | -16.4216 | 80.0288 | -43.8938 | 4.737 | -33.3283 | 106.4503 | -46.7665 | -148.9309 | -33.8225 | 169.7356 | -33.3315 | 115.2873 | -16.7943 | -145.406 | -48.8024 | -16.9565 | -34.4007 | -96.0018 | -44.6477 | 79.6517 | -30.2813 | -49.8044 | -16.8819 | -174.7064 | -14.7422 | 159.1055 | -21.9437 | 164.8323 | -16.2378 | -142.3433 | -12.298 | -8.0436 | -8.2668 | -72.6501 | -15.9976 | -19.3046 | -10.3796 | -22.441 | -49.2145 | -32.9361 | -47.0773 | -40.776 | -50.0071 | -42.5217 | -52.3896 | -35.6311 | -55.2657 | -42.1045 | -50.9688 | -42.9195 | -39.157 | 624 | -16.3278 | -30.2558 | -16.2572 | -33.2188 | -16.6963 | -30.6466 | -16.5324 | -30.0667 | 624 | -23.9494 | -43.584 | -29.0943 | -38.1017 | -30.6163 | -40.2704 | -23.7257 | -43.1465 | -29.7675 | -37.8879 | -31.5132 | -41.3811 | -21.2544 | -35.3956 | -30.4228 | -39.0634 | -31.0141 | -27.0378 | -21.0307 | -34.9581 | -31.096 | -38.8496 | -31.911 | -28.1485
625 | -11.6984 | 0 | -11.8351 | 0 | -11.9562 | 0 | -10.9405 | 0 | -33.8344 | -24.2425 | -17.0335 | 75.0507 | -42.0567 | 15.3815 | -32.6365 | 120.3681 | -46.0765 | -163.0709 | -32.3724 | 161.0675 | -33.4938 | 114.2398 | -17.5847 | -151.4281 | -48.8692 | -48.1728 | -32.5014 | -91.0368 | -45.034 | 65.1963 | -29.4458 | -56.6236 | -17.0249 | 165.7194 | -13.762 | 145.1935 | -23.9026 | 155.5055 | -17.3485 | -160.1904 | -11.7844 | -16.0889 | -8.4339 | -77.4441 | -16.3137 | -24.356 | -10.8127 | -25.9984 | -47.9861 | -33.3533 | -45.99 | -39.7439 | -49.0447 | -43.076 | -50.5265 | -37.0734 | -54.464 | -41.9523 | -50.5616 | -42.2374 | -40.0104 | 625 | -16.9304 | -30.0736 | -16.7937 | -31.7648 | -17.4716 | -29.8261 | -17.1811 | -29.2795 | 625 | -25.375 | -42.7656 | -28.0455 | -37.2096 | -31.2409 | -38.5703 | -25.2383 | -42.5078 | -28.8034 | -37.0885 | -32.1355 | -39.586 | -21.6549 | -34.2916 | -30.2539 | -38.7265 | -30.4023 | -28.0542 | -21.5182 | -34.0338 | -31.0118 | -38.6054 | -31.2969 | -29.0699