## Slide 1: 802.3an comment resolution
Olindo Savi
Siemon
Jan 2006

## Slide 2: Background
1. The present 802.3an objectives call out for supporting media reach over class E (UTP or FTP) or Class F cabling (S/FTP) 2. The present MDI spec not consistent with all cabling media types 3. Correct approach would be to reference the present (and future) ISO/IEC 11801 standard 4. The present standard provides a table (table 29) that summarizes the “Electrical characteristics of telecommunications outlets intended for use with balanced cabling” 5. Table 29 provides further reference to the applicable IEC test/component standard for the MDI outlet type

## Slide 3: Current 802.3an Draft Text Draft 3.0

## Slide 4: ISO-IEC 11801 Ed2.0 (2002)

## Slide 5: Proposed Resolution
Replace the following sentence
(reference: Pg 155, sub clause 55.8.1, Line 9):
Eight-pin connectors meeting the requirements of subclause 3
and Figures 1 through 4 of IEC 60603-7: 1996
With:
Eight-pin connectors meeting the requirements of Table 29 of
ISO/IEC 11801:2002 (or later version).

## Slide 6: Concluding Remarks
1. The cabling objectives call out for supporting media defined in
ISO/IEC 11801:2002. Why not follow same logic for MDI outlet?
2. Table 29 of ISO/IEC 11801:2002 provides further reference to the
applicable IEC test/component standard for the MDI outlet type
3. Present transmission requirements in Clause 55.8 will not change