GR–468–CORE Reliability Assurance for Optoelectronic Devices

Issue 1, December 1998 Introduction  1-11

1.5.3.1 Central Office Environment

A “Central Office” (CO) environment, as described in GR-63-CORE, Network Equipment-Building

System (NEBS) Requirements: Physical Protection, restricts long-term ambient

temperatures to a range of 4-38°C. For short periods (up to 72 hours and for a total of not

more than 15 days per year), temperatures may go as low as 2°C or as high as 49°C. This

same environment can be achieved at remote sites with necessary environmental controls,

as in the case of Controlled Environment Vaults (CEVs).

However, increasing numbers of NEs are being deployed in locations without such

environmental controls, though. The exact operating conditions depend on a number of

factors, including type of system enclosure (above-ground cabinet, aerial enclosure,

pedestal, etc.), geographic location, and local effects (such as shade from a nearby building

or trees). Such non-CO types of conditions are commonly called “uncontrolled

environments.” In this GR, however, these are subdivided into two categories.

1.5.3.2 Remote Terminal (RT) Environment

Remote Terminal (RT) environments are based on the criteria (including temperature

extremes) stated in GR-487-CORE, Generic Requirements for Electronic Equipment

Cabinets. For example, that document defines a temperature range of -40°C to +46°C for

the air temperature outside the enclosure. Inside the enclosure, the air temperature

surrounding the equipment can reach +65°C under maximum solar loading and equipment

power dissipation.6 In addition, it is assumed that there is sufficient thermal mass inside the

enclosure that the time constant for temperature change is on the order of one or more

hours.

1.5.3.3 Uncontrolled Environment

As used here, “uncontrolled” (UNC) environments exhibit conditions that do not meet the

criteria for CO or RT environments described in Sections 1.5.3.1 and 1.5.3.2, respectively.

The temperature extremes for a UNC environment are assumed to be similar to that for a

RT; however, the thermal time constant at the optoelectronic device level is on the order of

minutes (due to the small thermal mass of the electronics in the enclosure and the relatively

small size of the enclosure itself). In addition, other conditions such as mechanical shock

and vibration might be more severe than those experienced in a CO or RT environment. An

example of a UNC environment would probably be a pedestal (such as the optical network

unit of an FITL system).

6. Depending on the location of the optoelectronic device in the system and on the ventilation provided by the

system’s physical design, the device’s ambient operating environment could be 5-20°C higher than the maximum

65°C described for the “system.” As with other types of devices, such as integrated circuits, many reliability tests

need to go beyond the manufacturer's normal maximum-rated operating conditions in order to accelerate aging or

stresses.