## Sheet1
Results of Fiber Survey Conducted at National Laboratories in California
31-October-1997 through 4-November-1997 (Data starts at row 66)
15-December-1997 through 19-December-1997 (Data starts at row 786)
14-January-1998 (Data starts at row 1146)
Howard Frazier, Ben Goldman, Hon Wah Chin and Jeff Hirschman - Cisco Systems
Mike Bennet, Cedric Hui, Ted Sopher and Bob Fink - Lawrence Berkeley National Lab
Lynn Jepsen and Ed Forsman - Lawrence Livermore National Lab
Rick Maurer and Herb ?? - Sandia National Lab
Todd Rhyne and Jeff Moore - Siecor
Bhavesh Patel - Extreme Networks
GBICIDs represent different optical transceivers from vendors A, B, C, D.
The transceiver vendors were HP, IBM, Fujikura, and Vixel (not necessarily in that order)
GBICIDs A1, A2, B4, B5, D3 are LWL. (1000BASE-LX)
GBICIDs A3, B1, B2, B6, C1,C3, D1, D2 are SWL (1000BASE-SX)
GBICIDs A8, A20, A25, A34 are SWL (1000BASE-SX) with known CPR characteristics
GBICID A8 has a CPR of 18.48 dB, A20 has a CPR of 15.97 dB, A25 has a CPR of 15.8 dB, A34 has a CPR of 13.9 dB
GBIC A2 was used as receiver for all LWL tests (Except as indicated)
GBIC D1 was used as receiver for all SWL tests (Except as indicated)
1 m Offset (OFS) and 3 m single mode (SMF) cable insert done between transmitting component and 5 m jumper cable during testing in October
15 um (15UOFF) and 19 um (19UOFF) offset jumpers were used as noted during week of 15-December
JMPRID is a means of identifying the mulimode SC to ST jumper cables used in the tests, which were different at each lab
Test performed was a simple bit error rate test using two Network Interface Cards in two different PCs
Cisco (Granite) Systems FX1000 Gigabit Ethernet ASIC
Vitesse SerDes
Dell Dimension 200 MHz Pentium Pro PCs
Sun Solaris x86 operating system
Cisco (Granite) Systems fxdebug diagnostic routines
FX1000 ASIC placed in special "tester" mode
Generates back to back 1 kB packets with minimum IPG and random data content
Checks, counts, and discards packets at the receiver
|  | Reports | symbol errors D14(8B/10B coding violations, including disparity errors)
CRC errors, sequence Errors (1000BASE-X delimiter rules),
and incorrect receive packet length.
Two test stations were used, one transmitting, one receiving.
During week of December 15th, an HP 8158B optical attenuator was used to adjust the optical
power level at the receiver to be -16 dBm for 1000BASE-LX and -14 dBm for 1000BASE-SX, as
measured with a FOTEC optical power meter.
Lawrence Berkeley National Lab 31-October-1997
Lab test reference cable
|  |  | 260 m | inc. 5 meter jumpers
Cable | Fiber | Transmit | Receive | Test | Err | CRC | Symbol | Packet | Sequence | Length | P[r] | Modal B/W | Modal B/W
name/ | name/ | GBICID/ | GBICID/ | time | ??? | error | error | count | error | error | (dBm) | 850 nm | 1300 nm
ID tag | ID tag | JMPRID | JMPRID | (min) |  | count | count |  | count | count |  | (MHz*km) | (MHz*km)
| Red | A3/J1 | D1/J4 | nom | no
|  | B1/J1 | D1/J4 | nom | no
|  | C1/J1 | D1/J4 | nom | no
|  | D2/J1 | D1/J4 | nom | no
|  | A1/J1 | A2/J4 | nom | no
| Orange | A3/J1 | D1/J4 | nom | no
|  | B1/J1 | D1/J4 | nom | no
|  | C1/J1 | D1/J4 | nom | no
|  | D2/J1 | D1/J4 | nom | no
|  | A1/J1 | A2/J4 | nom | no
Lawrence Berkeley National Lab 1-November-1997
Node 2 to building 48 |  |  |  | Node 2 is definitely not a benign environment. Lots of networking gear, microwave, and power equipment
FGI 62.5 um |  |  | 299 m | inc. 5 meter jumpers
Cable | Fiber | Transmit | Receive | Test | Err | CRC | Symbol | Packet | Sequence | Length | P[r] | Modal B/W | Modal B/W
name/ | name/ | GBICID/ | GBICID/ | time | ??? | error | error | count | error | error | (dBm) | 850 nm | 1300 nm
ID tag | ID tag | JMPRID | JMPRID | (min) |  | count | count |  | count | count |  | (MHz*km) | (MHz*km)
N2-B48
| T1.1 A3 | A3/J2 | D1/J3 | nom | no
|  | B1/J2 | D1/J3 | nom | no
|  | C1/J2 | D1/J3 | nom | no
|  | D2/J2 | D1/J3 | nom | no
|  | A1/J2 | A2/J3 | nom | no
| T1.1 A4 | A3/J2 | D1/J3 | nom | no
|  | B1/J2 | D1/J3 | nom | no
|  | C1/J2 | D1/J3 | nom | no
|  | D2/J2 | D1/J3 | nom | no
|  | A1/J2 | A2/J3 | nom | no
| T1.1 A5 | A3/J2 | D1/J3 | nom | no
|  | B1/J2 | D1/J3 | nom | no
|  | C1/J2 | D1/J3 | nom | no
|  | D2/J2 | D1/J3 | nom | no
|  | A1/J2 | A2/J3 | nom | no
| T1.1 A6 | A3/J2 | D1/J3 | nom | no
|  | B1/J2 | D1/J3 | nom | no
|  | C1/J2 | D1/J3 | nom | no
|  | D2/J2 | D1/J3 | nom | no
|  | A1/J2 | A2/J3 | nom | no
| T1.1 C1 | A3/J2 | D1/J3 | nom | no
|  | B1/J2 | D1/J3 | nom | no
|  | C1/J2 | D1/J3 | nom | no
|  | D2/J2 | D1/J3 | nom | no
|  | A1/J2 | A2/J3 | nom | no
| T1.1 C1 | A3/J2 | D1/J3 | nom | no
|  | B1/J2 | D1/J3 | nom | no
|  | C1/J2 | D1/J3 | nom | no
|  | D2/J2 | D1/J3 | nom | no
|  | A1/J2 | A2/J3 | nom | no
Lawrence Berkeley National Lab 1-November-1997
Node 2 to building 25. |  |  | Over filled Modal Bandwith is spec'd, not measured
ATT 62.5 um |  |  | 433 m | inc. 5 meter jumpers
Cable | Fiber | Transmit | Receive | Test | Err | CRC | Symbol | Packet | Sequence | Length | P[r] | Modal B/W | Modal B/W
name/ | name/ | GBICID/ | GBICID/ | time | ??? | error | error | count | error | error | (dBm) | 850 nm | 1300 nm
ID tag | ID tag | JMPRID | JMPRID | (min) |  | count | count |  | count | count |  | (MHz*km) | (MHz*km)
N2-B25
| C1-3 | A3/J2 | D1/J3 | nom | no | [6 empty] | 200 | 500
|  | B1/J2 | D1/J3 | nom | no | [6 empty] | 200 | 500
|  | C1/J2 | D1/J3 | nom | no | [6 empty] | 200 | 500
|  | D2/J2 | D1/J3 | nom | no | [6 empty] | 200 | 500
|  | A1/J2 | A2/J3 | nom | no | [6 empty] | 200 | 500
| C1-4 | A3/J2 | D1/J3 | nom | no | [6 empty] | 200 | 500
|  | B1/J2 | D1/J3 | nom | no | [6 empty] | 200 | 500
|  | C1/J2 | D1/J3 | nom | YES | 15714783 | 93476026 | 23634283 | 23611074 | 6804795 |  | 200 | 500
|  | D2/J2 | D1/J3 | nom | no | [6 empty] | 200 | 500
|  | A1/J2 | A2/J3 | nom | YES | not recorded, testing continued below when failure seen | [5 empty] | 200 | 500
|  | A1/J1 | A2/J4 | 14.5 | YES | 38021 | 20068 | 101777083 | 17627 | 780 |  | 200 | 500
|  | A1/J1/SMF | A2/J4 | 5 | no |  |  | 35515680 |  |  |  | 200 | 500
|  | A1/J1/OFS | A2/J4 | 5 | no |  |  | 35577170 |  |  |  | 200 | 500
|  | B1/J1 | D1/J4 | 5 | no |  |  | 35507387 |  |  |  | 200 | 500
|  | D2/J1 | D1/J4 | 5 | no |  |  | 35532209 |  |  |  | 200 | 500
| C1-5 | A1/J2 | A2/J3 | nom | no | [6 empty] | 200 | 500
| C1-6 | A1/J2 | A2/J3 | nom | no | [6 empty] | 200 | 500
| C1-7 | A1/J2 | A2/J3 | nom | no | [6 empty] | 200 | 500
| C1-8 | A1/J2 | A2/J3 | nom | no | [6 empty] | 200 | 500
| C1-9 | A1/J2 | A2/J3 | nom | no | [6 empty] | 200 | 500
| C1-10 | A1/J2 | A2/J3 | nom | no | [6 empty] | 200 | 500
| C1-11 | A1/J2 | A2/J3 | nom | no | [6 empty] | 200 | 500
| C1-12 | A1/J2 | A2/J3 | nom | no | [6 empty] | 200 | 500
| C1-13 | A3/J2 | D1/J3 | nom | no | [6 empty] | 200 | 500
|  | B1/J2 | D1/J3 | nom | no | [6 empty] | 200 | 500
|  | C1/J2 | D1/J3 | nom | YES | n/a | n/a | n/a | n/a | n/a |  | 200 | 500
|  | D2/J2 | D1/J3 | nom | no | [6 empty] | 200 | 500
|  | A1/J2 | A2/J3 | nom | YES | 28178323 | 23172271 | 42523538 | 23016162 | 724027 |  | 200 | 500
|  | A1/J1/OFS | A2/J4 | 5 | YES |  | high | 0 |  |  |  | 200 | 500
|  | A1/J1/SMF | A2/J4 | 5 | YES | 323547 | 182815 | 35534574 | 50098 | 1457 |  | 200 | 500
|  | A1/J1 | A2/J4 | 5 | YES | 23212444 | 31863922 | 35386542 | 29016055 | 1774800 |  | 200 | 500
| ********** | B1/J1 | D1/J4 | 5 | YES |  | high | 0 |  |  |  | 200 | 500
| ********** | D2/J1 | D1/J4 | 5 | YES |  | high | 0 |  |  |  | 200 | 500
| ********** | [5 empty] | results marked with asterisks may reflect configuration error
| C1-14 | A1/J2 | A2/J3 | nom | no | [6 empty] | 200 | 500
| C1-15 | A1/J2 | A2/J3 | nom | no | [6 empty] | 200 | 500
| C1-16 | A1/J2 | A2/J3 | nom | no | [6 empty] | 200 | 500
| C1-17 | A1/J2 | A2/J3 | nom | no | [6 empty] | 200 | 500
| C1-18 | A1/J2 | A2/J3 | nom | no | [6 empty] | 200 | 500
| C1-19 | A1/J2 | A2/J3 | nom | no | [6 empty] | 200 | 500
| C1-20 | A1/J2 | A2/J3 | nom | no | [6 empty] | 200 | 500
Lawrence Berkeley National Lab 2-November-1997
Node 2 to building 5. |  |  |  |  | Overfilled bandwidth was measured with an instrument having a maximum frequency of 1450 MHz
ATT 62.5 um |  |  | 489 m | inc. 5 meter jumpers |  |  | Catalog B/W spec is 200/500 MHz*km at 850nm/1300nm
Cable | Fiber | Transmit | Receive | Test | Err | CRC | Symbol | Packet | Sequence | Length | P[r] | Modal B/W | Modal B/W
name/ | name/ | GBICID/ | GBICID/ | time | ??? | error | error | count | error | error | (dBm) | 860 nm | 1286 nm
ID tag | ID tag | JMPRID | JMPRID | (min) |  | count | count |  | count | count |  | (MHz*km) | (MHz*km)
N2-B5
| C1-1 | A1/J2 | A2/J3 | nom | no | [6 empty] | 695 | 309
| C1-2 | A1/J2 | A2/J3 | nom | no | [6 empty] | 229 | 302
| C1-3 | A1/J2 | A2/J3 | nom | no | [6 empty] | 695 | 565
| C1-4 | A1/J2 | A2/J3 | nom | no | [6 empty] | 253 | 518
| C1-5 | A1/J2 | A2/J3 |  | YES | 0 | high | 0 | 0 | 0 |  | 203 | 177
|  | A1/J1/OFS | A2/J4 | 5 | YES | 2141108 | 1559691 | 35552355 | 742741 | 31690 |  | 203 | 177
|  | A1/J1/SMF | A2/J4 | 5 | YES | 2873688 | 920993472 | 5940449 | 9601727 | 2840975 |  | 203 | 177
|  | B1/J2 | D1/J3 | 5 | YES | 22224564 | 20105797 | 35204998 | 18100042 | 1110167 |  | 203 | 177
|  | D2/J2 | D1/J3 | 5 | YES | 7190107 | 195686146 | 12316458 | 12905141 | 4807060 |  | 203 | 177
| C1-6 | A1/J2 | A2/J3 | nom | no | [6 empty] | 695 | 695
| C1-7 | A1/J2 | A2/J3 | nom | no | [6 empty] | 303 | 695
| C1-8 | A1/J2 | A2/J3 | nom | no | [6 empty] | 274 | 610
| C1-9 | A1/J2 | A2/J3 | nom | no | [6 empty] | 370 | 615
| C1-10 | A1/J2 | A2/J3 | nom | no | [6 empty] | 695 | 546
| C1-11 | A1/J2 | A2/J3 | nom | no | [6 empty] | 306 | 550
| C1-12 | A1/J2 | A2/J3 | nom | no | [6 empty] | 280 | 532
| C1-13 | A1/J2 | A2/J3 | nom | no | [6 empty] | 239 | 526
| C1-14 | A1/J2 | A2/J3 | nom | YES | 2986014 | 1470701 | 45984410 | 1891563 | 61990 |  | 436 | 326
|  | A3/J2 | A2/J3 | nom | YES | 9775 | 8623 | 42802926 | 99 | 4 |  | 436 | 326
|  | B1/J2 | D1/J3 | nom | YES | 9397537 | 7830931 | 37850806 | 3938161 | 355556 |  | 436 | 326
|  | C1/J2 | D1/J3 | nom | YES | 0 | high | 0 | 0 | 0 |  | 436 | 326
|  | D2/J2 | D1/J3 | nom | YES | 7471408 | 5772854 | 37642078 | 2210251 | 54367 |  | 436 | 326
|  | A1/J2 | A2/J3 | nom | YES | 67050 | 32679 | 33181649 | 47967 | 1404 |  | 436 | 326
|  | A1/J2/OFS | A2/J3 | 20 | YES | 828 | 395 | 116317207 | 19 | 2 |  | 436 | 326
|  | A1/J2/OFS | A2/J3 | 10 | YES | 149 | 58 | 66425929 | 2 | 0 |  | 436 | 326
|  | A1/J1/OFS | A2/J4 | 5 | YES | 43384 | 24835 | 37571521 | 25054 | 2986 |  | 436 | 326
|  | A1/J1/OFS | A2/J4 | 5 | YES | 1606965 | 1117431 | 36203122 | 431645 | 22789 |  | 436 | 326
|  | A1/J1 | A2/J4 | 5 | YES | 4 | 2 | 37380992 | 2 | 0 |  | 436 | 326
|  | A1/J1/SMF | A2/J4 | 6 | no | 0 | 0 | 42605300 | 0 | 0 |  | 436 | 326
| ********** | B1/J2 | D1/J3 | 5 | no | 0 | 0 | 35538166 | 0 | 0 |  | 436 | 326
| ********** | D2/J2 | D1/J3 | 5 | no | 0 | 0 | 37087487 | 0 | 0 |  | 436 | 326
| ********** | [5 empty] | Results marked with asterisk may reflect recording error
| C1-15 | A1/J2 | A2/J3 | nom | no | [6 empty] | 694 | 578
| C1-16 | A1/J2 | A2/J3 | nom | no | [6 empty] | 212 | 439
| RHS-3 | A1/J2 | A2/J3 | nom | no
| RHS-4 | A1/J2 | A2/J3 | nom | no
Lawrence Berkeley National Lab 2-November-1997
Node 1 to building 90. Very nice and cool networking equipment room to toasty warm telephone closet.
Lucent 62.5 um |  | v. 1997 | 684 m | inc. 5 meter jumpers
Cable | Fiber | Transmit | Receive | Test | Err | CRC | Symbol | Packet | Sequence | Length | P[r] | Modal B/W | Modal B/W
name/ | name/ | GBICID/ | GBICID/ | time | ??? | error | error | count | error | error | (dBm) | 860 nm | 1300 nm
ID tag | ID tag | JMPRID | JMPRID | (min) |  | count | count |  | count | count |  | (MHz*km) | (MHz*km)
N1-B90
| A1 | IN USE | [9 empty] | 342 | 967
| A2 | IN USE | [9 empty] | 243 | 1919
| A3 | A1/J1 | A2/J4 | 1 | YES | not recorded, testing continued below when failure seen | [5 empty] | 263 | 461
|  | A1/J1 | A2/J4 | 5 | YES | 1180 | 454 | 35906250 | 409 | 14 |  | 263 | 461
|  | A1/J1/OFS | A2/J4 | 5 | no | 0 | 0 | 35565376 | 0 | 0 |  | 263 | 461
|  | A1/J1/SMF | A2/J4 | 5 | no | 0 | 0 | 35977268 | 0 | 0 |  | 263 | 461
| A4 | A1/J1 | A2/J4 | 1 | no | [6 empty] | 156 | 499
| A5 | A1/J1 | A2/J4 | 1 | no | [6 empty] | 195 | 1468
| A6 | A1/J1 | A2/J4 | 1 | no | [6 empty] | 270 | 801
| B1 | A1/J1 | A2/J4 | 1 | no | [6 empty] | 377 | 380
| B2 | A1/J1 | A2/J4 | 1 | no | [6 empty] | 147 | 1128
| B3 | A1/J1 | A2/J4 | 1 | no | [6 empty] | 217 | 561
| B4 | A1/J1 | A2/J4 | 1 | no | [6 empty] | 218 | 674
| B5 | A1/J1 | A2/J4 | 1 | no | [6 empty] | 142 | 824
| B6 | A1/J1 | A2/J4 | 1 | no | [6 empty] | 460 | 349
| C1 | A1/J1 | A2/J4 | 1 | no | [6 empty] | 380 | 390
| C2 | A1/J1 | A2/J4 | 1 | no | [6 empty] | 243 | 1919
| C3 | A1/J1 | A2/J4 | 1 | no | [6 empty] | 202 | 868
| C4 | A1/J1 | A2/J4 | 1 | no | [6 empty] | 198 | 817
| C5 | A1/J1 | A2/J4 | 1 | no | [6 empty] | 149 | 466
| C6 | A1/J1 | A2/J4 | 1 | no | [6 empty] | 258 | 610
| D1 | A1/J1 | A2/J4 | 1 | no | [6 empty] | 377 | 380
| D2 | A1/J1 | A2/J4 | 1 | no | [6 empty] | 203 | 719
| D3 | A1/J1 | A2/J4 | 1 | no | [6 empty] | 366 | 380
| D4 | A1/J1 | A2/J4 | 1 | no | [6 empty] | 218 | 380
| D5 | A1/J1 | A2/J4 | 1 | YES | not recorded, testing continued below when failure seen | [5 empty] | 142 | 824
|  | A1/J1 | A2/J4 | 5 | YES | 179622 | 92910 | 38987057 | 9413 | 223 |  | 142 | 824
|  | A1/J1/OFS | A2/J4 | 5 | no | 0 | 0 | 35117977 | 0 | 0 |  | 142 | 824
|  | A1/J1/SMF | A2/J4 | 5 | YES | 277637 | 254798 | 35545209 | 3402 | 132 |  | 142 | 824
| D6 | A1/J1 | A2/J4 | 1 | no | [6 empty] | 460 | 349
| E1 | A1/J1 | A2/J4 | 1 | no | [6 empty] | 243 | 416
| E2 | A1/J1 | A2/J4 | 1 | no | [6 empty] | 243 | 1919
| E3 | A1/J1 | A2/J4 | 1 | no | [6 empty] | 488 | 477
| E4 | A1/J1 | A2/J4 | 1 | no | [6 empty] | 198 | 817
| E5 | A1/J1 | A2/J4 | 1 | no | [6 empty] | 139 | 347
| E6 | A1/J1 | A2/J4 | 1 | no | [6 empty] | 253 | 1356
Sandia National Labs California 4-November-1997
Siecor 50 um
Building 912 to building 904. |  |  | 460 m | inc. jumpers. Networking equipment room to auditorium
912BN04 ->904FA10
Cable | Fiber | Transmit | Receive | Test | Err | CRC | Symbol | Packet | Sequence | Length | P[r] | Modal B/W | Modal B/W
name/ | name/ | GBICID/ | GBICID/ | time | ??? | error | error | count | error | error | (dBm) | 850 nm | 1300 nm
ID tag | ID tag | JMPRID | JMPRID | (min) |  | count | count |  | count | count |  | (MHz*km) | (MHz*km)
912BN04 ->904FA10
| 1 | A1/JW | A2/JN | 1 | no | [5 empty] | -6
| 2 | A1/JW | A2/JN | 1 | no | [5 empty] | -6
| 3 | IN USE
| 4 | IN USE
| 5 | A1/JW | A2/JN | 1 | no | [5 empty] | -5.9
| 6 | A1/JW | A2/JN | 1 | no | [5 empty] | -6
| 7 | A1/JW | A2/JN | 1 | no | [5 empty] | -5.9
| 8 | A1/JW | A2/JN | 1 | no
| 9 | A1/JW | A2/JN | 1 | no
| 10 | A1/JW | A2/JN | 1 | no
| 11 | A1/JW | A2/JN | 1 | no
| 12 | A1/JW | A2/JN | 1 | no
Sandia National Labs California 4-November-1997
Siecor 50 um
Building 912 to building 904. |  |  | 460 m | inc. jumpers. Networking equipment room to auditorium
912BN05 ->904FA11
Cable | Fiber | Transmit | Receive | Test | Err | CRC | Symbol | Packet | Sequence | Length | P[r] | Modal B/W | Modal B/W
name/ | name/ | GBICID/ | GBICID/ | time | ??? | error | error | count | error | error | (dBm) | 850 nm | 1300 nm
ID tag | ID tag | JMPRID | JMPRID | (min) |  | count | count |  | count | count |  | (MHz*km) | (MHz*km)
912BN05 ->904FA11
| 1 | A1/JW | A2/JN | 1 | no | [5 empty] | -6
| 2 | A1/JW | A2/JN | 1 | no
| 3 | A1/JW | A2/JN | 1 | no
| 4 | A1/JW | A2/JN | 1 | no
| 5 | A1/JW | A2/JN | 1 | no
| 6 | A1/JW | A2/JN | 1 | no
| 7 | A1/JW | A2/JN | 1 | no
| 8 | A1/JW | A2/JN | 1 | no
| 9 | A1/JW | A2/JN | 1 | no
| 10 | A1/JW | A2/JN | 1 | no
| 11 | A1/JW | A2/JN | 1 | no
| 12 | A1/JW | A2/JN | 1 | no
Sandia National Labs California 4-November-1997
Siecor 50 um
Building 912 to building 904. |  |  | 460 m | inc. jumpers. Networking equipment room to auditorium
912BN06 ->904FA12
Cable | Fiber | Transmit | Receive | Test | Err | CRC | Symbol | Packet | Sequence | Length | P[r] | Modal B/W | Modal B/W
name/ | name/ | GBICID/ | GBICID/ | time | ??? | error | error | count | error | error | (dBm) | 850 nm | 1300 nm
ID tag | ID tag | JMPRID | JMPRID | (min) |  | count | count |  | count | count |  | (MHz*km) | (MHz*km)
912BN06 ->904FA12
| 1 | A1/JW | A2/JN | 1 | no
| 2 | A1/JW | A2/JN | 1 | no | [5 empty] | -6
| 3 | A1/JW | A2/JN | 1 | no
| 4 | A1/JW | A2/JN | 1 | no
| 5 | A1/JW | A2/JN | 1 | no
| 6 | A1/JW | A2/JN | 1 | no
| 7 | A1/JW | A2/JN | 1 | no
| 8 | A1/JW | A2/JN | 1 | no
| 9 | A1/JW | A2/JN | 1 | no
| 10 | A1/JW | A2/JN | 1 | no
| 11 | A1/JW | A2/JN | 1 | no
| 12 | A1/JW | A2/JN | 1 | no
| 1 | A3/JW | D1/JN | 1 | no | [5 empty] | -3.7
| 12 | B1/JW | D1/JN | 1 | no | [5 empty] | -6.1
Sandia National Labs California 4-November-1997
Siecor 62.5 um
Building 910 to building 943. |  |  | 752 m | inc. jumpers. Networking equipment room to pumphouse/telephone closet
910BK12 ->943FA12
Cable | Fiber | Transmit | Receive | Test | Err | CRC | Symbol | Packet | Sequence | Length | P[r] | Modal B/W | Modal B/W
name/ | name/ | GBICID/ | GBICID/ | time | ??? | error | error | count | error | error | (dBm) | 850 nm | 1300 nm
ID tag | ID tag | JMPRID | JMPRID | (min) |  | count | count |  | count | count |  | (MHz*km) | (MHz*km)
910BK12 ->943FA12
| 1 | IN USE
| 2 | IN USE
| 3 | A1/JW | A2/JN | 1 | no | [5 empty] | -6.5
| 4 | A1/JW | A2/JN | 1 | no
| 5 | A1/JW | A2/JN | 1 | no
| 6 | A1/JW | A2/JN | 1 | no
| 7 | A1/JW | A2/JN | 1 | no
| 8 | A1/JW | A2/JN | 1 | no
Sandia National Labs California 4-November-1997
ATT 50 um
Building 910 to building 943. |  |  | 754 m | inc. jumpers. Networking equipment room to pumphouse/telephone closet
910BK09 ->943FA09 |  |  |  | Note that because these fibers were terminated with biconic connectors, an additional 1 m long
50 um jumper had to be inserted at each end of the cable
Cable | Fiber | Transmit | Receive | Test | Err | CRC | Symbol | Packet | Sequence | Length | P[r] | Modal B/W | Modal B/W
name/ | name/ | GBICID/ | GBICID/ | time | ??? | error | error | count | error | error | (dBm) | 850 nm | 1300 nm
ID tag | ID tag | JMPRID | JMPRID | (min) |  | count | count |  | count | count |  | (MHz*km) | (MHz*km)
910BK09 ->943FA09
| 1 | A1/JW | A2/JN | [7 empty] | -5.6
| 2 | A1/JW | A2/JN | [7 empty] | -5.6
| 3 | A1/JW | A2/JN | 1 | YES | not recorded, see below |  |  |  |  | -5.6
| 3 | A1/JW | A2/JN | 3.5 | YES | 54 | 21 | 20669924 | 14 | 0 | -5.6
| 3 | A1/JW/SMF | A2/JN | 1 | YES | lots of errors, much higher than without SMF jumper |  |  |  |  | -6.6
| 3 | A1/JW/OFS | A2/JN | 5 | no | [5 empty] | -11
Lawrence Livermore National Lab California 3-November-1997
ATT 62.5 um |  | v. 1990 | 450.8 m |  | Over filled Modal B/W was spec'd, not measured
Node 9 building 430 to building 6179.
Cable | Fiber | Transmit | Receive | Test | Err | CRC | Symbol | Packet | Sequence | Length | P[r] | Modal B/W | Modal B/W
name/ | name/ | GBICID/ | GBICID/ | time | ??? | error | error | count | error | error | (dBm) | 850 nm | 1300 nm
ID tag | ID tag | JMPRID | JMPRID | (min) |  | count | count |  | count | count |  | (MHz*km) | (MHz*km)
LGUM0902
| 1 | A1 | A2 | 1 | no | [6 empty] | 200 | 800
| 2 | IN USE
| 3 | IN USE
| 4 | A1 | A2 | 1 | no | [6 empty] | 200 | 800
| 5 | A1 | A2 | 1 | no | [6 empty] | 200 | 800
| 6 | A1 | A2 | 1 | no | [6 empty] | 200 | 800
| 7 | A1 | A2 | 1 | no | [6 empty] | 200 | 800
| 8 | A1 | A2 | 1 | no | [6 empty] | 200 | 800
Lawrence Livermore National Lab California 3-November-1997
ATT 62.5 um |  | v. 1993 | 461 m |  | Over filled Modal B/W was spec'd, not measured
Node 9 building 430 to building 6127.
Cable | Fiber | Transmit | Receive | Test | Err | CRC | Symbol | Packet | Sequence | Length | P[r] | Modal B/W | Modal B/W
name/ | name/ | GBICID/ | GBICID/ | time | ??? | error | error | count | error | error | (dBm) | 850 nm | 1300 nm
ID tag | ID tag | JMPRID | JMPRID | (min) |  | count | count |  | count | count |  | (MHz*km) | (MHz*km)
LGUM0914
| 1 | A1 | A2 | 1 | YES |  | LOTS, dead fiber |  |  |  |  | 200 | 500
| 2 | A1 | A2 | 1 | no | [6 empty] | 200 | 500
| 3 | IN USE
| 4 | IN USE
| 5 | A1 | A2 | 1 | no | [6 empty] | 200 | 500
| 6 | A1 | A2 | 1 | no | [6 empty] | 200 | 500
| 7 | A1 | A2 | 1 | no | [6 empty] | 200 | 500
| 8 | A1 | A2 | 1 | no | [6 empty] | 200 | 500
Lawrence Livermore National Lab California 3-November-1997
ATT 62.5 um |  | v. 1990 | 484 m |  | Over filled Modal B/W was spec'd, not measured
Node 9 building 430 to building 6203.
Cable | Fiber | Transmit | Receive | Test | Err | CRC | Symbol | Packet | Sequence | Length | P[r] | Modal B/W | Modal B/W
name/ | name/ | GBICID/ | GBICID/ | time | ??? | error | error | count | error | error | (dBm) | 850 nm | 1300 nm
ID tag | ID tag | JMPRID | JMPRID | (min) |  | count | count |  | count | count |  | (MHz*km) | (MHz*km)
LGUM0913
| 1 | IN USE | [9 empty] | 200 | 800
| 2 | IN USE | [9 empty] | 200 | 800
| 3 | A1 | A2 | 1 | no | [6 empty] | 200 | 800
| 4 | A1 | A2 | 1 | no | [6 empty] | 200 | 800
| 5 | A1 | A2 | 1 | no | [6 empty] | 200 | 800
| 6 | A1 | A2 | 1 | no | [6 empty] | 200 | 800
| 7 | A1 | A2 | 1 | no | [6 empty] | 200 | 800
| 8 | A1 | A2 | 1 | no | [6 empty] | 200 | 800
Lawrence Livermore National Lab California 3-November-1997
ATT 62.5 um |  | v. 1990 | 533 m |  | Over filled Modal B/W was spec'd, not measured
Node 9 building 430 to building 611.
Cable | Fiber | Transmit | Receive | Test | Err | CRC | Symbol | Packet | Sequence | Length | P[r] | Modal B/W | Modal B/W
name/ | name/ | GBICID/ | GBICID/ | time | ??? | error | error | count | error | error | (dBm) | 850 nm | 1300 nm
ID tag | ID tag | JMPRID | JMPRID | (min) |  | count | count |  | count | count |  | (MHz*km) | (MHz*km)
LGUM0906
| 1 | IN USE
| 2 | IN USE
| 3 | A1 | A2 | 1 | no | [6 empty] | 200 | 800
| 4 | A1 | A2 | 1 | no | [6 empty] | 200 | 800
| 5 | A1 | A2 | 1 | no | [6 empty] | 200 | 800
| 6 | A1 | A2 | 1 | no | [6 empty] | 200 | 800
| 7 | A1 | A2 | 1 | no | [6 empty] | 200 | 800
| 8 | A1 | A2 | 1 | no | [6 empty] | 200 | 800
Lawrence Livermore National Lab California 3-November-1997
Siecor 62.5 um |  | v. 1995 | 622 m |  | Over filled Modal B/W was spec'd, not measured
Node 9 building 430 to building 415.
Cable | Fiber | Transmit | Receive | Test | Err | CRC | Symbol | Packet | Sequence | Length | P[r] | Modal B/W | Modal B/W
name/ | name/ | GBICID/ | GBICID/ | time | ??? | error | error | count | error | error | (dBm) | 850 nm | 1300 nm
ID tag | ID tag | JMPRID | JMPRID | (min) |  | count | count |  | count | count |  | (MHz*km) | (MHz*km)
LGUM0919
| 1 | IN USE
| 2 | IN USE
| 3 | A1 | A2 | 1 | no | [6 empty] | 160 | 500
| 4 | A1 | A2 | 1 | no | [6 empty] | 160 | 500
| 5 | A1 | A2 | 1 | no | [6 empty] | 160 | 500
| 6 | A1 | A2 | 1 | YES | 12 | 5 | ~7000000 |  |  |  | 160 | 500
| 7 | A1 | A2 | 1 | no | [6 empty] | 160 | 500
| 8 | A1 | A2 | 1 | no | [6 empty] | 160 | 500
| 9 | A1 | A2 | 1 | no | [6 empty] | 160 | 500
| 10 | A1 | A2 | 1 | no | [6 empty] | 160 | 500
| 11 | A1 | A2 | 1 | no | [6 empty] | 160 | 500
| 12 | A1 | A2 | 1 | no | [6 empty] | 160 | 500
| 6 | A1 | A2 | 5 | YES | 18 | 5 | ~36000000 |  |  |  | 160 | 500
| 6 | A1/SMF | A2 | 5 | YES | Lots | Lots | Few |  |  |  | 160 | 500
| 6 | A1/OFS | A2 | 5 | no | 0 | 0 | ~36000000 | 0 | 0 |  | 160 | 500
END | END | END | END | END | END | END | END | END | END | END | END | END | END | END
LGUM0919 (160/500) |  |  | LGUM0906(200/800) |  |  | LGUM0913(200/800) |  |  | LGUM0914(200/500) |  |  | LGUM0902(200/800)
[9 empty] | 1 | 461 |  | 1 | 451
[9 empty] | 2 | 461
3 | 622 |  | 3 | 533 |  | 3 | 484
4 | 622 |  | 4 | 533 |  | 4 | 484 |  |  |  |  | 4 | 451
5 | 622 |  | 5 | 533 |  | 5 | 484 |  | 5 | 461 |  | 5 | 451
6 | 622 |  | 6 | 533 |  | 6 | 484 |  | 6 | 461 |  | 6 | 451
7 | 622 |  | 7 | 533 |  | 7 | 484 |  | 7 | 461 |  | 7 | 451
8 | 622 |  | 8 | 533 |  | 8 | 484 |  | 8 | 461 |  | 8 | 451
9 | 622
10 | 622
11 | 622
12 | 622
910BK09-943FA09(50 u) |  |  | 910BK12-943FA12(62.5 u) |  |  | 912BN06-904FA12(50 u) |  |  | 912BN05-904FA11(50 u) |  |  | 912BN04-904FA10(50 u)
1 | 754 |  |  |  |  | 1 | 460 |  | 1 | 460 |  | 1 | 460
2 | 754 |  |  |  |  | 2 | 460 |  | 2 | 460 |  | 2 | 460
3 | 754 |  | 3 | 752 |  | 3 | 460 |  | 3 | 460 |  | 3 | 460
|  |  | 4 | 752 |  | 4 | 460 |  | 4 | 460 |  | 4 | 460
|  |  | 5 | 752 |  | 5 | 460 |  | 5 | 460 |  | 5 | 460
|  |  | 6 | 752 |  | 6 | 460 |  | 6 | 460 |  | 6 | 460
|  |  | 7 | 752 |  | 7 | 460 |  | 7 | 460 |  | 7 | 460
|  |  | 8 | 752 |  | 8 | 460 |  | 8 | 460 |  | 8 | 460
[6 empty] | 9 | 460 |  | 9 | 460 |  | 9 | 460
[6 empty] | 10 | 460 |  | 10 | 460 |  | 10 | 460
[6 empty] | 11 | 460 |  | 11 | 460 |  | 11 | 460
[6 empty] | 12 | 460 |  | 12 | 460 |  | 12 | 460
Test Cable |  |  | N2-B48 |  |  | N2-B25 |  |  | N2-B5 |  |  | N1-B90
1 | 260 |  | 1 | 299 |  |  |  |  | 1 | 489
2 | 260 |  | 2 | 299 |  |  |  |  | 2 | 489
|  |  | 3 | 299 |  | 3 | 433 |  | 3 | 489 |  | 3 | 684
|  |  | 4 | 299 |  | 4 | 433 |  | 4 | 489 |  | 4 | 684
|  |  | 5 | 299 |  | 5 | 433 |  | 5 | 489 |  | 5 | 684
|  |  | 6 | 299 |  | 6 | 433 |  | 6 | 489 |  | 6 | 684
[6 empty] | 7 | 433 |  | 7 | 489 |  | 7 | 684
[6 empty] | 8 | 433 |  | 8 | 489 |  | 8 | 684
[6 empty] | 9 | 433 |  | 9 | 489 |  | 9 | 684
[6 empty] | 10 | 433 |  | 10 | 489 |  | 10 | 684
[6 empty] | 11 | 433 |  | 11 | 489 |  | 11 | 684
[6 empty] | 12 | 433 |  | 12 | 489 |  | 12 | 684
[6 empty] | 13 | 433 |  | 13 | 489 |  | 13 | 684
[6 empty] | 14 | 433 |  | 14 | 489 |  | 14 | 684
[6 empty] | 15 | 433 |  | 15 | 489 |  | 15 | 684
[6 empty] | 16 | 433 |  | 16 | 489 |  | 16 | 684
[6 empty] | 17 | 433 |  | 17 | 489 |  | 17 | 684
[6 empty] | 18 | 433 |  | 18 | 489 |  | 18 | 684
[6 empty] | 19 | 433 |  |  |  |  | 19 | 684
[6 empty] | 20 | 433 |  |  |  |  | 20 | 684
[12 empty] | 21 | 684
[12 empty] | 22 | 684
[12 empty] | 23 | 684
[12 empty] | 24 | 684
[12 empty] | 25 | 684
[12 empty] | 26 | 684
[12 empty] | 27 | 684
[12 empty] | 28 | 684
[12 empty] | 29 | 684
[12 empty] | 30 | 684
Test Cable (62.5) |  |  | N2-B48(62.5) |  |  |  | N2-B25(62.5) |  | N2-B5(62.5) |  |  | 912BN06-904FA12(50)
| 1 | 260 |  | 1 | 299 | [6 empty] | 1 | 460
| 2 | 260 |  | 2 | 299
|  |  |  | 3 | 299 |  | 3 | 433
|  |  |  | 4 | 299 |  | 4 | 433
|  |  |  | 5 | 299 |  |  |  | 5 | 489
|  |  |  | 6 | 299
[12 empty] | 12 | 460
[7 empty] | 13 | 433
[9 empty] | 14 | 489
Lawrence Berkeley National Lab 15-December-1997
Node 1 to B55 |  |  |  | Nice computer room to some poor dude's office FULL OF SCUBA GEAR
Berktek 62.5um |  |  | 404 m | inc. 2 meter jumpers
Cable | Fiber | Transmit | Receive | Test | Err | CRC | Symbol | Packet | Sequence | Length | P[r] | Modal B/W | Modal B/W
name/ | name/ | GBICID/ | GBICID/ | time | ??? | error | error | count | error | error | (dBm) | 850 nm | 1300 nm
ID tag | ID tag | JMPRID | JMPRID | (min) |  | count | count |  | count | count |  | (MHz*km) | (MHz*km)
N1-B55
| A1 | A1 | A2 | 1 | NO | [5 empty] | -16
| A2 | A1 | A2 | 5 | NO | [5 empty] | -16.5
| A3 | IN USE
| A4 | IN USE
| A5 | IN USE
| A6 | IN USE
| B1 | IN USE
| B2 | IN USE
| B3 | A1 | A2 | 1 | NO | [5 empty] | -16.5
| B3 | A1 | A2 | 5 | NO |  |  | 35513992 |  |  | -16.5
| B4 | A1 | A2 | 1 | NO | [5 empty] | -16.3
| B5 | A1 | A2 | 1 | NO | [5 empty] | -16.2
| B6 | A1 | A2 | 1 | YES |  |  | NOT RECORDED SEE BELOW |  |  | -15.3
| B6 | A1 | A2 | 5 | YES | 3 | 0 | 35521303 | 0 | 0 | -15.3
| B6 | A1 | A2 | 5 | NO |  |  | 35519628 |  |  | -16.2
| B6 | A1 | A2 | 10 | YES | 2 | 0 | 71027460 | 0 | 0 | -16.2
| B6 | A1/15UOFF | A2 | 10 | NO | 0 | 0 | 71029834 | 0 | 0 | -16.4
| B6 | A1/19UOFF | A2 | 10 | YES | 0 | 447 | 71028607 | 0 | 60 | -16.4
| C1 | A1 | A2 | 1 | NO | [5 empty] | -16.5
| C2 | A1 | A2 | 1 | YES | 19 | 8 | 7113667 | 1 | 0 | -16.9
| C2 | A1 | A2 | 1 | YES | 26 | 9 | 7113654 | 2 | 0 | -16.5
| C2 | A1/15UOFF | A2 | 1 | NO | 0 | 0 | 7114756 | 0 | 0 | -16.6
| C2 | A1/15UOFF | A2 | 5 | NO | 0 | 0 | 35520817 | 0 | 0 | -16.6
| C2 | A1/19UOFF | A2 | 5 | NO | 0 | 0 | 35519619 | 0 | 0 | -16.6
| C3 | A1 | A2 | 1 | NO | [5 empty] | -16.2
| C4 | A1 | A2 | 1 | NO | [5 empty] | -16.1
| C5 | A1 | A2 | 1 | NO | [5 empty] | -16
| C6 | A1 | A2 | 1 | NO | [5 empty] | -16.6
| B3 | D2 | D1 | 1 | YES | 87 | 71 | 7112366 | 19 | 0 | -14.2
| B3 | C3 | D1 | 1 | YES | 43 | 22 | 7112345 | 220 | 15 | -14.2
| B3 | B1 | D1 | 1 | YES | 299 | 98 | 7113510 | 312 | 39 | -14
| B3 | A8 | D1 | 1 | YES | 0 | 0 | 7113510 | 17 | 4 | -14
| B3 | A20 | D1 | 1 | NO | 0 | 0 | 7114761 | 0 | 0 | -14
| B3 | A25 | D1 | 1 | NO | 0 | 0 | 7114746 | 0 | 0 | -14
| B3 | A34 | D1 | 1 | NO | 0 | 0 | 7113569 | 0 | 0 | -14.5
| B6 | D2 | D1 | 1 | NO | [5 empty] | -14.2
| B6 | C3 | D1 | 1 | NO | [5 empty] | -14.1
| B6 | B1 | D1 | 1 | NO | [5 empty] | -14.2
| B6 | A8 | D1 | 1 | NO | [5 empty] | -14.2
| B6 | A20 | D1 | 1 | NO | [5 empty] | -14.4
| B6 | A25 | D1 | 1 | NO | [5 empty] | -14.6
| B6 | A34 | D1 | 1 | NO | [5 empty] | -14.4
Lawrence Berkeley National Lab 16-December-1997
Node 2 to B7 |  |  |  | WAREHOUSE KINDA THING TO GOOD OLD NODE 2
Berktek 62.5um |  |  | 330 | inc. jumpers
Cable | Fiber | Transmit | Receive | Test | Err | CRC | Symbol | Packet | Sequence | Length | P[r] | Modal B/W | Modal B/W
name/ | name/ | GBICID/ | GBICID/ | time | ??? | error | error | count | error | error | (dBm) | 850 nm | 1300 nm
ID tag | ID tag | JMPRID | JMPRID | (min) |  | count | count |  | count | count |  | (MHz*km) | (MHz*km)
N2-B7 | B7 ID TAG
D1-1 | C1-2 | IN USE
D1-2 | C1-2 | IN USE
D1-3 | C1-3 | IN USE
D1-4 | C1-4 | IN USE
D1-5 | C1-5 | A1 | A2 | 1
D1-6 | C1-6 | A1 | A2 | 1 | NO | [5 empty] | -16
E1-1 | C1-7 | A1 | A2 | 1 | NO | [5 empty] | -16
E1-2 | C1-8 | A1 | A2 | 1 | YES | 0 | 0 | 7111167 | 2821 | 566 | -16 |  |  | Very Weird | Errors during one minute test
E1-2 | C1-8 | A1 | A2 | 5 | NO | 0 | 0 | ~35000000 | 0 | 0 | -16 |  |  | are probably the result of physical disturbance
E1-2 | C1-8 | A1 | A2 | 10 | NO | 0 | 0 | 71029813 | 0 | 0 | -16 |  |  | of the fiber patch panel or cabling.
E1-3 | C1-9 | A1 | A2 | 1 | NO | [5 empty] | -16
E1-4 | C1-10 | A1 | A2 | 1 | NO | [5 empty] | -16
E1-5 | C1-11 | A1 | A2 | 1 | NO | [5 empty] | -16.1
E1-6 | C1-12 | A1 | A2 | 1 | NO | [5 empty] | -16.2
F1-1 | C1-13 | A1 | A2 | 1 | NO | [5 empty] | -16
F1-2 | C1-14 | A1 | A2 | 1 | NO | [5 empty] | -16
F1-3 | C1-15 | A1 | A2 | 1 | NO | [5 empty] | -16.1
F1-4 | C1-16 | A1 | A2 | 1 | NO | [5 empty] | -16
| C1-B1 | A1 | A2 | 1 | NO | [5 empty] | -16.1
| C1-B2 | A1 | A2 | 1 | NO | [5 empty] | -16.2
| C1-B3 | A1 | A2 | 1 | NO | [5 empty] | -16.2
| C1-B4 | A1 | A2 | 1 | NO | [5 empty] | -16
| C1-B1 | B2 | D1 | 1 | NO | [5 empty] | -14
| C1-B2 | B2 | D1 | 1 | NO | [5 empty] | -14
| C1-B3 | B2 | D1 | 1 | NO | [5 empty] | -14
| C1-B4 | B2 | D1 | 1 | NO | [5 empty] | -14
D1-5 | C1-5 | B2 | D1 | 1 | NO | [5 empty] | -14
D1-5 | C1-5 | B2 | D1 | 5 | NO |  |  | 35519570 |  |  | -14
D1-6 | C1-6 | B2 | D1 | 1 | NO | [5 empty] | -14
E1-1 | C1-7 | B2 | D1 | 1 | NO | [5 empty] | -14
E1-2 | C1-8 | B2 | D1 | 1 | NO | [5 empty] | -14
E1-3 | C1-9 | B2 | D1 | 1 | NO | [5 empty] | -14
E1-4 | C1-10 | B2 | D1 | 1 | NO | [5 empty] | -14
E1-5 | C1-11 | B2 | D1 | 1 | NO | [5 empty] | -14
E1-6 | C1-12 | B2 | D1 | 1 | NO | [5 empty] | -14
F1-2 | C1-14 | B2 | D1 | 1 | NO | [5 empty] | -14
F1-3 | C1-15 | B2 | D1 | 1 | NO | [5 empty] | -14
F1-4 | C1-16 | B2 | D1 | 1 | NO | [5 empty] | -14
| C1-B1 | C3 | D1 | 1 | NO | [5 empty] | -14
| C1-B2 | C3 | D1 | 1 | NO | [5 empty] | -14
| C1-B3 | C3 | D1 | 1 | NO | [5 empty] | -14
| C1-B4 | C3 | D1 | 1 | NO | [5 empty] | -14
F1-4 | C1-16 | C3 | D1 | 1 | YES | 17976 | 10770 | 7111078 | 4789 | 452 | -14
F1-4 | C1-16 | B2 | D1 | 1 | NO | [5 empty] | -14
F1-4 | C1-16 | D2 | D1 | 1 | NO | [5 empty] | -14
F1-4 | C1-16 | A8 | D1 | 1 | YES | 30 | 21 | 7114761 | 12 | 1 | -14
F1-4 | C1-16 | A20 | D1 | 1 | NO | [5 empty] | -14
F1-4 | C1-16 | A25 | D1 | 1 | NO | [5 empty] | -14
F1-4 | C1-16 | A34 | D1 | 1 | NO | [5 empty] | -14
F1-1 | C1-13 | A8 | D1 | 1 | YES | 0 | 1 | 7114715 | 0 | 0 | -14
F1-1 | C1-13 | A8 | D1 | 5 | NO |  |  | 35519564 |  |  | -14
F1-1 | C1-13 | C3 | D1 | 5 | YES | 12015 | 5639 | 35521932 | 5186 | 562 | -14
F1-1 | C1-13 | A8 | D1 | 30 | YES | 3 | 4 | 213067135 | 2 | 0 | -14
F1-1 | C1-13 | A8 | D1 | 5 | NO | [5 empty] | -14 |  |  | TRANSMIT FROM N2
D1-5 | C1-5 | A8 | D1 | 1 | NO | [5 empty] | -14 |  |  | TRANSMIT FROM N2
D1-6 | C1-6 | A8 | D1 | 1 | NO | [5 empty] | -14 |  |  | TRANSMIT FROM N2
E1-6 | C1-12 | A8 | D1 | 1 | NO | [5 empty] | -14 |  |  | TRANSMIT FROM N2
Lawrence Berkeley National Lab 16-December-1997
NODE2 TO B25 |  |  |  | PCB SHOP TO GOOD OLD NODE 2
LIGHTGUIIDE 62.5 UM |  |  | 424 | inc. jumpers
ALL OF THE RESULTS FOR THIS CABLE ARE QUESTIONABLE DUE TO A BROKEN FERRULE ON ONE OF THE JUMPERS,
WHICH WAS FOUND THE NEXT DAY WHEN TESTING RESUMED AT LAWRENCE LIVERMORE LABS
Cable | Fiber | Transmit | Receive | Test | Err | CRC | Symbol | Packet | Sequence | Length | P[r] | Modal B/W | Modal B/W
name/ | name/ | GBICID/ | GBICID/ | time | ??? | error | error | count | error | error | (dBm) | 850 nm | 1300 nm
ID tag | ID tag | JMPRID | JMPRID | (min) |  | count | count |  | count | count |  | (MHz*km) | (MHz*km)
N2-B25 | B25TAG
| C1-4 | A1 | A2 | 1 | YES | 14937 | 13253 | 7107045 |  |  | -16
| C1-4 | A1/15UOFF | A2 | 1 | YES | 4191201 | 33353981 | 6653408 | 7679407 | 3310805 | -16
| C1-4 | A1/19UOFF | A2 | 1 | YES | 3536414 | 77147025 | 5285932 | 5830658 | 3605403 | -16
| C1-4 | A1/SM | A2 | 1 | YES | 838962 | 726223 | 7107063 | 192000 | 7660 | -16
| C1-13 | A1/SM | A2 | 1 | YES | LOTS |  | NONE |  |  | -16
| C1-13 | A1 | B4 | 1 | YES | 343518 | 112851267 | 576314 | 959961 | 360671 | -16
| C1-13 | A1/SM | B4 | 1 | YES | 22308 | 186806609 | 32348 | 52768 | 22192 | -16
| C1-13 | A1/15UOFF | B4 | 1 | YES | LOTS |  | NONE |  |  | -16
| C1-13 | A1/19UOFF | B4 | 1 | YES | LOTS |  | NONE |  |  | -16
| C1-6 | A1 | A2 | 1 | YES | 3744096 | 2380952 | 7105691 | 1825514 | 61605 | -16
| C1-6 | A1/15UOFF | A2 | 1 | YES | 3962257 | 11473345 | 6549071 | 6131427 | 1087086 | -16
| C1-6 | A1/19UOFF | A2 | 1 | YES | 4827260 | 4362433 | 7085219 | 2525091 | 138595 | -16
| C1-5 | A1 | A2 | 1 | NO | 0 | 0 | 7107088 | 0 | 0 | -16
| C1-13 | B5 | B4 | 1 | YES | 221875 | 102005483 | 369920 | 659842 | 240378 | -16
| C1-13 | B5/15UOFF | B4 | 1 | YES | 5 | 158894207 | 6 | 3245 | 1433 | -16
| C1-13 | B5/19UOFF | B4 | 1 | YES | LOTS |  | NONE |  |  | -16
Lawrence Livermore Lab 17-December-1997
Node 1 from B451
LIGHTGUIIDE 62.5 UM |  |  | 461 m | inc. jumpers
Cable | Fiber | Transmit | Receive | Test | Err | CRC | Symbol | Packet | Sequence | Length | P[r] | Modal B/W | Modal B/W
name/ | name/ | GBICID/ | GBICID/ | time | ??? | error | error | count | error | error | (dBm) | 850 nm | 1300 nm
ID tag | ID tag | JMPRID | JMPRID | (min) |  | count | count |  | count | count |  | (MHz*km) | (MHz*km)
N1-B451 | Node 1 TAG
| 111-42 | A1 | A2 | 1 | NO | 0 | 0 | 7107104 | 0 | 0 | -16
| 111-07 | A1 | A2 | 1 | NO | 0 | 0 | 7107014 | 0 | 0 | -16
| 111-08 | A1 | A2 | 1 | NO | 0 | 0 | 7107002 | 0 | 0 | -16
| 111-05 | A1 | A2 | 1 | NO | 0 | 0 | 7107052 | 0 | 0 | -16
| 111-06 | A1 | A2 | 1 | NO | 0 | 0 | 7107045 | 0 | 0 | -16
| 111-13 | A1 | A2 | 1 | NO | 0 | 0 | 7107042 | 0 | 0 | -16
| 111-14 | A1 | A2 | 1 | NO | 0 | 0 | 7107073 | 0 | 0 | -16
| 111-15 | A1 | A2 | 1 | NO | 0 | 0 | 7106995 | 0 | 0 | -16
| 111-16 | A1 | A2 | 1 | NO | 0 | 0 | 7105873 | 0 | 0 | -16
| 111-17 | A1 | A2 | 1 | NO | 0 | 0 | 7107002 | 0 | 0 | -16
| 111-18 | A1 | A2 | 1 | NO | 0 | 0 | 7107048 | 0 | 0 | -16
| 111-19 | A1 | A2 | 1 | NO | 0 | 0 | 7107067 | 0 | 0 | -16
| 111-20 | A1 | A2 | 1 | NO | 0 | 0 | 7107063 | 0 | 0 | -16
| 111-29 | A1 | A2 | 1 | NO | 0 | 0 | 7107050 | 0 | 0 | -16
| 111-30 | A1 | A2 | 1 | NO | 0 | 0 | 7107055 | 0 | 0 | -16
| 111-31 | A1 | A2 | 1 | NO | 0 | 0 | 7107012 | 0 | 0 | -16
| 111-32 | A1 | A2 | 1 | NO | 0 | 0 | 7107032 | 0 | 0 | -16
| 111-37 | A1 | A2 | 1 | NO | 0 | 0 | 7106993 | 0 | 0 | -16
| 111-38 | A1 | A2 | 1 | NO | 0 | 0 | 7107022 | 0 | 0 | -16
| 111-39 | A1 | A2 | 1 | NO | 0 | 0 | 7107050 | 0 | 0 | -16
| 111-40 | A1 | A2 | 1 | NO | 0 | 0 | 7107005 | 0 | 0 | -16
| 111-41 | A1 | A2 | 1 | NO | 0 | 0 | 7107010 | 0 | 0 | -16
| 111-45 | A1 | A2 | 1 | NO | 0 | 0 | 7107063 | 0 | 0 | -16
| 111-46 | A1 | A2 | 1 | NO | 0 | 0 | 7107056 | 0 | 0 | -16
| 111-47 | A1 | A2 | 1 | NO | 0 | 0 | 7107014 | 0 | 0 | -16
| 111-48 | A1 | A2 | 1 | NO | 0 | 0 | 7107015 | 0 | 0 | -16
| 104-7 | A1 | A2 | 1 | NO | 0 | 0 | 7107017 | 0 | 0 | -16
| 104-8 | A1 | A2 | 1 | NO | 0 | 0 | 7105851 | 0 | 0 | -16
| 104-1 | A1 | A2 | 1 | NO | 0 | 0 | 7107017 | 0 | 0 | -16
| 104-2 | A1 | A2 | 1 | NO | 0 | 0 | 7107036 | 0 | 0 | -16
| 104-5 | A1 | A2 | 1 | NO | 0 | 0 | 7107018 | 0 | 0 | -16
| 104-6 | A1 | A2 | 1 | NO | 0 | 0 | 7107059 | 0 | 0 | -16
| 104-6 | C3 | D1 | 1 | NO | 0 | 0 | 7107047 | 0 | 0 | -14
| 104-7 | C3 | D1 | 1 | NO | 0 | 0 | 7105874 | 0 | 0 | -14
| 104-8 | C3 | D1 | 1 | NO | 0 | 0 | 7107019 | 0 | 0 | -14
| 111-6 | C3 | D1 | 1 | YES | 642 | 317 | 7105868 | 86 | 2 | -14
| 111-6 | C3 | D1 | 5 | YES | 2716 | 1394 | 35513188 | 419 | 10 | -14
| 111-6 | B1 | D1 | 1 | NO | 0 | 0 | 7107062 | 0 | 0 | -14
| 111-6 | A8 | D1 | 1 | YES | 77 | 63 | 7107005 | 22 | 0 | -14
| 111-6 | D2 | D1 | 1 | YES | 1 | 1 | 7107011 | 0 | 0 | -14
| 111-6 | D2 | D1 | 5 | YES | 35 | 15 | 35513217 | 6 | 1 | -14
| 111-6 | A20 | D1 | 5 | YES | 4 | 6 | 35512140 | 1 | 0 | -14
| 111-6 | A20 | D1 | 1 | YES | 1 | 1 | 7107049 | 0 | 0 | -14
| 111-13 | A1 | A2 | 5 | YES | 2100 | 1300 | 35512090 | 125 | 0 | -16
| 111-13 | A8 | D1 | 1 | NO | 0 | 0 | 7107066 | 0 | 0 | -14
| 111-13 | C3 | D1 | 1 | YES | 8 | 3 | 7107072 | 0 | 0 | -14
| 111-13 | D2 | D1 | 1 | NO | 0 | 0 | 7105869 | 0 | 0 | -14
| 111-13 | B1 | D1 | 1 | NO | 0 | 0 | 7105890 | 0 | 0 | -14
| 111-13 | A20 | D1 | 1 | NO | 0 | 0 | 7107064 | 0 | 0 | -14
| 111-13 | A1/15UOFF | A2 | 1 | NO | 0 | 0 | 7107031 | 0 | 0 | -16
| 111-13 | A1/15UOFF | A2 | 5 | NO | 0 | 0 | 35513264 | 0 | 0 | -16
| 111-13 | A1/19UOFF | A2 | 5 | NO | 0 | 0 | 35513264 | 0 | 0 | -16
| 111-6 | A25 | D1 | 1 | YES | 14 | 7 | 7107026 | 10 | 0 | -14
| 111-6 | A34 | D1 | 1 | YES | 6014 | 4656 | 7106896 | 2398 | 57 | -14
| 111-5 | A34 | D1 | 1 | YES | 3536187 | 3162311 | 6969276 | 1833278 | 72439 | -14
| 111-5 | A20 | D1 | 1 | YES | 18948 | 8269 | 7106695 | 13372 | 594 | -14
| 111-5 | A25 | D1 | 1 | YES | 1478 | 982 | 7107026 | 660 | 28 | -14
| 111-5 | A8 | D1 | 1 | YES | 165130 | 125606 | 7102776 | 63359 | 1650 | -14
| 111-5 | C3 | D1 | 1 | YES | 4884261 | 4013254 | 6989446 | 2704361 | 141518 | -14
| 111-5 | B1 | D1 | 1 | YES | 352 | 270 | 7107060 | 201 | 12 | -14
| 111-5 | D10 | D1 | 1 | YES | 19726 | 9538 | 7106953 | 6016 | 164 | -14
| 111-5 | B2 | D1 | 1 | NO | 0 | 0 | 7107059 | 0 | 0 | -14
Lawrence Livermore Lab 18-December-1997
Node 9 from B415
LIGHTGUIIDE 62.5 UM |  |  | 610 m | inc. jumpers
Cable | Fiber | Transmit | Receive | Test | Err | CRC | Symbol | Packet | Sequence | Length | P[r] | Modal B/W | Modal B/W
name/ | name/ | GBICID/ | GBICID/ | time | ??? | error | error | count | error | error | (dBm) | 850 nm | 1300 nm
ID tag | ID tag | JMPRID | JMPRID | (min) |  | count | count |  | count | count |  | (MHz*km) | (MHz*km)
N9-B415 | Node 9 TAG
| 919-5 | A1 | A2 | 1 | NO | 0 | 0 | 7107031 | 0 | 0 | -16
| 919-6 | A1 | A2 | 1 | NO | 0 | 0 | 7106994 | 0 | 0 | -16
| 919-6 | A1 | A2 | 5 | NO | 0 | 0 | 35511999 | 0 | 0 | -16
| 919-3 | A1 | A2 | 1 | NO | 0 | 0 | 7107001 | 0 | 0 | -16
| 919-4 | A1 | A2 | 1 | NO | 0 | 0 | 7107058 | 0 | 0 | -16
| 919-7 | A1 | A2 | 1 | NO | 0 | 0 | 7107038 | 0 | 0 | -16
| 919-8 | A1 | A2 | 1 | NO | 0 | 0 | 7107013 | 0 | 0 | -16
| 919-10 | A1 | A2 | 1 | NO | 0 | 0 | 7107012 | 0 | 0 | -16
| 919-11 | A1 | A2 | 1 | NO | 0 | 0 | 7106991 | 0 | 0 | -16
| 919-12 | A1 | A2 | 1 | NO | 0 | 0 | 7107040 | 0 | 0 | -16
| 919-12 | B1 | D1 | 1 | NO | 0 | 0 | 7107003 | 0 | 0 | -14
| 919-12 | D2 | D1 | 1 | NO | 0 | 0 | 7107048 | 0 | 0 | -14
| 919-12 | A8 | D1 | 1 | YES | 4137 | 3010 | 7106877 | 1217 | 30 | -14
| 919-12 | A34 | D1 | 1 | NO | 0 | 0 | 7107041 | 0 | 0 | -14
Sandia Lab 18-December-1997
Siecor 50 um
Building 912 from building 904. |  |  | 480 m | inc. jumpers. Networking equipment room to auditorium
912BN04 ->904FA10
Cable | Fiber | Transmit | Receive | Test | Err | CRC | Symbol | Packet | Sequence | Length | P[r] | Modal B/W | Modal B/W
name/ | name/ | GBICID/ | GBICID/ | time | ??? | error | error | count | error | error | (dBm) | 850 nm | 1300 nm
ID tag | ID tag | JMPRID | JMPRID | (min) |  | count | count |  | count | count |  | (MHz*km) | (MHz*km)
B912-904 | B912 TAG
| N5-1 | A8 | D1 | 1 | YES | 4 | 4 | 7113530 | 0 | 0 | -14
| N5-1 | A8 | D1 | 1 | YES | 1 | 2 | 7114690 | 2 | 0 | -14
| N5-1 | A34 | D1 | 1 | NO | 0 | 0 | 7112364 | 0 | 0 | -14
| N5-1 | A20 | D1 | 1 | YES | 2 | 1 | 7114706 | 4 | 0 | -14
| N5-1 | A20 | D1 | 5 | YES | 103 | 78 | 35522025 | 0 | 40 | -14
| N5-1 | D2 | D1 | 1 | NO | 0 | 0 | 7113599 | 0 | 0 | -14
| N5-1 | B1 | D1 | 1 | NO | 0 | 0 | 7113560 | 0 | 0 | -14
| N5-1 | C3 | D1 | 1 | NO | 0 | 0 | 7114726 | 0 | 0 | -14
| N5-2 | C3 | D1 | 1 | YES | 3 | 2 | 7113536 | 0 | 0 | -14
| N5-2 | B1 | D1 | 1 | NO | 0 | 0 | 7114716 | 0 | 0 | -15
| N5-2 | D2 | D1 | 1 | NO | 0 | 0 | 7114764 | 0 | 0 | -14
| N5-2 | C3 | D1 | 1 | NO | 0 | 0 | 7113582 | 0 | 0 | -14
| N5-2 | A34 | D1 | 1 | NO | 0 | 0 | 7113549 | 0 | 0 | -14
| N5-2 | A20 | D1 | 1 | NO | 0 | 0 | 7114714 | 0 | 0 | -14
| N5-2 | A8 | D1 | 1 | NO | 0 | 0 | 7114714 | 0 | 0 | -14
| N5-3 | A8 | D1 | 1 | NO | 0 | 0 | 7113544 | 0 | 0 | -14
| N5-3 | A20 | D1 | 1 | NO | 0 | 0 | 7113569 | 0 | 0 | -14
| N5-3 | A34 | D1 | 1 | NO | 0 | 0 | 7113590 | 0 | 0 | -14
| N5-3 | C3 | D1 | 1 | NO | 0 | 0 | 7114746 | 0 | 0 | -14
| N5-3 | D2 | D1 | 1 | NO | 0 | 0 | 7114742 | 0 | 0 | -14
| N5-3 | B1 | D1 | 1 | NO | 0 | 0 | 7114671 | 0 | 0 | -14
| N5-4 | B1 | D1 | 1 | NO | 0 | 0 | 7114784 | 0 | 0 | -14.5
| N5-4 | D2 | D1 | 1 | NO | 0 | 0 | 7112390 | 0 | 0 | -14
| N5-4 | C3 | D1 | 1 | NO | 0 | 0 | 7113545 | 0 | 0 | -14
| N5-4 | A34 | D1 | 1 | NO | 0 | 0 | 7113015 | 0 | 0 | -14
| N5-4 | A20 | D1 | 1 | NO | 0 | 0 | 7113555 | 0 | 0 | -14
| N5-4 | A8 | D1 | 1 | NO | 0 | 0 | 7113544 | 0 | 0 | -14
| N5-5 | A8 | D1 | 1 | NO | 0 | 0 | 7115923 | 0 | 0 | -14
| N5-5 | A20 | D1 | 1 | NO | 0 | 0 | 7113501 | 0 | 0 | -14
| N5-5 | A34 | D1 | 1 | NO | 0 | 0 | 7114759 | 0 | 0 | -14
| N5-5 | C3 | D1 | 1 | NO | 0 | 0 | 7113507 | 0 | 0 | -14
| N5-5 | D2 | D1 | 1 | NO | 0 | 0 | 7114699 | 0 | 0 | -14
| N5-5 | B1 | D1 | 1 | NO | 0 | 0 | 7113557 | 0 | 0 | -15.5
| N5-5 | C1 | D1 | 1 | YES | 83561 | 52133 | 7114362 | 10533 | 412 | -18.7
| N5-6 | A8 | D1 | 1 | NO | 0 | 0 | 7114703 | 0 | 0 | -14
| N5-6 | A20 | D1 | 1 | NO | 0 | 0 | 7113572 | 0 | 0 | -14
| N5-6 | A34 | D1 | 1 | NO | 0 | 0 | 7114712 | 0 | 0 | -14
| N5-6 | B1 | D1 | 1 | NO | 0 | 0 | 7114702 | 0 | 0 | -14
| N5-6 | D2 | D1 | 1 | NO | 0 | 0 | 7114695 | 0 | 0 | -14
| N5-6 | C3 | D1 | 1 | NO | 0 | 0 | 7114737 | 0 | 0 | -14
| N5-7 | A8 | D1 | 1 | NO | 0 | 0 | 7114726 | 0 | 0 | -14
| N5-7 | A20 | D1 | 1 | NO | 0 | 0 | 7113557 | 0 | 0 | -14
| N5-7 | A34 | D1 | 1 | NO | 0 | 0 | 7114711 | 0 | 0 | -14
| N5-7 | B1 | D1 | 1 | NO | 0 | 0 | 7114714 | 0 | 0 | -14
| N5-7 | D2 | D1 | 1 | NO | 0 | 0 | 7111178 | 0 | 0 | -14
| N5-7 | C3 | D1 | 1 | NO | 0 | 0 | 7111167 | 0 | 0 | -14
| N5-9 | A8 | D1 | 1 | YES | 107 | 77 | 7113512 | 55 | 2 | -14
| N5-9 | A20 | D1 | 1 | YES | 2 | 1 | 7114713 | 0 | 0 | -14
| N5-9 | A20 | D1 | 5 | YES | 12614 | 9637 | 35520421 | 4711 | 86 | -14
| N5-9 | A34 | D1 | 1 | YES | 30 | 23 | 7114738 | 6 | 0 | -14
| N5-9 | B1 | D1 | 1 | NO | 0 | 0 | 7113527 | 0 | 0 | -14
| N5-9 | B1 | D1 | 5 | NO |  |  | 35520820 |  |  | -14
| N5-9 | D2 | D1 | 1 | YES | 33 | 27 | 7114720 | 0 | 0 | -14
| N5-9 | C3 | D1 | 1 | YES | 157 | 80 | 7115890 | 9 | 0 | -14
| N5-9 | B4 | D1 | 1 | NO |  |  | 7112341 |  |  | -14
| N5-9 | B2 | D1 | 1 | YES | 31566 | 24034 | 7111984 | 7895 | 292 | -14
| N5-8 | A8 | D1 | 1 | NO | 0 | 0 | 7113530 | 0 | 0 | -14
| N5-8 | A8 | D1 | 1 | YES | 40 | 17 | 7113543 | 14 | 0 | -14
| N5-8 | A20 | D1 | 1 | YES | 1 | 0 | 7114718 | 0 | 0 | -14
| N5-8 | A34 | D1 | 1 | NO | 0 | 0 | 7113560 | 0 | 0 | -14
| N5-8 | B1 | D1 | 1 | NO | 0 | 0 | 7113510 | 0 | 0 | -14.3
| N5-8 | B1 | D1 | 5 | YES | 1 | 1 | 35520747 | 0 | 0 | -14.3
| N5-8 | D2 | D1 | 1 | YES | 143 | 111 | 7114764 | 31 | 1 | -14
| N5-8 | C3 | D1 | 1 | YES | 1031 | 661 | 7114704 | 67 | 0 | -14
| N5-4 | A20 | D1 | 30 | NO | 0 | 0 | 213067240 | 0 | 0 | -14
| N5-4 | A8 | D1 | 1 | NO | 0 | 0 | 7111180 | 0 | 0 | -14
| N5-4 | A8 | D1 | 5 | YES | 351255 | 290924 | 35511513 | 131446 | 4676 | -14 |  |  | TRAY WAS MOVED DURING TEST
| N5-4 | A8 | D1 | 5 | NO | 0 | 0 | 35521970 | 0 | 0 | -14
| N5-12 | A8 | D1 | 1 | NO | 0 | 0 | 7114739 | 0 | 0 | -14
| N5-12 | A20 | D1 | 1 | YES | 5 | 4 | 7114710 | 2 | 0 | -14
| N5-12 | A25 | D1 | 1 | YES | 18468 | 15977 | 7114158 | 6930 | 163 | -14
| N5-12 | A34 | D1 | 1 | YES | 87 | 61 | 7114684 | 62 | 1 | -14
| N5-12 | A8 | D1 | 5 | YES | 86293 | 54824 | 35520622 | 25321 | 498 | -14
| N5-12 | A20 | D1 | 5 | YES | 110895 | 69035 | 35518307 | 24641 | 753 | -14
| N5-12 | A25 | D1 | 5 | YES | 324140 | 242701 | 35513148 | 109929 | 2282 | -14
| N5-12 | A34 | D1 | 5 | YES | 3383 | 3057 | 35521912 | 1902 | 35 | -14
| N5-12 | B1 | D1 | 5 | YES | 18 | 7 | 35521973 | 5 | 0 | -14
| N5-12 | D2 | D1 | 5 | YES | 1353 | 1122 | 35519610 | 604 | 15 | -14
| N5-12 | C3 | D1 | 5 | YES | 907531 | 659951 | 35511581 | 206445 | 10062 | -14
| N5-1 | A8 | D1 | 5 | YES | 13 | 8 | 35520812 | 3 | 0 | -14
| N5-1 | A20 | D1 | 5 | NO | 0 | 0 | 35520817 | 0 | 0 | -14
| N5-1 | A25 | D1 | 5 | YES | 165 | 141 | 35521993 | 57 | 0 | -14
| N5-1 | A34 | D1 | 5 | YES | 1 | 1 | 35521961 | 0 | 0 | -14
| N5-1 | B1 | D1 | 5 | YES | 1 | 0 | 35522002 | 1 | 0 | -14
| N5-1 | D2 | D1 | 5 | YES | 3 | 57 | 35522013 | 45 | 35 | -14
| N5-1 | C3 | D1 | 5 | YES | 485 | 281 | 35521996 | 30 | 1 | -14
LOSS TESTING W/ POWER METER AND SOURCE
|  | 850 | 1300M | 1300S
| N5-1 | -31.6 | -26.4 | -10.9
| N5-2 | -29.7 | -26.1 | -12.8
N5-3
| N5-4 | -29.6 | -29.6 | -11.3
| N5-5 | -30.1 | -26.1 | -11.8
N5-6
N5-7
| N5-8 | -30 | -26.1 | -11.8
| N5-9 | -31.5 | -26.5 | -13
N5-10
| N5-11 | -28.9 | -26.1 | -10.9
| N5-12 | -30 | -26.9 | -10.9
Sandia Lab 14-January-1998
Siecor 50 um |  |  |  |  | Tests marked "Other" were performed with another vendor's 1000BASE-X implementation
Building 912 from building 904. |  |  | 465 m | inc. jumpers. Networking equipment room to auditorium
912BN05->904FA11
Cable | Fiber | Transmit | Receive | Test | Err | CRC | Symbol | Packet | Sequence | Length | P[r] | Modal B/W | Modal B/W
name/ | name/ | GBICID/ | GBICID/ | time | ??? | error | error | count | error | error | (dBm) | 850 nm | 1300 nm
ID tag | ID tag | JMPRID | JMPRID | (min) |  | count | count |  | count | count |  | (MHz*km) | (MHz*km)
B912-904 | B912 TAG
Other | N5-9 | A8 | D2 | 5 | YES | 0 | 7 | 1433824 |  |  | -14
Other | N5-9 | A25 | D2 | 5 | YES | 0 | 2 | 1097105 |  |  | -14
Other | N5-9 | A34 | D2 | 5 | YES | 4 | 880 | 1107658 |  |  | -14
Other | N5-9 | D1 | D2 | 5 | YES | 1 | 2553 | 1125839 |  |  | -14
Other | N5-9 | B1 | D2 | 5 | YES | 2 | 91 | 1032576 |  |  | -14
Other | N5-9 | C3 | D2 | 5 | YES | 345 | 350000 | 1062524 |  |  | -14
Other | N5-9 | A8 | D2 | 5 | NO | 0 | 0 | 1116675 |  |  | -13
Other | N5-9 | A25 | D2 | 5 | YES | 0 | 5 | 1075500 |  |  | -13
Other | N5-9 | A34 | D2 | 5 | YES | 0 | 1 | 1040682 |  |  | -13
Other | N5-9 | D1 | D2 | 5 | YES | 0 | 712 | 1055329 |  |  | -13
Other | N5-9 | B1 | D2 | 5 | NO | 0 | 0 | 1042968 |  |  | -13
Other | N5-9 | C3 | D2 | 5 | YES | 19 | 18856 | 1038642 |  |  | -13
Other | N5-9 | A8 | B6 | 5 | NO | 0 | 0 | 1043674 |  |  | -14
Other | N5-9 | A25 | B6 | 5 | NO | 0 | 0 | 1022841 |  |  | -14
Other | N5-9 | A34 | B6 | 5 | NO | 0 | 0 | 1049061 |  |  | -14
Other | N5-9 | D1 | B6 | 5 | NO | 0 | 0 | 1022916 |  |  | -14
Other | N5-9 | B1 | B6 | 5 | NO | 0 | 0 | 1025806 |  |  | -14
Other | N5-9 | C3 | B6 | 5 | YES | 0 | 100 | 1032005 |  |  | -14
Other | N5-1 | A8 | D2 | 5 | YES | 0 | 3 | 1083428 |  |  | -14
Other | N5-1 | A25 | D2 | 5 | NO | 0 | 0 | 1169393 |  |  | -14
Other | N5-1 | A34 | D2 | 5 | YES | 0 | 1 | 1095237 |  |  | -14
Other | N5-1 | D1 | D2 | 5 | YES | 1 | 1312 | 1052561 |  |  | -14
Other | N5-1 | B1 | D2 | 5 | NO | 0 | 0 | 1136341 |  |  | -14
Other | N5-1 | C3 | D2 | 5 | YES | 19 | 18164 | 1074396 |  |  | -14
Other | N5-1 | A25 | D2 | 45 | YES | 0 | 2 | 15.8M |  |  | -14
CISCO | N5-9 | B1 | B6 | 5 | NO | 0 | 0 | 35521970 | 0 | 0 | -14
CISCO | N5-9 | A8 | B6 | 5 | YES | 0 | 0 | 35.5M | 1686 | 83 | -14
CISCO | N5-9 | A25 | B6 | 5 | NO | 0 | 0 | 35.5M | 0 | 0 | -14
CISCO | N5-9 | A34 | B6 | 5 | NO | 0 | 0 | 35.5M | 0 | 0 | -14
CISCO | N5-9 | D1 | B6 | 5 | YES | 5 | 6 | 35.5M | 0 | 0 | -14
CISCO | N5-9 | C3 | B6 | 5 | YES | 121 | 39 | 35.5M | 51 | 5 | -14
CISCO | N5-9 | B1 | B6 | 30 | NO | 0 | 0 | 213M | 0 | 0 | -14
Other | N5-12 | A8 | D2 | 5 | YES | 28 | 11532 | 1142201 |  |  | -14
Other | N5-12 | A25 | D2 | 5 | YES | 6 | 5666 | 1038877 |  |  | -14
Other | N5-12 | A34 | D2 | 5 | YES | 63 | 24312 | 1247514 |  |  | -14
Other | N5-12 | D1 | D2 | 5 | YES | 388 | 36534 | 1373129 |  |  | -14
Other | N5-12 | B1 | D2 | 5 | YES | 302 | 78817 | 2774349 |  |  | -14
Other | N5-12 | C3 | D2 | 5 | YES |  | LOTS |  |  |  | -14
CISCO | N5-9 | A1 | A2 | 5 | YES | 748 | 292 | 35.5M | 86 | 0 | -16
CISCO | N5-9 | D3 | A2 | 5 | NO | 0 | 0 | 35.5M | 0 | 0 | -16
CISCO | N5-9 | A1/15UOF | A2 | 5 | YES | 20 | 2 | 35.5M | 0 | 0 | -16
CISCO | N5-9 | D3/15UOF | A2 | 5 | YES | 708 | 450 | 35.5M | 28 | 2 | -16
CISCO | N5-9 | A1/19UOF | A2 | 5 | NO | 0 | 0 | 35.5M | 0 | 0 | -16
CISCO | N5-9 | D3/19UOF | A2 | 5 | YES | 1056 | 735 | 35.5M | 49 | 2 | -16
CISCO | N5-1 | A1 | A2 | 5 | YES | 52536 | 42.5M | 30.4M | 302504 | 50502 | -16
CISCO | N5-1 | D3 | A2 | 5 | YES | 185221 | 1083844 | 35.5M | 194772 | 5805 | -16
CISCO | N5-1 | A1/15UOF | A2 | 5 | YES | 1 | 0 | 35.5M | 0 | 0 | -16
CISCO | N5-1 | D3/15UOF | A2 | 5 | YES | 207283 | 131767 | 35.5M | 43769 | 1057 | -16
CISCO | N5-1 | A1/19UOF | A2 | 5 | NO | 0 | 0 | 35.5M | 0 | 0 | -16
CISCO | N5-1 | D3/19UOF | A2 | 5 | YES | 84834 | 43000 | 35.5M | 3736 | 68 | -16
CISCO | N5-1 | A1/SM | A2 | 1 | YES | 191 | 51 | 7.1M | 44 | 1 | -16
CISCO | N5-1 | D3/SM | A2 | 1 | YES | 673 | 243 | 7.1M | 49 | 2 | -16
Other | N5-5 | A8 | D2 | 5 | NO | 0 | 0 | 1048225 |  |  | -14
Other | N5-5 | A25 | D2 | 5 | NO | 0 | 0 | 1347819 |  |  | -14
Other | N5-5 | A34 | D2 | 5 | NO | 0 | 0 | 1038143 |  |  | -14
Other | N5-5 | D1 | D2 | 5 | YES | 0 | 1 | 1082628 |  |  | -14
Other | N5-5 | B1 | D2 | 5 | NO | 0 | 0 | 1079146 |  |  | -14
Other | N5-5 | C3 | D2 | 5 | NO | 0 | 0 | 1020602 |  |  | -14
Sandia Lab 14-January-1998
Siecor 50 um |  |  |  |  | Tests marked "Other" were performed with another vendor's 1000BASE-X implementation
Building 912 from building 904. |  |  | 465 m | inc. jumpers. Networking equipment room to auditorium
912BN03->904FA12
Cable | Fiber | Transmit | Receive | Test | Err | CRC | Symbol | Packet | Sequence | Length | P[r] | Modal B/W | Modal B/W
name/ | name/ | GBICID/ | GBICID/ | time | ??? | error | error | count | error | error | (dBm) | 850 nm | 1300 nm
ID tag | ID tag | JMPRID | JMPRID | (min) |  | count | count |  | count | count |  | (MHz*km) | (MHz*km)
B912-904 | B912 TAG
Other | N3-12 | A8 | D2 | 5 | NO | 0 | 0 | 1052310 |  |  | -14
Other | N3-12 | A25 | D2 | 5 | NO | 0 | 0 | 1106198 |  |  | -14
Other | N3-12 | A34 | D2 | 5 | NO | 0 | 0 | 1108992 |  |  | -14
Other | N3-12 | D1 | D2 | 5 | NO | 0 | 0 | 1025663 |  |  | -14
Other | N3-12 | B1 | D2 | 5 | [6 empty] | -14
Other | N3-12 | C3 | D2 | 5 | NO | 0 | 0 | 1101951 |  |  | -14